{"text_format":"1","workbook":"xlsx","n_sheets":8,"sheets":["tank level","tank level pred","predict","dataregression1","dataregression2","dataregression3","dataregression4","dataregression6"],"not_rendered":{"charts":10,"images":0,"macros":1,"external_links":0,"defined_names":3,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"tank level","index":0,"n_rows":3593,"n_cols":63,"rows_kept":1125,"cut":true,"hidden":false,"merged":[[1,2,1,27],[1,31,1,32]],"bounds":{"rows_first":500,"rows_last":125,"rows_between":500,"halvings":2}}
[1,2,3,4,5,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,32,33,34,35,36,37,38,39,40,41,42,43,44,45,46,47,48,49,50,51,52,53,54,55,56,57,58,59,60,61,62,63]
[null,null,"Temperature at Indicated level",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Tunnel",null,null,null,null,null,null,null,null,null,null,{"$f":"62.4*60/7.48","v":500.53475935828874},null,19.528595278139452,-0.30357220165589999,3.4086741154860478E-5,6.0846877279660351E-2]
[null,null,51,49,47,45,43,41,39,37,35,33,31,29,27,25,23,21,19,17,15,13,11,9,7,5,3,1,null,null,null,null,null,null,null,null,null,{"$f":"MAX(AL6:AL3593)","v":168025.22738}]
[null,null,"51 feet ","49 feet","47 feet ","45 feet ","43 feet ","41 feet ","39 feet ","37 feet ","35 feet ","33 feet ","31 feet ","29 feet ","27 feet ","25 feet ","23 feet ","21 feet ","19 feet ","17 feet ","15 feet ","13 feet ","11 feet ","9 feet ","7 feet ","5 feet ","3 feet ","1 feet ","TES Flow Rate","Plant Flow (gpm)","Primary Loop Flow Rate","Return Temp","Supply Temp","Height of chilled water","Height of chilled water","ft^3 of chilled water"," cooling capacity (kBtu)","load","OAT","Twb","Secondary loop load","ChWST(opt)","dT (regressed) 44","dT (regressed) 42","Tank cooling capacity (kBtu/h)","Plant flow predicted (gpm) 44","TES tank Flow predicted","TES tank flow pred- current","x ( tank chilled water ratio)","V tank flow meas","V tank flow (44)","x (predicted) 44","x (predicted) 44","x (meas)","x (meas)","Plant flow predicted (gpm) 42","v tank flow (42)","x (predicted) 42","x (meas) 42","Temperature to keep the tank full","tank ratio (actual)"]
[null,"Date","TT-246","TT-247","TT-248","TT-249","TT-250","TT-251","TT-252","TT-253","TT-254","TT-255","TT-256","TT-257","TT-258","TT-259","TT-260","TT-261","TT-262","TT-263","TT-264","TT-265","TT-266","TT-267","TT-268","TT-269","TT-270","TT-271"]
["2013-01-01","2013-01-01",37.719389999999997,37.741610000000001,37.37471,37.691330000000001,37.872,37.333069999999999,37.4236,37.683660000000003,37.465949999999999,37.268749999999997,37.688479999999998,37.526670000000003,37.55151,37.841000000000001,38.171370000000003,37.660809999999998,37.520130000000002,38.03698,37.762779999999999,37.588169999999998,37.970469999999999,37.349550000000001,37.698050000000002,37.27787,37.658740000000002,37.327979999999997,1490.9970000000001,5411.74,6902.7370000000001,49.00994,37.938380000000002,51,51,{"$f":"3.1416*(138/2)^2*AI6","v":762815.03760000004},{"$f":"62.4*AJ6*(AF6-AB6)/1000","v":556057.30481444206},{"$f":"500*AC6*(C6-AB6)/1000","v":291.79556788500037},45,44,29958.2020572,44,{"$f":"19.5286-0.30357*AP6+0.0000341*AO6+0.060847*AN6","v":9.8703626901505217},{"$f":"19.5286-0.30357*42+0.0000341*AO6+0.060847*AN6","v":10.477502690150519},{"$f":"62.4*AJ6*AQ6/1000","v":469825.89180463913},{"$f":"AO6*1000/(500*AQ6)","v":6070.3345961328887},{"$f":"AL6*1000/(500*AQ6)","v":59.125601975331371},{"$f":"AU6-AC6","v":-1431.8713980246687},0,{"$f":"AE6-AD6","v":1490.9970000000003},{"$f":"AE6-AT6","v":832.40240386711139},{"$f":"1+AY6*60/$BK$7","v":1.0087525520676848},{"$f":"IF(AZ6>1,1,IF(AZ6<0,0,AZ6))","v":1},{"$f":"1+AX6*60/$BK$7","v":1.0156775482802967},{"$f":"IF(BB6>1,1,BB6)","v":1},{"$f":"AO6*1000/(500*AR6)","v":5718.576829450496},{"$f":"AE6-BD6","v":1184.1601705495041},{"$f":"1+BE6*60/$BK$7","v":1.0124512177055984},{"$f":"IF(BF6>1,1,IF(BF6<0,0,BF6))","v":1},44,1]
["2013-01-01T01:00:00","2013-01-01T01:00:00",37.734250000000003,37.73518,37.37171,37.697049999999997,37.879060000000003,37.341270000000002,37.439360000000001,37.66469,37.453499999999998,37.262279999999997,37.68524,37.524639999999998,37.549750000000003,37.83596,38.173839999999998,37.660899999999998,37.524929999999998,38.059980000000003,37.76202,37.575360000000003,37.96481,37.352519999999998,37.68186,37.297780000000003,37.666679999999999,37.308329999999998,1469.077,5431.933,6901.01,48.68618,37.825029999999998,51,51,{"$f":"3.1416*(138/2)^2*AI7","v":762815.03760000004},{"$f":"62.4*AJ7*(AF7-AB7)/1000","v":541581.77271476691},{"$f":"500*AC7*(C7-AB7)/1000","v":312.8546379200036},46,44,29498.519551475008,44,{"$f":"19.5286-0.30357*AP7+0.0000341*AO7+0.060847*AN7","v":9.8546875167052974},{"$f":"19.5286-0.30357*42+0.0000341*AO7+0.060847*AN7","v":10.461827516705299},{"$f":"62.4*AJ7*AQ7/1000","v":469079.75890412845},{"$f":"AO7*1000/(500*AQ7)","v":5986.6981071637683},{"$f":"AL7*1000/(500*AQ7)","v":63.493568393653106},-1405.5834316063469,0,{"$f":"AE7-AD7","v":1469.0770000000002},914.31189283623189,{"$f":"IF(AZ6>1,1+AY7*60/$BK$7,IF(AZ6<0,AY7*60/$BK$7,AZ6+AY7*60/$BK$7))","v":1.0096138146778226},{"$f":"IF(AZ7>1,1,IF(AZ7<0,0,AZ7))","v":1},{"$f":"IF(BB6>1,1+AX7*60/$BK$7,BB6+AX7*60/$BK$7)","v":1.0154470636728132},{"$f":"IF(BB7>1,1,BB7)","v":1},5639.2670409394896,1261.7429590605107,{"$f":"IF(BF6>1,1+BE7*60/$BK$7,IF(BF6<0,BE7*60/$BK$7,BF6+BE7*60/$BK$7))","v":1.0132669858879633},{"$f":"IF(BF7>1,1,IF(BF7<0,0,BF7))","v":1},44,1,"tank capacity",{"$f":"3.1416*(138/2)^2*51*7.4805","v":5706237.8887668001}]
["2013-01-01T02:00:00","2013-01-01T02:00:00",37.761510000000001,37.695480000000003,37.369320000000002,37.740090000000002,37.911580000000001,37.370240000000003,37.42315,37.668700000000001,37.465859999999999,37.259810000000002,37.689,37.52787,37.544260000000001,37.834209999999999,38.174379999999999,37.668239999999997,37.532829999999997,38.091769999999997,37.798360000000002,37.567740000000001,37.962249999999997,37.413159999999998,37.660139999999998,37.282290000000003,37.672229999999999,37.289400000000001,1538.498,5365.665,6904.1629999999996,48.814100000000003,37.786009999999997,51,51,762815.03760000004,{"$f":"62.4*AJ8*(AF8-AB8)/1000","v":548571.78254291229},363.17014539000053,45,43,29586.518264925013,44,9.7968412728339445,10.403981272833942,466326.29745923879,6040.0117631724142,74.140253021563112,-1464.357746978437,0,1538.4979999999996,864.15123682758531,{"$f":"IF(AZ7>1,1+AY8*60/$BK$7,IF(AZ7<0,AY8*60/$BK$7,AZ7+AY8*60/$BK$7))","v":1.0090863849738414},1,{"$f":"IF(BB7>1,1+AX8*60/$BK$7,BB7+AX8*60/$BK$7)","v":1.0161770122100446},1,5687.5377779041191,1216.6252220958804,{"$f":"IF(BF7>1,1+BE8*60/$BK$7,IF(BF7<0,BE8*60/$BK$7,BF7+BE8*60/$BK$7))","v":1.0127925815131988},1,44,1,"minimum height",{"$f":"3.1416*(138/2)^2*5*7.4805","v":559435.08713400003}]
["2013-01-01T03:00:00","2013-01-01T03:00:00",37.763280000000002,37.686439999999997,37.375889999999998,37.753619999999998,37.90531,37.359209999999997,37.426430000000003,37.705109999999998,37.457610000000003,37.24973,37.684399999999997,37.522649999999999,37.54269,37.833599999999997,38.174520000000001,37.667630000000003,37.549320000000002,38.114460000000001,37.761620000000001,37.548679999999997,37.968260000000001,37.34657,37.62641,37.240070000000003,37.627850000000002,37.293469999999999,1560.816,5334.89,6895.7060000000001,48.472110000000001,37.776150000000001,51,51,762815.03760000004,532099.44477561233,366.64348248000192,44,43,28530.8850222,44,{"$f":"19.5286-0.30357*AP9+0.0000341*AO9+0.060847*AN9","v":9.7608441792570204},10.367984179257022,464612.84810351959,5845.98719090949,75.125363287565605,-1485.6906367124345,0,1560.8159999999998,1049.7188090905101,1.0110375925037087,1,1.0164116817114048,1,5503.6513422312237,1392.0546577687765,1.0146371884758869,1,44,1,"Xmin=",{"$f":"BK8/BK7","v":9.8039215686274508E-2}]
["2013-01-01T04:00:00","2013-01-01T04:00:00",37.723869999999998,37.685690000000001,37.378270000000001,37.736440000000002,37.911059999999999,37.352919999999997,37.433639999999997,37.698920000000001,37.456209999999999,37.249049999999997,37.699739999999998,37.517060000000001,37.546819999999997,37.840060000000001,38.174410000000002,37.666040000000002,37.60275,38.121540000000003,37.815240000000003,37.521360000000001,37.976170000000003,37.31559,37.642099999999999,37.253630000000001,37.629089999999998,37.313890000000001,1653.3810000000001,5246.31,6899.6909999999998,48.77646,37.80518,51,51,762815.03760000004,545614.41576986015,338.92657118999784,44,43,28779.367988400001,44,9.7693174484044398,10.376457448404441,465016.17282001243,5891.7868398473129,69.385926494865316,-1583.9950735051348,0,1653.3809999999994,1007.9041601526869,1.0105979194677828,1,1.0173849849820122,1,5547.0507408721314,1352.6402591278684,1.0142227536127506,1,44,1]
["2013-01-01T05:00:00","2013-01-01T05:00:00",37.689830000000001,37.69059,37.403840000000002,37.701329999999999,37.905079999999998,37.34055,37.433280000000003,37.702269999999999,37.449800000000003,37.262450000000001,37.712989999999998,37.507010000000001,37.555819999999997,37.838230000000003,38.176340000000003,37.678379999999997,37.614910000000002,38.069249999999997,37.76437,37.545990000000003,37.928550000000001,37.311929999999997,37.639429999999997,37.246549999999999,37.640340000000002,37.335659999999997,1563.5509999999999,5331.3559999999998,6894.9070000000002,48.580100000000002,37.683190000000003,51,51,762815.03760000004,535231.50229479512,276.88142883500268,43,42,29047.653254979996,44,9.7176189759948191,10.324758975994818,462555.343196292,5978.3478497635388,56.98544664469263,-1506.5655533553072,0,1563.5510000000004,916.55915023646139,1.0096374441595657,1,1.0164404397132967,1,5626.7954191504359,1268.1115808495642,1.0133339507279844,1,44,1,"Tavrg (winter)",{"$f":"AVERAGE(BH6:BH1413)","v":43.68181818181818}]
["2013-01-01T06:00:00","2013-01-01T06:00:00",37.661990000000003,37.685200000000002,37.385829999999999,37.699260000000002,37.901159999999997,37.330100000000002,37.429749999999999,37.681319999999999,37.45731,37.256019999999999,37.722070000000002,37.505519999999997,37.553330000000003,37.834440000000001,38.181240000000003,37.724240000000002,37.633519999999997,38.10407,37.759540000000001,37.524279999999997,37.899329999999999,37.296559999999999,37.633769999999998,37.251869999999997,37.634369999999997,37.337679999999999,1645.5840000000001,5256.4430000000002,6902.027,49.20693,37.804029999999997,51,51,762815.03760000004,564972.24482610915,266.83967352000337,42,40,29969.346942350006,44,9.6273547307341367,10.234494730734136,458258.7959610023,6225.8736237642897,55.433643193420686,-1590.1503568065793,0,1645.5839999999998,676.15337623571031,1.0071096234270229,1,1.0173030010183011,1,5856.5366890760542,1045.4903109239458,1.0109931306542486,1,44,1,"Tavrg (summer)",{"$f":"AVERAGE(BH1424:BH3593)","v":42.133271633503007}]
["2013-01-01T07:00:00","2013-01-01T07:00:00",37.644590000000001,37.679639999999999,37.368490000000001,37.700699999999998,37.90034,37.32029,37.430869999999999,37.678150000000002,37.44943,37.24973,37.731450000000002,37.504300000000001,37.547060000000002,37.837730000000001,38.203189999999999,37.7498,37.582689999999999,38.076599999999999,37.783149999999999,37.446869999999997,37.88026,37.28105,37.62274,37.24944,37.630400000000002,37.32855,1656.4010000000001,5249.9480000000003,6906.3490000000002,48.90063,37.906460000000003,51,51,762815.03760000004,550827.05435535696,261.74448602000081,41,39,28859.410401579989,44,9.5286588946938782,10.135798894693878,453560.90788528952,6057.3918576622827,54.938368329200166,-1601.4626316708,0,1656.4009999999998,848.95714233771741,1.0089266219763704,1,1.0174167397043936,1,5694.5507110816861,1211.798288918314,1.0127418272340574,1,44,1]
["2013-01-01T08:00:00","2013-01-01T08:00:00",37.64349,37.698830000000001,37.352040000000002,37.705719999999999,37.897350000000003,37.318109999999997,37.444119999999998,37.657739999999997,37.447800000000001,37.252569999999999,37.740639999999999,37.499920000000003,37.549010000000003,37.843510000000002,38.254089999999998,37.725670000000001,37.609830000000002,38.078870000000002,37.758879999999998,37.439500000000002,37.881720000000001,37.275100000000002,37.619900000000001,37.2468,37.634860000000003,37.304000000000002,1639.835,5260.098,6899.9340000000002,49.279730000000001,37.979610000000001,51,51,762815.03760000004,570040.65644681663,278.35379207499824,39,38,29719.869305879998,44,9.4971535433305085,10.104293543330508,452061.26392431482,6258.6898632909097,58.618361976568352,-1581.2166380234316,0,1639.8360000000002,641.24413670909053,1.0067425594502966,1,1.017242561897689,1,5882.621912839626,1017.3120871603742,1.0106968420208666,1,44,1]
["2013-01-01T09:00:00","2013-01-01T09:00:00",37.643050000000002,37.686779999999999,37.339379999999998,37.70722,37.882910000000003,37.32217,37.44415,37.65842,37.443080000000002,37.265790000000003,37.749090000000002,37.495049999999999,37.54853,37.868290000000002,38.273020000000002,37.715420000000002,37.593029999999999,38.111269999999998,37.724640000000001,37.453870000000002,37.896000000000001,37.292279999999998,37.636499999999998,37.252560000000003,37.630159999999997,37.340989999999998,1577.5139999999999,5324.326,6901.8389999999999,49.214179999999999,37.99192,51,51,762815.03760000004,565159.78747999331,238.25193942000351,40,38,29875.485348379996,44,9.5024600503797583,10.109600050379758,452313.85184687102,6287.9475819918962,50.145317771787312,-1527.3686822282125,0,1577.5129999999999,613.89141800810376,1.0064549508447582,1,1.0165872474728626,1,5910.3199334295632,991.51906657043673,1.0104256333426511,1,44,1]
["2013-01-01T10:00:00","2013-01-01T10:00:00",37.641190000000002,37.674709999999997,37.339599999999997,37.678800000000003,37.885800000000003,37.322519999999997,37.430770000000003,37.660380000000004,37.467770000000002,37.248779999999996,37.723190000000002,37.499940000000002,37.554630000000003,37.942329999999998,38.250160000000001,37.732230000000001,37.585360000000001,38.071260000000002,37.729990000000001,37.464590000000001,37.902360000000002,37.29654,37.647880000000001,37.26435,37.644579999999998,37.282670000000003,1567.49,5334.7240000000002,6902.2150000000001,49.267139999999998,37.936410000000002,51,51,762815.03760000004,570456.67746076267,280.98825739999887,40,38,30223.158634259988,44,9.5143157094282671,10.121455709428266,452878.17716704955,6353.1965003663208,59.066414439359406,-1508.4235855606405,0,1567.491,549.01849963367931,1.0057728245159334,1,1.0164818680597147,1,5972.0971966723573,930.11780332764283,1.0097800108035313,1,44,1]
["2013-01-01T11:00:00","2013-01-01T11:00:00",37.685499999999998,37.69614,37.335799999999999,37.681229999999999,37.917560000000002,37.328220000000002,37.411059999999999,37.676740000000002,37.464779999999998,37.242429999999999,37.71358,37.511249999999997,37.577849999999998,37.97757,38.270020000000002,37.741950000000003,37.591810000000002,38.058019999999999,37.736240000000002,37.482390000000002,37.923220000000001,37.313630000000003,37.652369999999998,37.268560000000001,37.649560000000001,37.285620000000002,1505.5139999999999,5398.5259999999998,6904.04,49.02234,37.989269999999998,51,51,762815.03760000004,558663.86210548191,301.01246915999701,40,38,29781.157627410004,44,9.4992434750946817,10.106383475094681,452160.74396225641,6270.2167189399615,63.376093043450858,-1442.1379069565489,0,1505.5140000000001,633.82328106003843,1.0066645305724926,1,1.0158301917587109,1,5893.5340620708048,1010.5059379291952,1.0106252766634751,1,44,1]
["2013-01-01T12:00:00","2013-01-01T12:00:00",37.710909999999998,37.701749999999997,37.336849999999998,37.678669999999997,37.88796,37.352420000000002,37.417929999999998,37.687519999999999,37.470759999999999,37.251840000000001,37.698970000000003,37.522329999999997,37.625149999999998,37.936439999999997,38.242359999999998,37.71246,37.56176,38.058320000000002,37.744349999999997,37.518819999999998,37.947040000000001,37.325040000000001,37.648580000000003,37.265799999999999,37.648859999999999,37.270699999999998,1468.088,5434.3710000000001,6902.4589999999998,49.394240000000003,37.918779999999998,51,51,762815.03760000004,577076.36194697476,323.13350924000031,42,39,31180.953517830014,44,9.6078235149580049,10.214963514958004,457329.11676297168,6490.742355807376,67.26466378923962,-1400.8233362107603,0,1468.0879999999997,411.71664419262379,1.0043291217669328,1,1.0154366645269737,1,6104.9564146109833,797.50258538901653,1.0083855871514817,1,44,1]
["2013-01-01T13:00:00","2013-01-01T13:00:00",37.659730000000003,37.682130000000001,37.33464,37.683459999999997,37.883029999999998,37.33079,37.438339999999997,37.678469999999997,37.45138,37.252139999999997,37.695169999999997,37.543120000000002,37.684579999999997,37.950740000000003,38.285609999999998,37.719619999999999,37.560169999999999,38.063890000000001,37.745669999999997,37.513480000000001,37.942770000000003,37.331629999999997,37.660600000000002,37.274149999999999,37.648890000000002,37.277470000000001,1559.671,5402.0330000000004,6779.7079999999996,49.233820000000001,37.92024,51,51,762815.03760000004,569118.17506806657,298.09991823000178,43,39,30558.166254070005,44,9.5865864692637874,10.193726469263787,456318.24064364348,6375.1923277476581,62.19104562103734,-1497.4799543789627,0,1377.6749999999993,404.51567225234157,1.0042534049242706,1,1.0144859891247653,1,5995.4848398589575,784.22316014104217,1.0082459565348811,1,44,1]
["2013-01-01T14:00:00","2013-01-01T14:00:00",37.780839999999998,37.775770000000001,37.420650000000002,37.754519999999999,37.907809999999998,37.334429999999998,37.430819999999997,37.667349999999999,37.448630000000001,37.238880000000002,37.708829999999999,37.549770000000002,37.664479999999998,37.908389999999997,38.25638,37.699649999999998,37.564210000000003,38.070160000000001,37.74342,37.504660000000001,37.938290000000002,37.327280000000002,37.663829999999997,37.285550000000001,37.666780000000003,37.27805,1904.3109999999999,5412.5360000000001,6084.99,49.416339999999998,39.129980000000003,51,51,762815.03760000004,577778.45690758142,478.73426384499749,41,38,27837.646904479985,44,9.4329697594427682,10.040109759442768,449006.1377398895,5902.2020878660023,101.50234253974278,-1802.8086574602571,0,672.45399999999972,182.78791213399745,1.0019219799352617,1,1.0070707251934636,1,5545.2873666642045,539.70263333579533,1.0056748699636051,1,44,1]
["2013-01-01T15:00:00","2013-01-01T15:00:00",37.63158,37.654769999999999,37.318019999999997,37.700290000000003,37.890540000000001,37.323889999999999,37.429989999999997,37.658659999999998,37.45073,37.236350000000002,37.717730000000003,37.61842,37.662230000000001,37.881239999999998,38.266629999999999,37.695120000000003,37.577579999999998,38.081539999999997,37.758400000000002,37.51173,37.932670000000002,37.338830000000002,37.670999999999999,37.293660000000003,37.681220000000003,37.55744,1455.74,5445.3379999999997,6901.0789999999997,49.298079999999999,38.541600000000003,51,51,762815.03760000004,558850.45276619913,53.96428179999991,40,37,29286.33464511999,44,9.4215230113985928,10.028663011398592,448461.27644381125,6216.9003057548198,11.455532557679144,-1444.2844674423209,0,1455.741,684.17869424517994,1.0071940081109345,1,1.0153068381835157,1,5840.5262220563409,1060.5527779436588,1.0111515096140464,1,44,1]
["2013-01-01T16:00:00","2013-01-01T16:00:00",37.586820000000003,37.650489999999998,37.308230000000002,37.694110000000002,37.902070000000002,37.322200000000002,37.432000000000002,37.657240000000002,37.449019999999997,37.232640000000004,37.740929999999999,37.651809999999998,37.679340000000003,37.91095,38.238399999999999,37.7438,37.630510000000001,38.117179999999998,37.778419999999997,37.50123,37.932380000000002,37.34299,37.717089999999999,37.314549999999997,37.691839999999999,37.682299999999998,1531.3530000000001,5372.2920000000004,6903.6450000000004,49.450980000000001,38.707790000000003,51,51,762815.03760000004,560185.14718622796,-73.106792219996109,39,36,28857.776845739994,44,9.346062190439735,9.9532021904397343,444869.36714764277,6175.3872931124215,-15.644405254392257,-1546.9974052543923,0,1531.3530000000001,728.25770688757893,1.0076574904981219,1,1.0161018839016291,1,5798.6919774338576,1104.9530225661429,1.0116183696940642,1,44,1]
["2013-01-01T17:00:00","2013-01-01T17:00:00",37.610320000000002,37.65672,37.307400000000001,37.681849999999997,37.896650000000001,37.3172,37.418460000000003,37.653449999999999,37.450609999999998,37.230020000000003,37.77834,37.612749999999998,37.597830000000002,37.901809999999998,38.229329999999997,37.730989999999998,37.634740000000001,38.129899999999999,37.792870000000001,37.487630000000003,37.935949999999998,37.34948,37.693330000000003,37.335169999999998,37.914439999999999,37.823790000000002,2009.8109999999999,5363.0069999999996,6079.0050000000001,49.482840000000003,38.918500000000002,51,51,762815.03760000004,554966.79664172942,-214.51717708500092,38,35,28328.314685189998,44,9.2671605307649791,9.8743005307649803,441113.67510417313,6113.6989245294908,-46.296203971615697,-2056.1072039716155,0,715.9980000000005,-34.693924529490687,0.99963520001928641,0.99963520001928641,1.007528582025045,1,5737.7866101864238,341.21838981357632,1.0035878461059462,1,44,1]
["2013-01-01T18:00:00","2013-01-01T18:00:00",37.730919999999998,37.765610000000002,37.341369999999998,37.696919999999999,37.877800000000001,37.289679999999997,37.413510000000002,37.649880000000003,37.452350000000003,37.233429999999998,37.810130000000001,37.60378,37.599159999999998,37.897959999999998,38.240409999999997,37.752749999999999,37.620869999999996,38.121049999999997,37.779229999999998,37.481319999999997,37.927520000000001,37.339230000000001,37.735819999999997,37.325049999999997,38.005040000000001,37.749920000000003,1593.0609999999999,5305.2439999999997,6898.3040000000001,49.204650000000001,37.853230000000003,51,51,762815.03760000004,545241.2344484257,-15.134079500004347,38,35,30111.026423239993,44,9.3279510010324849,9.9350910010324842,444007.28071961366,6456.0858906542471,-3.2448882929014524,-1596.3058882929013,0,1593.0600000000004,442.21810934575296,1.0042850388584588,1,1.0167507212042743,1,6061.5502002167404,836.75379978325964,1.0087983061634758,1,44,1]
["2013-01-01T19:00:00","2013-01-01T19:00:00",37.5777,37.6509,37.31718,37.686169999999997,37.881360000000001,37.28331,37.412109999999998,37.655909999999999,37.445430000000002,37.240949999999998,37.861879999999999,37.580359999999999,37.636090000000003,37.883940000000003,38.260930000000002,37.749479999999998,37.62097,38.11345,37.803649999999998,37.520350000000001,37.932429999999997,37.343040000000002,37.698329999999999,37.406329999999997,37.84431,37.622669999999999,1655.528,5241.2629999999999,6896.7910000000002,49.248550000000002,37.903010000000002,51,51,762815.03760000004,553387.91597438476,-37.224547079999404,37,34,29732.479508510001,44,9.2541955512401923,9.8613355512401917,440496.5465083273,6425.7296798802636,-8.0449017689086535,-1663.5729017689087,0,1655.5280000000002,471.06132011973659,1.0049531196837804,1,1.0174075602763675,1,6030.1121189960422,866.67888100395794,1.0091129626689075,1,44,1]
["2013-01-01T20:00:00","2013-01-01T20:00:00",37.572569999999999,37.64864,37.300980000000003,37.680199999999999,37.880090000000003,37.28546,37.414099999999998,37.663020000000003,37.458419999999997,37.260640000000002,37.840179999999997,37.553759999999997,37.632559999999998,37.893380000000001,38.253349999999998,37.746169999999999,37.611939999999997,38.113720000000001,37.812440000000002,37.492629999999998,37.927059999999997,37.3782,37.745950000000001,37.41892,37.802370000000003,37.531829999999999,1672.633,5227.607,6900.24,49.008110000000002,37.758949999999999,51,51,762815.03760000004,546267.00708578725,34.071534209999626,37,34,29403.093780060008,44,9.2429634979000461,9.8501034979000472,439961.90460680955,6362.2654761625408,7.3724264339549768,-1665.260573566045,0,1672.6329999999998,537.97452383745895,1.005656699222756,1,1.0175874160797893,1,5970.1085955753624,930.13140442463737,1.0097801538164648,1,44,1]
["2013-01-01T21:00:00","2013-01-01T21:00:00",37.550289999999997,37.638109999999998,37.309330000000003,37.680149999999998,37.885309999999997,37.270809999999997,37.42418,37.684939999999997,37.456409999999998,37.330759999999998,37.839390000000002,37.580590000000001,37.59666,37.914810000000003,38.242429999999999,37.739939999999997,37.614490000000004,38.120010000000001,37.775219999999997,37.472059999999999,37.931530000000002,37.368639999999999,37.753219999999999,37.40672,37.809710000000003,37.489490000000004,1697.193,5204.4260000000004,6901.62,49.152630000000002,37.762860000000003,51,51,762815.03760000004,555161.47924436547,51.594667199994319,36,33,29638.607561009994,44,9.1901475178304413,9.7972875178304406,437447.88200027461,6450.083092465291,11.228256586717881,-1685.9647434132821,0,1697.1939999999995,451.53690753470892,1.0047478242197747,1,1.0178456702971435,1,6050.3700656063456,851.24993439365426,1.008950730246309,1,44,1]
["2013-01-01T22:00:00","2013-01-01T22:00:00",37.535510000000002,37.638849999999998,37.308720000000001,37.676819999999999,37.876869999999997,37.274270000000001,37.423940000000002,37.679290000000002,37.472149999999999,37.305399999999999,37.823560000000001,37.55659,37.594920000000002,37.908540000000002,38.255560000000003,37.746169999999999,37.615830000000003,38.109949999999998,37.774340000000002,37.453479999999999,37.945950000000003,37.381689999999999,37.740099999999998,37.379710000000003,37.768839999999997,37.479819999999997,1802.37,5096.683,6899.0540000000001,48.556519999999999,37.764159999999997,51,51,762815.03760000004,527247.13560379669,50.186992650005024,36,33,27502.618870940008,44,9.117310303499055,9.7244503034990544,433980.85548320872,6033.0553541399186,11.009166295622116,-1791.3608337043777,0,1802.3710000000001,865.99864586008152,1.0091058101264745,1,1.0189515863355236,1,5656.3852994434055,1242.6687005565946,1.013066423708022,1,44,1]
["2013-01-01T23:00:00","2013-01-01T23:00:00",37.542270000000002,37.640929999999997,37.30688,37.670090000000002,37.869320000000002,37.281230000000001,37.442880000000002,37.679259999999999,37.521030000000003,37.321199999999997,37.822670000000002,37.521430000000002,37.624470000000002,37.910879999999999,38.260770000000001,37.735460000000003,37.616660000000003,38.103490000000001,37.759950000000003,37.451140000000002,37.926099999999998,37.354990000000001,37.70205,37.350020000000001,37.741329999999998,37.433059999999998,1957.011,4940.0510000000004,6897.0619999999999,48.367469999999997,37.772500000000001,51,51,762815.03760000004,520474.18021771009,106.86258565500437,36,33,26169.846071734992,44,9.0718627510461634,9.6790027510461627,431817.56751377828,5769.4537031475911,23.559127510539337,-1933.4518724894606,0,1957.0109999999995,1127.6082968524088,1.0118565855700359,1,1.020577596358391,1,5407.55008441472,1489.5119155852799,1.0156619329017198,1,44,1]
["2013-01-02","2013-01-02",37.551450000000003,37.636319999999998,37.303489999999996,37.668410000000002,37.872819999999997,37.293970000000002,37.442230000000002,37.682319999999997,37.510350000000003,37.265050000000002,37.800629999999998,37.546140000000001,37.627459999999999,37.914520000000003,38.245780000000003,37.730809999999998,37.594299999999997,38.094749999999998,37.754919999999998,37.439419999999998,37.907179999999997,37.338920000000002,37.689720000000001,37.339440000000003,37.726559999999999,37.390039999999999,1907.5930000000001,4988.2169999999996,6895.81,47.961950000000002,37.786299999999997,51,51,762815.03760000004,503219.30406719825,153.95229306500343,36,33,25379.175158025013,44,9.044900872888654,9.6520408728886533,430534.19132510788,5611.8194139853977,34.041786688113469,-1873.5512133118866,0,1907.5930000000008,1283.9905860146027,1.0135009154302057,1,1.020057975540297,1,5258.820490350774,1636.9895096492264,1.017212631596083,1,44,1]
["2013-01-02T01:00:00","2013-01-02T01:00:00",37.545020000000001,37.645449999999997,37.299799999999998,37.672910000000002,37.890419999999999,37.297550000000001,37.437399999999997,37.735900000000001,37.538379999999997,37.279760000000003,37.81756,37.565179999999998,37.626429999999999,37.913980000000002,38.245629999999998,37.733460000000001,37.601799999999997,38.11063,37.765509999999999,37.444519999999997,37.909869999999998,37.331899999999997,37.680500000000002,37.322040000000001,37.712380000000003,37.363329999999998,1978.703,4918.5249999999996,6897.2280000000001,48.021680000000003,37.7622,51,51,762815.03760000004,507333.81853464735,179.7552740350032,35,32,25230.754433500006,44,8.9789927261823514,9.5861327261823508,427396.98605965398,5619.952082136836,40.039073316285169,-1938.6639266837149,0,1978.7030000000004,1277.2759178631641,1.0134303119788706,1,1.0208056835894828,1,5264.0110781249487,1633.2169218750514,1.0171729635571995,1,44,1]
["2013-01-02T02:00:00","2013-01-02T02:00:00",37.52787,37.639020000000002,37.287689999999998,37.680819999999997,37.884219999999999,37.283160000000002,37.450470000000003,37.734380000000002,37.502870000000001,37.255009999999999,37.8279,37.557360000000003,37.617939999999997,37.902920000000002,38.246090000000002,37.744529999999997,37.622219999999999,38.123049999999999,37.779139999999998,37.44059,37.919629999999998,37.342680000000001,37.695,37.317140000000002,37.696930000000002,37.344209999999997,1978.172,4920.8230000000003,6898.9949999999999,47.650919999999999,37.827129999999997,51,51,762815.03760000004,490595.8746737754,181.65553476000323,35,32,24170.565889585007,44,8.9428402968348504,9.5499802968348497,425676.14277432638,5405.5680493678774,40.625914973411028,-1937.546085026589,0,1978.1719999999996,1493.4269506321225,1.0157030987464304,1,1.0208001002260441,1,5061.9090591413797,1837.0859408586202,1.0193166072989184,1,44,1]
["2013-01-02T03:00:00","2013-01-02T03:00:00",37.585720000000002,37.628909999999998,37.284860000000002,37.68036,37.888689999999997,37.286119999999997,37.499760000000002,37.74109,37.506770000000003,37.256160000000001,37.812809999999999,37.524209999999997,37.600070000000002,37.880760000000002,38.222020000000001,37.728589999999997,37.616459999999996,38.113860000000003,37.765039999999999,37.420380000000002,37.899920000000002,37.340719999999997,37.700740000000003,37.32931,37.697980000000001,37.413119999999999,2042.2739999999999,4857.0069999999996,6899.2809999999999,47.813940000000002,37.760210000000001,51,51,762815.03760000004,495075.47852074006,176.24824620000282,33,31,24415.518493055006,44,8.8903461806131769,9.4974861806131763,423177.44077698688,5492.5911763249342,39.649355068836428,-2002.6246449311634,0,2042.2740000000003,1406.6898236750658,1.0147910744462048,1,1.021474120495611,1,5141.4696539160832,1757.8113460839168,1.0184830500972732,1,44,1]
["2013-01-02T04:00:00","2013-01-02T04:00:00",37.572960000000002,37.640889999999999,37.291840000000001,37.676749999999998,37.892380000000003,37.309440000000002,37.508580000000002,37.709440000000001,37.488340000000001,37.234920000000002,37.811140000000002,37.513309999999997,37.597659999999998,37.879989999999999,38.217390000000002,37.728369999999998,37.60521,38.110660000000003,37.74933,37.40128,37.893520000000002,37.324779999999997,37.701430000000002,37.332169999999998,37.707630000000002,37.361440000000002,2060.502,4848.0559999999996,6908.558,47.53895,37.703319999999998,51,51,762815.03760000004,484445.99881544098,217.91869152000018,32,30,23841.842517640005,44,8.8099368298515248,9.4170768298515242,419349.9831528893,5412.4888698076657,49.471113295978711,-2011.0308867040212,0,2060.5020000000004,1496.0691301923343,1.015730880759151,1,1.0216657844292429,1,5063.5336099335846,1845.0243900664154,1.0194000785739954,1,44,1]
["2013-01-02T05:00:00","2013-01-02T05:00:00",37.528489999999998,37.681980000000003,37.297370000000001,37.685989999999997,37.890419999999999,37.346359999999997,37.521529999999998,37.69455,37.47831,37.222119999999997,37.805660000000003,37.507899999999999,37.589790000000001,37.877130000000001,38.206499999999998,37.722020000000001,37.599879999999999,38.095680000000002,37.739550000000001,37.378810000000001,37.890140000000002,37.311129999999999,37.692779999999999,37.319270000000003,37.708289999999998,37.322859999999999,1947.8620000000001,4950.53,6898.393,47.925420000000003,37.75412,51,51,762815.03760000004,504678.23359551054,200.26943152999934,32,30,25176.662894500005,44,8.8554542047024505,9.4625942047024498,421516.59464461106,5686.1369981746657,45.23075313825273,-1902.6312468617473,0,1947.8630000000003,1212.2560018253344,1.0127466399977305,1,1.0204814068880781,1,5321.3024567804941,1577.0905432195059,1.0165828054206167,1,44,1]
["2013-01-02T06:00:00","2013-01-02T06:00:00",37.507179999999998,37.660229999999999,37.28754,37.668349999999997,37.915059999999997,37.349080000000001,37.481639999999999,37.671149999999997,37.466059999999999,37.219810000000003,37.802779999999998,37.504869999999997,37.591709999999999,37.869289999999999,38.20111,37.717280000000002,37.597140000000003,38.0961,37.736980000000003,37.372590000000002,37.87894,37.304409999999997,37.679569999999998,37.309950000000001,37.705120000000001,37.33999,1930.903,4963.3549999999996,6894.2579999999998,47.813560000000003,37.687249999999999,51,51,762815.03760000004,498538.35366542899,161.41383628499801,31,29,25130.235685025011,44,8.7930240368593537,9.4001640368593531,418544.93998478126,5715.9483653591597,36.714066880374631,-1894.1889331196253,0,1930.9030000000002,1178.3096346408402,1.0123897004395184,1,1.0203030757319229,1,5346.7653514312851,1547.4926485687147,1.0162715892193883,1,44,1]
["2013-01-02T07:00:00","2013-01-02T07:00:00",37.49577,37.637790000000003,37.272500000000001,37.684719999999999,37.940399999999997,37.343069999999997,37.470039999999997,37.675460000000001,37.463619999999999,37.217190000000002,37.800020000000004,37.492350000000002,37.587719999999997,37.860579999999999,38.198270000000001,37.712380000000003,37.596829999999997,38.095599999999997,37.736020000000003,37.371130000000001,37.874760000000002,37.304180000000002,37.680840000000003,37.307130000000001,37.692369999999997,37.331580000000002,1898.54,4997.24,6895.78,48.247050000000002,37.789059999999999,51,51,762815.03760000004,519572.64268863224,155.86064129999795,32,30,26130.542973800006,44,8.8879815154065813,9.4951215154065807,423064.88352104975,5879.9723938455245,35.072224448222897,-1863.4677755517771,0,1898.54,1015.8076061544753,1.0106810226908434,1,1.0199627849768138,1,5503.99337836828,1391.7866216317198,1.0146343701271716,1,44,1]
["2013-01-02T08:00:00","2013-01-02T08:00:00",37.49635,37.6233,37.279040000000002,37.708590000000001,37.934440000000002,37.306570000000001,37.463799999999999,37.669499999999999,37.460569999999997,37.210700000000003,37.791150000000002,37.492890000000003,37.587829999999997,37.85904,38.193680000000001,37.71161,37.592700000000001,38.0901,37.735889999999998,37.37547,37.864570000000001,37.301679999999998,37.672989999999999,37.301630000000003,37.691450000000003,37.379300000000001,1860.3969999999999,5037.8829999999998,6898.28,48.267400000000002,37.782119999999999,51,51,762815.03760000004,518269.84003969579,108.87973442499906,32,30,26411.806931120009,44,8.8975726163511943,9.5047126163511937,423521.41664917761,5936.856729347207,24.47403109133591,-1835.922968908664,0,1860.3969999999999,961.42327065279278,1.0101091818048327,1,1.0195617186272132,1,5557.6234647396113,1340.6565352603884,1.0140967470483442,1,44,1]
["2013-01-02T09:00:00","2013-01-02T09:00:00",37.499510000000001,37.621639999999999,37.291339999999998,37.723849999999999,37.950040000000001,37.296799999999998,37.458030000000001,37.671039999999998,37.459949999999999,37.213419999999999,37.785049999999998,37.492019999999997,37.5839,37.860889999999998,38.19359,37.711239999999997,37.59357,38.092770000000002,37.73771,37.38205,37.869399999999999,37.302660000000003,37.678820000000002,37.30395,37.711379999999998,37.350020000000001,1792.681,5107.3410000000003,6900.0219999999999,48.284599999999998,37.804169999999999,51,51,762815.03760000004,520482.2721596288,133.99394134500011,33,31,26763.564918314998,44,8.9704145637145434,9.5775545637145427,426988.66845694778,5967.0742591036997,29.874637430249333,-1762.8063625697507,0,1792.6809999999996,932.94774089630027,1.0098097670557993,1,1.0188496978388759,1,5588.8096988162833,1311.2123011837166,1.013787146558663,1,44,1]
["2013-01-02T10:00:00","2013-01-02T10:00:00",37.538760000000003,37.592950000000002,37.336489999999998,37.716540000000002,37.917099999999998,37.317630000000001,37.453270000000003,37.678170000000001,37.472270000000002,37.223750000000003,37.782049999999998,37.501190000000001,37.58475,37.860430000000001,38.196669999999997,37.70834,37.584150000000001,38.084159999999997,37.733220000000003,37.406509999999997,37.877459999999999,37.301859999999998,37.66968,37.294359999999998,37.689190000000004,37.369450000000001,1788.5820000000001,5115.9120000000003,6904.4939999999997,48.52702,37.835149999999999,51,51,762815.03760000004,531096.51997425698,151.41240921000264,34,31,27349.333017720004,44,8.9903892559042529,9.5975292559042522,427939.45698074932,6084.1265576479673,33.683170972951068,-1754.898829027049,0,1788.5819999999994,820.36744235203241,1.0086260067492139,1,1.0188065976378688,1,5699.2445218950734,1205.2494781049263,1.0126729677409092,1,44,1]
["2013-01-02T11:00:00","2013-01-02T11:00:00",37.572650000000003,37.628149999999998,37.370080000000002,37.71555,37.907350000000001,37.321190000000001,37.453949999999999,37.683709999999998,37.478949999999998,37.23742,37.769629999999999,37.516629999999999,37.588079999999998,37.867469999999997,38.203519999999997,37.698729999999998,37.576549999999997,38.077550000000002,37.74118,37.440109999999997,37.892110000000002,37.310470000000002,37.666550000000001,37.281320000000001,37.693660000000001,37.325490000000002,1110.645,5196.424,6307.0680000000002,48.439540000000001,38.351990000000001,51,51,762815.03760000004,529024.98284302861,137.25350910000051,36,33,26209.593460600001,44,9.0732181370064602,9.6803581370064595,431882.08342241566,5777.3533193697394,30.254647695549565,-1080.3903523044505,0,1110.6440000000002,529.71468063026077,1.0055698485512465,1,1.0116782092332994,1,5415.0049181351915,892.06308186480874,1.0093798726858645,1,44,1]
["2013-01-02T12:00:00","2013-01-02T12:00:00",37.620690000000003,37.647309999999997,37.385800000000003,37.73368,37.905929999999998,37.327240000000003,37.44896,37.688600000000001,37.481400000000001,37.250830000000001,37.763109999999998,37.525919999999999,37.58869,37.866990000000001,38.209290000000003,37.700679999999998,37.579180000000001,38.081420000000001,37.740749999999998,37.456949999999999,37.900640000000003,37.31326,37.66319,37.281300000000002,37.704149999999998,37.319110000000002,519.38800000000003,5285.5439999999999,5804.9319999999998,49.077260000000003,39.708289999999998,51,51,762815.03760000004,559683.92278384184,78.318516520000344,37,33,24760.05158484001,44,9.023788759043045,9.6309287590430444,429529.26191909,5487.728546399564,17.358233578221718,-502.02976642177833,0,519.38799999999992,317.20345360043575,1.0033353336448683,1,1.0054612654795461,1,5141.7785769812372,663.15342301876262,1.0069729314053755,1,44,1]
["2013-01-02T13:00:00","2013-01-02T13:00:00",37.654170000000001,37.68289,37.392960000000002,37.736020000000003,37.90654,37.33963,37.445770000000003,37.697760000000002,37.488199999999999,37.26679,37.753520000000002,37.528509999999997,37.587060000000001,37.871589999999998,38.212389999999999,37.700650000000003,37.579419999999999,38.07723,37.746540000000003,37.46893,37.908679999999997,37.346499999999999,37.68233,37.284230000000001,37.710430000000002,37.378619999999998,371.1728,5431.5460000000003,5802.7190000000001,49.356529999999999,39.598869999999998,51,51,762815.03760000004,570144.42370201158,51.138332520000482,37,33,26499.589571180004,44,9.0831070043772399,9.6902470043772393,432352.79013069608,5834.9174040137559,11.260096901942564,-359.91270309805742,0,371.17299999999977,-32.198404013755862,0.99966143994020495,0.99966143994020495,1.0039028131028047,1,5469.3321149006251,333.38688509937492,1.0035054993317647,1,44,1]
["2013-01-02T14:00:00","2013-01-02T14:00:00",37.637500000000003,37.683590000000002,37.386270000000003,37.732729999999997,37.905160000000002,37.34451,37.446910000000003,37.700659999999999,37.485550000000003,37.27422,37.740729999999999,37.534309999999998,37.589750000000002,37.867080000000001,38.210459999999998,37.699249999999999,37.577370000000002,38.073749999999997,37.750489999999999,37.48442,37.910530000000001,37.332940000000001,37.671550000000003,37.284309999999998,37.703429999999997,37.373890000000003,399.0711,5392.2309999999998,5791.3029999999999,49.71011,39.791139999999999,51,51,762815.03760000004,587199.85728405276,52.599566335499979,39,34,26742.688761035002,44,9.1522436867512944,9.7593836867512938,435643.67259089358,5843.9634424829565,11.494354419702052,-387.57674558029794,0,399.07200000000012,-52.660442482956569,0.99910772545956661,0.99910772545956661,1.0041961657517182,1,5480.4052426669405,310.89775733305942,1.0032690304546723,1,44,1]
["2013-01-02T15:00:00","2013-01-02T15:00:00",37.633279999999999,37.687390000000001,37.381619999999998,37.728789999999996,37.901600000000002,37.35304,37.444249999999997,37.700360000000003,37.490020000000001,37.280250000000002,37.743189999999998,37.539189999999998,37.589060000000003,37.868580000000001,38.213030000000003,37.699069999999999,37.578780000000002,38.066969999999998,37.756970000000003,37.497520000000002,37.924750000000003,37.373649999999998,37.70955,37.29063,37.709310000000002,37.361550000000001,352.45580000000001,5443.5159999999996,5795.9709999999995,50.008380000000002,39.873379999999997,51,51,762815.03760000004,601984.78716297843,47.886407266999655,40,35,27585.017330000013,44,9.2418140909530013,9.8489540909530007,439907.19322882942,5969.6109570097378,10.362988650437499,-342.09281134956251,0,352.45499999999993,-173.63995700973828,0.99728193452275804,0.99728193452275804,1.0037059969128925,1,5601.6135470341787,194.35745296582081,1.0020436314442667,1,44,1]
["2013-01-02T16:00:00","2013-01-02T16:00:00",37.614199999999997,37.698520000000002,37.377650000000003,37.726939999999999,37.89817,37.354430000000001,37.453380000000003,37.701590000000003,37.498199999999997,37.280439999999999,37.737720000000003,37.545430000000003,37.586080000000003,37.876109999999997,38.211689999999997,37.702390000000001,37.577500000000001,38.06879,37.761270000000003,37.502459999999999,37.926659999999998,37.400579999999998,37.831580000000002,37.29692,37.688659999999999,37.425330000000002,288.70679999999999,5509.7920000000004,5798.5,49.987349999999999,39.89967,51,51,762815.03760000004,597947.86013863364,27.264026657999182,40,35,27790.509281279996,44,9.248821366491649,9.8559613664916483,440240.73715040705,6009.5244961622075,5.8956759088842103,-282.8111240911158,0,288.70799999999963,-211.02449616220747,0.99506305230709413,0.99506305230709413,1.0030357094004265,1,5639.3299948926997,159.17000510730031,1.0016736421601418,1,44,1]
["2013-01-02T17:00:00","2013-01-02T17:00:00",37.581020000000002,37.687170000000002,37.375190000000003,37.7224,37.904380000000003,37.352269999999997,37.453530000000001,37.70252,37.497950000000003,37.274149999999999,37.742910000000002,37.544199999999996,37.586210000000001,37.883450000000003,38.217550000000003,37.69988,37.585880000000003,38.072920000000003,37.756050000000002,37.494509999999998,37.929200000000002,37.434339999999999,37.761670000000002,37.292070000000002,37.711039999999997,37.407730000000001,371.91250000000002,5430.35,5802.2619999999997,50.259250000000002,39.963030000000003,51,51,762815.03760000004,611727.96122987033,32.224358562500278,40,35,27956.039138499993,44,9.2544659346228499,9.8616059346228511,440509.41666496434,6041.632080336637,6.9640666009569205,-364.9484333990431,0,371.91199999999935,-239.37008033663733,0.99254612169533829,0.99254612169533829,1.0039105835464603,1,5669.6727335960322,132.58926640396749,1.0013941507766262,1,44,1]
["2013-01-02T18:00:00","2013-01-02T18:00:00",37.551900000000003,37.681460000000001,37.380000000000003,37.71228,37.909469999999999,37.362369999999999,37.455800000000004,37.700020000000002,37.497509999999998,37.268770000000004,37.753970000000002,37.541589999999999,37.583120000000001,37.876300000000001,38.217219999999998,37.70194,37.593249999999998,38.077710000000003,37.753970000000002,37.474249999999998,37.925870000000003,37.338410000000003,37.76717,37.282240000000002,37.727060000000002,37.587960000000002,385.59769999999997,5416.7160000000003,5802.3130000000001,49.967959999999998,39.89902,51,51,762815.03760000004,589283.77032645093,-6.9523265309998239,38,33,27270.294200519995,44,9.1093880322377334,9.7165280322377328,433603.75807784358,5987.2944492015476,-1.5264091300965199,-387.12410913009649,0,385.59699999999975,-184.98144920154755,0.9906010771373569,0.9906010771373569,1.0040544787040064,1,5613.1766635246559,189.13633647534425,1.0019887324029833,1,44,1]
["2013-01-02T19:00:00","2013-01-02T19:00:00",37.557110000000002,37.692700000000002,37.384610000000002,37.714730000000003,37.908549999999998,37.362389999999998,37.463059999999999,37.697789999999998,37.49286,37.264339999999997,37.75817,37.5396,37.586770000000001,37.886110000000002,38.216380000000001,37.70438,37.599649999999997,38.076160000000002,37.755049999999997,37.475070000000002,37.923769999999998,37.334429999999998,37.706139999999998,37.309339999999999,37.74391,38.261090000000003,410.13780000000003,5393.1130000000003,5803.25,50.156610000000001,39.9069,51,51,762815.03760000004,566222.68785086472,-144.3644042220003,38,33,27638.922123615001,44,9.1219582444152731,9.7290982444152725,434202.09588283417,6059.8659592717058,-31.652064250652401,-441.78986425065244,0,410.13699999999972,-256.61595927170583,0.98790280940712216,0.98790280940712216,1.0043125121103771,1,5681.7027496829687,121.54725031703128,1.0012780460894171,1,44,1]
["2013-01-02T20:00:00","2013-01-02T20:00:00",37.554450000000003,37.688630000000003,37.382350000000002,37.710549999999998,37.928109999999997,37.348559999999999,37.45543,37.709139999999998,37.494819999999997,37.26802,37.765360000000001,37.53586,37.586860000000001,37.884590000000003,38.213099999999997,37.705509999999997,37.59789,38.074779999999997,37.759010000000004,37.470379999999999,37.923679999999997,37.373019999999997,37.67013,37.32967,37.822479999999999,38.365940000000002,465.00420000000003,5337.29,5802.2939999999999,50.183909999999997,39.826479999999997,51,51,762815.03760000004,562531.33434611373,-188.67312912899982,34,31,27640.303782350005,44,9.0003113589781361,9.6074513589781354,428411.74569714232,6142.0772415340498,-41.92591158322351,-506.93011158322355,0,465.00399999999991,-339.78324153404992,0.98433005361084236,0.98433005361084236,1.0048894281212712,1,5753.9305169669633,48.363483033036573,1.0005085327738781,1,44,1]
["2013-01-02T21:00:00","2013-01-02T21:00:00",37.5548,37.695059999999998,37.381900000000002,37.716340000000002,37.919060000000002,37.350059999999999,37.449680000000001,37.707230000000003,37.491779999999999,37.259619999999998,37.766120000000001,37.537399999999998,37.586640000000003,37.880020000000002,38.213729999999998,37.702550000000002,37.594650000000001,38.074759999999998,37.754280000000001,37.454749999999997,37.925080000000001,37.361179999999997,37.679479999999998,37.332810000000002,37.826549999999997,38.662489999999998,513.86630000000002,5284.9269999999997,5798.7929999999997,50.049750000000003,39.73715,51,51,762815.03760000004,542029.68549980514,-284.60228092349956,35,31,27250.669090100007,44,8.9870248159724113,9.5941648159724107,427779.31078946718,6064.4472777393667,-63.336262389680542,-577.20256238968057,0,513.86599999999999,-265.65427773936699,0.9815367496906291,0.9815367496906291,1.0054032027057083,1,5680.6756216513959,118.11737834860378,1.0012419816416815,1,44,1]
["2013-01-02T22:00:00","2013-01-02T22:00:00",37.552810000000001,37.701889999999999,37.380989999999997,37.720610000000001,37.930750000000003,37.355690000000003,37.46284,37.732199999999999,37.490879999999997,37.258400000000002,37.772260000000003,37.537939999999999,37.595759999999999,37.881329999999998,38.217039999999997,37.709049999999998,37.598669999999998,38.075629999999997,37.753720000000001,37.460500000000003,37.915039999999998,37.346449999999997,37.665680000000002,37.343089999999997,37.876240000000003,38.837009999999999,709.28440000000001,5086.8130000000001,5796.0969999999998,49.958350000000003,39.682139999999997,51,51,762815.03760000004,529371.98435237294,-455.4315132399995,36,32,26136.579309365017,44,9.0098813544493481,9.6170213544493475,428867.27421194711,5801.7588203773612,-101.0960067781789,-810.38040677817889,0,709.28399999999965,-5.6618203773614368,0.98147721673226607,0.98147721673226607,1.0074579855991943,1,5435.4832636974106,360.61373630258913,1.003791784464638,1,44,1]
["2013-01-02T23:00:00","2013-01-02T23:00:00",37.560459999999999,37.694870000000002,37.370060000000002,37.722349999999999,37.928959999999996,37.348269999999999,37.471699999999998,37.718940000000003,37.492019999999997,37.26099,37.776739999999997,37.534149999999997,37.60304,37.887659999999997,38.213549999999998,37.705249999999999,37.59704,38.080530000000003,37.755920000000003,37.451689999999999,37.919060000000002,37.376959999999997,37.66818,37.357199999999999,38.149700000000003,38.903019999999998,742.75599999999997,5051.2060000000001,5793.9610000000002,49.354280000000003,39.386839999999999,51,51,762815.03760000004,497476.40528772451,-498.59724767999955,34,31,25173.79636632001,44,8.9162034560915142,9.5233434560915136,424408.23825552035,5646.7523403408595,-111.8407066719322,-854.59670667193222,0,742.75500000000011,147.20865965914072,0.98302508763280039,0.98302508763280039,1.0078099267623823,1,5286.7559554870068,507.20504451299348,1.0053331640327663,1,44,1]
["2013-01-03","2013-01-03",37.575960000000002,37.705379999999998,37.359229999999997,37.722949999999997,37.9285,37.347360000000002,37.467669999999998,37.718879999999999,37.489840000000001,37.247109999999999,37.78228,37.536589999999997,37.599550000000001,37.884790000000002,38.209269999999997,37.707889999999999,37.597670000000001,38.077300000000001,37.75264,37.439340000000001,37.911279999999998,37.394060000000003,37.670610000000003,37.361510000000003,38.806899999999999,38.841250000000002,798.43470000000002,5006.2169999999996,5804.6509999999998,49.292960000000001,39.353560000000002,51,51,762815.03760000004,497497.82513397996,-505.12572078150015,33,30,24879.396624899997,44,8.8453174249090907,9.45245742490909,421034.08738971606,5625.4389593385795,-114.21313594897737,-912.64783594897744,0,798.4340000000002,179.21204066142036,0.98490946796346501,0.98490946796346501,1.0083953807979698,1,5264.1118613955105,540.53913860448938,1.0056836656565116,1,44,1]
["2013-01-03T01:00:00","2013-01-03T01:00:00",37.579219999999999,37.702570000000001,37.342509999999997,37.73518,37.940350000000002,37.343290000000003,37.467610000000001,37.705869999999997,37.498269999999998,37.242420000000003,37.786729999999999,37.53237,37.608789999999999,37.875300000000003,38.206009999999999,37.706099999999999,37.598109999999998,38.081620000000001,37.751240000000003,37.419989999999999,37.899380000000001,37.355629999999998,37.675040000000003,37.464230000000001,38.966410000000003,38.752459999999999,915.83640000000003,4879.9260000000004,5795.7629999999999,48.866950000000003,39.25685,51,51,762815.03760000004,481446.26834646118,-537.24794896799995,33,30,23448.288426300009,44,8.7965166353368307,9.40365663533683,418711.18647904973,5331.2667726006384,-122.15015812277331,-1037.9865581227734,0,915.83699999999953,464.49622739936149,0.98979355695295945,0.98979355695295945,1.0096298508879509,1,4987.0575533748442,808.70544662515567,1.0085033830946708,1,44,1]
["2013-01-03T02:00:00","2013-01-03T02:00:00",37.563630000000003,37.692819999999998,37.330359999999999,37.741840000000003,37.91677,37.335650000000001,37.46266,37.693260000000002,37.48686,37.236020000000003,37.796880000000002,37.519010000000002,37.598100000000002,37.871600000000001,38.200949999999999,37.705370000000002,37.597160000000002,38.083150000000003,37.744370000000004,37.39893,37.899729999999998,37.312869999999997,37.699860000000001,37.465150000000001,38.840009999999999,38.701549999999997,948.05510000000004,4851.866,5799.9210000000003,48.905439999999999,39.355730000000001,51,51,762815.03760000004,485701.67780261493,-539.40542969599733,30,28,23166.956629429991,44,8.665229221063564,9.2723692210635633,412461.95041448099,5347.1076271393767,-124.49882534781717,-1072.5539253478173,0,948.05500000000029,452.81337286062353,0.99455480296149368,0.99455480296149368,1.0099686169957933,1,4996.9875178833063,802.93348211669399,1.0084426919918359,1,44,1]
["2013-01-03T03:00:00","2013-01-03T03:00:00",37.551049999999996,37.697650000000003,37.32685,37.739600000000003,37.910800000000002,37.325279999999999,37.464979999999997,37.680700000000002,37.484810000000003,37.22672,37.805630000000001,37.516599999999997,37.591329999999999,37.871299999999998,38.191789999999997,37.701709999999999,37.607729999999997,38.084820000000001,37.754179999999998,37.385100000000001,37.904640000000001,37.306330000000003,37.719769999999997,37.972830000000002,38.912190000000002,38.642620000000001,986.75250000000005,4811.29,5798.0420000000004,48.917140000000003,38.982419999999998,51,51,762815.03760000004,489063.64167160995,-538.55471321250218,29,27,23899.409494400014,44,8.629358863759041,9.2364988637590404,410754.53366202815,5539.0927348660925,-124.81917178674429,-1111.5716717867444,0,986.75200000000041,258.94926513390783,0.99727760495659101,0.99727760495659101,1.0103755085494333,1,5174.993219167357,623.04878083264339,1.0065512387633804,1,44,1]
["2013-01-03T04:00:00","2013-01-03T04:00:00",37.56474,37.680529999999997,37.331069999999997,37.747599999999998,37.913699999999999,37.320770000000003,37.460619999999999,37.680709999999998,37.481749999999998,37.226869999999998,37.805070000000001,37.514609999999998,37.590960000000003,37.862740000000002,38.194319999999998,37.704940000000001,37.609830000000002,38.091149999999999,37.747329999999998,37.386159999999997,37.942630000000001,37.331389999999999,37.690170000000002,38.311329999999998,38.880400000000002,38.576189999999997,955.49950000000001,4844.7960000000003,5800.2950000000001,48.843589999999999,38.718859999999999,51,51,762815.03760000004,488724.73210418469,-483.21998463749827,31,29,24526.125702539997,44,8.7724238864566146,9.379563886456614,417564.3798637297,5591.6417218289871,-110.16795150164182,-1065.6674515016418,0,955.4989999999998,208.65327817101297,0.99947155426860723,0.99947155426860723,1.0100468892320207,1,5229.6942585899724,570.60074141002769,1.0059997576602964,1,44,1]
["2013-01-03T05:00:00","2013-01-03T05:00:00",37.55048,37.665939999999999,37.327579999999998,37.750419999999998,37.923160000000003,37.306449999999998,37.461469999999998,37.6768,37.471789999999999,37.214410000000001,37.808079999999997,37.51135,37.587299999999999,37.862780000000001,38.196260000000002,37.709049999999998,37.614460000000001,38.091799999999999,37.743200000000002,37.385829999999999,37.904899999999998,37.330150000000003,37.698090000000001,38.406770000000002,38.843940000000003,38.54654,874.12070000000006,4921.8230000000003,5795.9440000000004,48.993980000000001,39.24089,51,51,762815.03760000004,497294.57459284161,-435.33833222099997,30,28,24001.491341535002,44,8.6936868547463444,9.3008268547463437,413816.52405512379,5521.59095273401,-100.15045158506618,-974.27115158506626,0,874.12100000000009,274.35304726599043,1.0023563240866278,1,1.0091912151267382,1,5161.1521677315604,634.79183226843998,1.0066747147031996,1,44,1]
["2013-01-03T06:00:00","2013-01-03T06:00:00",37.53651,37.65204,37.325150000000001,37.735280000000003,37.925109999999997,37.297870000000003,37.46405,37.673850000000002,37.466459999999998,37.213720000000002,37.80856,37.508369999999999,37.583629999999999,37.861530000000002,38.195920000000001,37.709809999999997,37.618659999999998,38.098219999999998,37.743569999999998,37.36374,37.909880000000001,37.330350000000003,37.780140000000003,38.373759999999997,38.844880000000003,38.521549999999998,829.14869999999996,4972.152,5801.3,48.864460000000001,38.450229999999998,51,51,762815.03760000004,492318.98230590933,-408.37231772399912,29,28,25890.567261480006,44,8.7581043436164698,9.3652443436164674,416882.77451686451,5912.3678471245657,-93.255869467152436,-922.40456946715244,0,829.14800000000014,-111.06784712456556,0.99883214283081456,0.99883214283081456,1.0087183326334737,1,5529.0745893090389,272.22541069096133,1.0028623981263753,1,44,1]
["2013-01-03T07:00:00","2013-01-03T07:00:00",37.540970000000002,37.65222,37.334440000000001,37.73077,37.91283,37.2986,37.461219999999997,37.673720000000003,37.471159999999998,37.2149,37.809069999999998,37.506079999999997,37.581629999999997,37.857430000000001,38.188499999999998,37.710450000000002,37.614699999999999,38.094290000000001,37.741399999999999,37.3825,37.893140000000002,37.315530000000003,38.149160000000002,38.435029999999998,38.816769999999998,38.564340000000001,783.35630000000003,5019.7209999999995,5803.0780000000004,49.228900000000003,39.42924,51,51,762815.03760000004,507629.41241297731,-400.83166836549998,30,28,24595.779547430007,44,8.7139520825673635,9.3210920825673647,414781.14197571302,5645.1491388470959,-91.997675582215095,-875.35397558221507,0,783.35700000000088,157.92886115290457,1.0004927345996624,1,1.0082368490266636,1,5277.4458892922867,525.63211070771376,1.0055269211093614,1,44,1]
["2013-01-03T08:00:00","2013-01-03T08:00:00",37.522030000000001,37.660380000000004,37.339880000000001,37.730759999999997,37.90925,37.299390000000002,37.461350000000003,37.674799999999998,37.471260000000001,37.216099999999997,37.793480000000002,37.506959999999999,37.570369999999997,37.841880000000003,38.18533,37.683689999999999,37.603870000000001,38.062980000000003,37.745640000000002,37.411569999999998,37.880830000000003,37.311300000000003,38.477870000000003,38.330010000000001,38.822479999999999,38.53237,725.37850000000003,5074.3270000000002,5799.7060000000001,49.137439999999998,39.16666,51,51,762815.03760000004,504797.70873795933,-366.43945684499977,32,30,25297.499082529997,44,8.8595747187142742,9.4667147187142735,421712.72970378475,5710.7705247055565,-82.721681001450705,-808.10018100145078,0,725.37899999999991,88.935475294443677,1.0009351395125274,1,1.0076272214457933,1,5344.514931356417,455.19106864358309,1.0047862470249234,1,44,1]
["2013-01-03T09:00:00","2013-01-03T09:00:00",37.579329999999999,37.670459999999999,37.357320000000001,37.723529999999997,37.908589999999997,37.315779999999997,37.455889999999997,37.67756,37.475349999999999,37.226739999999999,37.77281,37.512439999999998,37.5535,37.861289999999997,38.18938,37.656480000000002,37.601779999999998,38.000680000000003,37.755690000000001,37.410139999999998,37.902560000000001,37.33408,38.672849999999997,38.398969999999998,38.764809999999997,38.546019999999999,500.53140000000002,5305.451,5805.982,49.865279999999998,39.77872,51,51,762815.03760000004,538792.90873226058,-241.92934953299996,35,32,26756.874919279995,44,9.0310334347474495,9.6381734347474488,429874.10600744892,5925.5399977440666,-53.577334483595671,-554.10873448359564,0,500.53099999999995,-119.5579977440666,0.99874287052091437,0.99874287052091437,1.0052629877312196,1,5552.2708945693739,253.71110543062605,1.0026677237476911,1,44,1]
["2013-01-03T10:00:00","2013-01-03T10:00:00",37.616340000000001,37.68468,37.364440000000002,37.718800000000002,37.905990000000003,37.338430000000002,37.45429,37.692630000000001,37.482559999999999,37.249420000000001,37.77355,37.528619999999997,37.552770000000002,37.87818,38.20382,37.659680000000002,37.595260000000003,37.998629999999999,37.762430000000002,37.464680000000001,37.92971,37.35454,38.768949999999997,38.382190000000001,38.775089999999999,38.559449999999998,353.58260000000001,5449.3440000000001,5802.9269999999997,49.795450000000002,39.68817,51,51,762815.03760000004,534829.76117835287,-166.73364294299952,39,35,27539.022812160008,44,9.2402456778946576,9.8473856778946569,439832.53730310651,5960.668963172986,-36.088573562903129,-389.67117356290316,0,353.58299999999963,-157.74196317298629,0.99708424394857831,0.99708424394857831,1.0037178576171462,1,5593.1642596226147,209.76274037738494,1.0022056150949155,1,44,1]
["2013-01-03T11:00:00","2013-01-03T11:00:00",37.767859999999999,37.696980000000003,37.388979999999997,37.715409999999999,37.904269999999997,37.369250000000001,37.446210000000001,37.708849999999998,37.496850000000002,37.285809999999998,37.759320000000002,37.555439999999997,37.559060000000002,37.885420000000003,38.200580000000002,37.640059999999998,37.576129999999999,37.98283,37.774990000000003,37.555190000000003,37.960610000000003,37.388199999999998,38.77469,38.361919999999998,38.694209999999998,38.555570000000003,279.14170000000001,5526.4570000000003,5800.2520000000004,50.068109999999997,39.90128,51,51,762815.03760000004,547992.97069742158,-109.94135425350058,43,37,28093.274410654991,44,9.3808396574033353,9.9879796574033364,446524.76269325789,5989.5010333075779,-23.439555150425182,-302.58125515042519,0,273.79500000000007,-189.24903330757752,0.99509432655995911,0.99509432655995911,1.0028789020577531,1,5625.4168258806103,174.8351741193901,1.0018383584161141,1,44,1]
["2013-01-03T12:00:00","2013-01-03T12:00:00",37.790320000000001,37.650449999999999,37.36983,37.715890000000002,37.894039999999997,37.382260000000002,37.437829999999998,37.716729999999998,37.499969999999998,37.311399999999999,37.735250000000001,37.583260000000003,37.558219999999999,37.892209999999999,38.205179999999999,37.634459999999997,37.569899999999997,37.991500000000002,37.781100000000002,37.605339999999998,37.975650000000002,37.41169,38.762230000000002,38.371600000000001,38.647280000000002,38.589239999999997,120.61799999999999,5753.223,5794.8639999999996,50.514099999999999,40.006210000000003,51,51,762815.03760000004,567619.2618267436,-48.182066279999724,45,38,30227.11721473499,44,9.5144506970224647,10.121590697022464,452884.60253041435,6353.938483110649,-10.128186652977925,-130.74618665297791,0,41.640999999999622,-559.07448311064945,0.98921576530111743,0.98921576530111743,1.0004378471505575,1,5972.7997544154996,-177.93575441550001,0.99812903957510313,0.99812903957510313,44,1]
["2013-01-03T13:00:00","2013-01-03T13:00:00",37.791240000000002,37.637369999999997,37.36674,37.71837,37.892359999999996,37.391199999999998,37.430169999999997,37.723950000000002,37.509509999999999,37.327620000000003,37.714649999999999,37.597700000000003,37.553750000000001,37.877020000000002,38.209009999999999,37.683010000000003,37.572249999999997,38.005659999999999,37.77843,37.640999999999998,38.008920000000003,37.417960000000001,38.793370000000003,38.374789999999997,38.657069999999997,38.600749999999998,100.03579999999999,5800.7650000000003,5799.0550000000003,50.493479999999998,39.979559999999999,51,51,762815.03760000004,566089.88480407884,-40.489990228999794,47,39,30494.389574399996,44,9.5844116844870406,10.19155168448704,456214.72163129371,6363.3304950280963,-8.4491341903719199,-108.48493419037192,0,-1.7100000000000364,-564.27549502809597,0.98328251639673248,0.98328251639673248,0.99998201967706224,0.99998201967706224,5984.248624439927,-185.19362443992668,0.99618176403507175,0.99618176403507175,44,1]
["2013-01-03T14:00:00","2013-01-03T14:00:00",37.820569999999996,37.631079999999997,37.386679999999998,37.753079999999997,37.902290000000001,37.396639999999998,37.424160000000001,37.725709999999999,37.514060000000001,37.334980000000002,37.700200000000002,37.609580000000001,37.557070000000003,37.885190000000001,38.208849999999998,37.688139999999997,37.551189999999998,37.970730000000003,37.776679999999999,37.621499999999997,38.000660000000003,37.419460000000001,39.102130000000002,38.385820000000002,38.677799999999998,38.558,123.7272,5866.62,5799.7169999999996,51.474170000000001,40.021419999999999,51,51,762815.03760000004,614805.27914195473,-45.620074548000211,48,39,33594.46610250001,44,9.6901242940952521,10.297264294095251,461246.60573153407,6933.7533932296492,-9.4157872826872051,-133.14298728268722,0,-66.903000000000247,-1134.0363932296495,0.97135834062275617,0.97135834062275617,0.99927854742822697,0.99927854742822697,6524.9303393648042,-725.2133393648046,0.98855628447917265,0.98855628447917265,44,1]
["2013-01-03T15:00:00","2013-01-03T15:00:00",37.791849999999997,37.654690000000002,37.392470000000003,37.815190000000001,37.911839999999998,37.419429999999998,37.420810000000003,37.727870000000003,37.518650000000001,37.345829999999999,37.691589999999998,37.596939999999996,37.570749999999997,37.863289999999999,38.21602,37.688890000000001,37.571210000000001,38.012830000000001,37.775849999999998,37.62236,37.99447,37.407829999999997,39.308050000000001,38.414819999999999,38.733460000000001,38.506689999999999,127.58499999999999,5910.7820000000002,5801.8230000000003,51.34299,39.947020000000002,51,51,762815.03760000004,611003.49442984059,-45.601430700000151,48,39,33679.547174269996,44,9.6930255586426082,10.300165558642608,461384.70493276021,6949.2331306689366,-9.4091221412988997,-136.9941221412989,0,-108.95899999999983,-1147.4101306689363,0.95929354255752608,0.95929354255752608,0.99813286438320892,0.99813286438320892,6539.612782439277,-737.78978243927668,0.98079856602977178,0.98079856602977178,44,1]
["2013-01-03T16:00:00","2013-01-03T16:00:00",38.098010000000002,37.756399999999999,37.415500000000002,37.83446,37.94491,37.443829999999998,37.431669999999997,37.741050000000001,37.516120000000001,37.336759999999998,37.694339999999997,37.589469999999999,37.575710000000001,37.87894,38.205599999999997,37.695050000000002,37.576770000000003,38.05003,37.776730000000001,37.619590000000002,37.99897,37.403289999999998,39.415019999999998,38.436639999999997,38.746760000000002,38.486809999999998,161.63419999999999,5910.4340000000002,5797.8980000000001,51.645679999999999,40.073520000000002,51,51,762815.03760000004,626357.71622258716,-31.421688479999695,49,39,34198.243958719991,44,9.7107131189923521,10.317853118992351,462226.62676238659,{"$f":"AO70*1000/(500*AQ70)","v":7043.4052658469691},-6.4715511816623854,{"$f":"AU70-AC70","v":-168.10575118166238},0,{"$f":"AE70-AD70","v":-112.53600000000006},{"$f":"AE70-AT70","v":-1245.5072658469689},0.94619727187839242,0.94619727187839242,0.99694956986734373,0.99694956986734373,{"$f":"AO70*1000/(500*AR70)","v":6628.9456855652188},{"$f":"AE70-BD70","v":-831.04768556521867},0.97206025856592204,0.97206025856592204,44,1]
["2013-01-03T17:00:00","2013-01-03T17:00:00",38.609389999999998,37.765030000000003,37.450020000000002,37.855020000000003,37.998840000000001,37.439059999999998,37.44594,37.734810000000003,37.518830000000001,37.326479999999997,37.715260000000001,37.582230000000003,37.580449999999999,37.88908,38.208100000000002,37.696449999999999,37.577269999999999,38.058529999999998,37.776000000000003,37.611379999999997,37.995930000000001,37.393990000000002,39.50891,38.439140000000002,38.749180000000003,38.482509999999998,184.50489999999999,5956.8649999999998,5803.1620000000003,51.429690000000001,40.013890000000004,51,51,{"$f":"3.1416*(138/2)^2*AI71","v":762815.03760000004},{"$f":"62.4*AJ71*(AF71-AB71)/1000","v":616281.34454727173},{"$f":"500*AC71*(C71-AB71)/1000","v":11.70499085599999},47,39,34001.189733499989,44,{"$f":"19.5286-0.30357*AP71+0.0000341*AO71+0.060847*AN71","v":9.7039935699123507},{"$f":"19.5286-0.30357*42+0.0000341*AO71+0.060847*AN71","v":10.31113356991235},{"$f":"62.4*AJ71*AQ71/1000","v":461906.77852193773},7007.6694689745345,{"$f":"AL71*1000/(500*AQ71)","v":2.4124069686714997},-182.0924930313285,0,-153.70299999999952,-1204.5074689745343,0.93353210622156935,{"$f":"IF(AZ71>1,1,IF(AZ71<0,0,AZ71))","v":0.93353210622156935},0.99533341222026162,{"$f":"IF(BB71>1,1,BB71)","v":0.99533341222026162},6595.0439887064749,-791.88198870647466,0.96373377091353696,{"$f":"IF(BF71>1,1,IF(BF71<0,0,BF71))","v":0.96373377091353696},44,1]
["2013-01-03T18:00:00","2013-01-03T18:00:00",38.747309999999999,37.836469999999998,37.4968,37.847659999999998,37.952080000000002,37.450029999999998,37.48901,37.743110000000001,37.511249999999997,37.315379999999998,37.730350000000001,37.578789999999998,37.597050000000003,37.889710000000001,38.215789999999998,37.69746,37.575530000000001,38.06044,37.77064,37.600749999999998,37.988790000000002,37.390410000000003,39.562010000000001,38.441029999999998,38.757170000000002,38.466279999999998,147.86930000000001,5914.4179999999997,5801.1329999999998,51.248750000000001,39.886069999999997,51,51,762815.03760000004,608441.20482106251,20.777854689500096,44,37,33601.819560120013,44,9.5686810470000943,10.175821047000092,455465.94866134657,7023.291798539909,4.3428879251888581,-143.52641207481116,0,-113.28499999999985,-1222.1587985399092,{"$f":"IF(AZ71>1,1+AY72*60/$BK$7,IF(AZ71<0,AY72*60/$BK$7,AZ71+AY72*60/$BK$7))","v":0.9206813402104379},0.9206813402104379,{"$f":"IF(BB71>1,1+AX72*60/$BK$7,BB71+AX72*60/$BK$7)","v":0.99414224211265345},0.99414224211265345,6604.2473437612352,-803.11434376123543,{"$f":"IF(BF71>1,1+BE72*60/$BK$7,IF(BF71<0,BE72*60/$BK$7,BF71+BE72*60/$BK$7))","v":0.95528917719610118},0.95528917719610118,44,1]
["2013-01-03T19:00:00","2013-01-03T19:00:00",38.814830000000001,37.829070000000002,37.588909999999998,37.810090000000002,37.982529999999997,37.419339999999998,37.529040000000002,37.748179999999998,37.522379999999998,37.306510000000003,37.738950000000003,37.578040000000001,37.594250000000002,37.892249999999997,38.21217,37.701479999999997,37.57761,38.06176,37.770659999999999,37.60483,37.993040000000001,37.397280000000002,39.633450000000003,38.447510000000001,38.755679999999998,38.467179999999999,117.1785,5860.0820000000003,5800.2479999999996,51.109789999999997,39.93815,51,51,762815.03760000004,601783.91660475719,20.368552762500091,42,36,32733.363237239992,44,9.4782196863898847,10.085359686389884,451160.01880276453,6907.0699604574475,4.2979701750842567,-112.88052982491574,0,-59.834000000000742,-1106.8219604574479,0.90904331899190804,0.90904331899190804,0.99351309904676988,0.99351309904676988,6491.2634264127264,-691.01542641272681,0.94802328215404852,0.94802328215404852,44,1]
["2013-01-03T20:00:00","2013-01-03T20:00:00",38.840530000000001,37.847720000000002,37.5989,37.77261,38.018129999999999,37.406149999999997,37.532969999999999,37.756680000000003,37.546469999999999,37.304389999999998,37.742400000000004,37.574590000000001,37.592970000000001,37.889279999999999,38.209119999999999,37.702530000000003,37.5762,38.063470000000002,37.770769999999999,37.600409999999997,37.992930000000001,37.397239999999996,39.695270000000001,38.441290000000002,38.753540000000001,38.465200000000003,104.5921,5832.6450000000004,5793.0460000000003,50.705509999999997,39.85004,51,51,762815.03760000004,582634.57405206468,19.628276446499907,44,37,31658.051409074993,44,9.5023985530494581,10.109538553049457,452310.92459495954,6663.1706157842564,4.1312256767426172,-100.46087432325739,0,-39.59900000000016,-870.12461578425609,0.89989412508083222,0.89989412508083222,0.99309672313565034,0.99309672313565034,6263.0062179298202,-469.96021792981992,0.94308174034919345,0.94308174034919345,44,1]
["2013-01-03T21:00:00","2013-01-03T21:00:00",38.865349999999999,37.80491,37.64161,37.747959999999999,38.03331,37.458730000000003,37.522480000000002,37.777850000000001,37.549700000000001,37.320149999999998,37.745350000000002,37.570259999999998,37.597230000000003,37.880099999999999,38.211680000000001,37.693579999999997,37.575229999999998,38.065779999999997,37.774230000000003,37.600380000000001,37.999989999999997,37.411009999999997,39.732680000000002,38.434179999999998,38.76511,38.463639999999998,110.7471,5755.9979999999996,5803.9290000000001,50.824680000000001,39.959910000000001,51,51,762815.03760000004,588381.28080420662,22.244108770500077,44,38,31268.797195229999,44,9.5499719843573434,10.157111984357343,454575.40367157315,6548.4584135843834,4.658465764493438,-106.08863423550656,0,47.931000000000495,-744.52941358438329,0.89206554069899224,0.89206554069899224,0.99360070843315451,0.99360070843315451,6157.0251944423007,-353.09619444230066,0.93936900139937785,0.93936900139937785,44,1]
["2013-01-03T22:00:00","2013-01-03T22:00:00",38.965089999999996,37.867849999999997,37.680790000000002,37.811900000000001,38.032890000000002,37.454239999999999,37.530070000000002,37.7986,37.533520000000003,37.312910000000002,37.751390000000001,37.566369999999999,37.590870000000002,37.883479999999999,38.204389999999997,37.697479999999999,37.574950000000001,38.067610000000002,37.777679999999997,37.59937,38.017710000000001,37.408149999999999,39.75611,38.442300000000003,38.78105,38.4831,193.18819999999999,5610.94,5799.4570000000003,50.365009999999998,39.818950000000001,51,51,762815.03760000004,565574.85650077241,46.557390258999618,43,37,29586.65494819999,44,9.4317639337336203,10.03890393373362,448948.74084810895,6273.8327965101935,9.8724672470825077,-183.31573275291748,0,188.51700000000073,-474.37579651019314,0.88707756992990772,0.88707756992990772,0.99558292863155651,0.99558292863155651,5894.3994570523337,-94.942457052333339,0.93837069962258823,0.93837069962258823,44,1]
["2013-01-03T23:00:00","2013-01-03T23:00:00",38.850020000000001,37.946339999999999,37.677810000000001,37.845999999999997,38.011609999999997,37.441519999999997,37.523690000000002,37.781149999999997,37.526699999999998,37.324280000000002,37.767339999999997,37.569360000000003,37.59507,37.884979999999999,38.206330000000001,37.700609999999998,37.582259999999998,38.06532,37.775419999999997,37.592469999999999,38.010980000000004,37.417610000000003,39.664490000000001,38.448929999999997,38.832619999999999,38.546469999999999,273.60239999999999,5522.94,5793.2669999999998,50.172730000000001,39.769269999999999,51,51,762815.03760000004,553406.00384455628,41.526004260000178,43,37,28728.842686200009,44,9.4025125355994206,10.009652535599422,447556.38429077121,6110.8863354189643,8.8329590846650969,-264.76944091533488,0,270.32700000000023,-317.61933541896451,0.88373786336726101,0.88373786336726101,0.99842536533261472,0.99842536533261472,5740.2277619578927,53.039238042107172,0.93892839706608089,0.93892839706608089,44,1]
["2013-01-04","2013-01-04",38.773150000000001,38.009079999999997,37.715499999999999,37.865000000000002,38.029429999999998,37.467399999999998,37.528739999999999,37.775570000000002,37.52187,37.322890000000001,37.78349,37.569020000000002,37.595179999999999,37.885159999999999,38.206249999999997,37.693530000000003,37.58155,38.068719999999999,37.773110000000003,37.56617,38.01323,37.422280000000001,39.492710000000002,38.456099999999999,38.89228,38.641399999999997,356.71080000000001,5442.9440000000004,5799.6549999999997,49.710320000000003,39.617310000000003,51,51,762815.03760000004,526876.81026186317,23.498323950000678,43,38,27467.844110719998,44,9.4203594841755525,10.027499484175552,448405.89294551796,5831.5914922059719,4.988838056440092,-351.7219619435599,0,356.71099999999933,-31.936492205972172,0.8834020572600304,0.8834020572600304,1.0021761132714857,1,5478.5032208811663,321.15177911883347,0.94230524659860082,0.94230524659860082,44,1]
["2013-01-04T01:00:00","2013-01-04T01:00:00",38.726430000000001,37.954740000000001,37.69735,37.84928,38.008789999999998,37.443240000000003,37.548679999999997,37.762340000000002,37.511800000000001,37.315100000000001,37.79862,37.560209999999998,37.593209999999999,37.883929999999999,38.20223,37.693300000000001,37.582360000000001,38.071040000000004,37.768479999999997,37.54795,38.01979,37.444580000000002,39.32338,38.466070000000002,38.861969999999999,38.722639999999998,446.72129999999999,5357.2569999999996,5803.9790000000003,49.520719999999997,39.641269999999999,51,51,762815.03760000004,513984.91879536712,0.84653686350048707,40,36,26463.376334324996,44,9.2644131330004846,9.8715531330004822,440982.899909242,5712.9093779422701,0.1827502403762768,-446.53854975962372,0,446.72200000000066,91.069622057730157,0.88435963691758734,0.88435963691758734,1.0046971963879678,1,5361.5426018137414,442.43639818625888,0.94695738070318025,0.94695738070318025,44,1]
["2013-01-04T02:00:00","2013-01-04T02:00:00",38.90596,37.957470000000001,37.631839999999997,37.85351,37.99174,37.410809999999998,37.547750000000001,37.739730000000002,37.516399999999997,37.343229999999998,37.794980000000002,37.558520000000001,37.587580000000003,37.883580000000002,38.200609999999998,37.699869999999997,37.58558,38.067709999999998,37.76746,37.558329999999998,37.992179999999998,37.51388,39.134720000000002,38.457439999999998,38.81776,38.69462,619.82349999999997,5177.1989999999996,5797.0230000000001,49.579970000000003,39.703440000000001,51,51,762815.03760000004,518138.94097924372,65.496749244999961,40,36,25566.380619735006,44,9.2338255791329651,9.8409655791329627,439526.9427955008,5537.5489607495119,14.186265201502748,-605.63723479849727,0,619.82400000000052,259.4740392504882,0.88708795681214991,0.88708795681214991,1.0065173308097111,1,5195.9089611992185,601.1140388007816,0.95327797984943163,0.95327797984943163,44,1]
["2013-01-04T03:00:00","2013-01-04T03:00:00",39.144460000000002,37.83793,37.599589999999999,37.858339999999998,37.974739999999997,37.426690000000001,37.548200000000001,37.741669999999999,37.543520000000001,37.337769999999999,37.785260000000001,37.564619999999998,37.581710000000001,37.877949999999998,38.202269999999999,37.693930000000002,37.580219999999997,38.069249999999997,37.761470000000003,37.551110000000001,38.01793,37.691699999999997,38.995750000000001,38.439979999999998,38.785980000000002,38.652659999999997,599.9,5199.1120000000001,5799.0129999999999,49.309730000000002,39.502980000000001,51,51,762815.03760000004,507272.89097196411,147.51541000000145,40,36,25493.195803000002,44,9.2313299768823001,9.8384699768823012,439408.15298100107,5523.1902373421235,31.95973069306789,-567.94026930693212,0,599.90099999999984,275.82276265787641,0.88998818040641181,0.88998818040641181,1.0063078442752724,1,5182.349666747371,616.66333325262895,0.95976207685281711,0.95976207685281711,44,1]
["2013-01-04T04:00:00","2013-01-04T04:00:00",39.044530000000002,37.810679999999998,37.601709999999997,37.843780000000002,37.968000000000004,37.436819999999997,37.552720000000001,37.752560000000003,37.556170000000002,37.307810000000003,37.79327,37.563549999999999,37.579180000000001,37.88008,38.20543,37.694209999999998,37.581479999999999,38.071770000000001,37.775329999999997,37.541739999999997,38.093209999999999,38.076740000000001,38.916629999999998,38.405200000000001,38.817050000000002,38.628680000000003,568.99130000000002,5235.085,5804.0770000000002,49.85145,39.791420000000002,51,51,762815.03760000004,534200.01769843174,118.30751605249971,41,36,26332.556076274996,44,9.2599521622009782,9.8670921622009775,440770.55922329286,5687.406503840095,25.552511283034413,-543.43878871696563,0,568.99200000000019,116.67049615990527,0.89121494835861637,0.89121494835861637,1.0059828420520649,1,5337.4501106111475,466.62688938885276,0.96466856934561118,0.96466856934561118,44,1]
["2013-01-04T05:00:00","2013-01-04T05:00:00",38.850990000000003,37.868499999999997,37.576369999999997,37.851379999999999,37.959380000000003,37.433030000000002,37.552160000000001,37.751300000000001,37.53539,37.289830000000002,37.795859999999998,37.567709999999998,37.577950000000001,37.880540000000003,38.207000000000001,37.696159999999999,37.58211,38.072740000000003,37.798020000000001,37.549950000000003,38.090739999999997,38.631309999999999,38.846960000000003,38.402070000000002,39.022109999999998,38.57976,413.14339999999999,5384.63,5797.7740000000003,49.684130000000003,39.630220000000001,51,51,762815.03760000004,528564.21815023723,56.028442191000565,40,35,27068.292701650003,44,9.2241937811262673,9.8313337811262649,439068.47250112199,5868.9774616475997,12.148149425403666,-400.9952505745963,0,413.14400000000023,-71.203461647599397,0.89046625757808195,0.89046625757808195,1.0043441301402449,1,5506.5351872427418,291.23881275725853,0.96773088975812593,0.96773088975812593,44,1]
["2013-01-04T06:00:00","2013-01-04T06:00:00",38.71181,37.925190000000001,37.566409999999998,37.826520000000002,37.96743,37.436369999999997,37.54224,37.761539999999997,37.526890000000002,37.27834,37.799790000000002,37.573070000000001,37.581330000000001,37.885869999999997,38.204770000000003,37.701790000000003,37.580550000000002,38.06523,37.808579999999999,37.543109999999999,38.012230000000002,38.927500000000002,38.83325,38.68526,39.002519999999997,38.553530000000002,354.46609999999998,5447.9870000000001,5802.4530000000004,50.166640000000001,39.726019999999998,51,51,762815.03760000004,552780.06833730312,28.052447153999601,40,35,28440.181015970007,44,9.2709751726445795,9.8781151726445771,441295.25075435539,6135.3159697562523,6.0516712927400791,-348.4144287072599,0,354.46600000000035,-332.86296975625191,0.88696626711594384,0.88696626711594384,1.0037271421932596,1,5758.2201703274895,44.232829672510888,0.96819598950196506,0.96819598950196506,44,1]
["2013-01-04T07:00:00","2013-01-04T07:00:00",38.584029999999998,37.959859999999999,37.553910000000002,37.817300000000003,37.964829999999999,37.440469999999998,37.523910000000001,37.766770000000001,37.525649999999999,37.277549999999998,37.803040000000003,37.566929999999999,37.585380000000001,37.890940000000001,38.208590000000001,37.706290000000003,37.580860000000001,38.064369999999997,37.819940000000003,37.639389999999999,38.022410000000001,39.040860000000002,38.849260000000001,38.711039999999997,39.002220000000001,38.520380000000003,290.26330000000002,5507.116,5797.3789999999999,50.276389999999999,39.716909999999999,51,51,762815.03760000004,559582.05951498065,9.2376295224993541,40,35,29076.14062984,44,9.2926613954775448,9.8998013954775441,442327.50755202497,6257.8715380699177,1.9881558424145374,-288.27514415758549,0,290.26299999999992,-460.49253806991783,0.88212427615398514,0.88212427615398514,1.0030520599280104,1,5874.0856444095234,-76.706644409523506,0.96738943380725217,0.96738943380725217,44,1]
["2013-01-04T08:00:00","2013-01-04T08:00:00",38.498759999999997,37.990819999999999,37.536250000000003,37.802990000000001,37.96875,37.455010000000001,37.535550000000001,37.769959999999998,37.519889999999997,37.285789999999999,37.812959999999997,37.564480000000003,37.584110000000003,37.899859999999997,38.202750000000002,37.700470000000003,37.583640000000003,38.074489999999997,37.808190000000003,37.648409999999998,38.072000000000003,39.042729999999999,38.85463,38.673819999999999,39.022840000000002,38.524839999999998,254.93100000000001,5548.0079999999998,5802.9390000000003,50.191490000000002,39.724780000000003,51,51,762815.03760000004,555328.55404516112,-3.3243002400000412,41,36,29034.695406839997,44,9.3520951133732453,9.9592351133732429,445156.53221810708,6209.238690338203,-0.71092096470370181,-255.6419209647037,0,254.93100000000049,-406.29969033820271,0.8778521126207609,0.8778521126207609,1.0026805507057657,1,5830.7078960014233,-27.768896001422945,0.96709744917699947,0.96709744917699947,44,1]
["2013-01-04T09:00:00","2013-01-04T09:00:00",38.401629999999997,38.010089999999998,37.523110000000003,37.788080000000001,37.964219999999997,37.446210000000001,37.560609999999997,37.764069999999997,37.533760000000001,37.29092,37.817169999999997,37.565440000000002,37.584449999999997,37.905970000000003,38.206600000000002,37.693339999999999,37.587290000000003,38.088329999999999,37.812759999999997,37.654580000000003,38.031210000000002,39.008470000000003,38.855789999999999,38.675289999999997,39.002870000000001,38.534680000000002,270.94049999999999,5543.17,5801.6009999999997,50.407890000000002,39.827240000000003,51,51,762815.03760000004,565160.73947316024,-18.02431676250059,41,36,29325.170830249994,44,9.3620003253115254,9.9691403253115247,445628.01692221634,6264.7233093904397,-3.85052683960483,-274.7910268396048,0,258.43099999999959,-463.12230939044002,0.87298247011634866,0.87298247011634866,1.00271735253634,1,5883.189497452202,-81.588497452202319,0.96623956173126768,0.96623956173126768,44,1]
["2013-01-04T10:00:00","2013-01-04T10:00:00",38.400880000000001,37.989780000000003,37.531039999999997,37.792879999999997,37.952309999999997,37.427529999999997,37.561489999999999,37.764850000000003,37.536499999999997,37.302790000000002,37.805790000000002,37.569229999999997,37.587859999999999,37.902709999999999,38.20955,37.697200000000002,37.589640000000003,38.08764,37.821910000000003,37.669550000000001,38.036180000000002,38.9786,38.857590000000002,38.59789,38.996810000000004,38.588450000000002,115.0278,5798.732,5802.2269999999999,50.472340000000003,39.799770000000002,51,51,762815.03760000004,565669.10382429813,-10.787882223000052,42,37,30943.68659062,44,9.478038712740144,10.085178712740142,451151.4045188672,6529.5548010425964,-2.2763954758908609,-117.30419547589086,0,3.4949999999998909,-727.32780104259655,0.86533475740032884,0.86533475740032884,1.0000367492565307,1,6136.4676763794505,-334.24067637945063,0.96272508494749287,0.96272508494749287,44,1]
["2013-01-04T11:00:00","2013-01-04T11:00:00",38.455269999999999,37.964570000000002,37.553910000000002,37.791080000000001,37.947940000000003,37.434660000000001,37.537709999999997,37.756520000000002,37.535130000000002,37.315730000000002,37.807639999999999,37.584710000000001,37.586559999999999,37.894710000000003,38.211039999999997,37.69802,37.584980000000002,38.081400000000002,37.823410000000003,37.674309999999998,38.03839,38.979999999999997,38.83502,38.524679999999996,38.967179999999999,38.618960000000001,121.0671,5831.308,5807.5690000000004,50.768830000000001,39.830150000000003,51,51,762815.03760000004,578329.66095123102,-9.9087367995001525,43,38,31893.406096719995,44,9.5712711478981536,10.178411147898153,455589.23657917645,6664.4034222609553,-2.0705163705817919,-123.13761637058178,0,-23.738999999999578,-856.83442226095485,0.85632530733220913,0.85632530733220913,0.99975038895542645,0.99975038895542645,6266.8732149429825,-459.30421494298207,0.95789558897592997,0.95789558897592997,44,1]
["2013-01-04T12:00:00","2013-01-04T12:00:00",38.535429999999998,37.920859999999998,37.560009999999998,37.789389999999997,37.935960000000001,37.456049999999998,37.540799999999997,37.76746,37.545200000000001,37.326070000000001,37.804900000000004,37.585000000000001,37.602550000000001,37.89564,38.2134,37.697580000000002,37.584339999999997,38.074260000000002,37.82931,37.665779999999998,38.044879999999999,38.972880000000004,38.879730000000002,38.582990000000002,38.954639999999998,38.648650000000004,153.51750000000001,5914.7870000000003,5806.4009999999998,50.577750000000002,39.831809999999997,51,51,762815.03760000004,567821.08437813155,-8.6906256750004154,45,39,31779.973107390011,44,9.6282500829619995,10.235390082961999,458301.41442114813,6601.4016739401795,-1.805234720768047,-155.32273472076807,0,-108.38600000000042,-795.00067394017969,0.84796602730108528,0.84796602730108528,0.99861073089581387,0.99861073089581387,6209.8215797933262,-403.4205797933264,0.95365369873941364,0.95365369873941364,44,1]
["2013-01-04T13:00:00","2013-01-04T13:00:00",38.557980000000001,37.886859999999999,37.566949999999999,37.803440000000002,37.93817,37.471550000000001,37.569870000000002,37.78716,37.570329999999998,37.345260000000003,37.801960000000001,37.584090000000003,37.599730000000001,37.895499999999998,38.210549999999998,37.692489999999999,37.578189999999999,38.064329999999998,37.833950000000002,37.625129999999999,38.057580000000002,38.953629999999997,38.940800000000003,38.585560000000001,39.020850000000003,38.666330000000002,188.03550000000001,5965.9009999999998,5794.5420000000004,51.09348,39.862380000000002,51,51,762815.03760000004,591528.0942174762,-10.186823212500141,46,39,33501.815360549997,44,9.6869649037947561,10.294104903794755,461096.219832648,6916.8858756628815,-2.1032022545079254,-190.13870225450793,0,-171.35899999999947,-1122.3438756628811,0.83616479611296068,0.83616479611296068,0.99680892378569674,0.99680892378569674,6508.9321847109004,-714.39018471090003,0.94614202258461566,0.94614202258461566,44,1]
["2013-01-04T14:00:00","2013-01-04T14:00:00",38.693069999999999,37.838590000000003,37.594589999999997,37.833030000000001,37.931469999999997,37.462910000000001,37.576230000000002,37.80433,37.583559999999999,37.378,37.786679999999997,37.618679999999998,37.603230000000003,37.8917,38.20984,37.689970000000002,37.572270000000003,38.03351,37.848660000000002,37.605159999999998,38.099960000000003,38.795940000000002,39.071339999999999,38.612879999999997,39.041170000000001,38.652790000000003,274.3759,6066.02,5799.3729999999996,50.990479999999998,39.91751,51,51,762815.03760000004,587269.82878182153,5.5259306259994041,47,40,33584.428739699993,44,9.7506290200237711,10.35776902002377,464126.61001406441,6888.6691660058914,1.1334511065186506,-273.24244889348137,0,-266.64700000000084,-1089.2961660058918,0.82471105527102773,0.82471105527102773,0.99400518158078532,0.99400518158078532,6484.8769411200719,-685.50394112007234,0.93893407975626419,0.93893407975626419,44,1]
["2013-01-04T15:00:00","2013-01-04T15:00:00",38.587730000000001,37.93938,37.59534,37.811819999999997,37.963279999999997,37.503810000000001,37.51972,37.78734,37.561520000000002,37.368569999999998,37.723869999999998,37.608800000000002,37.597250000000003,37.896790000000003,38.22757,37.727110000000003,37.627839999999999,38.093089999999997,37.854840000000003,37.660339999999998,38.110500000000002,38.489780000000003,39.204050000000002,38.625579999999999,39.058920000000001,38.603580000000001,329.48250000000002,6124.7150000000001,5797.15,51.433340000000001,39.917439999999999,51,51,762815.03760000004,610692.19266425609,-2.6111488125000601,49,41,35265.802734250006,44,9.8688108732379263,10.475950873237926,469752.02584978373,7146.920371102301,-0.52917192274520719,-330.01167192274522,0,-327.56500000000051,-1349.7703711023014,0.81051847798195853,0.81051847798195853,0.99056089825732097,0.99056089825732097,6732.7163254155266,-935.56632541552699,0.92909677878508734,0.92909677878508734,44,1]
["2013-01-04T16:00:00","2013-01-04T16:00:00",38.215130000000002,37.947339999999997,37.563139999999997,37.833469999999998,37.981990000000003,37.487180000000002,37.507469999999998,37.80547,37.613660000000003,37.441800000000001,37.842320000000001,37.745550000000001,37.741419999999998,38.035429999999998,38.37688,37.885770000000001,37.809449999999998,38.259030000000003,37.967619999999997,37.775300000000001,38.163820000000001,37.952829999999999,39.408459999999998,38.633749999999999,39.078060000000001,38.624459999999999,281.15359999999998,6080.4459999999999,5800.89,51.642229999999998,40.085680000000004,51,51,762815.03760000004,619641.40442993259,-57.542301543999585,50,41,35134.489110649978,44,9.864333078673166,10.471473078673164,469538.88435835647,7123.5407057799512,-11.666739370025308,-292.82033937002529,0,-279.55599999999959,-1322.6507057799508,0.79661105878672622,0.79661105878672622,0.98762142038644218,0.98762142038644218,6710.5151007277118,-909.62510072771147,0.91953224482986917,0.91953224482986917,44,1]
["2013-01-04T17:00:00","2013-01-04T17:00:00",37.983609999999999,37.833199999999998,37.475679999999997,37.778410000000001,37.948900000000002,37.44473,37.490110000000001,37.783299999999997,37.597479999999997,37.415329999999997,37.811869999999999,37.70767,37.751640000000002,38.104259999999996,38.47287,37.975619999999999,37.890740000000001,38.364829999999998,38.095469999999999,37.89622,38.289099999999998,37.777470000000001,39.45138,38.617809999999999,39.05677,38.684640000000002,244.06639999999999,6036.4840000000004,5797.44,51.68374,40.027810000000002,51,51,762815.03760000004,618752.71880860825,-85.548934196000346,48,40,35180.417475059992,44,9.8050522358995469,10.412192235899546,466717.13649585505,7175.9775733275173,-17.449970104754229,-261.51637010475423,0,-239.04400000000078,-1378.5375733275177,0.78211599986840163,0.78211599986840163,0.98510791844705847,0.98510791844705847,6757.5428263346175,-960.10282633461793,0.9094369472444882,0.9094369472444882,44,1]
["2013-01-04T18:00:00","2013-01-04T18:00:00",37.908920000000002,37.790979999999998,37.458269999999999,37.833500000000001,38.023699999999998,37.539239999999999,37.62182,37.916849999999997,37.736199999999997,37.570450000000001,37.979849999999999,37.887970000000003,37.936500000000002,38.262549999999997,38.604680000000002,38.105400000000003,38.040149999999997,38.544699999999999,38.28989,38.09207,38.426200000000001,37.794490000000003,39.529110000000003,38.615409999999997,39.027430000000003,38.724249999999998,221.85220000000001,6010.1459999999997,5799.5829999999996,51.508760000000002,40.027119999999996,51,51,762815.03760000004,608538.30812408892,-90.441377112999547,46,39,34503.166359720017,44,9.7211109728664535,10.328250972866453,462721.56105432793,7098.6055927198413,-18.607210094697887,-240.45941009469789,0,-210.5630000000001,-1299.0225927198417,0.76845702576277863,0.76845702576277863,0.98289388877527228,0.98289388877527228,6681.3183471943012,-881.73534719430154,0.90016566871335579,0.90016566871335579,44,1]
["2013-01-04T19:00:00","2013-01-04T19:00:00",37.89517,37.850900000000003,37.547319999999999,37.936500000000002,38.126719999999999,37.649180000000001,37.739660000000001,38.062420000000003,37.88147,37.70825,38.134700000000002,38.022709999999996,38.037089999999999,38.336060000000003,38.661529999999999,38.148919999999997,38.06165,38.528910000000003,38.300739999999998,38.119079999999997,38.517829999999996,37.918759999999999,39.55274,38.620750000000001,39.027000000000001,38.7806,166.8982,5962.38,5799.4009999999998,51.044780000000003,39.96902,51,51,762815.03760000004,583770.77789678983,-73.888336612999964,47,40,33018.944954400009,44,9.7313460229450417,10.338486022945041,463208.74594122532,6786.1002735996308,-15.185635458606127,-182.08383545860613,0,-162.97900000000027,-986.69927359963094,0.75808207162136054,0.75808207162136054,0.98118019576235915,0.98118019576235915,6387.5783903210558,-588.17739032105601,0.89398109595154784,0.89398109595154784,44,1]
["2013-01-04T20:00:00","2013-01-04T20:00:00",37.969700000000003,37.948950000000004,37.68526,38.060209999999998,38.262790000000003,37.769449999999999,37.849510000000002,38.154820000000001,37.963859999999997,37.782069999999997,38.2136,38.077359999999999,38.0822,38.38982,38.714489999999998,38.178750000000001,38.112789999999997,38.583669999999998,38.320349999999998,38.133710000000001,38.532400000000003,37.989890000000003,39.748130000000003,38.614150000000002,39.01146,38.788049999999998,153.1771,5909.4449999999997,5796.7460000000001,51.152970000000003,39.948740000000001,51,51,762815.03760000004,588565.96747859009,-62.676239892499638,46,39,33105.390476175009,44,9.6734468152375683,10.280586815237568,460452.76343583164,6844.5903737285353,-12.958408949697706,-166.13550894969771,0,-112.69899999999961,-1047.8443737285352,0.7470641884469702,0.7470641884469702,0.9799951873326701,0.9799951873326701,6440.3698098453342,-643.62380984533411,0.8872135146933704,0.8872135146933704,44,1]
["2013-01-04T21:00:00","2013-01-04T21:00:00",37.985529999999997,38.002209999999998,37.803910000000002,38.176470000000002,38.360950000000003,37.854329999999997,37.917160000000003,38.199669999999998,38.0062,37.82282,38.255180000000003,38.154829999999997,38.191249999999997,38.467649999999999,38.780970000000003,38.289940000000001,38.201680000000003,38.624510000000001,38.362110000000001,38.168410000000002,38.559159999999999,37.969059999999999,39.831829999999997,38.642670000000003,39.0383,38.715829999999997,112.206,5860.0069999999996,5800.1170000000002,51.020429999999998,40.00206,51,51,762815.03760000004,585694.75608714472,-40.972020899999983,46,39,32283.862664294993,44,9.6454327168524596,10.252572716852459,459119.3019238225,6694.1242787145802,-8.4956314771474872,-120.70163147714749,0,-59.889999999999418,-894.00727871458002,0.7376638729030861,0.7376638729030861,0.97936545543749731,0.97936545543749731,6297.7095712238242,-497.59257122382405,0.88198142397871537,0.88198142397871537,44,1]
["2013-01-04T22:00:00","2013-01-04T22:00:00",38.065800000000003,38.133870000000002,37.887250000000002,38.249679999999998,38.454619999999998,37.940719999999999,38.026850000000003,38.319679999999998,38.129199999999997,37.94811,38.388280000000002,38.245080000000002,38.259410000000003,38.562190000000001,38.87988,38.368180000000002,38.274529999999999,38.718670000000003,38.440390000000001,38.236229999999999,38.586060000000003,37.980049999999999,39.930030000000002,38.677669999999999,39.059719999999999,38.752079999999999,128.58539999999999,5736.7790000000005,5798.8059999999996,51.066450000000003,40.050350000000002,51,51,762815.03760000004,586159.80474918755,-44.12279415599977,45,39,31598.465570950004,44,9.6220606759693954,10.229200675969395,458006.80076293432,6567.9206637857851,-9.1711735441856437,-137.75657354418564,0,62.026999999999134,-769.11466378578552,0.72957677931766252,0.72957677931766252,0.98001765747893799,0.98001765747893799,6178.0908541918898,-379.28485419189019,0.87799331628059207,0.87799331628059207,44,1]
["2013-01-04T23:00:00","2013-01-04T23:00:00",38.150410000000001,38.181919999999998,37.944099999999999,38.3187,38.514299999999999,37.998759999999997,38.079030000000003,38.359389999999998,38.16075,37.969059999999999,38.41527,38.254060000000003,38.265300000000003,38.565770000000001,38.888399999999997,38.378509999999999,38.288449999999997,38.74492,38.466149999999999,38.284410000000001,38.642560000000003,37.988300000000002,39.855939999999997,38.663319999999999,39.038269999999997,38.843739999999997,243.62360000000001,5562.8689999999997,5801.9589999999998,50.45149,39.90795,51,51,762815.03760000004,552524.93416856753,-84.455775293999508,46,39,29326.165908130002,44,9.5445752574672333,10.151715257467233,454318.52131541597,6145.096060756935,-17.697125962294702,-261.32072596229472,0,239.09000000000015,-343.13706075693517,0.72596875875372047,0.72596875875372047,0.98253164309952346,0.98253164309952346,5777.578500649679,24.380499350320861,0.87824967256813824,0.87824967256813824,44,1]
["2013-01-05","2013-01-05",38.138390000000001,38.164679999999997,37.896769999999997,38.283349999999999,38.514319999999998,37.994259999999997,38.078449999999997,38.346559999999997,38.155189999999997,37.94688,38.39235,38.237020000000001,38.260860000000001,38.563650000000003,38.882899999999999,38.369790000000002,38.269469999999998,38.725189999999998,38.458489999999998,38.26567,38.570099999999996,37.988630000000001,39.719459999999998,38.664700000000003,39.027119999999996,38.835000000000001,201.79900000000001,5603.652,5796.92,50.38888,40.049880000000002,51,51,762815.03760000004,549960.74057345535,-70.287600694999966,45,40,28968.079013999995,44,9.5932114943774014,10.200351494377401,456633.58957558678,6039.2870585576557,-14.653612241572212,-216.45261224157221,0,193.26800000000003,-242.36705855765558,0.72342031548918595,0.72342031548918595,0.98456381915422808,0.98456381915422808,5679.8197650282291,117.10023497177099,0.87948095914175572,0.87948095914175572,44,1]
["2013-01-05T01:00:00","2013-01-05T01:00:00",38.1845,38.154730000000001,37.933450000000001,38.283160000000002,38.510739999999998,37.996009999999998,38.087699999999998,38.3489,38.131430000000002,37.907730000000001,38.39293,38.208930000000002,38.25076,38.551479999999998,38.872369999999997,38.364190000000001,38.269269999999999,38.723950000000002,38.448219999999999,38.235320000000002,38.59937,38.002459999999999,39.648260000000001,38.714039999999997,39.02355,39.007170000000002,310.8877,5494.5069999999996,5805.1679999999997,50.26511,40.069310000000002,51,51,762815.03760000004,535874.09768246906,-127.87899207950035,45,41,28010.447235299998,44,9.6214032507237306,10.228543250723732,457975.50754585251,5822.5284826707639,-26.582191546722918,-337.46989154672292,0,310.66100000000006,-17.360482670764213,0.7232377733343458,0.7232377733343458,0.98783036015082648,0.98783036015082648,5476.9181786112285,328.24982138877112,0.88293244323114106,0.88293244323114106,44,1]
["2013-01-05T02:00:00","2013-01-05T02:00:00",38.098370000000003,38.184139999999999,37.9039,38.289499999999997,38.523629999999997,37.984639999999999,38.065280000000001,38.320610000000002,38.128410000000002,37.921080000000003,38.407519999999998,38.21698,38.248089999999998,38.55077,38.86918,38.35812,38.26829,38.716650000000001,38.434539999999998,38.239280000000001,38.647599999999997,38.022689999999997,39.56073,38.749290000000002,39.03942,39.217269999999999,282.82299999999998,5518.9110000000001,5801.0249999999996,49.830930000000002,40.048990000000003,51,51,762815.03760000004,505206.58980315377,-158.2253273499995,43,40,26992.828133669995,44,9.525855439358148,10.132995439358147,453427.46436911979,5667.2764573233471,-33.220182346302899,-316.0431823463029,0,282.11399999999958,133.74854267665251,0.72464411367925097,0.72464411367925097,0.99079673490245079,0.99079673490245079,5327.7095198968727,473.3154801031269,0.8879092649760062,0.8879092649760062,44,1]
["2013-01-05T03:00:00","2013-01-05T03:00:00",38.144739999999999,38.231810000000003,37.936540000000001,38.308900000000001,38.51831,37.987099999999998,38.072409999999998,38.315869999999997,38.13017,37.922339999999998,38.392409999999998,38.210059999999999,38.232930000000003,38.540999999999997,38.866430000000001,38.36092,38.256659999999997,38.719729999999998,38.424729999999997,38.208669999999998,38.620370000000001,38.008049999999997,39.506839999999997,38.785490000000003,39.05001,39.402009999999997,282.73439999999999,5523.2730000000001,5798.1639999999998,50.082470000000001,40.10548,51,51,762815.03760000004,508386.2469806826,-177.73673954399976,43,40,27552.819744135002,44,9.5449511532750044,10.152091153275004,454336.41382743965,5773.2762172766597,-37.24204277001791,-319.97644277001791,0,274.89099999999962,24.887782723340024,0.72490580395443915,0.72490580395443915,0.99368716119057821,0.99368716119057821,5428.0087379330971,370.15526206690265,0.89180137675910154,0.89180137675910154,44,1]
["2013-01-05T04:00:00","2013-01-05T04:00:00",38.173470000000002,38.217610000000001,37.965539999999997,38.334449999999997,38.51858,37.997100000000003,38.05912,38.327359999999999,38.129579999999997,37.91966,38.402099999999997,38.212800000000001,38.233919999999998,38.544260000000001,38.86112,38.35051,38.259219999999999,38.708019999999998,38.407989999999998,38.207569999999997,38.603490000000001,38.047759999999997,39.472679999999997,38.774090000000001,39.073650000000001,39.077300000000001,891.73069999999996,5491.3209999999999,5309.3310000000001,49.790100000000002,40.914149999999999,51,51,762815.03760000004,509925.61993159994,-402.98647929049963,42,40,24370.345314975009,44,9.4364287752406479,10.043568775240647,449170.7857100828,5165.1627740608928,-85.410802940166889,-977.1415029401669,0,-181.98999999999978,144.16822593910729,0.72642170527593419,0.72642170527593419,0.99177357114879328,0.99177357114879328,4852.9254611274546,456.40553887254555,0.89660039370619748,0.89660039370619748,44,1]
["2013-01-05T05:00:00","2013-01-05T05:00:00",38.376930000000002,38.380310000000001,38.034779999999998,38.342230000000001,38.520150000000001,37.971960000000003,38.085189999999997,38.343260000000001,38.137900000000002,37.927019999999999,38.420160000000003,38.211950000000002,38.230310000000003,38.524239999999999,38.846620000000001,38.339449999999999,38.243600000000001,38.701709999999999,38.411769999999997,38.175710000000002,38.597729999999999,38.038179999999997,39.694279999999999,38.827159999999999,39.073340000000002,39.144489999999998,102.1635,5756.73,5801.7439999999997,50.213839999999998,41.115810000000003,51,51,762815.03760000004,526897.27811495168,-39.208308029999799,39,37,26187.451120949983,44,9.3158510832243948,9.9229910832243942,443431.32876593102,5622.1274657572139,-8.4175471848416556,-110.58104718484165,0,45.014000000000124,179.61653424278575,0.72831033877924156,0.72831033877924156,0.99224688474921585,0.99224688474921585,5278.1365822694233,523.60741773057634,0.90210602555615604,0.90210602555615604,44,1]
["2013-01-05T06:00:00","2013-01-05T06:00:00",38.297910000000002,38.300820000000002,37.999079999999999,38.345880000000001,38.543579999999999,37.983939999999997,38.094760000000001,38.348289999999999,38.143520000000002,37.918810000000001,38.437139999999999,38.214309999999998,38.250500000000002,38.541440000000001,38.855499999999999,38.368600000000001,38.265630000000002,38.726570000000002,38.433230000000002,38.177889999999998,38.600490000000001,38.032179999999997,39.79365,38.787869999999998,39.00665,39.202669999999998,112.2624,5864.2809999999999,5798.4459999999999,50.495199999999997,41.178539999999998,51,51,762815.03760000004,537520.56986466551,-50.785264511999777,38,36,27317.756110729995,44,9.2935474833758924,9.9006874833758935,442369.68503325107,5878.865128648762,-10.929145109086367,-123.19154510908636,0,-65.835000000000036,-80.419128648762126,0.72746474702281927,0.72746474702281927,0.99155464231611012,0.99155464231611012,5518.3553983698321,280.09060163016784,0.90505112466092574,0.90505112466092574,44,1]
["2013-01-05T07:00:00","2013-01-05T07:00:00",38.2789,38.313249999999996,38.033340000000003,38.383710000000001,38.56268,38.01023,38.123849999999997,38.372660000000003,38.165480000000002,37.943150000000003,38.471179999999997,38.251139999999999,38.301110000000001,38.611020000000003,38.930190000000003,38.448869999999999,38.357300000000002,38.826549999999997,38.523870000000002,38.248390000000001,38.662790000000001,38.090809999999998,39.933729999999997,38.76661,39.016840000000002,39.18647,128.06290000000001,5910.7380000000003,5803.4840000000004,50.29618,41.033740000000002,51,51,762815.03760000004,528818.400325806,-58.113023076499985,39,38,27373.928040359991,44,9.4171569461762772,10.024296946176277,448253.45323091163,5813.6289321321856,-12.341946387565745,-140.40484638756575,0,-107.25399999999991,-10.144932132185204,0.72735807500181404,0.72735807500181404,0.99042688701998616,0.99042688701998616,5461.5157925467593,341.96820745324112,0.90864685495593955,0.90864685495593955,44,1]
["2013-01-05T08:00:00","2013-01-05T08:00:00",38.304630000000003,38.352710000000002,38.031999999999996,38.390830000000001,38.592280000000002,38.039580000000001,38.170720000000003,38.421050000000001,38.226509999999998,38.01643,38.544930000000001,38.314419999999998,38.353180000000002,38.652859999999997,38.964730000000003,38.46613,38.374160000000003,38.82985,38.523110000000003,38.251170000000002,38.668700000000001,38.1158,39.901020000000003,38.77402,39.05021,39.04251,186.98269999999999,5981.3580000000002,5802.9579999999996,50.66151,41.116390000000003,51,51,762815.03760000004,553060.43032496248,-68.985397337999714,40,38,28546.389936479995,44,9.4571378968339683,10.064277896833968,450156.53282257559,6037.0040593437188,-14.589064490874017,-201.57176449087402,0,-178.40000000000055,-234.04605934371921,0.72489712545250284,0.72489712545250284,0.98855104514156189,0.98855104514156189,5672.8143298706309,130.14367012936873,0.91001529075549392,0.91001529075549392,44,1]
["2013-01-05T09:00:00","2013-01-05T09:00:00",38.357019999999999,38.377279999999999,38.079300000000003,38.441369999999999,38.64967,38.109780000000001,38.237690000000001,38.493989999999997,38.292209999999997,38.078290000000003,38.58663,38.368720000000003,38.406849999999999,38.716790000000003,39.055259999999997,38.578600000000002,38.512689999999999,38.965850000000003,38.70787,38.468299999999999,38.907910000000001,38.408520000000003,38.808839999999996,38.949550000000002,39.095399999999998,38.88899,285.584,6088.4790000000003,5802.8950000000004,50.516640000000002,41.078859999999999,51,51,762815.03760000004,553472.16736965766,-75.961060240000165,41,39,28730.862668310012,44,9.5242754169893722,10.131415416989372,453352.25584418658,6033.1860242218509,-15.951042344806844,-301.53504234480687,0,-285.58399999999983,-230.29102422185042,0.72247565937929337,0.72247565937929337,0.98554818400362521,0.98554818400362521,5671.6384603342249,131.25653966577556,0.91139542816537122,0.91139542816537122,44,1]
["2013-01-05T10:00:00","2013-01-05T10:00:00",38.420349999999999,38.429200000000002,38.145150000000001,38.518030000000003,38.753549999999997,38.232900000000001,38.351329999999997,38.606140000000003,38.412170000000003,38.214910000000003,38.721800000000002,38.527610000000003,38.56268,38.875039999999998,39.208289999999998,38.718170000000001,38.629829999999998,39.099609999999998,38.822249999999997,38.590359999999997,39.01587,38.485030000000002,38.884349999999998,39.29121,39.109389999999998,38.782780000000002,375.62470000000002,6175.8980000000001,5800.2939999999999,50.96499,41.02252,51,51,762815.03760000004,579869.03390214825,-68.068830010500633,42,39,30701.84029403,44,9.591485754026424,10.198625754026423,456551.44492448593,6401.8945722025665,-14.193594560034857,-389.81829456003487,0,-375.60400000000027,-601.60057220256658,0.71614994442737867,0.71614994442737867,0.98159877978331322,0.98159877978331322,6020.7798647595037,-220.48586475950378,0.90907706146853007,0.90907706146853007,44,1]
["2013-01-05T11:00:00","2013-01-05T11:00:00",38.512929999999997,38.497579999999999,38.259619999999998,38.648009999999999,38.877540000000003,38.395519999999998,38.495530000000002,38.755360000000003,38.563209999999998,38.365650000000002,38.842300000000002,38.650239999999997,38.683880000000002,38.98048,39.300260000000002,38.809350000000002,38.728360000000002,39.204819999999998,38.930480000000003,38.718110000000003,39.150869999999998,38.660809999999998,39.031460000000003,38.951070000000001,39.205390000000001,38.711390000000002,479.47629999999998,6277.32,5797.8440000000001,51.042479999999998,41.031390000000002,51,51,762815.03760000004,586955.67103673634,-47.57843324900103,45,41,31421.407739399987,44,9.7377170039135414,10.344857003913539,463512.00245865638,6453.547115154789,-9.7719893132814359,-489.24828931328142,0,-479.47599999999966,-655.70311515478897,0.70925535158421393,0.70925535158421393,0.9765571813500209,0.9765571813500209,6074.788221338009,-276.9442213380089,0.90616504595074177,0.90616504595074177,44,1]
["2013-01-05T12:00:00","2013-01-05T12:00:00",38.710979999999999,38.664990000000003,38.415709999999997,38.797750000000001,38.99868,38.50271,38.579740000000001,38.85472,38.663730000000001,38.48612,38.905299999999997,38.748080000000002,38.776290000000003,39.073990000000002,39.403109999999998,38.900370000000002,38.821939999999998,39.289490000000001,39.025730000000003,38.86721,39.276670000000003,38.775469999999999,39.05782,38.785620000000002,39.404649999999997,38.687260000000002,626.40250000000003,6419.0820000000003,5792.6790000000001,51.341799999999999,40.99586,51,51,762815.03760000004,602351.7805288278,7.4291336499991543,47,42,33205.718613539997,44,9.8594090047217158,10.466549004721713,469304.5001205958,6735.8436185450119,1.5070139896704373,-624.89548601032959,0,-626.40300000000025,-943.16461854501176,0.69933815601406379,0.69933815601406379,0.96997067361363865,0.96997067361363865,6345.1131024294818,-552.43410242948175,0.90035630702469394,0.90035630702469394,44,1]
["2013-01-05T13:00:00","2013-01-05T13:00:00",38.891089999999998,38.825490000000002,38.544240000000002,38.91225,39.10472,38.674289999999999,38.718150000000001,39.013260000000002,38.806820000000002,38.635210000000001,39.017879999999998,38.907049999999998,38.90775,39.18873,39.506489999999999,39.001269999999998,38.909320000000001,39.375039999999998,39.136949999999999,39.05247,39.452399999999997,38.904879999999999,39.176070000000003,38.810130000000001,39.257689999999997,38.849020000000003,758.74339999999995,6561.741,5802.9979999999996,51.69932,40.989240000000002,51,51,762815.03760000004,611669.88964668778,15.96016741899825,50,43,35138.385524639991,44,9.9861599463902238,10.593299946390225,475337.80163908098,7037.4169276833472,3.1964573979745832,-755.54694260202541,0,-758.74300000000039,-1234.4189276833476,0.68635847708991582,0.68635847708991582,0.96199263608919217,0.96199263608919217,6634.0773323639833,-831.07933236398367,0.89161766680080812,0.89161766680080812,44,1]
["2013-01-05T14:00:00","2013-01-05T14:00:00",39.021909999999998,38.917540000000002,38.728549999999998,39.138109999999998,39.300179999999997,38.828530000000001,38.848619999999997,39.146439999999998,38.950809999999997,38.778030000000001,39.102800000000002,39.038040000000002,39.022820000000003,39.301490000000001,39.637729999999998,39.127899999999997,39.028709999999997,39.511589999999998,39.333159999999999,39.282470000000004,39.662509999999997,39.105260000000001,39.340949999999999,38.942860000000003,39.285209999999999,38.880789999999998,962.19179999999994,6760.3220000000001,5798.13,52.05668,40.955089999999998,51,51,762815.03760000004,627167.8624076402,67.892253408000386,51,44,37525.161555990002,44,10.12839600905926,10.73553600905926,482108.18962664151,7409.8922519273392,13.406318897340647,-948.78548110265933,0,-962.19200000000001,-1611.7622519273391,0.66941110528370118,0.66941110528370118,0.95187537124230426,0.95187537124230426,6990.8314823450119,-1192.7014823450118,0.87907663883532905,0.87907663883532905,44,1]
["2013-01-05T15:00:00","2013-01-05T15:00:00",39.230809999999998,39.111719999999998,38.826160000000002,39.188580000000002,39.351689999999998,38.897030000000001,38.895200000000003,39.219169999999998,39.027630000000002,38.866300000000003,39.20326,39.164479999999998,39.184139999999999,39.478099999999998,39.814309999999999,39.304079999999999,39.198180000000001,39.692230000000002,39.482790000000001,39.413200000000003,39.79757,39.233440000000002,39.473970000000001,39.03633,39.353670000000001,38.899360000000001,1061.2439999999999,6858.79,5797.5460000000003,52.634880000000003,40.999070000000003,51,51,762815.03760000004,653806.05920794653,175.87466189999824,52,45,39903.788634949997,44,10.270354192451796,10.877494192451795,488865.35065557907,7770.6742897489003,34.248996403504258,-1026.9950035964957,0,-1061.2439999999997,-1973.1282897489,0.64866403870626499,0.64866403870626499,0.94071659356054149,0.94071659356054149,7336.9450590266242,-1539.3990590266239,0.86289015216195997,0.86289015216195997,44,1]
["2013-01-05T16:00:00","2013-01-05T16:00:00",39.334949999999999,39.195790000000002,38.953040000000001,39.317160000000001,39.527180000000001,39.10848,39.201889999999999,39.592759999999998,39.416179999999997,39.26191,39.594000000000001,39.53604,39.562190000000001,39.831189999999999,40.179340000000003,39.64752,39.52713,39.983170000000001,39.7378,39.610680000000002,39.940440000000002,39.333930000000002,39.457180000000001,39.046059999999997,39.364739999999998,38.949629999999999,962.35069999999996,6761.8190000000004,5799.4679999999998,52.603209999999997,41.078600000000002,51,51,762815.03760000004,649905.74320305535,185.40648586200004,53,46,38963.663432794987,44,10.29914292305831,10.90628292305831,490235.68439667113,7566.3894993749254,36.004255353501577,-926.34644464649841,0,-962.35100000000057,-1766.9214993749256,0.63008519708958521,0.63008519708958521,0.9305976568590647,0.9305976568590647,7145.1774555411776,-1345.7094555411777,0.84874027462330726,0.84874027462330726,44,1]
["2013-01-05T17:00:00","2013-01-05T17:00:00",39.42174,39.411479999999997,39.232640000000004,39.661499999999997,39.847610000000003,39.418559999999999,39.49089,39.833370000000002,39.660260000000001,39.504330000000003,39.872709999999998,39.790390000000002,39.793469999999999,40.065629999999999,40.396859999999997,39.866889999999998,39.751620000000003,40.205069999999999,39.936889999999998,39.798769999999998,40.133159999999997,39.57056,39.784930000000003,39.364739999999998,39.676920000000003,39.102539999999998,803.38710000000003,6602.1369999999997,5798.75,52.725720000000003,41.167870000000001,51,51,762815.03760000004,648458.71358933009,128.22058116000085,51,45,38153.254562725007,44,10.210660980588925,10.817800980588924,486023.97416531673,7473.219341089989,25.115040329662463,-778.27205967033751,0,-803.38699999999972,-1674.469341089989,0.6124784722344615,0.6124784722344615,0.92215019621342775,0.92215019621342775,7053.7911782969286,-1255.0411782969286,0.83554375667826064,0.83554375667826064,44,1]
["2013-01-05T18:00:00","2013-01-05T18:00:00",39.555030000000002,39.53642,39.373730000000002,39.858490000000003,40.13964,39.634160000000001,39.682450000000003,39.968330000000002,39.748220000000003,39.568300000000001,39.953009999999999,39.863430000000001,39.891800000000003,40.185879999999997,40.523890000000002,39.999420000000001,39.909399999999998,40.374549999999999,40.117739999999998,39.98639,40.347380000000001,39.776859999999999,39.994680000000002,39.602400000000003,39.974420000000002,39.493029999999997,712.74059999999997,6510.8710000000001,5798.13,52.281140000000001,41.241950000000003,51,51,762815.03760000004,608709.6668941353,22.094958600001679,46,42,35937.371017244994,44,9.9525583516880545,10.559698351688056,473738.37721136893,7221.735306108435,4.44005607789361,-708.30054392210639,0,-712.74099999999999,-1423.6053061084349,0.59750953472580015,0.59750953472580015,0.9146558609204346,0.9146558609204346,6806.5146977423092,-1008.3846977423091,0.82494078444963281,0.82494078444963281,44,1]
["2013-01-05T19:00:00","2013-01-05T19:00:00",39.78539,39.762390000000003,39.582520000000002,39.951000000000001,40.261369999999999,39.8018,39.88167,40.167990000000003,39.990400000000001,39.825420000000001,40.236199999999997,40.112430000000003,40.122459999999997,40.380270000000003,40.708799999999997,40.187469999999998,40.085680000000004,40.536879999999996,40.286369999999998,40.147489999999998,40.503300000000003,39.923479999999998,40.132660000000001,39.739460000000001,40.140320000000003,39.756399999999999,655.24019999999996,6458.35,5803.11,52.036749999999998,41.232109999999999,51,51,762815.03760000004,584540.46437224827,9.4977066990000942,45,41,34890.073371999992,44,9.8559985019852014,10.463138501985199,469142.16135554877,7079.9672635851994,1.9272946717853217,-653.31290532821458,0,-655.24000000000069,-1276.8572635851997,0.58408362481658871,0.58408362481658871,0.90776613764454495,0.90776613764454495,6669.1410737572114,-866.03107375721174,0.81583463335002238,0.81583463335002238,44,1]
["2013-01-05T20:00:00","2013-01-05T20:00:00",39.928469999999997,39.892829999999996,39.670909999999999,40.069670000000002,40.338949999999997,39.875909999999998,40.001710000000003,40.320210000000003,40.120269999999998,39.948419999999999,40.363549999999996,40.208350000000003,40.212110000000003,40.460940000000001,40.779539999999997,40.252400000000002,40.16386,40.619459999999997,40.367730000000002,40.215940000000003,40.56288,40.012360000000001,40.256819999999998,39.896380000000001,40.299129999999998,39.933869999999999,547.64520000000005,6348.6859999999997,5801.0410000000002,51.837359999999997,41.303959999999996,51,51,762815.03760000004,566602.05712788424,-1.4786420400004454,43,40,33436.624556200004,44,9.7455888973664209,10.35272889736642,463886.70189755142,6861.8992465885121,-0.30344847408862552,-547.94864847408871,0,-547.64499999999953,-1060.858246588512,0.57292890325816681,0.57292890325816681,0.90200775521455812,0.90200775521455812,6459.4803723114555,-658.43937231145537,0.80891126928620394,0.80891126928620394,44,1]
["2013-01-05T21:00:00","2013-01-05T21:00:00",40.137720000000002,40.169890000000002,39.932899999999997,40.318770000000001,40.524900000000002,40.036009999999997,40.110439999999997,40.392209999999999,40.187840000000001,40.008949999999999,40.447969999999998,40.293680000000002,40.301470000000002,40.562739999999998,40.854880000000001,40.335250000000002,40.245550000000001,40.69211,40.429369999999999,40.2746,40.641779999999997,40.104149999999997,40.356639999999999,40.006010000000003,40.408430000000003,40.011690000000002,507.03100000000001,6308.6220000000003,5801.59,51.62753,41.292409999999997,51,51,762815.03760000004,552910.01540458831,31.950558465000025,44,40,32600.182702320009,44,9.7170662301491131,10.324206230149112,462529.03268288408,6709.881754468548,6.5761738591154426,-500.45482614088456,0,-507.03200000000015,-908.29175446854788,0.56337838918384198,0.56337838918384198,0.89667641071174864,0.89667641071174864,6315.2908757517453,-513.70087575174512,0.80350980283038365,0.80350980283038365,44,1]
["2013-01-05T22:00:00","2013-01-05T22:00:00",40.12838,40.244959999999999,40.018990000000002,40.391559999999998,40.581200000000003,40.091999999999999,40.183669999999999,40.463679999999997,40.272170000000003,40.093600000000002,40.528329999999997,40.369120000000002,40.394539999999999,40.668190000000003,40.991329999999998,40.462290000000003,40.37135,40.830399999999997,40.561079999999997,40.398150000000001,40.768590000000003,40.239719999999998,40.486899999999999,40.14237,40.526600000000002,40.154490000000003,289.4957,6086.1930000000002,5797.4769999999999,51.448419999999999,41.208710000000004,51,51,762815.03760000004,537587.20938635012,-3.7793663635003973,43,40,31160.425662014983,44,9.6679705150747122,10.275110515074712,460192.09341907821,6446.1151621073559,-0.78183241407438053,-290.27753241407436,0,-288.71600000000035,-648.63816210735604,0.55655808297069664,0.55655808297069664,0.89364061719285215,0.89364061719285215,6065.2244306860212,-267.74743068602129,0.80069448980728197,0.80069448980728197,44,1]
["2013-01-05T23:00:00","2013-01-05T23:00:00",40.352879999999999,40.415840000000003,40.144680000000001,40.508240000000001,40.696129999999997,40.176729999999999,40.254440000000002,40.514139999999998,40.306620000000002,40.112850000000002,40.553649999999998,40.39152,40.409730000000003,40.682090000000002,40.996859999999998,40.476399999999998,40.376139999999999,40.829819999999998,40.556130000000003,40.387889999999999,40.761310000000002,40.220309999999998,40.468130000000002,40.115250000000003,40.503729999999997,40.121099999999998,279.54899999999998,6068.0389999999998,5799.5619999999999,50.832210000000003,41.231999999999999,51,51,762815.03760000004,509845.17650899495,32.396933610000076,42,39,29127.224344095015,44,9.5377913501336415,10.144931350133641,453995.60964408447,6107.750374238768,6.7933827488365299,-272.75561725116347,0,-268.47699999999986,-308.18837423876812,0.55331754116105214,0.55331754116105214,0.89081763288795468,0.89081763288795468,5742.2220690948925,57.339930905107394,0.80129740821365947,0.80129740821365947,44,1]
["2013-01-06","2013-01-06",40.38523,40.470230000000001,40.182310000000001,40.553519999999999,40.714970000000001,40.200229999999998,40.283230000000003,40.54768,40.332090000000001,40.130240000000001,40.572879999999998,40.409849999999999,40.440950000000001,40.711060000000003,41.0349,40.522179999999999,40.422870000000003,40.889200000000002,40.624020000000002,40.449570000000001,40.826450000000001,40.289709999999999,40.536389999999997,40.179729999999999,40.561369999999997,40.169199999999996,235.10939999999999,6036.9960000000001,5804.1949999999997,50.759160000000001,41.270440000000001,51,51,762815.03760000004,504078.47790034796,25.395341841000409,36,34,28641.682342560001,44,9.2169993678812965,9.8241393678812976,438726.02088865975,6214.9689284710967,5.5105443382140562,-229.59885566178593,0,-232.80100000000039,-410.77392847109695,0.5489983318696231,0.5489983318696231,0.88836977489950708,0.88836977489950708,5830.8786693723277,-26.68366937232804,0.80101683453384642,0.80101683453384642,44,1]
["2013-01-06T01:00:00","2013-01-06T01:00:00",40.50029,40.544179999999997,40.24494,40.607849999999999,40.788139999999999,40.258980000000001,40.355649999999997,40.63053,40.416049999999998,40.199530000000003,40.667479999999998,40.479050000000001,40.503959999999999,40.779580000000003,41.094329999999999,40.581539999999997,40.485529999999997,40.927320000000002,40.668300000000002,40.471469999999997,40.860019999999999,40.33,40.597050000000003,40.236629999999998,40.627800000000001,40.230670000000003,159.91999999999999,5951.3069999999998,5803.433,50.504130000000004,41.262120000000003,51,51,762815.03760000004,489013.18603376276,21.558815199999696,39,37,27501.019403535,44,9.360643761660544,9.9677837616605434,445563.44495590474,5875.8820661831105,4.6062676347754188,-155.31373236522458,0,-147.8739999999998,-72.449066183110517,0.54823654379563758,0.54823654379563758,0.88681490807254459,0.88681490807254459,5517.9807389709222,285.45226102907782,0.80401831046170091,0.80401831046170091,44,1]
["2013-01-06T02:00:00","2013-01-06T02:00:00",40.470689999999998,40.52214,40.250639999999997,40.638959999999997,40.830719999999999,40.294139999999999,40.404870000000003,40.663879999999999,40.446359999999999,40.231160000000003,40.714080000000003,40.51558,40.552819999999997,40.831620000000001,41.153709999999997,40.648020000000002,40.548079999999999,40.987639999999999,40.723619999999997,40.506999999999998,40.906309999999998,40.380159999999997,40.660969999999999,40.311010000000003,40.709530000000001,40.31071,90.817149999999998,5827.7020000000002,5799.3289999999997,50.151609999999998,41.278060000000004,51,51,762815.03760000004,468423.47781951306,7.2644638284998795,34,33,25856.202541049985,44,9.0611675066498059,9.6683075066498052,431308.47753458214,5707.0355496848815,1.6034277753211463,-89.213722224678847,0,-28.373000000000502,92.293450315118207,0.54920699177324617,0.54920699177324617,0.88651657140429052,0.88651657140429052,5348.6512553032135,450.67774469678625,0.80875710074856211,0.80875710074856211,44,1]
["2013-01-06T03:00:00","2013-01-06T03:00:00",40.500749999999996,40.561669999999999,40.252569999999999,40.64132,40.831150000000001,40.273919999999997,40.392760000000003,40.632649999999998,40.431950000000001,40.210540000000002,40.736359999999998,40.520629999999997,40.570740000000001,40.859090000000002,41.170659999999998,40.665570000000002,40.559890000000003,41.017270000000003,40.725140000000003,40.478499999999997,40.898069999999997,40.366500000000002,40.653849999999998,40.30294,40.693890000000003,40.305889999999998,175.63399999999999,5672.4489999999996,5803.3710000000001,50.016150000000003,41.284910000000004,51,51,762815.03760000004,462205.05845316063,17.112020619999864,36,35,24763.756803379998,44,9.1456091069952592,9.7527491069952585,435327.86886123545,5415.441774006892,3.7421281447315051,-171.89187185526848,0,130.92200000000048,387.92922599310805,0.55328599338749829,0.55328599338749829,0.8878931911935678,0.8878931911935678,5078.3131057104583,725.05789428954176,0.81638094582922593,0.81638094582922593,44,1]
["2013-01-06T04:00:00","2013-01-06T04:00:00",40.572870000000002,40.623289999999997,40.300020000000004,40.68365,40.864170000000001,40.309609999999999,40.434199999999997,40.663490000000003,40.462800000000001,40.209949999999999,40.754989999999999,40.504440000000002,40.553739999999998,40.841929999999998,41.150460000000002,40.654960000000003,40.553870000000003,41.009410000000003,40.715609999999998,40.440570000000001,40.877510000000001,40.348880000000001,40.646540000000002,40.292999999999999,40.685740000000003,40.28539,201.79060000000001,5615.5839999999998,5801.2780000000002,49.801909999999999,41.192300000000003,51,51,762815.03760000004,452983.10064515984,29.005380844000221,34,32,24173.994081119992,44,8.9429571981661926,9.550097198166192,425681.70723775844,5406.2640680147761,6.48675381113262,-195.3038461888674,0,185.69400000000041,395.01393198522419,0.55743948933020526,0.55743948933020526,0.8898457280869092,0.8898457280869092,5062.5650356232773,738.71296437672299,0.8241483713601272,0.8241483713601272,44,1]
["2013-01-06T05:00:00","2013-01-06T05:00:00",40.592570000000002,40.634680000000003,40.306719999999999,40.687730000000002,40.867840000000001,40.304780000000001,40.431570000000001,40.668010000000002,40.46367,40.213839999999998,40.762900000000002,40.501690000000004,40.55527,40.847700000000003,41.154620000000001,40.661839999999998,40.560600000000001,41.021090000000001,40.727980000000002,40.44567,40.88776,40.360990000000001,40.659550000000003,40.311709999999998,40.698520000000002,40.295740000000002,115.07380000000001,5760.0029999999997,5801.1289999999999,49.912030000000001,41.17859,51,51,762815.03760000004,457732.11855836422,17.078678026999995,35,33,25152.320300160005,44,9.0371651222354572,9.6443051222354566,430165.97223696398,5566.4182207480262,3.7796538618020441,-111.29414613819796,0,41.126000000000204,234.71077925197369,0.55990742828221451,0.55990742828221451,0.89027816011096794,0.89027816011096794,5215.9943057317832,585.13469426821666,0.83030095075489907,0.83030095075489907,44,1]
["2013-01-06T06:00:00","2013-01-06T06:00:00",40.594769999999997,40.643630000000002,40.324979999999996,40.7102,40.891190000000002,40.321860000000001,40.443739999999998,40.66724,40.474800000000002,40.21801,40.779139999999998,40.511629999999997,40.577579999999998,40.886319999999998,41.190249999999999,40.703650000000003,40.607590000000002,41.073410000000003,40.773110000000003,40.479790000000001,40.928240000000002,40.409149999999997,40.706240000000001,40.362259999999999,40.747709999999998,40.34666,115.3848,5718.0039999999999,5800.4690000000001,50.010620000000003,41.24729,51,51,762815.03760000004,460001.19427172968,14.314061363999825,34,32,25054.377996660009,44,8.9729782896861074,9.5801182896861068,427110.70093728765,5584.4062445706559,3.1904816665951299,-112.19431833340487,0,82.465000000000146,216.06275542934418,0.56217928683043261,0.56217928683043261,0.89114526381334602,0.89114526381334602,5230.4944968442387,569.97450315576134,0.83629412363972888,0.83629412363972888,44,1]
["2013-01-06T07:00:00","2013-01-06T07:00:00",40.651470000000003,40.703510000000001,40.3872,40.778579999999998,40.966079999999998,40.392940000000003,40.529139999999998,40.748930000000001,40.551769999999998,40.300310000000003,40.858040000000003,40.585929999999998,40.641669999999998,40.94021,41.240929999999999,40.758040000000001,40.653680000000001,41.122979999999998,40.815809999999999,40.521859999999997,40.96819,40.45232,40.754640000000002,40.412170000000003,40.808810000000001,40.398670000000003,172.97630000000001,5638.63,5801.5060000000003,50.051020000000001,41.095320000000001,51,51,762815.03760000004,459448.56223832961,21.864204320000052,34,31,25248.939345499999,44,8.9187658316815508,9.5259058316815501,424530.20645816089,5661.9805524683334,4.9029663369640817,-168.07333366303592,0,162.8760000000002,139.52544753166694,0.56364637022497177,0.56364637022497177,0.89285787380095938,0.89285787380095938,5301.1104228064696,500.3955771935307,0.84155568742604003,0.84155568742604003,44,1]
["2013-01-06T08:00:00","2013-01-06T08:00:00",40.68524,40.743479999999998,40.415149999999997,40.806199999999997,40.983240000000002,40.414430000000003,40.553879999999999,40.766939999999998,40.572200000000002,40.318150000000003,40.874119999999998,40.595500000000001,40.665649999999999,40.959359999999997,41.264800000000001,40.776870000000002,40.69455,41.163449999999997,40.865699999999997,40.57403,41.01511,40.502479999999998,40.806159999999998,40.462420000000002,40.852429999999998,40.44059,93.413870000000003,5807.0379999999996,5801.6180000000004,50.325580000000002,41.137909999999998,51,51,762815.03760000004,470522.14675599901,11.426851647750004,34,31,26676.574410730012,44,8.9674481874058944,9.5745881874058938,426847.46995812969,{"$f":"AO134*1000/(500*AQ134)","v":5949.6467341055286},2.5485180196074411,{"$f":"AU134-AC134","v":-90.86535198039256},0,{"$f":"AE134-AD134","v":-5.4199999999991633},{"$f":"AE134-AT134","v":-148.0287341055282},0.56208987639848473,0.56208987639848473,0.89280088353761267,0.89280088353761267,{"$f":"AO134*1000/(500*AR134)","v":5572.3700881087543},{"$f":"AE134-BD134","v":229.24791189124608},0.84396618537260348,0.84396618537260348,44,1]
["2013-01-06T09:00:00","2013-01-06T09:00:00",40.75215,40.771769999999997,40.443040000000003,40.833770000000001,41.010579999999997,40.462449999999997,40.574689999999997,40.792569999999998,40.602469999999997,40.366459999999996,40.894390000000001,40.645420000000001,40.703020000000002,40.989939999999997,41.296300000000002,40.798470000000002,40.700769999999999,41.161850000000001,40.870220000000003,40.588790000000003,41.014589999999998,40.49841,40.787799999999997,40.443429999999999,40.833539999999999,40.429189999999998,133.78139999999999,5897.5619999999999,5803.8810000000003,50.383119999999998,41.170430000000003,51,51,{"$f":"3.1416*(138/2)^2*AI135","v":762815.03760000004},{"$f":"62.4*AJ135*(AF135-AB135)/1000","v":473803.66720238869},{"$f":"500*AC135*(C135-AB135)/1000","v":21.603020472000129},38,34,27166.205230889984,44,{"$f":"19.5286-0.30357*AP135+0.0000341*AO135+0.060847*AN135","v":9.1666855983733484},{"$f":"19.5286-0.30357*42+0.0000341*AO135+0.060847*AN135","v":9.7738255983733495},{"$f":"62.4*AJ135*AQ135/1000","v":436331.10264996992},5927.1598091486194,{"$f":"AL135*1000/(500*AQ135)","v":4.71337655037141},-129.06802344962858,0,-93.680999999999585,-123.27880914861908,0.56079362329913918,{"$f":"IF(AZ135>1,1,IF(AZ135<0,0,AZ135))","v":0.56079362329913918},0.89181584574045647,{"$f":"IF(BB135>1,1,BB135)","v":0.89181584574045647},5558.9707341230305,244.91026587696979,0.84654136997567542,{"$f":"IF(BF135>1,1,IF(BF135<0,0,BF135))","v":0.84654136997567542},44,1]
["2013-01-06T10:00:00","2013-01-06T10:00:00",40.870609999999999,40.84198,40.511220000000002,40.881250000000001,41.054209999999998,40.52957,40.621789999999997,40.859990000000003,40.659109999999998,40.444699999999997,40.91863,40.71519,40.753300000000003,41.022239999999996,41.327350000000003,40.821210000000001,40.73171,41.189349999999997,40.909739999999999,40.697809999999997,41.097059999999999,40.571249999999999,40.829990000000002,40.48339,40.867939999999997,40.472540000000002,312.3947,6111.2749999999996,5799.7709999999997,50.54101,41.196460000000002,51,51,762815.03760000004,479255.73206936696,62.17747911449954,43,37,28553.557400624995,44,9.3965353073613134,10.003675307361313,447271.87026877975,6077.4650371942798,13.234128767821318,-299.16057123217865,0,-311.50399999999991,-277.6940371942801,{"$f":"IF(AZ135>1,1+AY136*60/$BK$7,IF(AZ135<0,AY136*60/$BK$7,AZ135+AY136*60/$BK$7))","v":0.55787372361103527},0.55787372361103527,{"$f":"IF(BB135>1,1+AX136*60/$BK$7,BB135+AX136*60/$BK$7)","v":0.88854044076009397},0.88854044076009397,5708.613389243761,91.157610756238682,{"$f":"IF(BF135>1,1+BE136*60/$BK$7,IF(BF135<0,BE136*60/$BK$7,BF135+BE136*60/$BK$7))","v":0.84749987481756806},0.84749987481756806,44,1]
["2013-01-06T11:00:00","2013-01-06T11:00:00",41.030209999999997,40.882710000000003,40.560339999999997,40.89575,41.051400000000001,40.555770000000003,40.593780000000002,40.86168,40.665129999999998,40.476790000000001,40.88729,40.761049999999997,40.779800000000002,41.08379,41.391590000000001,40.868290000000002,40.774540000000002,41.23075,40.947769999999998,40.799509999999998,41.156779999999998,40.613010000000003,40.840769999999999,40.485970000000002,40.870280000000001,40.488709999999998,475.07510000000002,6273.1149999999998,5798.04,51.032150000000001,41.261450000000004,51,51,762815.03760000004,501864.14179408085,128.62658332499981,48,39,30646.362365249995,44,9.5895939566550261,10.196733956655025,456461.39601594704,6391.5870690191023,26.826283554109192,-448.24881644589084,0,-475.07499999999982,-593.54706901910231,0.55163268970474599,0.55163268970474599,0.88354511800004687,0.88354511800004687,6011.0153889517269,-212.97538895172693,0.84526047933735871,0.84526047933735871,44,1]
["2013-01-06T12:00:00","2013-01-06T12:00:00",41.127409999999998,40.900620000000004,40.569339999999997,40.950940000000003,41.096490000000003,40.62341,40.627589999999998,40.907040000000002,40.709339999999997,40.542369999999998,40.904429999999998,40.811070000000001,40.808680000000003,41.107570000000003,41.422490000000003,40.896479999999997,40.796610000000001,41.260649999999998,40.97916,40.8536,41.194920000000003,40.6404,40.866129999999998,40.500999999999998,40.893659999999997,40.512880000000003,589.14790000000005,6389.5439999999999,5800.3969999999999,51.477559999999997,41.305689999999998,51,51,762815.03760000004,521915.02187585051,181.02452949349851,51,41,32496.805463639994,44,9.7743880663101237,10.381528066310125,465257.53249992733,6649.3790185491753,37.040585715528294,-552.10731428447173,0,-589.14699999999993,-848.98201854917534,0.54270580615977004,0.54270580615977004,0.87735034997791672,0.87735034997791672,6260.505246640485,-460.10824664048505,0.84042252912627924,0.84042252912627924,44,1]
["2013-01-06T13:00:00","2013-01-06T13:00:00",41.128410000000002,40.868560000000002,40.531390000000002,40.965479999999999,41.104489999999998,40.652880000000003,40.646549999999998,40.945999999999998,40.751840000000001,40.593989999999998,40.916629999999998,40.850189999999998,40.83276,41.102710000000002,41.415860000000002,40.888559999999998,40.796759999999999,41.246510000000001,40.985419999999998,40.850180000000002,41.203009999999999,40.65316,40.880989999999997,40.525039999999997,40.939120000000003,40.552120000000002,833.85649999999998,6628.1120000000001,5794.2560000000003,51.877420000000001,41.27299,51,51,762815.03760000004,539080.41066867183,240.27158119250007,53,41,35143.674868080008,44,9.8646463130015292,10.47178631300153,469553.7942053689,7125.176869597627,48.713673773751815,-785.14282622624819,0,-833.85599999999977,-1330.9208695976267,0.5287114277737831,0.5287114277737831,0.8685825136249159,0.8685825136249159,6712.06875649218,-917.81275649217969,0.83077190353670505,0.83077190353670505,44,1]
["2013-01-06T14:00:00","2013-01-06T14:00:00",41.284170000000003,40.979309999999998,40.673850000000002,41.06673,41.174840000000003,40.695399999999999,40.667549999999999,40.956949999999999,40.754339999999999,40.589950000000002,40.866680000000002,40.818399999999997,40.819809999999997,41.075209999999998,41.409080000000003,40.889769999999999,40.680079999999997,41.187060000000002,41.023119999999999,40.89667,41.235770000000002,40.685319999999997,40.913229999999999,40.553809999999999,40.942549999999997,40.567140000000002,1258.8979999999999,7057.4970000000003,5798.5990000000002,54.380839999999999,42.42944,51,51,762815.03760000004,657527.40049745538,451.33381647000073,55,42,42173.484822899998,44,10.165209832460892,10.77234983246089,483860.51504297799,8297.6122515889529,88.799704857786978,-1170.0982951422129,0,-1258.8980000000001,-2499.0132515889527,0.50243478140569042,0.50243478140569042,0.85534544193733442,0.85534544193733442,7829.9508424459837,-2031.3518424459835,0.80941262743875408,0.80941262743875408,44,1]
["2013-01-06T15:00:00","2013-01-06T15:00:00",41.181420000000003,40.949559999999998,40.611530000000002,40.981549999999999,41.135759999999998,40.696539999999999,40.638579999999997,40.944299999999998,40.760669999999998,40.60933,40.868639999999999,40.834490000000002,40.833860000000001,41.094560000000001,41.43045,40.901389999999999,40.75103,41.190689999999996,41.010060000000003,40.903660000000002,41.24859,40.698439999999998,40.909790000000001,40.546689999999998,40.936950000000003,40.55818,1226.4079999999999,7024.2380000000003,5797.83,53.124769999999998,42.112130000000001,51,51,762815.03760000004,598165.390577276,382.17326096000164,57,43,38677.702184159993,44,10.106850644479856,10.713990644479857,481082.63763371669,7653.759523058734,75.626577339150941,-1150.7814226608489,0,-1226.4080000000004,-1855.929523058734,0.48292003744404505,0.48292003744404505,0.84244999638557128,0.84244999638557128,7220.0365797571076,-1422.2065797571076,0.79445839727015033,0.79445839727015033,44,1]
["2013-01-06T16:00:00","2013-01-06T16:00:00",44.719059999999999,40.968559999999997,40.648699999999998,40.997810000000001,41.140189999999997,40.717570000000002,40.68394,40.990049999999997,40.796959999999999,40.648910000000001,40.918909999999997,40.866259999999997,40.875639999999997,41.130490000000002,41.460799999999999,40.928350000000002,40.805500000000002,41.227379999999997,41.040300000000002,40.945639999999997,41.27261,40.718690000000002,40.92559,40.562130000000003,40.949869999999997,40.568010000000001,1297.5029999999999,7092.7950000000001,5795.2920000000004,53.241700000000002,41.846420000000002,49,49,732900.72239999997,579605.92912395613,2692.9999140749987,56,43,40412.192503799997,44,10.165996764379582,10.773136764379579,464921.58164586313,7950.4633811018739,529.80538485137902,-767.69761514862091,0,-1297.5029999999997,-2155.1713811018735,0.46025882257940187,0.46025882257940187,0.82880700050675338,0.82880700050675338,7502.400347764883,-1707.1083477648826,0.77650847950252133,0.77650847950252133,44,0.9863570041211821]
["2013-01-06T17:00:00","2013-01-06T17:00:00",50.154620000000001,41.133319999999998,40.718429999999998,41.025449999999999,41.173720000000003,40.720440000000004,40.718690000000002,41.00253,40.806469999999997,40.650669999999998,40.951610000000002,40.875160000000001,40.898049999999998,41.186039999999998,41.506230000000002,40.974730000000001,40.854329999999997,41.276670000000003,41.060679999999998,40.961779999999997,41.279600000000002,40.733510000000003,40.946280000000002,40.58708,40.971350000000001,40.59657,1046.4559999999999,6849.1040000000003,5802.6480000000001,53.361449999999998,42.248869999999997,49,49,732900.72239999997,583776.32185699686,5001.0393854000004,54,42,38055.608064160006,44,10.024790234987858,10.631930234987857,458463.78272017854,7592.3001224186901,997.7344698836099,-48.721530116389999,0,-1046.4560000000001,-1789.6521224186899,0.44144097280897676,0.44144097280897676,0.81780371581657207,0.81780371581657207,7158.7392360656258,-1356.0912360656257,0.76224943952731938,0.76224943952731938,44,0.9753537194310008]
["2013-01-06T18:00:00","2013-01-06T18:00:00",52.162689999999998,41.268300000000004,40.772779999999997,41.092039999999997,41.211590000000001,40.712179999999996,40.733029999999999,41.014189999999999,40.819659999999999,40.643770000000004,40.991390000000003,40.877870000000001,40.902859999999997,41.163029999999999,41.480119999999999,40.950769999999999,40.825290000000003,41.238100000000003,41.026009999999999,40.918570000000003,41.252740000000003,40.716830000000002,40.933810000000001,40.571260000000002,40.961750000000002,40.593389999999999,952.28689999999995,6754.0209999999997,5801.7330000000002,52.94923,41.718780000000002,49,49,732900.72239999997,565069.6934599902,5508.6464160849982,48,38,37925.347569724989,44,9.7769603521276238,10.384100352127623,447129.77742891078,7758.1060378283782,1126.8627912327022,174.57589123270225,1,-952.28799999999956,-1956.3730378283781,0.42087008450080099,0.42087008450080099,0.80779058963540118,0.80779058963540118,7304.5032855358286,-1502.7702855358284,0.74644809740142426,0.74644809740142426,44,0.9653405932498299]
["2013-01-06T19:00:00","2013-01-06T19:00:00",52.816890000000001,45.322069999999997,40.710459999999998,41.062690000000003,41.209769999999999,40.700899999999997,40.734720000000003,41.002879999999998,40.795259999999999,40.616999999999997,40.98498,40.850720000000003,40.872540000000001,41.14499,41.4724,40.960389999999997,40.851849999999999,41.262819999999998,41.051369999999999,40.925139999999999,41.262650000000001,40.724850000000004,40.939869999999999,40.577199999999998,40.961620000000003,40.590580000000003,759.02359999999999,6557.6409999999996,5798.6170000000002,52.773380000000003,41.858400000000003,47,47,702986.40720000002,534414.99082209636,4640.0289154579996,47,38,35788.260181089994,44,9.7040856721751698,10.311225672175169,425682.8360830294,7375.9159574831046,956.30419437917794,197.28059437917796,1,-759.02399999999943,-1577.2989574831045,0.40428508764406479,0.40428508764406479,0.79980959744969993,0.79980959744969993,6941.6112727829395,-1142.9942727829393,0.73442973123726885,0.73442973123726885,44,0.95735960106412865]
["2013-01-06T20:00:00","2013-01-06T20:00:00",53.15878,49.675310000000003,40.720480000000002,41.052810000000001,41.222969999999997,40.719940000000001,40.76634,41.024880000000003,40.812530000000002,40.630800000000001,41.018999999999998,40.86889,40.898910000000001,41.181930000000001,41.507309999999997,40.995449999999998,40.87923,41.291269999999997,41.070050000000002,40.939810000000001,41.277729999999998,40.73565,40.945819999999998,40.584269999999997,40.97166,40.59628,680.29100000000005,6478.4660000000003,5798.1750000000002,52.222580000000001,41.377249999999997,47,47,702986.40720000002,510003.36604023213,4273.0778437500003,45,37,35130.550831890017,44,9.6208107833674497,10.227950783367451,422029.8705137113,7303.0333145360373,888.29890535573952,208.00790535573947,1,-680.29100000000017,-1504.8583145360371,0.38846179029259814,0.38846179029259814,0.79265646770017573,0.79265646770017573,6869.5189439156911,-1071.3439439156909,0.7231647545769927,0.7231647545769927,44,0.95020647131460445]
["2013-01-06T21:00:00","2013-01-06T21:00:00",53.237290000000002,51.363109999999999,40.737290000000002,41.07,41.235799999999998,40.736199999999997,40.783549999999998,41.04701,40.837940000000003,40.656759999999998,41.04468,40.889760000000003,40.917619999999999,41.1965,41.516199999999998,40.991709999999998,40.878189999999996,41.28913,41.066380000000002,40.927930000000003,41.284550000000003,40.747120000000002,40.978819999999999,40.621409999999997,40.999870000000001,40.623840000000001,566.27189999999996,6363.9279999999999,5797.6559999999999,51.98771,41.346600000000002,47,47,702986.40720000002,498491.51933492266,3571.3211485274992,45,37,33859.628940039991,44,9.5774723468553642,10.184612346855364,420128.77141080797,7070.6816399542731,745.7752983646244,179.50339836462445,1,-566.27199999999993,-1273.0256399542732,0.37507616917301256,0.37507616917301256,0.78670222592787153,0.78670222592787153,6649.1738294770958,-851.5178294770958,0.71421120746512012,0.71421120746512012,44,0.94425222954230026]
["2013-01-06T22:00:00","2013-01-06T22:00:00",53.206049999999998,52.100479999999997,40.767319999999998,41.101309999999998,41.27411,40.768949999999997,40.827950000000001,41.091180000000001,40.891159999999999,40.706380000000003,41.106200000000001,40.946390000000001,40.9589,41.225439999999999,41.529640000000001,40.997540000000001,40.891159999999999,41.303710000000002,41.074210000000001,40.932830000000003,41.282170000000001,40.752450000000003,40.983739999999997,40.626370000000001,41.00882,40.621720000000003,358.79379999999998,6159.6459999999997,5800.8519999999999,51.539729999999999,41.396819999999998,47,47,702986.40720000002,478933.26771723694,2257.5897905769989,42,35,31238.36750493,44,9.3663933319181147,9.9735333319181123,410869.50508201431,6670.3087085779671,482.06170947012203,123.26790947012205,1,-358.79399999999987,-869.45670857796722,0.36593399817846395,0.36593399817846395,0.78292957564240429,0.78292957564240429,6264.2528911912168,-463.40089119121694,0.70933863572635547,0.70933863572635547,44,0.94047957925683301]
["2013-01-06T23:00:00","2013-01-06T23:00:00",53.094569999999997,52.629930000000002,41.721420000000002,41.168460000000003,41.324840000000002,40.807009999999998,40.871720000000003,41.131,40.923340000000003,40.730649999999997,41.158639999999998,40.98321,40.992829999999998,41.270380000000003,41.566879999999998,41.004959999999997,40.894240000000003,41.300460000000001,41.069989999999997,40.917000000000002,41.269219999999997,40.744329999999998,40.989089999999997,40.625459999999997,41.013390000000001,40.609670000000001,270.47629999999998,6072.991,5803.6459999999997,51.39226,41.341070000000002,47,47,702986.40720000002,472992.88635522436,1688.4347789349993,43,36,30520.393204644995,44,9.4027574082783953,10.009897408278395,412464.66444885393,6491.7963698125759,359.13609287600337,88.659792876003394,1,-269.34500000000025,-688.15036981257617,0.35869822865857848,0.35869822865857848,0.78009746448352435,0.78009746448352435,6098.0431586449613,-294.39715864496156,0.70624310591091077,0.70624310591091077,44,0.93764746809795307]
["2013-01-07","2013-01-07",52.775379999999998,52.670740000000002,43.927709999999998,41.164169999999999,41.336799999999997,40.814970000000002,40.896819999999998,41.141150000000003,40.923679999999997,40.72757,41.168349999999997,40.97777,40.996839999999999,41.24635,41.54927,41.018410000000003,40.904690000000002,41.318579999999997,41.080730000000003,40.891550000000002,41.260359999999999,40.753819999999997,40.98921,40.636279999999999,41.025370000000002,40.622500000000002,185.8871,5967.9520000000002,5799.1540000000005,51.048490000000001,41.335250000000002,45,45,673072.09200000006,437888.43698939536,1129.5318099239996,38,33,28984.075042239998,44,9.1678279589403857,9.7749679589403851,385046.01054941397,6322.9971530988378,246.41208691585231,60.52498691585231,1,-168.79799999999977,-523.84315309883732,0.35319011809631046,0.35319011809631046,0.77832258579857894,0.77832258579857894,5930.2649715041916,-131.11097150419118,0.70486449912241045,0.70486449912241045,44,0.93587258941300766]
["2013-01-07T01:00:00","2013-01-07T01:00:00",52.632809999999999,52.471119999999999,46.691470000000002,41.167960000000001,41.345329999999997,40.809100000000001,40.90204,41.131,40.930639999999997,40.711730000000003,41.199840000000002,40.989820000000002,41.020609999999998,41.29907,41.609769999999997,41.079990000000002,40.976410000000001,41.371540000000003,41.118389999999998,40.879280000000001,41.251390000000001,40.748690000000003,41.007939999999998,40.657249999999998,41.042169999999999,40.641080000000002,159.32730000000001,5944.875,5793.4570000000003,50.616599999999998,41.273240000000001,45,45,673072.09200000006,418968.83278772107,955.30498161449987,34,31,27772.553639999991,44,9.0048210791240013,9.6119610791240007,378199.77073704946,6168.3743399156428,212.17633825711346,52.849038257113449,1,-151.41799999999967,-374.91733991564251,0.34924793397545179,0.34924793397545179,0.77673045448945766,0.77673045448945766,5778.7486677029028,14.708332297097513,0.70501915442333352,0.70501915442333352,44,0.93428045810388638]
["2013-01-07T02:00:00","2013-01-07T02:00:00",52.551969999999997,52.377589999999998,47.99418,41.34243,41.45008,40.83381,40.93967,41.157409999999999,40.94746,40.722799999999999,41.225879999999997,40.99409,41.038060000000002,41.327530000000003,41.624450000000003,41.095230000000001,40.983789999999999,41.36721,41.101909999999997,40.866729999999997,41.251609999999999,40.74559,41.017879999999998,40.6629,41.051639999999999,40.650379999999998,206.58410000000001,5786.1450000000004,5800.0010000000002,50.456910000000001,41.285690000000002,45,45,673072.09200000006,411871.30373131158,1229.3396293595001,33,30,26533.004373449996,44,8.9017054491346457,9.508845449134645,373868.94536265184,5961.3305618934683,276.20316946771288,69.619069467712876,1,13.855999999999767,-161.32956189346805,0.34755158448874995,0.34755158448874995,0.77687614767929758,0.77687614767929758,5580.6994688013647,219.30153119863553,0.70732506807930307,0.70732506807930307,44,0.9344261512937263]
["2013-01-07T03:00:00","2013-01-07T03:00:00",52.472740000000002,52.307270000000003,49.013129999999997,41.212739999999997,41.397489999999998,40.82938,40.92998,41.153129999999997,40.951920000000001,40.715269999999997,41.225909999999999,40.985889999999998,41.025539999999999,41.304090000000002,41.603549999999998,41.092700000000001,40.974629999999998,41.378039999999999,41.120220000000003,40.87453,41.255220000000001,40.748019999999997,41.018949999999997,40.667180000000002,41.061300000000003,40.659089999999999,105.48090000000001,5771.2219999999998,5801.2780000000002,50.062550000000002,41.20485,45,45,673072.09200000006,394942.48524047132,623.05721714250024,35,33,25559.8765547,44,9.051062790515271,9.6582027905152703,380141.90867549344,5647.9282369987613,137.676034641017,32.195134641016992,1,30.056000000000495,153.3497630012389,0.34916402791635176,0.34916402791635176,0.77719218077065366,0.77719218077065366,5292.8846306273035,508.39336937269672,0.71267072712068491,0.71267072712068491,44,0.93474218438508239]
["2013-01-07T04:00:00","2013-01-07T04:00:00",52.397379999999998,52.2376,50.003309999999999,41.174320000000002,41.351260000000003,40.795110000000001,40.916879999999999,41.135800000000003,40.938920000000003,40.699689999999997,41.220759999999999,40.963949999999997,41.010950000000001,41.284239999999997,41.584220000000002,41.07432,40.973959999999998,41.387990000000002,41.137929999999997,40.881219999999999,41.269219999999997,40.766889999999997,41.03416,40.675690000000003,41.066299999999998,40.661389999999997,101.8466,5831.7039999999997,5798.7839999999997,50.370660000000001,41.220500000000001,45,45,673072.09200000006,407786.41305123339,597.63533956700007,33,30,26680.512336319996,44,8.9067354706685133,9.5138754706685127,374080.20475072804,5991.0867285064751,134.19851561441811,32.351915614418118,1,-32.920000000000073,-192.30272850647543,0.34714200150677949,0.34714200150677949,0.77684603326707891,0.77684603326707891,5608.7579490769258,190.02605092307385,0.71466881470091514,0.71466881470091514,44,0.93439603688150763]
["2013-01-07T05:00:00","2013-01-07T05:00:00",52.306440000000002,52.17454,50.918399999999998,41.170180000000002,41.359850000000002,40.797829999999998,40.9236,41.149070000000002,40.949829999999999,40.70655,41.244709999999998,40.970039999999997,41.024970000000003,41.295409999999997,41.59646,41.083060000000003,40.976990000000001,41.415999999999997,41.159570000000002,40.899509999999999,41.287610000000001,40.794179999999997,41.064660000000003,40.707619999999999,41.094380000000001,40.683720000000001,150.18270000000001,5917.9750000000004,5798.4380000000001,50.315809999999999,41.281619999999997,45,45,673072.09200000006,404544.87631785421,872.76573547200019,31,29,26732.05528262501,44,8.847646085137514,9.4547860851375134,371598.46837146493,6042.7496817555011,197.2876688497052,47.104968849705187,1,-119.53700000000026,-244.31168175550101,0.34457311090125692,0.34457311090125692,0.77558912457525608,0.77558912457525608,5654.7139283556216,143.72407164437845,0.71618004582495198,0.71618004582495198,44,0.93313912818968481]
["2013-01-07T06:00:00","2013-01-07T06:00:00",52.213120000000004,52.037559999999999,51.343859999999999,41.203510000000001,41.390250000000002,40.828620000000001,40.941229999999997,41.152369999999998,40.955869999999997,40.712389999999999,41.239759999999997,40.969070000000002,41.029440000000001,41.316040000000001,41.616799999999998,41.10322,41.003120000000003,41.430660000000003,41.172510000000003,40.911810000000003,41.299959999999999,40.811410000000002,41.080399999999997,40.71998,41.114620000000002,40.690759999999997,130.1198,5890.1559999999999,5795.183,50.383029999999998,41.201839999999997,45,45,673072.09200000006,407072.4181760397,749.64358936400038,29,27,27039.320682820002,44,8.7364298352841629,9.3435698352841623,366927.41940478585,6190.016103286318,171.61325701635818,41.493457016358178,1,-94.972999999999956,-394.83310328631796,0.34042151633773288,0.34042151633773288,0.77459050164521359,0.77459050164521359,5787.7922805716717,7.3907194283283388,0.71625775782615908,0.71625775782615908,44,0.93214050525964232]
["2013-01-07T07:00:00","2013-01-07T07:00:00",52.189610000000002,52.038559999999997,51.495280000000001,41.25996,41.39761,40.836469999999998,40.955309999999997,41.173020000000001,40.980820000000001,40.739849999999997,41.270740000000004,41.008940000000003,41.061570000000003,41.324689999999997,41.614190000000001,41.106569999999998,41.004930000000002,41.433860000000003,41.17501,40.917430000000003,41.303609999999999,40.819679999999998,41.092149999999997,40.737819999999999,41.132249999999999,40.713160000000002,156.3253,5951.28,5795.415,50.824719999999999,41.204239999999999,45,45,673072.09200000006,424682.47177721158,897.02974459249992,29,27,28627.0851072,44,8.7905726021555211,9.3977126021555204,369201.39929154771,6513.1331945726506,204.08903610500661,47.763736105006615,1,-155.86499999999978,-717.71819457265065,0.33287484679576856,0.33287484679576856,0.77295161098164522,0.77295161098164522,6092.3516857993527,-296.93668579935274,0.71313552536840719,0.71313552536840719,44,0.93050161459607394]
["2013-01-07T08:00:00","2013-01-07T08:00:00",52.138500000000001,52.017479999999999,51.558239999999998,41.640300000000003,41.426909999999999,40.864870000000003,40.978360000000002,41.19473,40.997439999999997,40.759610000000002,41.276940000000003,41.03152,41.078609999999998,41.337400000000002,41.628300000000003,41.120910000000002,41.009599999999999,41.429969999999997,41.177379999999999,40.923259999999999,41.317929999999997,40.82779,41.100490000000001,40.739989999999999,41.131250000000001,40.715440000000001,284.22640000000001,6079.4639999999999,5797.0290000000005,50.942100000000003,41.169930000000001,45,45,673072.09200000006,429516.63707925793,1623.367610392,31,29,29704.777858440008,44,8.9490159249728052,9.5561559249728045,375855.97108567634,6638.6691246233922,362.80360298876843,78.57720298876842,1,-282.43499999999949,-841.64012462339178,0.32402516186117902,0.32402516186117902,0.76998186097641674,0.76998186097641674,6216.8884835404233,-419.85948354042284,0.70872078320316778,0.70872078320316778,44,0.92753186459084547]
["2013-01-07T09:00:00","2013-01-07T09:00:00",52.205089999999998,52.048900000000003,51.616169999999997,41.899039999999999,41.423870000000001,40.882950000000001,40.97766,41.205869999999997,41.011580000000002,40.777000000000001,41.274329999999999,41.04918,41.089170000000003,41.353360000000002,41.643039999999999,41.124809999999997,41.021999999999998,41.44323,41.201900000000002,40.974620000000002,41.366250000000001,40.867710000000002,41.12547,40.763550000000002,41.14293,40.729570000000002,429.19510000000002,6229.402,5800.2070000000003,51.245939999999997,41.23319,45,45,673072.09200000006,441684.36974351277,2462.6184769759993,38,34,31186.722437749988,44,9.3037852351272754,9.9109252351272765,390756.17516369163,6704.0933662143707,529.37990607912195,100.18480607912193,1,-429.19499999999971,-903.88636621437036,0.3145209696017528,0.3145209696017528,0.76546895764115719,0.76546895764115719,6293.4028252407634,-493.19582524076304,0.70353492343158353,0.70353492343158353,44,0.92301896125558591]
["2013-01-07T10:00:00","2013-01-07T10:00:00",52.30453,52.073689999999999,51.62585,46.997750000000003,41.445390000000003,40.91666,41.001849999999997,41.241930000000004,41.051670000000001,40.822369999999999,41.295549999999999,41.092419999999997,41.121389999999998,41.390860000000004,41.689819999999997,41.15363,41.049469999999999,41.4557,41.209069999999997,41.011960000000002,41.387889999999999,40.894170000000003,41.15972,40.785969999999999,41.163539999999998,40.752650000000003,702.21730000000002,6502.9560000000001,5800.7380000000003,51.357680000000002,41.314459999999997,43,43,643157.77679999999,425612.14910431177,4055.964991761999,40,36,32655.308879160017,44,9.4755580327793574,10.082698032779357,380282.99951002945,6892.5352504187249,856.08994799693266,153.87264799693264,1,-702.21799999999985,-1091.7972504187246,0.30304093033558743,0.30304093033558743,0.75808526968048828,0.75808526968048828,6477.494173284962,-676.75617328496173,0.69641896170888129,0.69641896170888129,44,0.91563527329491701]
["2013-01-07T11:00:00","2013-01-07T11:00:00",52.451920000000001,52.06944,51.667119999999997,51.067500000000003,41.463909999999998,40.949910000000003,40.990270000000002,41.254449999999999,41.060090000000002,40.868960000000001,41.278489999999998,41.134329999999999,41.14911,41.41769,41.726570000000002,41.197290000000002,41.092460000000003,41.492339999999999,41.252540000000003,41.108530000000002,41.471510000000002,40.954140000000002,41.179220000000001,40.810630000000003,41.180970000000002,40.772959999999998,1002.576,6802.4080000000004,5799.8310000000001,52.061369999999997,41.295380000000002,43,43,643157.77679999999,453038.26958250982,5854.5225004800022,49,41,36617.328251959982,44,9.9148978933918368,10.522037893391836,397915.04602592479,7386.3248307105614,1180.9546731453427,178.37867314534265,1,-1002.5770000000002,-1586.4938307105613,0.2863592511455168,0.2863592511455168,0.74754336428281476,0.74754336428281476,6960.1209619206538,-1160.2899619206537,0.68421873468149308,0.68421873468149308,44,0.90509336789724348]
["2013-01-07T12:00:00","2013-01-07T12:00:00",52.46837,52.067749999999997,51.694339999999997,52.001359999999998,41.47551,40.971359999999997,40.989530000000002,41.259790000000002,41.072119999999998,40.89029,41.250700000000002,41.147289999999998,41.155630000000002,41.402679999999997,41.703409999999998,41.165210000000002,41.048639999999999,41.464089999999999,41.249830000000003,41.13091,41.464280000000002,40.927329999999998,41.130110000000002,40.759349999999998,41.14593,40.745869999999996,1168.5229999999999,6965.9880000000003,5797.4650000000001,52.342039999999997,41.547350000000002,43,43,643157.77679999999,465389.61559551908,6849.0054337500014,51,42,37597.840501859988,44,10.009180361113426,10.616320361113425,401698.88857138139,7512.6711969205808,1368.5447132832194,200.02171328321947,1,-1168.5230000000001,-1715.2061969205806,0.26832418604284619,0.26832418604284619,0.73525656843470966,0.73525656843470966,7083.0267405225095,-1285.5617405225094,0.67070129886214269,0.67070129886214269,44,0.89280657204913838]
["2013-01-07T13:00:00","2013-01-07T13:00:00",52.477080000000001,52.130159999999997,51.717610000000001,52.02319,47.953499999999998,40.975920000000002,40.991210000000002,41.266280000000002,41.072319999999998,40.89602,41.232529999999997,41.135170000000002,41.121749999999999,41.39199,41.687950000000001,41.153170000000003,41.032240000000002,41.463329999999999,41.245939999999997,41.137279999999997,41.47186,40.938560000000003,41.131149999999998,40.765059999999998,41.150269999999999,40.747779999999999,1559.71,7361.6530000000002,5801.9430000000002,55.317250000000001,42.829549999999998,41,41,613243.46160000004,557521.05030818691,9147.1532515000017,54,44,45965.057084050015,44,10.416196446566106,11.023336446566105,398590.25641330384,8825.6893617253645,1756.3327071304482,196.62270713044813,1,-1559.71,-3023.7463617253643,0.23653007138445253,0.23653007138445253,0.71885651610176626,0.71885651610176626,8339.5907050208298,-2537.6477050208296,0.64401841860561082,0.64401841860561082,44,0.87640651971619499]
["2013-01-07T14:00:00","2013-01-07T14:00:00",52.363410000000002,52.252560000000003,51.72486,51.989379999999997,52.109699999999997,43.40316,40.999650000000003,41.279539999999997,41.092689999999997,40.924019999999999,41.2517,41.16377,41.138300000000001,41.384810000000002,41.690550000000002,41.159730000000003,41.0364,41.473280000000003,41.253700000000002,41.15551,41.478549999999998,40.945610000000002,41.137329999999999,40.764150000000001,41.147660000000002,40.76,2548.7550000000001,8352.1749999999993,5803.4189999999999,57.712130000000002,41.753369999999997,39,39,583329.14639999997,617053.10300785839,14787.124627275005,54,43,66645.178151500018,44,11.060541574966152,11.667681574966149,402600.82360035507,12050.979185746421,2673.8518230867476,125.09682308674746,1,-2548.7559999999994,-6247.5601857464208,0.17083817096741671,0.17083817096741671,0.69205683424815023,0.69205683424815023,11423.893894137811,-5620.4748941378111,0.58492020009072365,0.58492020009072365,44,0.84960683786257896]
["2013-01-07T15:00:00","2013-01-07T15:00:00",54.458329999999997,52.6584,51.806069999999998,52.078690000000002,52.229219999999998,52.192839999999997,42.933450000000001,41.328859999999999,41.125999999999998,40.960769999999997,41.268079999999998,41.191040000000001,41.171729999999997,41.411250000000003,41.726059999999997,41.178109999999997,41.061500000000002,41.494489999999999,41.265810000000002,41.166670000000003,41.493769999999998,40.961939999999998,41.152149999999999,40.779359999999997,41.152450000000002,40.779170000000001,2779.0990000000002,8580.8989999999994,5801.8019999999997,56.466230000000003,41.472270000000002,39,39,583329.14639999997,571004.88552591647,19007.869938419994,55,44,64330.828185020007,44,11.042469241109183,11.649609241109182,401942.99536962324,11651.52952303957,3442.6846973061088,663.58569730610861,1,-2779.0969999999998,-5849.7275230395699,0.1093294049075028,0.1093294049075028,0.66283516083557614,0.66283516083557614,11044.289444148761,-5242.4874441487609,0.52979644731691422,0.52979644731691422,44,0.82038516445000487]
["2013-01-07T16:00:00","2013-01-07T16:00:00",55.91328,54.420659999999998,52.49568,52.263240000000003,52.224620000000002,51.948799999999999,51.616149999999998,43.573210000000003,41.158140000000003,40.981740000000002,41.312269999999998,41.227170000000001,41.217129999999997,41.465980000000002,41.778410000000001,41.237189999999998,41.080680000000001,41.513950000000001,41.284320000000001,41.188090000000003,41.511490000000002,40.985610000000001,41.181539999999998,40.797159999999998,41.170630000000003,40.792810000000003,3727.7530000000002,8450.3809999999994,4722.6279999999997,54.38017,42.134309999999999,35,35,523500.516,443850.57419525215,28182.688701954994,54,43,51741.091336330006,44,10.552312214568854,11.159452214568855,344706.39149356162,9806.588411001454,5341.5191152219868,1613.7661152219866,1,-3727.7529999999997,-5083.9604110014543,5.5872533566653337E-2,5.5872533566653337E-2,0.62363855102715871,0.62363855102715871,9273.0521788123478,-4550.4241788123481,0.4819496074110256,0.4819496074110256,44,0.78118855464158743]
["2013-01-07T17:00:00","2013-01-07T17:00:00",55.431750000000001,54.928469999999997,53.886569999999999,53.413469999999997,52.443620000000003,51.896509999999999,52.094670000000001,51.695689999999999,42.308880000000002,41.020020000000002,41.341419999999999,41.242019999999997,41.234490000000001,41.492130000000003,41.810099999999998,41.26258,41.140470000000001,41.548580000000001,41.32338,41.2089,41.526800000000001,40.994390000000003,41.190829999999998,40.81456,41.193309999999997,40.810859999999998,2206.7080000000001,8361.16,6154.4530000000004,52.630600000000001,40.7027,35,35,523500.516,386108.73531271651,16132.017465060004,52,42,49865.540182000004,44,10.427508920206201,11.0346489202062,340629.513140127,9564.2287268384189,3094.1268117833451,887.41881178334506,1,-2206.7069999999994,-3409.7757268384184,2.0019393967785473E-2,2.0019393967785473E-2,0.60043544898673296,0.60043544898673296,9037.9930603298581,-2883.5400603298576,0.45162973519532623,0.45162973519532623,44,0.75798545260116168]
["2013-01-07T18:00:00","2013-01-07T18:00:00",54.96696,54.823819999999998,54.422269999999997,54.154809999999998,53.332859999999997,52.013730000000002,51.979889999999997,52.435780000000001,47.771299999999997,41.430529999999997,41.429789999999997,41.290170000000003,41.280009999999997,41.523780000000002,41.841299999999997,41.315989999999999,41.200800000000001,41.622729999999997,41.382100000000001,41.257710000000003,41.531570000000002,41.000660000000003,41.186920000000001,40.818359999999998,41.198590000000003,40.827919999999999,1758.999,7765.95,6006.951,51.930929999999996,40.66854,33,33,493586.20079999999,341970.25345669099,12435.278610480002,49,41,43731.578810249986,44,10.157493837429527,10.764633837429525,312848.56467485416,8610.702504017816,2448.4934590178191,689.49445901781905,1,-1758.9989999999998,-2603.7515040178159,-7.3585550918937453E-3,0,0.58193991093568809,0.58193991093568809,8125.0471629033318,-2118.0961629033318,0.42935835915886994,0.42935835915886994,43,0.73948991455011681]
["2013-01-07T19:00:00","2013-01-07T19:00:00",54.627679999999998,54.501510000000003,54.346769999999999,54.48265,53.712949999999999,52.071539999999999,52.015419999999999,52.276670000000003,51.725610000000003,41.287820000000004,41.397869999999998,41.288879999999999,41.287779999999998,41.53349,41.854909999999997,41.328209999999999,41.214320000000001,41.638100000000001,41.381860000000003,41.277450000000002,41.569499999999998,41.034179999999999,41.199440000000003,40.828609999999998,41.208509999999997,40.833269999999999,806.41899999999998,6797.71,5991.2920000000004,52.168790000000001,40.556899999999999,33,33,493586.20079999999,349131.51005568681,5562.0371588950002,47,40,39467.130385950004,44,9.9512291461608964,10.558369146160896,306495.65778273216,7932.1116630453844,1117.8593271647833,311.4403271647833,1,-806.41799999999967,-1940.819663045384,-2.0407347547140096E-2,0,0.57346057990477362,0.57346057990477362,7475.9898691931148,-1484.6978691931145,0.41374704503420789,0.41374704503420789,43,0.73101058351920234]
["2013-01-07T20:00:00","2013-01-07T20:00:00",54.551929999999999,54.402729999999998,54.093739999999997,54.622799999999998,53.810609999999997,52.249600000000001,52.0657,52.295450000000002,52.186230000000002,42.181399999999996,41.416600000000003,41.278120000000001,41.288409999999999,41.538690000000003,41.858350000000002,41.337510000000002,41.223500000000001,41.633830000000003,41.381959999999999,41.242130000000003,41.560540000000003,41.039569999999998,41.207970000000003,40.829329999999999,41.21284,40.841349999999998,619.97159999999997,6586.152,5966.1809999999996,52.019689999999997,40.50535,33,33,493586.20079999999,344290.40080348187,4250.0851097639998,48,41,37917.596709839992,44,9.9592370478055443,10.566377047805545,306742.29938307987,7614.5585305040813,853.49612412337945,233.52452412337948,1,-619.97100000000046,-1648.3775305040817,-1.7332374457248431E-2,0,0.56694170341817851,0.56694170341817851,7177.0288980393379,-1210.8478980393384,0.40101521097846698,0.40101521097846698,43,0.72449170703260724]
["2013-01-07T21:00:00","2013-01-07T21:00:00",54.490070000000003,54.288640000000001,53.968440000000001,54.686689999999999,53.92991,52.405029999999996,52.117649999999998,52.337389999999999,52.203679999999999,42.05368,41.402589999999996,41.271389999999997,41.277450000000002,41.542000000000002,41.867229999999999,41.341450000000002,41.241860000000003,41.664299999999997,41.41245,41.249160000000003,41.558999999999997,41.045859999999998,41.242190000000001,40.848959999999998,41.22316,40.850569999999998,594.46169999999995,6547.2969999999996,5952.8360000000002,51.820450000000001,40.52046,33,33,493586.20079999999,337869.87888775091,4054.0801785750014,46,40,36992.195313515003,44,9.8668338601908623,10.473973860190862,303896.30163212772,7498.2909082446904,821.75908422493296,227.29738422493301,1,-594.46099999999933,-1545.4549082446902,-1.6250162769628432E-2,0,0.56069105970242761,0.56069105970242761,7063.6409460813593,-1110.804946081359,0.38933530942790523,0.38933530942790523,43,0.71824106331685633]
["2013-01-07T22:00:00","2013-01-07T22:00:00",54.440710000000003,54.22072,53.86253,54.548160000000003,54.002409999999998,52.466900000000003,52.12312,52.33728,52.178530000000002,42.866619999999998,41.425870000000003,41.301699999999997,41.305320000000002,41.551699999999997,41.880870000000002,41.350650000000002,41.244770000000003,41.663800000000002,41.426859999999998,41.282710000000002,41.574019999999997,41.057409999999997,41.2515,40.861829999999998,41.232140000000001,40.856189999999998,398.20269999999999,6358.3580000000002,5961.1559999999999,51.489159999999998,40.42501,33,33,493586.20079999999,327493.12536847143,2704.696271102001,46,40,35174.913332849996,44,9.8048645446501865,10.412004544650186,301987.66041303647,7174.9922036490407,551.70497435943878,153.50227435943879,1,-397.20200000000023,-1213.8362036490407,-1.2763255517670345E-2,0,0.55651455664304494,0.55651455664304494,6756.6073721939147,-795.45137219391472,0.38097129039084587,0.38097129039084587,43,0.71406456025747367]
["2013-01-07T23:00:00","2013-01-07T23:00:00",54.399120000000003,54.188949999999998,53.847929999999998,54.308729999999997,54.082900000000002,52.515630000000002,52.15766,52.359929999999999,52.123840000000001,43.638120000000001,41.503410000000002,41.341290000000001,41.332610000000003,41.583939999999998,41.893470000000001,41.364359999999998,41.246639999999999,41.661920000000002,41.430500000000002,41.266330000000004,41.568249999999999,41.042299999999997,41.220210000000002,40.865679999999998,41.240760000000002,40.877949999999998,315.39780000000002,6295.8770000000004,5980.6949999999997,50.88279,40.450769999999999,31,31,463671.88560000004,289471.29294260143,2132.2736357130011,45,39,32839.357390770005,44,9.6643750870252578,10.271515087025257,279620.57883219194,6795.9608552151349,441.26466874731489,125.86686874731487,1,-315.1820000000007,-815.26585521513516,-8.5723645362215262E-3,0,0.55320047819615303,0.55320047819615303,6394.2577336525419,-413.56273365254219,0.37662275734633321,0.37662275734633321,43,0.71075048181058176]
["2013-01-08","2013-01-08",54.316839999999999,54.19849,53.866280000000003,54.332230000000003,54.048119999999997,52.675109999999997,52.14725,52.361530000000002,52.161079999999998,44.427880000000002,41.451799999999999,41.30348,41.295780000000001,41.576610000000002,41.897770000000001,41.381149999999998,41.269159999999999,41.690159999999999,41.439239999999998,41.262329999999999,41.56673,41.042110000000001,41.231050000000003,40.86533,41.239730000000002,40.881549999999997,346.28919999999999,6306.5969999999998,5960.308,50.674709999999997,40.462229999999998,31,31,463671.88560000004,283346.72890258778,2326.2479129340004,46,40,32202.997865279998,44,9.7035222272060491,10.310662227206048,280753.22795832879,6637.3832328618801,479.46464355217972,133.17544355217973,1,-346.28899999999976,-677.07523286188007,-7.1193165731287707E-3,0,0.54955931559392401,0.54955931559392401,6246.5430746646171,-286.23507466461706,0.37361305028282543,0.37361305028282543,43,0.70710931920835274]
["2013-01-08T01:00:00","2013-01-08T01:00:00",54.29889,54.166029999999999,53.817419999999998,54.259410000000003,54.091560000000001,52.667059999999999,52.127249999999997,52.3401,52.142060000000001,46.236960000000003,41.461179999999999,41.316249999999997,41.30545,41.596200000000003,41.914589999999997,41.394440000000003,41.269680000000001,41.687980000000003,41.414589999999997,41.262430000000002,41.58379,41.049900000000001,41.241720000000001,40.861339999999998,41.250419999999998,40.878830000000001,260.3374,6232.85,5972.5140000000001,50.35812,40.436680000000003,31,31,463671.88560000004,274265.48875123158,1746.8717641220001,45,39,30919.42365199999,44,9.5989053465332006,10.2060453465332,277726.33460351336,6442.2811843158852,363.97312007101124,103.63572007101124,1,-260.33600000000024,-469.76718431588506,-4.9395120933250309E-3,0,0.54682193234694276,0.54682193234694276,6059.0410099447063,-86.527009944706151,0.37270323532279676,0.37270323532279676,43,0.70437193596137149]
["2013-01-08T02:00:00","2013-01-08T02:00:00",54.27657,54.103340000000003,53.79092,54.201099999999997,54.180630000000001,52.726799999999997,52.12406,52.343649999999997,52.140729999999998,47.404969999999999,41.504649999999998,41.352089999999997,41.327120000000001,41.618400000000001,41.92512,41.393940000000001,41.271500000000003,41.692599999999999,41.43085,41.272750000000002,41.591769999999997,41.056130000000003,41.234670000000001,40.868830000000003,41.256500000000003,40.880989999999997,286.31950000000001,6250.6689999999999,5966.7470000000003,50.374200000000002,40.437510000000003,31,31,463671.88560000004,274668.23786043894,1917.7078839050002,45,40,31055.480072804996,44,9.6643918704826515,10.271531870482651,279621.06443007372,6426.7841140953333,396.86053910171745,110.54103910171744,1,-283.92199999999957,-460.03711409533298,-4.8372022659723384E-3,0,0.54383654682112459,0.54383654682112459,6046.9033177123802,-80.15631771237986,0.37186040697310413,0.37186040697310413,43,0.70138655043555331]
["2013-01-08T03:00:00","2013-01-08T03:00:00",54.244149999999998,54.078319999999998,53.760100000000001,54.157829999999997,54.176259999999999,52.778919999999999,52.09975,52.319009999999999,52.131129999999999,48.175069999999998,41.462119999999999,41.327390000000001,41.334980000000002,41.62077,41.926760000000002,41.393729999999998,41.271360000000001,41.678710000000002,41.416800000000002,41.258740000000003,41.565989999999999,41.037680000000002,41.221559999999997,40.866129999999998,41.250160000000001,40.877740000000003,287.233,6242.4059999999999,5955.8320000000003,50.456719999999997,40.466810000000002,31,31,463671.88560000004,277149.83204842039,1919.6370217649992,47,41,31180.537061729981,44,9.7295033138049938,10.336643313804993,281504.94200171682,6409.4817702541004,394.6012370521043,107.36823705210429,1,-286.57399999999961,-453.64977025410008,-4.7700405671535044E-3,0,0.54082327602253966,0.54082327602253966,6033.0101591272196,-77.17815912721926,0.37104889339131863,0.37104889339131863,43,0.69837327963696838]
["2013-01-08T04:00:00","2013-01-08T04:00:00",54.210520000000002,54.035600000000002,53.707850000000001,54.104340000000001,54.238370000000003,52.784149999999997,52.10492,52.316099999999999,52.111040000000003,48.894539999999999,41.486980000000003,41.34008,41.342039999999997,41.633189999999999,41.962249999999997,41.454329999999999,41.35322,41.769910000000003,41.515090000000001,41.307740000000003,41.603630000000003,41.058059999999998,41.240949999999998,40.875050000000002,41.249589999999998,40.869300000000003,312.39749999999998,6282.0469999999996,5969.6490000000003,50.483870000000003,40.443330000000003,31,31,463671.88560000004,278179.5619907112,2083.881887475,47,41,31537.572092689999,44,9.7416782083607316,10.348818208360729,281857.1997558127,6474.7718859411889,427.82810988080513,115.43060988080515,1,-312.39799999999923,-505.12288594118854,-5.3112705336266957E-3,0,0.53753847080316752,0.53753847080316752,6094.9127635097575,-125.26376350975715,0.36973176887651688,0.36973176887651688,43,0.69508847441759625]
["2013-01-08T05:00:00","2013-01-08T05:00:00",54.164020000000001,53.98612,53.662140000000001,54.05838,54.30545,52.869340000000001,52.097450000000002,52.311950000000003,52.112540000000003,49.95073,41.544699999999999,41.397419999999997,41.413719999999998,41.71416,42.047080000000001,41.546520000000001,41.423670000000001,41.855710000000002,41.579790000000003,41.374369999999999,41.65842,41.080599999999997,41.240180000000002,40.872920000000001,41.244509999999998,40.865360000000003,473.42869999999999,6434.0860000000002,5960.6570000000002,50.743989999999997,40.423960000000001,31,31,463671.88560000004,285819.64315287082,3147.9836577709998,47,41,33199.980271289984,44,9.7983663272509887,10.40550632725099,283497.36422317516,6776.6358518266388,642.5527588238665,169.12405882386651,1,-473.42900000000009,-815.97885182663867,-8.5798615592205894E-3,0,0.53256045541829911,0.53256045541829911,6381.2330178191369,-420.57601781913672,0.36530949249038436,0.36530949249038436,43,0.69011045903272783]
["2013-01-08T06:00:00","2013-01-08T06:00:00",54.132240000000003,53.955959999999997,53.603259999999999,53.977130000000002,54.170589999999997,53.000010000000003,52.124789999999997,52.319600000000001,52.118670000000002,51.531820000000003,41.671970000000002,41.545360000000002,41.549059999999997,41.80003,42.103490000000001,41.580449999999999,41.471359999999997,41.872709999999998,41.601489999999998,41.466419999999999,41.755800000000001,41.205599999999997,41.337470000000003,40.91386,41.277259999999998,40.889310000000002,511.32979999999998,6463.0140000000001,5951.6840000000002,51.262239999999998,40.454369999999997,31,31,463671.88560000004,300121.28716732073,3385.7523741570003,48,42,34925.707560090006,44,9.9180606277990702,10.52520062779907,286960.49446189101,7042.8501842784999,682.74484321403816,171.41504321403818,1,-511.32999999999993,-1091.1661842784997,-1.1473403726401422E-2,0,0.52718391826754418,0.52718391826754418,6636.5875188819728,-684.90351888197256,0.35810786298702701,0.35810786298702701,43,0.68473392188197291]
["2013-01-08T07:00:00","2013-01-08T07:00:00",54.066299999999998,53.90616,53.522660000000002,53.89837,54.010849999999998,53.148980000000002,52.137909999999998,52.317100000000003,52.122900000000001,51.945619999999998,41.684330000000003,41.535510000000002,41.510939999999998,41.76849,42.089300000000001,41.557940000000002,41.426409999999997,41.845170000000003,41.605499999999999,41.468400000000003,41.803089999999997,41.300669999999997,41.475020000000001,40.997700000000002,41.282550000000001,40.889060000000001,553.98209999999995,6497.3440000000001,5943.3620000000001,51.41769,40.499699999999997,31,31,463671.88560000004,304626.17483280698,3649.9775437019994,48,43,35468.968409280009,44,9.9974328227564495,10.604572822756449,289256.98015261715,7095.6152520564092,730.18295964816355,176.2008596481636,1,-553.98199999999997,-1152.2532520564091,-1.2115722560302451E-2,0,0.52135890349460012,0.52135890349460012,6689.3724060561553,-746.01040605615526,0.35026370625260761,0.35026370625260761,43,0.67890890710902885]
["2013-01-08T08:00:00","2013-01-08T08:00:00",54.014780000000002,53.843330000000002,53.477449999999997,53.843240000000002,53.954799999999999,53.362200000000001,52.117579999999997,52.280679999999997,52.112549999999999,51.942610000000002,41.647449999999999,41.504249999999999,41.506079999999997,41.785029999999999,42.09722,41.569330000000001,41.453200000000002,41.879959999999997,41.635980000000004,41.497509999999998,41.809699999999999,41.283180000000002,41.453299999999999,41.082030000000003,41.381880000000002,40.937730000000002,635.42129999999997,6589.7160000000003,5954.2939999999999,51.600940000000001,40.55247,31,31,463671.88560000004,308519.99488432362,4154.7180555824998,49,43,36403.139767260007,44,10.029288066063568,10.636428066063566,290178.6519101978,7259.3666723839578,828.51704492185365,193.09574492185368,1,-635.42200000000048,-1305.072672383958,-1.3722589536126083E-2,0,0.51467756269823184,0.51467756269823184,6844.9933645313404,-890.69936453134051,0.34089817279367396,0.34089817279367396,43,0.67222756631266056]
["2013-01-08T09:00:00","2013-01-08T09:00:00",53.936489999999999,53.788960000000003,53.437530000000002,53.786070000000002,53.899160000000002,53.460529999999999,52.187950000000001,52.265219999999999,52.083030000000001,51.916739999999997,41.661909999999999,41.493209999999998,41.488190000000003,41.763730000000002,42.071040000000004,41.547490000000003,41.423589999999997,41.84516,41.585749999999997,41.436430000000001,41.782429999999998,41.274169999999998,41.476930000000003,41.149140000000003,41.528309999999998,40.987360000000002,530.69389999999999,6494.8590000000004,5964.165,51.684840000000001,40.475180000000002,31,31,463671.88560000004,309511.53310074116,3436.0121506534992,48,43,36402.580568969992,44,10.029268997401878,10.636408997401876,290178.10019421292,7259.2689613570501,685.19692742185134,154.50302742185136,1,-530.69400000000041,-1295.1039613570501,-1.3617770446338058E-2,0,0.50909741679112153,0.50909741679112153,6844.9004880993098,-880.7354880993098,0.33163740758968785,0.33163740758968785,43,0.66664742040555025]
["2013-01-08T10:00:00","2013-01-08T10:00:00",53.914149999999999,53.755650000000003,53.405540000000002,53.75855,53.869109999999999,53.418500000000002,52.26182,52.272770000000001,52.068989999999999,51.899160000000002,41.694049999999997,41.516129999999997,41.513500000000001,41.770139999999998,42.095489999999998,41.550249999999998,41.44106,41.860300000000002,41.608249999999998,41.457999999999998,41.797229999999999,41.310540000000003,41.538460000000001,41.202719999999999,41.564599999999999,41.085099999999997,435.28030000000001,6385.7430000000004,5950.4629999999997,51.783410000000003,40.500790000000002,31,31,463671.88560000004,309535.54759504041,2792.1163663575003,49,45,36023.955843330004,44,10.138051894257554,10.745191894257553,293325.52941875363,7106.682076412505,550.81911110339149,115.53881110339148,1,-435.28000000000065,-1156.2190764125053,-1.2157422444885636E-2,0,0.50452053084470605,0.50452053084470605,6705.1302941517361,-754.66729415173631,0.32370222533269821,0.32370222533269821,43,0.66207053445913477]
["2013-01-08T11:00:00","2013-01-08T11:00:00",53.912190000000002,53.734250000000003,53.393999999999998,53.755209999999998,53.859369999999998,53.413609999999998,52.420180000000002,52.280749999999998,52.080970000000001,51.902639999999998,42.438319999999997,41.549300000000002,41.546590000000002,41.793379999999999,42.085009999999997,41.552579999999999,41.444110000000002,41.884419999999999,41.647629999999999,41.515309999999999,41.860469999999999,41.35472,41.569490000000002,41.201210000000003,41.554589999999997,41.09151,466.31029999999998,6421.5910000000003,5955.28,52.42127,40.495449999999998,31,31,463671.88560000004,327805.36979395646,2989.2075685020004,49,46,38291.369189810008,44,10.276217689372523,10.883357689372522,297323.09773092775,7452.4246852828437,581.7719435027899,115.46164350278991,1,-466.3110000000006,-1497.144685282844,-1.5742190015212265E-2,0,0.49961735986841738,0.49961735986841738,7036.6830315980706,-1081.4030315980708,0.31233147928938759,0.31233147928938759,43,0.6571673634828461]
["2013-01-08T12:00:00","2013-01-08T12:00:00",53.889270000000003,53.725490000000001,53.366190000000003,53.75159,53.85313,53.377929999999999,52.619399999999999,52.281829999999999,52.074530000000003,51.895589999999999,46.28763,41.558540000000001,41.544310000000003,41.820500000000003,42.115690000000001,41.570239999999998,41.441299999999998,41.879600000000003,41.635590000000001,41.487549999999999,41.830669999999998,41.322049999999997,41.541600000000003,41.167999999999999,41.522959999999998,41.079230000000003,387.08949999999999,6349.9449999999997,5962.8559999999998,52.19547,40.536560000000001,29,29,433757.57040000003,300877.40307351761,2479.3159892899998,49,46,37016.718629974996,44,10.232752105282149,10.839892105282146,276964.50236162264,7234.9487702075694,484.58439406739399,97.494894067394,1,-387.08899999999994,-1272.0927702075696,-1.3375812172623814E-2,0,0.4955471930697774,0.4955471930697774,6829.7208626158199,-866.86486261582013,0.30321656105940303,0.30321656105940303,43,0.65309719668420618]
["2013-01-08T13:00:00","2013-01-08T13:00:00",53.863259999999997,53.733809999999998,53.363039999999998,53.737960000000001,53.856879999999997,53.373530000000002,52.771819999999998,52.261450000000004,52.051929999999999,51.878340000000001,48.459739999999996,41.563920000000003,41.550449999999998,41.791969999999999,42.10304,41.555630000000001,41.44171,41.872669999999999,41.637860000000003,41.50132,41.84272,41.326099999999997,41.530619999999999,41.164949999999997,41.546529999999997,41.064300000000003,462.82389999999998,6417.3630000000003,5954.5389999999998,52.377090000000003,40.615200000000002,29,29,433757.57040000003,306197.31822235393,2961.8322915719987,48,47,37740.158848035004,44,10.318268416717995,10.925408416717994,279279.1272442487,7315.2116854969909,574.09483296114718,111.2709329611472,1,-462.82400000000052,-1360.6726854969911,-1.4307213039704366E-2,0,0.49068068723154967,0.49068068723154967,6908.6952923947883,-954.15629239478858,0.29318379014103885,0.29318379014103885,43,0.6482306908459784]
["2013-01-08T14:00:00","2013-01-08T14:00:00",53.839269999999999,53.710920000000002,53.369540000000001,53.739199999999997,53.859879999999997,53.352069999999998,52.897129999999997,52.250680000000003,52.030380000000001,51.858089999999997,50.186419999999998,41.578620000000001,41.558729999999997,41.825069999999997,42.119950000000003,41.566130000000001,41.451120000000003,41.891930000000002,41.652360000000002,41.507480000000001,41.856990000000003,41.339880000000001,41.540700000000001,41.167450000000002,41.551139999999997,41.12885,514.69929999999999,6464.1989999999996,5949.5,52.421889999999998,40.602539999999998,29,29,433757.57040000003,305662.75539259298,3271.0221383529997,48,47,38201.315225325001,44,10.333993849183583,10.941133849183583,279704.75922794593,7393.330358589873,633.06059324032219,118.3612932403222,1,-514.69899999999961,-1443.830358589873,-1.5181600067170408E-2,0,0.48526872569016466,0.48526872569016466,6983.0633190134213,-1033.5633190134213,0.28231606952552007,0.28231606952552007,43,0.64281872930459338]
["2013-01-08T15:00:00","2013-01-08T15:00:00",53.813789999999997,53.699240000000003,53.352829999999997,53.708570000000002,53.778309999999998,53.201430000000002,53.035850000000003,52.431240000000003,52.040469999999999,51.862830000000002,51.965400000000002,41.585560000000001,41.576050000000002,41.823090000000001,42.1402,41.588940000000001,41.460079999999998,41.902830000000002,41.662739999999999,41.520400000000002,41.86018,41.348269999999999,41.555459999999997,41.187849999999997,41.558590000000002,41.150089999999999,511.39789999999999,6461.5360000000001,5950.1379999999999,52.425849999999997,40.540790000000001,29,29,433757.57040000003,305195.04674964258,3238.0947931149994,49,48,38397.87152607998,44,10.401543419039328,11.008683419039329,281533.08779560274,7383.1103672163217,622.61813707144347,111.22023707144348,1,-511.39800000000014,-1432.9723672163218,-1.5067430364625134E-2,0,0.47989147353241574,0.47989147353241574,6975.9243797803329,-1025.7863797803329,0.27153012193858533,0.27153012193858533,43,0.6374414771468444]
["2013-01-08T16:00:00","2013-01-08T16:00:00",53.759729999999998,53.669040000000003,53.314599999999999,53.674880000000002,53.702530000000003,53.15992,53.129480000000001,52.476430000000001,52.027180000000001,51.847239999999999,52.199489999999997,41.582129999999999,41.569789999999998,41.831760000000003,42.148290000000003,41.588470000000001,41.474469999999997,41.91677,41.68526,41.549790000000002,41.885640000000002,41.371130000000001,41.573509999999999,41.201590000000003,41.566830000000003,41.113900000000001,464.77850000000001,6409.9830000000002,5945.2049999999999,52.425640000000001,40.517069999999997,29,29,433757.57040000003,306168.89842634136,2938.7549493274992,48,47,38166.865627155013,44,10.332819117885988,10.939959117885987,279672.96339571039,7387.5029053956096,568.81958656191887,104.04108656191886,1,-464.77800000000025,-1442.2979053956096,-1.5165486614936529E-2,0,0.47500442175791868,0.47500442175791868,6977.5152202817908,-1032.3102202817909,0.26067557741655645,0.26067557741655645,42,0.63255442537234741]
["2013-01-08T17:00:00","2013-01-08T17:00:00",53.731999999999999,53.624580000000002,53.267829999999996,53.592059999999996,53.632489999999997,53.076329999999999,53.069159999999997,52.729590000000002,52.07808,51.829729999999998,52.256180000000001,41.610250000000001,41.601640000000003,41.864800000000002,42.162390000000002,41.611550000000001,41.495699999999999,41.931449999999998,41.694110000000002,41.564369999999997,41.901499999999999,41.39002,41.590980000000002,41.220680000000002,41.584539999999997,41.158709999999999,421.61660000000001,6374.3069999999998,5952.69,52.320590000000003,40.54063,29,29,433757.57040000003,302112.71687353245,2650.5538903070001,48,47,37544.540743860009,44,10.311597839365627,10.918737839365628,279098.57824649574,7282.0025235138073,514.09178899282267,92.475188992822666,1,-421.61700000000019,-1329.3125235138077,-1.397746693453495E-2,0,0.47057119964325722,0.47057119964325722,6877.0843839659992,-924.39438396599962,0.2509557472729263,0.2509557472729263,42,0.62812120325768594]
["2013-01-08T18:00:00","2013-01-08T18:00:00",53.69932,53.540390000000002,53.190399999999997,53.532800000000002,53.606900000000003,53.089219999999997,53.12527,53.048250000000003,52.125790000000002,51.828400000000002,52.246630000000003,41.645180000000003,41.633949999999999,41.881309999999999,42.178440000000002,41.642470000000003,41.535310000000003,41.956440000000001,41.709499999999998,41.572330000000001,41.910209999999999,41.401710000000001,41.606250000000003,41.258150000000001,41.625979999999998,41.208120000000001,349.94260000000003,6297.0450000000001,5947.3320000000003,52.250790000000002,40.54569,29,29,433757.57040000003,298886.12269956764,2185.60150256,47,46,36853.770714750004,44,10.227195581372976,10.834335581372976,276814.10686063417,7207.013970060887,427.40974007394277,77.467140073942744,1,-349.71299999999974,-1259.6819700608867,-1.3245314982826158E-2,0,0.46689403433591764,0.46689403433591764,6803.1436608094673,-855.81166080946696,0.2419570513458511,0.2419570513458511,42,0.62444403795034631]
["2013-01-08T19:00:00","2013-01-08T19:00:00",53.640790000000003,53.524039999999999,53.17109,53.52319,53.631880000000002,53.125360000000001,53.144820000000003,52.939900000000002,52.232280000000003,51.842320000000001,52.261629999999997,41.732379999999999,41.658230000000003,41.90936,42.216540000000002,41.649239999999999,41.549289999999999,41.980159999999998,41.736280000000001,41.586280000000002,41.927129999999998,41.416049999999998,41.61054,41.261899999999997,41.643270000000001,41.21452,382.52789999999999,6333.3459999999995,5950.8180000000002,52.187910000000002,40.52843,29,29,433757.57040000003,297010.95749218337,2376.6974839664999,47,46,36921.760510040011,44,10.229514033392364,10.836654033392364,276876.85917821131,7218.6734168437952,464.67456346571475,82.146663465714767,1,-382.52799999999934,-1267.855416843795,-1.3331257212458734E-2,0,0.46287182557992057,0.46287182557992057,6814.236275564077,-863.41827556407679,0.23287837331950606,0.23287837331950606,42,0.62042182919434929]
["2013-01-08T20:00:00","2013-01-08T20:00:00",53.601860000000002,53.514519999999997,53.158340000000003,53.522289999999998,53.656700000000001,53.137569999999997,53.143940000000001,53.157429999999998,52.139899999999997,51.827579999999998,52.27946,42.483220000000003,41.66527,41.927050000000001,42.236800000000002,41.69941,41.541930000000001,41.966349999999998,41.720210000000002,41.557780000000001,41.901449999999997,41.389380000000003,41.611319999999999,41.272689999999997,41.652389999999997,41.25985,294.86070000000001,6245.8950000000004,5952.1369999999997,52.215870000000002,40.516930000000002,29,29,433757.57040000003,296540.81286671769,1819.5868540035003,47,46,36535.175425649999,44,10.216331482014667,10.823471482014664,276520.05401527812,7152.3081430880202,356.21139686134711,61.350696861347103,1,-293.75800000000072,-1200.1711430880205,-1.2619570019511346E-2,0,0.45978301639537933,0.45978301639537933,6751.10115758339,-798.96415758339026,0.22447741801594728,0.22447741801594728,42,0.61733302000980805]
["2013-01-08T21:00:00","2013-01-08T21:00:00",53.590879999999999,53.511589999999998,53.176879999999997,53.543210000000002,53.67268,53.145139999999998,53.156089999999999,53.113939999999999,52.266399999999997,51.848059999999997,52.282789999999999,42.883839999999999,41.66536,41.932459999999999,42.249960000000002,41.713630000000002,41.591949999999997,42.020099999999999,41.772590000000001,41.610010000000003,41.96698,41.464149999999997,41.665570000000002,41.302370000000003,41.66628,41.281469999999999,266.53449999999998,6213.2309999999998,5954.58,51.949669999999998,40.484070000000003,29,29,433757.57040000003,288750.54078257584,1640.4412198225,46,45,35619.210676799979,44,10.124250084078881,10.73139008407888,274027.73540014395,7036.4146244893291,324.06177370158264,57.527273701582658,1,-258.65099999999984,-1081.8346244893291,-1.1375284160013831E-2,0,0.45706335060111747,0.45706335060111747,6638.3218572298001,-683.74185722980019,0.21728800316267799,0.21728800316267799,42,0.61461335421554619]
["2013-01-08T22:00:00","2013-01-08T22:00:00",53.56747,53.531109999999998,53.178719999999998,53.509830000000001,53.608829999999998,53.102159999999998,53.166849999999997,53.249169999999999,52.24183,51.847479999999997,52.294800000000002,43.016179999999999,41.700960000000002,41.956899999999997,42.272300000000001,41.7408,41.62829,42.053330000000003,41.808860000000003,41.652259999999998,42.007649999999998,41.48171,41.67192,41.308590000000002,41.69059,41.27319,130.96129999999999,6020.85,5939.17,51.84404,40.401539999999997,29,29,433757.57040000003,286115.61969512125,805.037445682,47,46,34446.788062500011,44,10.145117472931251,10.75225747293125,274592.54200442979,6790.8110782175545,158.70441083210028,27.743110832100285,1,-81.680000000000291,-851.64107821755442,-8.9548430488053787E-3,0,0.45620450102359678,0.45620450102359678,6407.3592265102679,-468.18922651026787,0.2123650829938718,0.2123650829938718,42,0.6137545046380255]
["2013-01-08T23:00:00","2013-01-08T23:00:00",53.589509999999997,53.533189999999998,53.206470000000003,53.567959999999999,53.663539999999998,53.149979999999999,53.200180000000003,53.092610000000001,52.298900000000003,51.876060000000003,52.29242,42.5642,41.705509999999997,41.959719999999997,42.28069,41.749020000000002,41.632579999999997,42.053040000000003,41.804729999999999,41.658630000000002,42.006509999999999,41.489789999999999,41.697740000000003,41.346179999999997,41.707160000000002,41.312330000000003,124.3385,6013.35,5960.0839999999998,51.303069999999998,40.475540000000002,29,29,433757.57040000003,270414.08839524107,763.26307271499968,47,46,32554.863762749988,44,10.080602854309776,10.687742854309775,272846.35886056931,6458.9120776307054,151.4320291645416,27.093529164541607,1,-53.266000000000531,-498.82807763070559,-5.2450818282149415E-3,0,0.45564441922148835,0.45564441922148835,6091.9998182071549,-131.9158182071551,0.2109780133962284,0.2109780133962284,42,0.61319442283591707]
["2013-01-09","2013-01-09",53.605260000000001,53.53378,53.201639999999998,53.566459999999999,53.68139,53.170949999999998,53.199890000000003,53.190379999999998,52.16677,51.874920000000003,52.279820000000001,42.56156,41.703290000000003,41.959910000000001,42.283859999999997,41.752980000000001,41.629130000000004,42.053609999999999,41.812710000000003,41.68797,42.03275,41.509770000000003,41.700040000000001,41.341419999999999,41.68994,41.288139999999999,179.1489,6107.2150000000001,5939.7039999999997,51.359560000000002,40.560920000000003,29,29,433757.57040000003,272597.81138790533,1103.2992495840003,48,47,32974.808093799998,44,10.155769955998581,10.76290995599858,274880.8671432882,{"$f":"AO198*1000/(500*AQ198)","v":6493.8076062511009},217.27535270377572,{"$f":"AU198-AC198","v":38.126452703775726},1,{"$f":"AE198-AD198","v":-167.51100000000042},{"$f":"AE198-AT198","v":-554.10360625110116},-5.8262934394154838E-3,0,0.45388307309538561,0.45388307309538561,{"$f":"AO198*1000/(500*AR198)","v":6127.4893553154516},{"$f":"AE198-BD198","v":-187.78535531545185},0.20900348630174687,0.20900348630174687,42,0.61143307670981439]
["2013-01-09T01:00:00","2013-01-09T01:00:00",53.602379999999997,53.521560000000001,53.184069999999998,53.563380000000002,53.668950000000002,53.140979999999999,53.15616,53.173639999999999,52.305700000000002,51.886069999999997,52.281350000000003,42.811610000000002,41.696599999999997,41.961770000000001,42.280099999999997,41.746400000000001,41.631070000000001,42.057139999999997,41.821930000000002,41.685220000000001,42.031840000000003,41.495989999999999,41.706249999999997,41.345410000000001,41.703899999999997,41.307110000000002,149.59909999999999,6050.9930000000004,5950.125,51.104179999999999,40.43289,29,29,{"$f":"3.1416*(138/2)^2*AI199","v":433757.57040000003},{"$f":"62.4*AJ199*(AF199-AB199)/1000","v":265172.12468689657},{"$f":"500*AC199*(C199-AB199)/1000","v":919.68066312849965},49,48,32285.950545484997,44,{"$f":"19.5286-0.30357*AP199+0.0000341*AO199+0.060847*AN199","v":10.19312691360104},{"$f":"19.5286-0.30357*42+0.0000341*AO199+0.060847*AN199","v":10.800266913601039},{"$f":"62.4*AJ199*AQ199/1000","v":275891.98820492014},6334.847161061979,{"$f":"AL199*1000/(500*AQ199)","v":180.45113553944631},30.852035539446319,1,-100.86800000000039,-384.72216106197902,-4.045279939898787E-3,{"$f":"IF(AZ199>1,1,IF(AZ199<0,0,AZ199))","v":0},0.45282246536784693,{"$f":"IF(BB199>1,1,BB199)","v":0.45282246536784693},5978.7319709342582,-28.606970934258243,0.20870268947386936,{"$f":"IF(BF199>1,1,IF(BF199<0,0,BF199))","v":0.20870268947386936},42,0.61037246898227571]
["2013-01-09T02:00:00","2013-01-09T02:00:00",53.620040000000003,53.514479999999999,53.17604,53.557360000000003,53.682409999999997,53.162750000000003,53.183630000000001,53.186300000000003,52.208010000000002,51.86401,52.278080000000003,42.25629,41.700369999999999,41.971020000000003,42.273040000000002,41.745429999999999,41.634459999999997,42.062220000000003,41.823509999999999,41.677219999999998,42.028979999999997,41.50732,41.711219999999997,41.351100000000002,41.737430000000003,41.332610000000003,135.38929999999999,6049.02,5946.4319999999998,51.295909999999999,40.510899999999999,29,29,433757.57040000003,269671.38439277827,831.79327324949998,48,47,32619.370595100001,44,10.143649537292911,10.75078953729291,274552.81016500003,6431.4861185169266,164.0027625543311,28.613462554331107,1,-102.58800000000065,-485.05411851692679,{"$f":"IF(AZ199>1,1+AY200*60/$BK$7,IF(AZ199<0,AY200*60/$BK$7,AZ199+AY200*60/$BK$7))","v":-5.1002512826021067E-3},0,{"$f":"IF(BB199>1,1+AX200*60/$BK$7,BB199+AX200*60/$BK$7)","v":0.45174377216928308},0.45174377216928308,6068.2744243012467,-121.84242430124687,{"$f":"IF(BF199>1,1+BE200*60/$BK$7,IF(BF199<0,BE200*60/$BK$7,BF199+BE200*60/$BK$7))","v":0.20742153968646457},0.20742153968646457,42,0.60929377578371191]
["2013-01-09T03:00:00","2013-01-09T03:00:00",53.620719999999999,53.516820000000003,53.184310000000004,53.552840000000003,53.674999999999997,53.159269999999999,53.164389999999997,53.183459999999997,52.165430000000001,51.872799999999998,52.281410000000001,41.922379999999997,41.690510000000003,41.95872,42.272959999999998,41.74635,41.639719999999997,42.07244,41.821179999999998,41.686100000000003,42.041420000000002,41.51,41.71922,41.366979999999998,41.753570000000003,41.332120000000003,108.19670000000001,5988.8379999999997,5958.8389999999999,50.956789999999998,40.4437,29,29,433757.57040000003,260505.86484635019,664.79298380999978,49,48,31480.596444709994,44,10.165664338764611,10.772804338764612,275148.67318127031,6193.5148349656592,130.79184235406089,22.595142354060883,1,-29.998999999999796,-234.67583496565931,-2.4675715195222199E-3,0,0.45142833842202496,0.45142833842202496,5844.4571078731906,114.38189212680936,0.20862424340498964,0.20862424340498964,42,0.60897834203645373]
["2013-01-09T04:00:00","2013-01-09T04:00:00",53.616439999999997,53.512300000000003,53.182920000000003,53.545349999999999,53.664059999999999,53.158149999999999,53.177129999999998,53.194119999999998,52.251739999999998,51.881860000000003,52.279780000000002,41.792929999999998,41.694629999999997,41.957180000000001,42.279719999999998,41.759250000000002,41.654049999999998,42.079729999999998,41.830269999999999,41.687489999999997,42.052979999999998,41.510599999999997,41.719810000000003,41.365369999999999,41.746650000000002,41.319400000000002,157.1053,6084.0159999999996,5947.4690000000001,51.412179999999999,40.585140000000003,29,29,433757.57040000003,273175.95123821881,965.96507915599955,49,48,32935.94229631999,44,10.215291632304513,10.822431632304511,276491.90895180544,6448.3606502558214,189.12139054381225,32.016090543812254,1,-136.54699999999957,-500.89165025582133,-5.2667798996799747E-3,0,0.44999257283361016,0.44999257283361016,6086.6066731265018,-139.1376731265018,0.20716123738415332,0.20716123738415332,42,0.607542576448039]
["2013-01-09T05:00:00","2013-01-09T05:00:00",53.631079999999997,53.509050000000002,53.17559,53.52261,53.574750000000002,53.0411,53.068620000000003,53.130029999999998,52.37379,51.876559999999998,52.275179999999999,41.994579999999999,41.709350000000001,41.972769999999997,42.295900000000003,41.781669999999998,41.655900000000003,42.098730000000003,41.84451,41.704509999999999,42.058149999999998,41.514400000000002,41.71801,41.364379999999997,41.723599999999998,41.323909999999998,354.41699999999997,6300.2030000000004,5945.7860000000001,51.622610000000002,40.703020000000002,29,29,433757.57040000003,278749.47923337726,2180.9351349449998,50,49,34397.816838384999,44,10.32598855418893,10.933128554188929,279488.08413197566,6662.3774872248687,422.41672523649328,67.999725236493305,1,-354.41700000000037,-716.59148722486862,-7.5348224297014125E-3,0,0.44626594586597845,0.44626594586597845,6292.4014234161341,-346.61542341613404,0.20351664250213683,0.20351664250213683,42,0.60381594948040729]
["2013-01-09T06:00:00","2013-01-09T06:00:00",53.625860000000003,53.490720000000003,53.096960000000003,53.391930000000002,53.464320000000001,52.929549999999999,52.955060000000003,53.094659999999998,52.56129,51.920490000000001,52.27901,44.136890000000001,41.724429999999998,41.992049999999999,42.316800000000001,41.785629999999998,41.655929999999998,42.09657,41.854689999999998,41.730620000000002,42.087780000000002,41.548729999999999,41.75647,41.402540000000002,41.75461,41.35172,413.75560000000002,6371.2910000000002,5957.5349999999999,52.110080000000004,40.581090000000003,27,27,403843.25520000001,271108.72607604077,2539.2470800920009,51,50,36727.275113044998,44,10.466270081354835,11.073410081354833,263748.11295809841,7018.2165809905664,485.22483374770712,71.469233747707108,1,-413.75600000000031,-1060.6815809905665,-1.1152863953449318E-2,0,0.44191538066278724,0.44191538066278724,6633.4173200874375,-675.88232008743762,0.19640986917866954,0.19640986917866954,42,0.59946538427721607]
["2013-01-09T07:00:00","2013-01-09T07:00:00",53.580970000000001,53.327649999999998,52.996630000000003,53.381120000000003,53.481119999999997,52.964199999999998,52.989490000000004,53.15652,52.73498,51.960560000000001,52.277729999999998,46.808439999999997,41.761989999999997,42.022039999999997,42.330599999999997,41.787979999999997,41.680419999999998,42.125300000000003,41.887749999999997,41.767960000000002,42.108199999999997,41.569299999999998,41.770589999999999,41.408189999999998,41.77957,41.362670000000001,500.68599999999998,6452.3040000000001,5951.6180000000004,52.292960000000001,40.593730000000001,27,27,403843.25520000001,275441.33097811253,3058.7658769,51,50,37743.494262960005,44,10.500923154366937,11.108063154366935,264621.36413011083,7188.6049841749209,582.57085247366558,81.884852473665603,1,-500.68599999999969,-1236.9869841749205,-1.3006681546978944E-2,0,0.43665076313621365,0.43665076313621365,6795.6931354179105,-844.07513541791013,0.18753458057130662,0.18753458057130662,42,0.59420076675064248]
["2013-01-09T08:00:00","2013-01-09T08:00:00",53.506900000000002,53.348590000000002,53.017609999999998,53.344749999999998,53.45035,52.95194,52.98648,53.188839999999999,52.829459999999997,52.042479999999998,52.268900000000002,48.496090000000002,41.771889999999999,42.032760000000003,42.348529999999997,41.79365,41.683059999999998,42.116660000000003,41.886890000000001,41.764879999999998,42.110059999999997,41.5792,41.75591,41.391770000000001,41.773470000000003,41.358780000000003,556.93119999999999,6514.4040000000005,5957.473,52.24738,40.637529999999998,27,27,403843.25520000001,274390.75051881286,3382.8335246719994,51,50,37815.6266397,44,10.50338286841377,11.110522868413771,264683.34847918892,7200.6566100567088,644.14171454132236,87.210514541322368,1,-556.93100000000049,-1243.1836100567089,-1.3071837882931783E-2,0,0.43079474019230835,0.43079474019230835,6807.1731794381103,-849.70017943811035,0.17860014570194219,0.17860014570194219,42,0.58834474380673718]
["2013-01-09T09:00:00","2013-01-09T09:00:00",53.465330000000002,53.298720000000003,52.934750000000001,53.291319999999999,53.42933,52.916249999999998,52.8964,53.079140000000002,52.792729999999999,52.381010000000003,52.29034,50.228949999999998,41.790579999999999,42.05209,42.353209999999997,41.806370000000001,41.684629999999999,42.108969999999999,41.887880000000003,41.780889999999999,42.12032,41.583449999999999,41.755580000000002,41.386490000000002,41.766680000000001,41.349139999999998,600.42309999999998,6564.518,5964.0950000000003,52.525770000000001,40.597099999999998,27,27,403843.25520000001,281649.05442123697,3637.4201799945008,52,51,39152.984465530018,44,10.609833770274575,11.216973770274574,267365.89195171901,7380.5085571131922,685.66958894029244,85.246488940292465,1,-600.42299999999977,-1416.4135571131919,-1.4893317643502234E-2,0,0.42448140718687599,0.42448140718687599,6981.0245200513855,-1016.9295200513852,0.16790732630105501,0.16790732630105501,42,0.58203141080130483]
["2013-01-09T10:00:00","2013-01-09T10:00:00",53.434649999999998,53.260669999999998,52.981560000000002,53.341880000000003,53.448210000000003,52.937040000000003,52.940480000000001,53.157220000000002,52.894469999999998,52.637540000000001,52.356459999999998,51.584600000000002,41.86918,42.070770000000003,42.368009999999998,41.823140000000002,41.698689999999999,42.125230000000002,41.910719999999998,41.823880000000003,42.160519999999998,41.624209999999998,41.788980000000002,41.414299999999997,41.780790000000003,41.386620000000001,628.65499999999997,6591.01,5962.3540000000003,52.442149999999998,40.625149999999998,27,27,403843.25520000001,278597.35632526228,3787.0271498249995,53,52,38942.982584999998,44,10.663519706148501,11.270659706148502,268718.76782527036,7303.9641053123923,710.27714191617792,81.622141916177952,1,-628.65599999999995,-1341.6101053123921,-1.4106773655056991E-2,0,0.41787120958641255,0.41787120958641255,6910.5063235571515,-948.15232355715125,0.15793768596667287,0.15793768596667287,42,0.57542121320084139]
["2013-01-09T11:00:00","2013-01-09T11:00:00",53.399250000000002,53.294499999999999,52.958109999999998,53.31194,53.408709999999999,52.894489999999998,52.903770000000002,53.125230000000002,52.86186,52.663980000000002,52.670729999999999,52.066380000000002,42.351529999999997,42.084299999999999,42.400660000000002,41.863439999999997,41.733049999999999,42.133859999999999,41.917090000000002,41.83502,42.169289999999997,41.635539999999999,41.811599999999999,41.44014,41.823500000000003,41.444929999999999,617.26750000000004,6571.9250000000002,5954.6580000000004,52.408749999999998,40.628830000000001,27,27,403843.25520000001,276286.28091335628,3689.5066103000008,54,53,38708.375372999988,44,10.716366600219301,11.3235066002193,270050.49999714503,7224.1603552845718,688.57416845453918,71.306668454539135,1,-617.26699999999983,-1269.5023552845714,-1.3348574455162743E-2,0,0.41138076514263838,0.41138076514263838,6836.8177349320986,-882.15973493209822,0.14866194507964781,0.14866194507964781,42,0.56893076875706727]
["2013-01-09T12:00:00","2013-01-09T12:00:00",53.38702,53.263950000000001,52.928199999999997,53.280119999999997,53.377139999999997,52.88232,52.891620000000003,53.116070000000001,52.865340000000003,52.684649999999998,52.888809999999999,52.237609999999997,43.684089999999998,42.102290000000004,42.4193,41.876109999999997,41.746339999999996,42.166899999999998,41.950389999999999,41.861469999999997,42.191119999999998,41.640099999999997,41.820070000000001,41.453949999999999,41.832340000000002,41.480159999999998,736.36149999999998,6682.1289999999999,5945.768,52.426580000000001,40.651949999999999,27,27,403843.25520000001,275847.80406059045,4383.8766449450004,54,53,39339.798293635002,44,10.737898121812954,11.345038121812953,270593.09044677997,7327.2809720032974,816.52416426630055,80.162664266300567,1,-736.36099999999988,-1381.5129720032974,-1.452634466631249E-2,0,0.40363807006731123,0.40363807006731123,6935.1548881967874,-989.38688819678737,0.13825873118478571,0.13825873118478571,42,0.56118807368174006]
["2013-01-09T13:00:00","2013-01-09T13:00:00",53.354889999999997,53.226260000000003,52.908580000000001,53.277160000000002,53.375639999999997,52.877929999999999,52.873249999999999,53.105690000000003,52.872010000000003,52.698169999999998,52.977760000000004,52.447789999999998,45.33916,42.118980000000001,42.435180000000003,41.903790000000001,41.768929999999997,42.176879999999997,41.968200000000003,41.890450000000001,42.218600000000002,41.668460000000003,41.84037,41.465870000000002,41.856270000000002,41.480530000000002,847.52840000000003,6803.3670000000002,5955.8379999999997,52.591369999999998,40.768630000000002,25,25,373928.94,259251.07251947894,5031.9286659119989,56,54,40217.219582789985,44,10.82866518777314,11.435805187773139,252667.04082540405,7427.9181940540639,929.37191771219386,81.84351771219383,1,-847.52900000000045,-1472.0801940540641,-1.5478641683887476E-2,0,0.3947264647344691,0.3947264647344691,7033.5615065897018,-1077.7235065897021,0.12692667464317581,0.12692667464317581,42,0.55227646834889799]
["2013-01-09T14:00:00","2013-01-09T14:00:00",53.351709999999997,53.221020000000003,52.89461,53.257759999999998,53.365560000000002,52.882919999999999,52.900219999999997,53.136620000000001,52.910870000000003,52.741149999999998,53.039450000000002,52.886450000000004,49.020560000000003,42.195920000000001,42.459180000000003,41.918570000000003,41.7879,42.195140000000002,41.980310000000003,41.907420000000002,42.22963,41.682139999999997,41.837290000000003,41.455190000000002,41.848999999999997,41.481079999999999,1016.908,6958.2020000000002,5941.2929999999997,52.843089999999997,40.66751,25,25,373928.94,265111.6637875305,6035.6693060199987,56,55,42360.072553579987,44,10.962583474077078,11.569723474077078,255791.77841088513,7728.1185869640476,1101.1399494092577,84.231949409257709,1,-1016.9090000000006,-1786.8255869640479,-1.8788129290735266E-2,0,0.38403386109799748,0.38403386109799748,7322.5730327075198,-1381.2800327075201,0.11240277928900541,0.11240277928900541,42,0.54158386471242637]
["2013-01-09T15:00:00","2013-01-09T15:00:00",53.299300000000002,53.192810000000001,52.877519999999997,53.245699999999999,53.355559999999997,52.884480000000003,52.89799,53.15014,52.929850000000002,52.757449999999999,53.0762,52.987609999999997,51.65992,42.550800000000002,42.482889999999998,41.943710000000003,41.830970000000001,42.211089999999999,41.97983,41.910499999999999,42.225189999999998,41.686529999999998,41.847859999999997,41.460160000000002,41.837249999999997,41.498779999999996,1021.284,6954.5609999999997,5933.277,53.086689999999997,40.706290000000003,25,25,373928.94,270382.62595440098,6025.8411338400028,56,55,43050.123502199975,44,10.98611421142502,11.593254211425018,256340.82500813864,7837.1884132480545,1096.9922609348853,75.708260934885288,1,-1021.2839999999997,-1903.9114132480545,-2.0019264359756834E-2,0,0.37329525517330781,0.37329525517330781,7426.7539928132655,-1493.4769928132655,9.6699154358611622E-2,9.6699154358611622E-2,42,0.5308452587877367]
["2013-01-09T16:00:00","2013-01-09T16:00:00",53.294490000000003,53.17221,52.867260000000002,53.244959999999999,53.356430000000003,52.88552,52.902839999999998,53.152000000000001,52.943010000000001,52.792850000000001,53.123130000000003,53.041069999999998,52.398380000000003,43.385649999999998,42.506929999999997,41.959220000000002,41.835590000000003,42.217480000000002,41.992669999999997,41.926470000000002,42.238599999999998,41.69511,41.851840000000003,41.452820000000003,41.843470000000003,41.499760000000002,999.14930000000004,6960.357,5961.2079999999996,53.081090000000003,40.669280000000001,25,25,373928.94,270229.09372306848,5892.3481115945006,57,55,43195.314308085006,44,10.9910652179057,11.598205217905699,256456.34766350646,7860.0778817534283,1072.2069234918547,73.057623491854656,1,-999.14900000000034,-1898.8698817534287,-1.996625362035653E-2,0,0.36278939453997977,0.36278939453997977,7448.620454033462,-1487.4124540334624,8.105929689355687E-2,8.105929689355687E-2,42,0.52033939815440866]
["2013-01-09T17:00:00","2013-01-09T17:00:00",53.300629999999998,53.172049999999999,52.851939999999999,53.235250000000001,53.339010000000002,52.871409999999997,52.884430000000002,53.134149999999998,52.90936,52.76728,53.09901,53.020969999999998,52.886609999999997,45.454830000000001,42.521180000000001,41.969110000000001,41.848050000000001,42.231900000000003,42.011000000000003,41.941949999999999,42.2562,41.713009999999997,41.865479999999998,41.471679999999999,41.846890000000002,41.503610000000002,962.62620000000004,6907.84,5945.2150000000001,53.244169999999997,40.65793,23,23,344014.62479999999,252028.8790245337,5678.0602669619984,57,55,43471.866060799985,44,11.00049563267328,11.607635632673279,236142.27796773973,7903.6195299567053,1032.3280798543706,69.701879854370532,1,-962.625,-1958.4045299567051,-2.0592249059352953E-2,0,0.35266757678090943,0.35266757678090943,7490.2189276918689,-1545.0039276918687,6.4813876098184814E-2,6.4813876098184814E-2,42,0.51021758039533827]
["2013-01-09T18:00:00","2013-01-09T18:00:00",53.307499999999997,53.17051,52.861559999999997,53.245519999999999,53.344410000000003,52.874360000000003,52.897449999999999,53.148119999999999,52.934640000000002,52.792059999999999,53.131390000000003,53.065069999999999,53.062640000000002,49.244120000000002,42.624110000000002,41.985199999999999,41.856960000000001,42.26173,42.021250000000002,41.957140000000003,42.266539999999999,41.719259999999998,41.873869999999997,41.490450000000003,41.871859999999998,41.50441,1023.8339999999999,6972.375,5948.5410000000002,53.094630000000002,40.72992,23,23,344014.62479999999,248801.6035221261,6042.2024235299987,56,55,43105.697443125013,44,10.988009282810564,11.595149282810562,235874.23958123958,7845.9521344887744,1099.7810919184983,75.947091918498359,1,-1023.8339999999998,-1897.4111344887742,-1.9950915171875163E-2,0,0.34190215809394403,0.34190215809394403,7435.1259120100895,-1486.5849120100893,4.9182720079226465E-2,4.9182720079226465E-2,42,0.49945216170837287]
["2013-01-09T19:00:00","2013-01-09T19:00:00",53.298690000000001,53.17671,52.879420000000003,53.256039999999999,53.34966,52.881390000000003,52.896909999999998,53.147080000000003,52.934820000000002,52.795659999999998,53.133879999999998,53.063249999999996,53.062989999999999,52.039650000000002,42.861930000000001,42.002369999999999,41.885249999999999,42.293619999999997,42.050820000000002,41.975029999999997,42.283549999999998,41.743130000000001,41.870690000000003,41.493920000000003,41.871870000000001,41.512819999999998,982.2296,6947.6319999999996,5965.402,53.1464,40.705649999999999,23,23,344014.62479999999,249732.39150792095,5788.2151878760014,57,55,43216.876402000002,44,10.9918004853082,11.5989404853082,235955.62347737691,7863.475407830465,1053.1878186130859,70.958218613085933,1,-982.22999999999956,-1898.0734078304649,-1.9957878849393703E-2,0,0.33157419750961298,0.33157419750961298,7451.866221184714,-1486.464221184714,3.355283310121307E-2,3.355283310121307E-2,42,0.48912420112404181]
["2013-01-09T20:00:00","2013-01-09T20:00:00",53.29542,53.177280000000003,52.874299999999998,53.233710000000002,53.3399,52.874139999999997,52.89526,53.149479999999997,52.940249999999999,52.800289999999997,53.122579999999999,53.055779999999999,53.042949999999998,53.016449999999999,43.42,42.004959999999997,41.882689999999997,42.298389999999998,42.048250000000003,41.961860000000001,42.282380000000003,41.739989999999999,41.877920000000003,41.500129999999999,41.894620000000003,41.536119999999997,1024.8589999999999,6972.3029999999999,5947.4449999999997,52.872309999999999,40.728250000000003,23,23,344014.62479999999,243348.46532951837,6025.8122193500012,56,54,42336.032985089987,44,10.900916724791569,11.508056724791569,234004.66608824552,7767.4261814708925,1105.5606370509572,80.701637050957288,1,-1024.8580000000002,-1819.9811814708928,-1.9136754025488589E-2,0,0.32079801165850236,0.32079801165850236,7357.6336991607532,-1410.1886991607535,1.8724968648486769E-2,1.8724968648486769E-2,42,0.47834801527293119]
["2013-01-09T21:00:00","2013-01-09T21:00:00",53.315190000000001,53.195030000000003,52.873860000000001,53.2453,53.33473,52.862319999999997,52.881509999999999,53.133429999999997,52.924869999999999,52.789479999999998,53.11524,53.048870000000001,53.044609999999999,53.215260000000001,45.761200000000002,42.02178,41.900849999999998,42.309199999999997,42.077689999999997,41.988639999999997,42.289569999999998,41.748190000000001,41.892560000000003,41.50459,41.898800000000001,41.554839999999999,867.32159999999999,6825.4089999999997,5958.0879999999997,52.892719999999997,40.643050000000002,21,21,314100.30960000004,222220.85297615721,5100.0027892800008,56,54,41804.503932514977,44,10.882791584098761,11.489931584098761,213301.18404676818,7682.6802405362696,937.26003109933652,69.938431099336526,1,-867.32099999999991,-1724.5922405362699,-1.8133757556073209E-2,0,0.31167829723116597,0.31167829723116597,7276.7193827976162,-1318.6313827976164,4.8598118656601949E-3,4.8598118656601949E-3,41,0.4692283008455948]
["2013-01-09T22:00:00","2013-01-09T22:00:00",53.347709999999999,53.173169999999999,52.832360000000001,53.215980000000002,53.319130000000001,52.851889999999997,52.876690000000004,53.128729999999997,52.914610000000003,52.776490000000003,53.104320000000001,53.04466,53.031419999999997,53.276069999999997,48.163200000000003,42.036380000000001,41.906689999999998,42.302070000000001,42.077649999999998,42.01108,42.312809999999999,41.748719999999999,41.903480000000002,41.504440000000002,41.906939999999999,41.561500000000002,647.17690000000005,6615.8710000000001,5968.6930000000002,52.565669999999997,40.689680000000003,21,21,314100.30960000004,215680.18392280029,3813.8814252744992,56,55,39285.008918644977,44,10.857723804125794,11.464863804125793,212809.8590858574,7236.3249659596586,702.51951404865804,55.342614048657992,1,-647.17799999999988,-1267.6319659596584,-1.3328907669150245E-2,0,0.30487334434330243,0.30487334434330243,6853.1139296234314,-884.42092962343122,-4.4397050510581217E-3,0,41,0.46242334795773127]
["2013-01-09T23:00:00","2013-01-09T23:00:00",53.402349999999998,53.131480000000003,52.826259999999998,53.205309999999997,53.308540000000001,52.844430000000003,52.862990000000003,53.123139999999999,52.912350000000004,52.779530000000001,53.107799999999997,53.040469999999999,53.03781,53.262689999999999,50.142560000000003,42.057639999999999,41.915849999999999,42.324460000000002,42.083100000000002,42.014020000000002,42.325940000000003,41.76802,41.900779999999997,41.507489999999997,41.902439999999999,41.562890000000003,596.24929999999995,6557.0950000000003,5960.8450000000003,52.29128,40.641849999999998,21,21,314100.30960000004,210274.93471979551,3529.6348686889983,56,55,38193.20960292501,44,10.820493447459743,11.427633447459742,212080.1493328051,7059.4210492112779,652.39813430461027,56.148834304610318,1,-596.25,-1098.5760492112777,-1.1551317038925929E-2,0,0.29860388963472362,0.29860388963472362,6684.3602883351159,-723.51528833511566,-7.6076248740987321E-3,0,41,0.45615389324915245]
["2013-01-10","2013-01-10",53.318730000000002,53.133220000000001,52.824269999999999,53.206240000000001,53.310760000000002,52.847320000000003,52.861899999999999,53.127249999999997,52.917340000000003,52.778320000000001,53.10763,53.04336,53.03342,53.269680000000001,51.759619999999998,42.075409999999998,41.929630000000003,42.337110000000003,42.109209999999997,42.059829999999998,42.351739999999999,41.780090000000001,41.899099999999997,41.514949999999999,41.90746,41.568049999999999,563.59220000000005,6515.6180000000004,5952.0249999999996,52.13447,40.57123,21,21,314100.30960000004,207100.34550589067,3311.2957963480012,56,55,37670.827341160002,44,10.802680212333557,11.409820212333555,211731.01243031491,6974.3483285103139,613.05078577952395,49.458585779523901,1,-563.59300000000076,-1022.3233285103142,-1.074953426518907E-2,0,0.29267781703502199,0.29267781703502199,6603.2289098542242,-651.20390985422455,-6.8472845599673281E-3,0,41,0.45022782064945083]
["2013-01-10T01:00:00","2013-01-10T01:00:00",53.32217,53.127249999999997,52.829700000000003,53.219740000000002,53.318980000000003,52.861919999999998,52.88391,53.147979999999997,52.933149999999998,52.789189999999998,53.12162,53.053519999999999,53.03143,53.267530000000001,53.021140000000003,42.098520000000001,41.947690000000001,42.344560000000001,42.14378,42.08184,42.38541,41.809730000000002,41.941670000000002,41.527999999999999,41.912570000000002,41.565350000000002,538.9067,6484.402,5945.4949999999999,51.824390000000001,40.57349,21,21,314100.30960000004,201075.74074840412,3167.9145343469991,56,55,36477.679230900001,44,10.761993861773691,11.36913386177369,210933.56568313637,6778.9816086901383,588.72260568728723,49.815905687287227,1,-538.90700000000015,-833.48660869013838,-8.7639522740290115E-3,0,0.28701131300376648,0.28701131300376648,6416.9671453246738,-471.47214532467387,-4.9574394322340369E-3,0,41,0.44456131661819531]
["2013-01-10T02:00:00","2013-01-10T02:00:00",53.293059999999997,53.128839999999997,52.82629,53.209110000000003,53.307929999999999,52.850299999999997,52.876519999999999,53.129730000000002,52.924219999999998,52.770710000000001,53.105530000000002,53.038179999999997,53.019629999999999,53.249769999999998,53.173859999999998,42.130040000000001,41.968629999999997,42.370489999999997,42.133780000000002,42.131410000000002,42.426819999999999,41.85004,41.970379999999999,41.569690000000001,41.936430000000001,41.564300000000003,502.21710000000002,6464.0619999999999,5961.8450000000003,51.935560000000002,40.57441,21,21,314100.30960000004,203275.23696118681,2945.1919168979985,56,55,36719.58899565001,44,10.770242984751667,11.377382984751664,211095.24733301013,6818.7113415429903,546.91280801514938,44.695708015149364,1,-502.21699999999964,-856.86634154299009,-9.0097856932652813E-3,0,0.28173059730501876,0.28173059730501876,6454.839227063515,-492.9942270635147,-5.1837400053090796E-3,0,41,0.43928060091944759]
["2013-01-10T03:00:00","2013-01-10T03:00:00",53.287559999999999,53.127740000000003,52.82114,53.217979999999997,53.306269999999998,52.845469999999999,52.861440000000002,53.116630000000001,52.905009999999997,52.755420000000001,53.075870000000002,53.01755,53.00065,53.215200000000003,53.350250000000003,42.176929999999999,42.016930000000002,42.405720000000002,42.136839999999999,42.095970000000001,42.403010000000002,41.830219999999997,41.966560000000001,41.56156,41.942059999999998,41.564540000000001,525.46969999999999,6478.2910000000002,5952.8209999999999,51.790790000000001,40.62482,21,21,314100.30960000004,200433.0613613328,3080.0459012469992,56,55,36168.201478635005,44,10.751440670421454,11.358580670421453,210726.7246172656,6728.066049443627,572.95501052627992,47.485310526279932,1,-525.47000000000025,-775.24504944362707,-8.1515534180910433E-3,0,0.27620538075874301,0.27620538075874301,6368.4367841520125,-415.61578415201257,-4.3701204778390313E-3,0,41,0.43375538437317185]
["2013-01-10T04:00:00","2013-01-10T04:00:00",53.296979999999998,53.124920000000003,52.817250000000001,53.210099999999997,53.299399999999999,52.833880000000001,52.847760000000001,53.095059999999997,52.88082,52.736559999999997,53.053190000000001,52.984699999999997,52.963120000000004,53.194839999999999,53.369160000000001,42.662779999999998,42.054279999999999,42.446469999999998,42.194070000000004,42.163870000000003,42.498829999999998,41.956699999999998,42.071199999999997,41.60078,41.975230000000003,41.570920000000001,635.69200000000001,6573.7449999999999,5938.0529999999999,52.050289999999997,40.624499999999998,21,21,314100.30960000004,205394.17775216812,3727.0812667599989,56,55,37555.114941774991,44,10.798734419514528,11.405874419514527,211653.67544615982,6955.4659801446142,690.28112405926834,54.589124059268329,1,-635.69200000000001,-1017.4129801446143,-1.0697902891298756E-2,0,0.26952120096401616,0.26952120096401616,6585.2232911702476,-647.17029117024776,-6.8048718309931221E-3,0,41,0.427071204578445]
["2013-01-10T05:00:00","2013-01-10T05:00:00",53.296939999999999,53.129570000000001,52.814990000000002,53.211010000000002,53.283299999999997,52.821289999999998,52.825229999999998,53.074460000000002,52.857399999999998,52.713419999999999,53.036839999999998,52.974249999999998,52.953719999999997,53.198689999999999,53.457259999999998,46.102150000000002,42.096449999999997,42.50197,42.235190000000003,42.188369999999999,42.516010000000001,41.979689999999998,42.124130000000001,41.684710000000003,42.014569999999999,41.593449999999997,895.47429999999997,6848.2640000000001,5952.79,52.182310000000001,40.614440000000002,19,19,284185.99440000003,187774.43622053284,5240.0872576535012,56,55,39609.913838840002,44,10.868803061904444,11.475943061904443,192738.72421970894,7288.735220104265,964.24366653954758,68.769366539547605,1,-895.47400000000016,-1335.945220104265,-1.404720847058462E-2,0,0.26010546312634752,0.26010546312634752,6903.1213600787414,-950.33136007874145,-9.9925524866344654E-3,0,41,0.41765546674077636]
["2013-01-10T06:00:00","2013-01-10T06:00:00",53.294170000000001,53.127099999999999,52.818759999999997,53.211039999999997,53.294820000000001,52.83164,52.820900000000002,53.078330000000001,52.860790000000001,52.71275,53.034689999999998,52.979109999999999,52.960790000000003,53.211680000000001,53.501220000000004,49.972580000000001,42.110930000000003,42.517090000000003,42.240580000000001,42.196379999999998,42.5242,41.973109999999998,42.092779999999998,41.700589999999998,42.055819999999997,41.613059999999997,876.4769,6835.174,5958.6980000000003,52.888739999999999,40.734209999999997,19,19,284185.99440000003,199953.95680017842,5119.1115406795025,56,55,41539.163719110002,44,10.934590482821651,11.54173048282165,193905.3461103687,7597.7538956522303,936.31518230548761,59.83828230548761,1,-876.47599999999966,-1639.05589565223,-1.7234359249678463E-2,0,0.2508894856250371,0.2508894856250371,7198.0824332946586,-1239.3844332946583,-1.303189026592623E-2,0,41,0.40843948923946594]
["2013-01-10T07:00:00","2013-01-10T07:00:00",53.290849999999999,53.12135,52.805210000000002,53.196660000000001,53.273650000000004,52.814250000000001,52.826680000000003,53.080860000000001,52.865049999999997,52.720790000000001,53.056730000000002,52.989690000000003,52.977829999999997,53.228140000000003,53.521329999999999,52.157649999999997,42.136969999999998,42.531059999999997,42.286340000000003,42.201729999999998,42.521619999999999,41.982109999999999,42.126289999999997,41.729030000000002,42.091430000000003,41.629150000000003,761.96469999999999,6709.9210000000003,5947.9570000000003,52.79654,40.655410000000003,19,19,284185.99440000003,198033.62791696322,4442.9018709949978,57,55,40733.011575364995,44,10.907100694719947,11.514240694719946,193417.86403367497,7469.0814205251745,814.68063701764049,52.715937017640499,1,-761.96399999999994,-1521.1244205251742,-1.5994332344814781E-2,0,0.24287757990165335,0.24287757990165335,7075.2405921206446,-1127.2835921206442,-1.1853171361885859E-2,0,41,0.40042758351608215]
["2013-01-10T08:00:00","2013-01-10T08:00:00",53.284799999999997,53.123660000000001,52.811390000000003,53.210859999999997,53.266109999999998,52.799480000000003,52.816740000000003,53.063029999999998,52.85033,52.692439999999998,53.043219999999998,52.960889999999999,52.965769999999999,53.202660000000002,53.491799999999998,52.872750000000003,42.157049999999998,42.541969999999999,42.263750000000002,42.205629999999999,42.536200000000001,41.973610000000001,42.112789999999997,41.734650000000002,42.115960000000001,41.654000000000003,719.48519999999996,6666.5219999999999,5947.0370000000003,52.89143,40.697000000000003,19,19,284185.99440000003,199275.6616687444,4184.0942320799968,54,52,40647.217936229987,44,10.721634131625445,11.328774131625444,190128.94725483094,7582.2803571208415,780.49561861810537,61.010418618105405,1,-719.48499999999967,-1635.2433571208412,-1.7194271136223949E-2,0,0.23531233273854751,0.23531233273854751,7175.9252084934915,-1228.8882084934912,-1.2921524469696494E-2,0,41,0.39286233635297635]
["2013-01-10T09:00:00","2013-01-10T09:00:00",53.287509999999997,53.126959999999997,52.809420000000003,53.206890000000001,53.257739999999998,52.792960000000001,52.806339999999999,53.072859999999999,52.847200000000001,52.694240000000001,53.039319999999996,52.968249999999998,52.974589999999999,53.220419999999997,53.499830000000003,52.966990000000003,42.195869999999999,42.566200000000002,42.300600000000003,42.210610000000003,42.538290000000003,41.99586,42.165030000000002,41.797130000000003,42.184019999999997,41.676110000000001,869.23869999999999,6826.7740000000003,5957.5360000000001,52.813499999999998,40.726840000000003,19,19,284185.99440000003,197501.6317354464,5046.5391205899978,56,53,41256.448117419983,44,10.803255880804022,11.410395880804021,191576.3625512218,7637.7804196468796,934.26262902039377,65.02392902039378,1,-869.23800000000028,-1680.2444196468796,-1.7667448701582308E-2,0,0.22617246142286507,0.22617246142286507,7231.378919433756,-1273.8429194337559,-1.3394214656995855E-2,0,41,0.3837224650372939]
["2013-01-10T10:00:00","2013-01-10T10:00:00",53.32244,53.127690000000001,52.813870000000001,53.216500000000003,53.260919999999999,52.781480000000002,52.792679999999997,53.059130000000003,52.839799999999997,52.688569999999999,53.03154,52.965240000000001,52.964570000000002,53.20823,53.498170000000002,52.968200000000003,44.175669999999997,42.581299999999999,42.323639999999997,42.227409999999999,42.562060000000002,42.004739999999998,42.161819999999999,41.7973,42.168860000000002,41.687530000000002,969.29579999999999,6917.598,5948.3019999999997,53.163580000000003,40.726889999999997,19,19,284185.99440000003,203507.15929652911,5638.834698188999,57,53,43016.01093531002,44,10.863256972894073,11.470396972894072,192640.37428051329,7919.5421856710727,1038.148082524234,68.852282524234056,1,-969.29600000000028,-1971.240185671073,-2.0727213524185054E-2,0,0.21598049937471978,0.21598049937471978,7500.3526097591966,-1552.050609759197,-1.6319515309530328E-2,0,41,0.37353050298914858]
["2013-01-10T11:00:00","2013-01-10T11:00:00",53.367159999999998,53.11674,52.805999999999997,53.210369999999998,53.250729999999997,52.783920000000002,52.795090000000002,53.05536,52.83802,52.693069999999999,53.019370000000002,52.96593,52.953740000000003,53.199069999999999,53.490319999999997,52.976840000000003,49.61233,42.612110000000001,42.324489999999997,42.234540000000003,42.558709999999998,42.0047,42.132800000000003,41.766460000000002,42.130429999999997,41.687309999999997,1046.5820000000001,7009.6989999999996,5963.1170000000002,52.969560000000001,40.762700000000002,17,17,254271.67920000001,179010.41512562215,6111.9603863500015,57,52,42783.207167569992,44,10.794471364414138,11.401611364414137,171271.04965812803,7926.8739937765395,1132.4242160665963,85.842216066596166,1,-1046.5819999999994,-1963.7569937765393,-2.0648529192682522E-2,0,0.20497588981863785,0.20497588981863785,7504.7650371774234,-1541.6480371774232,-1.6210134248475179E-2,0,41,0.36252589343306663]
["2013-01-10T12:00:00","2013-01-10T12:00:00",53.407400000000003,53.08502,52.76764,53.176389999999998,53.236789999999999,52.789349999999999,52.793979999999998,53.058480000000003,52.843400000000003,52.691339999999997,53.007649999999998,52.962580000000003,52.946820000000002,53.198970000000003,53.494480000000003,52.985720000000001,52.008479999999999,42.641800000000003,42.370440000000002,42.24494,42.569209999999998,42.034460000000003,42.192120000000003,41.794490000000003,42.135399999999997,41.704680000000003,838.98569999999995,7038.3490000000002,6231.37,53.194870000000002,40.704880000000003,17,17,254271.67920000001,182309.70611112777,4909.2073655519998,57,51,43954.454313254995,44,10.773563892081995,11.380703892081996,170939.32014483021,8159.6869436230327,911.34324996392513,72.35754996392518,1,-806.97900000000027,-1928.3169436230328,-2.027588384373968E-2,0,0.19649065998002277,0.19649065998002277,7724.3823809238802,-1493.0123809238803,-1.5698739625240633E-2,0,41,0.35404066359445152]
["2013-01-10T13:00:00","2013-01-10T13:00:00",53.456870000000002,53.106789999999997,52.759270000000001,53.168689999999998,53.223059999999997,52.773310000000002,52.782800000000002,53.043700000000001,52.835290000000001,52.691279999999999,53.014510000000001,52.968649999999997,52.956130000000002,53.198430000000002,53.49485,52.980899999999998,52.665680000000002,42.76728,42.434780000000003,42.316760000000002,42.640160000000002,42.123060000000002,42.275709999999997,41.852780000000003,42.250779999999999,41.802619999999997,1293.752,8311.7849999999999,7018.0330000000004,53.081510000000002,40.736919999999998,17,17,254271.67920000001,178957.10350827433,7538.8546230000038,57,50,51302.788996575015,44,10.96329510478321,11.570435104783208,173949.70044556211,9359.009039935805,1375.2899198546345,81.537919854634538,1,-1293.7519999999995,-2340.9760399358047,-2.4614915314458332E-2,0,0.18288710514877196,0.18288710514877196,8867.9100711375122,-1849.8770711375118,-1.9451103587312554E-2,0,41,0.34043710876320071]
["2013-01-10T14:00:00","2013-01-10T14:00:00",53.511360000000003,53.121560000000002,52.76041,53.160420000000002,53.21893,52.77214,52.778709999999997,53.047269999999997,52.842289999999998,52.703499999999998,53.001440000000002,52.971730000000001,52.956510000000002,53.199440000000003,53.494390000000003,52.979430000000001,52.867989999999999,47.40457,42.507770000000001,42.405700000000003,42.697670000000002,42.155839999999998,42.299700000000001,41.92492,42.303350000000002,41.884309999999999,845.05060000000003,7870.2709999999997,7025.2209999999995,52.89705,40.574710000000003,15,15,224357.364,154177.25336940328,4912.7227893650015,58,51,48490.077577069991,44,10.928228645378088,11.535368645378087,152994.10289693828,8874.2794739343353,899.08858036983997,54.037980369839943,1,-845.05000000000018,-1849.0584739343358,-1.9442496194289689E-2,0,0.17400156602678529,0.17400156602678529,8407.2003362456326,-1381.979336245633,-1.4531248397121754E-2,0,41,0.33155156964121402]
["2013-01-10T15:00:00","2013-01-10T15:00:00",53.552999999999997,53.186570000000003,52.740720000000003,53.163490000000003,53.217149999999997,52.76887,52.776679999999999,53.045209999999997,52.838149999999999,52.691809999999997,53.00911,52.959510000000002,52.952030000000001,53.193680000000001,53.4925,52.981540000000003,52.846170000000001,50.610999999999997,42.538290000000003,42.40278,42.695880000000002,42.161459999999998,42.312840000000001,41.916969999999999,42.305390000000003,41.936129999999999,430.7568,7453.8869999999997,7023.13,52.579740000000001,40.40419,15,15,224357.364,149009.47046194813,2502.0228736079998,56,50,45377.586931425009,44,10.761245714361593,11.368385714361594,150656.35864222093,8433.5193407703027,465.00617865622849,34.249378656228487,1,-430.75699999999961,-1410.3893407703026,-1.4829974160875104E-2,0,0.16947223856028082,0.16947223856028082,7983.1188123921329,-959.98881239213279,-1.0094098750582585E-2,0,41,0.32702224217470954]
["2013-01-10T16:00:00","2013-01-10T16:00:00",53.623579999999997,53.20626,52.740630000000003,53.155810000000002,53.207410000000003,52.754910000000002,52.766750000000002,53.039670000000001,52.830060000000003,52.683700000000002,53.008540000000004,52.94652,52.944319999999998,53.184840000000001,53.483620000000002,52.972949999999997,52.825020000000002,51.636580000000002,42.561230000000002,42.45355,42.70478,42.188699999999997,42.34619,41.967910000000003,42.382440000000003,41.977310000000003,283.20659999999998,7313.3119999999999,7030.2539999999999,52.11074,40.43965,15,15,224357.364,141867.0017280996,1649.1502646909989,55,49,42677.161275040002,44,10.608314199478865,11.215454199478865,148515.33280140013,8045.9836450048815,310.9165572739189,27.709957273918917,1,-283.05799999999999,-1015.7296450048816,-1.0680202944266616E-2,0,0.1664959378292101,0.1664959378292101,7610.4204994253423,-580.16649942534241,-6.1003397762380155E-3,0,41,0.32404594144363885]
["2013-01-10T17:00:00","2013-01-10T17:00:00",53.61739,53.212330000000001,52.731259999999999,53.153689999999997,53.20487,52.747909999999997,52.765770000000003,53.030880000000003,52.823529999999998,52.669119999999999,53.001049999999999,52.933970000000002,52.925669999999997,53.173310000000001,53.468060000000001,52.952550000000002,52.797840000000001,52.139069999999997,42.570120000000003,42.442129999999999,42.727449999999997,42.200969999999998,42.362050000000004,41.982669999999999,42.386069999999997,42.01473,227.6738,7244.5439999999999,7033.1790000000001,52.019880000000001,40.42,15,15,224357.364,140071.09461849506,1320.8108461539998,54,49,42017.920527359995,44,10.585834089982978,11.192974089982977,148200.61352740298,7938.5186221877684,249.5430846406027,21.8692846406027,1,-211.36499999999978,-905.33962218776833,-9.5194729680303444E-3,0,0.16427347528081804,0.16427347528081804,7507.9099066196259,-474.73090661962578,-4.9917046839653085E-3,0,41,0.32182347889524682]
["2013-01-10T18:00:00","2013-01-10T18:00:00",53.506129999999999,53.222200000000001,52.727379999999997,53.151859999999999,53.203249999999997,52.746679999999998,52.761249999999997,53.02373,52.818710000000003,52.661610000000003,53.000190000000003,52.93412,52.929259999999999,53.174379999999999,53.467449999999999,52.946399999999997,52.823880000000003,52.271619999999999,42.591250000000002,42.470230000000001,42.748710000000003,42.203150000000001,42.381120000000003,42.006230000000002,42.410440000000001,42.039279999999998,107.71980000000001,7061.5649999999996,7025.8850000000002,51.756720000000001,40.374429999999997,15,15,224357.364,136043.18352943723,617.60339431500006,54,49,40188.39034192502,44,10.523447110659644,11.130587110659643,147327.20208591927,7637.8756731178883,117.37663292656327,9.6568329265632684,1,-35.679999999999382,-611.99067311788804,-6.4349648757824358E-3,0,0.16389830690513318,0.16389830690513318,7221.2525615000177,-195.36756150001747,-2.0542525423058295E-3,0,41,0.32144831051956196]
["2013-01-10T19:00:00","2013-01-10T19:00:00",53.338389999999997,53.2224,52.735849999999999,53.159930000000003,53.214469999999999,52.749540000000003,52.769410000000001,53.02843,52.817500000000003,52.658149999999999,53.011879999999998,52.932989999999997,52.930300000000003,53.171230000000001,53.47025,52.955869999999997,52.808300000000003,52.260800000000003,42.609749999999998,42.463259999999998,42.735430000000001,42.212200000000003,42.378050000000002,42.012300000000003,42.427750000000003,42.048819999999999,121.92829999999999,7019.2969999999996,7026.6220000000003,51.630330000000001,40.288359999999997,15,15,224357.364,134140.17718855356,688.25903891549979,51,48,39806.327997545013,44,10.449571784716287,11.056711784716285,146292.95494617784,7618.7481779428308,131.72961592974721,9.8013159297472185,1,7.3250000000007276,-592.12617794283051,-6.2260935083882111E-3,0,0.1639753278791212,0.1639753278791212,7200.3917209037463,-173.76972090374602,-1.8271553793348788E-3,0,41,0.32152533149354995]
["2013-01-10T20:00:00","2013-01-10T20:00:00",53.321559999999998,53.218350000000001,52.75264,53.162909999999997,53.215589999999999,52.744799999999998,52.782339999999998,53.027720000000002,52.821289999999998,52.65645,53.032699999999998,52.940359999999998,52.935459999999999,53.180480000000003,53.473289999999999,52.963290000000001,52.763550000000002,52.272120000000001,42.592419999999997,42.454129999999999,42.735639999999997,42.214939999999999,42.380360000000003,42.075139999999998,42.501100000000001,42.021839999999997,177.4451,6897.491,7034.165,51.524509999999999,40.132779999999997,15,15,224357.364,133036.42511090133,1002.5399726860001,51,48,39287.17757471501,44,10.431868755297783,11.039008755297782,146045.11431323245,7532.1456771133508,192.20716751768262,14.762067517682624,1,136.67399999999998,-497.98067711335079,-5.2361715738525397E-3,0,0.16541242884824539,0.16541242884824539,7117.8814050420096,-83.716405042009683,-8.8026198704556986E-4,0,41,0.32296243246267414]
["2013-01-10T21:00:00","2013-01-10T21:00:00",53.344880000000003,53.202100000000002,52.790590000000002,53.164819999999999,53.212409999999998,52.73903,52.78145,53.025329999999997,52.81953,52.651440000000001,53.028359999999999,52.93591,52.937289999999997,53.192680000000003,53.47363,52.949280000000002,52.763339999999999,52.380400000000002,42.690040000000003,42.526649999999997,42.790010000000002,42.276940000000003,42.462940000000003,42.104799999999997,42.537300000000002,42.069380000000002,1729.6510000000001,6503.2960000000003,5512.3209999999999,51.764060000000001,41.510210000000001,15,15,224357.364,135724.5458165076,9751.3399252500021,48,46,33341.910844799997,44,10.107441159807681,10.714581159807681,141503.16057693216,6597.4978864847335,1929.5368176915597,199.88581769155962,1,-990.97500000000036,-1085.1768864847336,-1.1410427405639648E-2,0,0.15499251626152183,0.15499251626152183,6223.651741025863,-711.33074102586306,-7.4795066896125332E-3,0,41,0.31254251987595061]
["2013-01-10T22:00:00","2013-01-10T22:00:00",53.390140000000002,53.196510000000004,52.777389999999997,53.164990000000003,53.217350000000003,52.74888,52.782350000000001,53.029240000000001,52.819240000000001,52.653880000000001,53.023960000000002,52.934519999999999,52.937469999999998,53.175939999999997,53.460709999999999,52.947319999999998,52.739490000000004,52.24785,42.88767,42.67042,42.932139999999997,42.344430000000003,42.484760000000001,42.121380000000002,42.56747,42.191339999999997,686.26179999999999,6341.1090000000004,7027.3710000000001,51.886099999999999,39.940190000000001,15,15,224357.364,135725.66580846877,3842.654322920002,49,47,37875.15870709499,44,10.322871911911941,10.93001191191194,144519.16945853108,7338.1049441075502,744.49326809641457,58.231468096414574,1,686.26199999999972,-310.73394410755009,-3.2673079899377014E-3,0,0.16220842993400608,0.16220842993400608,6930.488093213733,96.882906786267085,1.0187052346028798E-3,1.0187052346028798E-3,41,0.31975843354843486]
["2013-01-10T23:00:00","2013-01-10T23:00:00",53.39396,53.162350000000004,52.735770000000002,53.152279999999998,53.203690000000002,52.744459999999997,52.773769999999999,53.024299999999997,52.819740000000003,52.654060000000001,53.030360000000002,52.934229999999999,52.939729999999997,53.190989999999999,53.477939999999997,52.968139999999998,52.598350000000003,49.892189999999999,42.881140000000002,42.709829999999997,42.9069,42.328380000000003,42.472610000000003,42.139899999999997,42.582720000000002,42.612720000000003,806.08510000000001,6232.5129999999999,7038.598,51.355179999999997,39.857509999999998,15,15,224357.364,122393.56150166737,4345.2984617619986,48,46,35829.688872355,44,10.192274390547306,10.799414390547305,142690.81728270097,7030.7543732505446,852.66512561553293,46.580025615532918,1,806.08500000000004,7.8436267494553249,8.2474235063660604E-5,8.2474235063660604E-5,0.17068425953361158,0.17068425953361158,6635.4873656328291,403.11063436717086,5.2573364542447465E-3,5.2573364542447465E-3,41,0.32823426314804038]
["2013-01-11","2013-01-11",53.395499999999998,53.136180000000003,52.722630000000002,53.139769999999999,53.197800000000001,52.732550000000003,52.766190000000002,53.021369999999997,52.814030000000002,52.655200000000001,53.026879999999998,52.929130000000001,52.931710000000002,53.191180000000003,53.470649999999999,52.963990000000003,52.401609999999998,45.334949999999999,42.908050000000003,42.717919999999999,43.005629999999996,42.36092,42.532110000000003,42.180129999999998,42.610320000000002,42.952210000000001,885.08219999999994,6145.17,7030.2520000000004,51.166980000000002,39.88758,15,15,224357.364,115005.95452733588,4621.5850442189985,50,47,34656.915249000005,44,10.213129809990901,10.820269809990901,142982.79105922527,6786.7374436183491,905.02816084800463,19.945960848004688,1,885.08200000000033,243.51455638165135,2.6429832197419527E-3,2.6429832197419527E-3,0.17999072747890027,0.17999072747890027,6405.9244099439229,624.3275900560775,1.182202165201876E-2,1.182202165201876E-2,42,0.33754073109332905]
["2013-01-11T01:00:00","2013-01-11T01:00:00",53.372579999999999,53.055370000000003,52.722160000000002,53.145659999999999,53.198689999999999,52.732880000000002,52.773589999999999,53.00629,52.807160000000003,52.64555,53.027830000000002,52.922800000000002,52.93038,53.193100000000001,53.470509999999997,52.934060000000002,52.080300000000001,43.375160000000001,42.857280000000003,42.710279999999997,42.978729999999999,42.367710000000002,42.537269999999999,42.173119999999997,42.61063,42.647419999999997,967.34739999999999,6070.49,7037.8370000000004,50.827599999999997,39.884590000000003,17,17,254271.67920000001,129791.25773691517,5187.4778202920015,49,46,33214.716387449982,44,10.103103828812046,10.710243828812045,160301.43016268086,6575.1509536560852,1026.9077519520972,59.560351952097221,1,967.34700000000066,462.68604634391522,7.5080385016615958E-3,7.5080385016615958E-3,0.19016219616481997,0.19016219616481997,6202.4202097244097,835.41679027559076,2.060626941624371E-2,2.060626941624371E-2,43,0.34771219977924872]
["2013-01-11T02:00:00","2013-01-11T02:00:00",53.320839999999997,53.038760000000003,52.740209999999998,53.171100000000003,53.20476,52.736420000000003,52.771920000000001,53.004669999999997,52.805619999999998,52.634990000000002,53.027970000000003,52.919609999999999,52.931429999999999,53.184109999999997,53.471760000000003,52.887230000000002,50.839170000000003,43.126300000000001,42.825420000000001,42.708390000000001,42.975990000000003,42.38673,42.548430000000003,42.191780000000001,42.765059999999998,42.602420000000002,936.83720000000005,6093.6639999999998,7030.5010000000002,50.769880000000001,39.87941,17,17,254271.67920000001,129589.43518552708,5020.7072906119984,47,45,33181.432491040003,44,10.041121847944465,10.648261847944465,159317.98979170751,6609.1086222268341,1000.0291534436057,63.191953443605598,1,936.83700000000044,421.39237777316612,1.1938898756570124E-2,1.1938898756570124E-2,0.20001285803621766,0.20001285803621766,6232.2720768639492,798.22892313605098,2.8999493870212903E-2,2.8999493870212903E-2,44,0.35756286165064644]
["2013-01-11T03:00:00","2013-01-11T03:00:00",53.24333,53.026330000000002,52.733980000000003,53.167490000000001,53.213949999999997,52.741410000000002,52.781709999999997,53.019179999999999,52.818100000000001,52.653390000000002,53.038589999999999,52.923409999999997,52.932220000000001,53.17877,53.457709999999999,52.572479999999999,46.482619999999997,43.033540000000002,42.817459999999997,42.705910000000003,42.925910000000002,42.378410000000002,42.55836,42.197580000000002,43.08126,42.557839999999999,1093.222,5926.8180000000002,7020.04,50.813850000000002,39.9602,17,17,254271.67920000001,130994.41843438035,5840.8063743900002,48,45,32163.804092850009,44,10.006420719566187,10.613560719566186,158767.40250669583,6428.6331734899159,1167.4117125555401,74.189712555540154,1,1093.2219999999998,591.4068265100841,1.8157428422229355E-2,1.8157428422229355E-2,0.21150787827172621,0.21150787827172621,6060.8885072011271,959.15149279887282,3.908478836542182E-2,3.908478836542182E-2,44,0.36905788188615501]
["2013-01-11T04:00:00","2013-01-11T04:00:00",53.192250000000001,53.016710000000003,52.73836,53.175460000000001,53.215690000000002,52.745359999999998,52.794049999999999,53.026760000000003,52.818570000000001,52.650959999999998,53.04419,52.926139999999997,52.938589999999998,53.183459999999997,53.46407,52.195140000000002,42.882840000000002,43.03931,42.833649999999999,42.700310000000002,42.98574,42.385599999999997,42.566899999999997,42.215969999999999,43.042740000000002,42.388289999999998,1010.687,6021.01,7031.6980000000003,50.643180000000001,39.93262,19,19,284185.99440000003,146385.66529470729,5459.7109602600021,48,46,32244.194432800003,44,10.070009030158481,10.67714903015848,178573.54506280023,6404.0050681647799,1084.3507575631395,73.663757563139484,1,1010.6880000000001,627.69293183522041,2.4757499545140851E-2,2.4757499545140851E-2,0.2221350692830539,0.2221350692830539,6039.850964283376,991.8470357166243,4.9513870240916254E-2,4.9513870240916254E-2,44,0.37968507289748271]
["2013-01-11T05:00:00","2013-01-11T05:00:00",53.17615,53.017850000000003,52.740079999999999,53.177149999999997,53.214939999999999,52.747970000000002,52.792079999999999,53.03087,52.822539999999996,52.659399999999998,53.045929999999998,52.930349999999997,52.941749999999999,53.192590000000003,53.462209999999999,50.98621,42.6387,43.044649999999997,42.842269999999999,42.709710000000001,42.993639999999999,42.402859999999997,42.595950000000002,42.41384,42.935169999999999,42.394570000000002,882.24440000000004,6160.8819999999996,7043.1260000000002,50.576279999999997,39.908140000000003,19,19,284185.99440000003,145087.94927592718,4755.9942890759994,46,44,32862.57584973998,44,9.9694018364761341,10.576541836476133,176789.45696706255,6592.6875832213127,954.11828454435977,71.873884544359726,1,882.2440000000006,450.4384167786875,2.9493773344718109E-2,2.9493773344718109E-2,0.23141169620115107,0.23141169620115107,6214.2383319289274,828.88766807107277,5.8229465533949587E-2,5.8229465533949587E-2,44,0.38896169981557988]
["2013-01-11T06:00:00","2013-01-11T06:00:00",53.169490000000003,53.017060000000001,52.737639999999999,53.17333,53.20158,52.749400000000001,52.782850000000003,53.029000000000003,52.820880000000002,52.658149999999999,53.040550000000003,52.934260000000002,52.93544,53.188220000000001,53.366680000000002,47.499679999999998,42.646880000000003,43.052370000000003,42.846769999999999,42.728319999999997,42.99306,42.430709999999998,42.607529999999997,42.640279999999997,42.871339999999996,42.453270000000003,839.87220000000002,6185.7709999999997,7025.6440000000002,50.981520000000003,39.933480000000003,19,19,284185.99440000003,151233.21450068831,4500.1276335420007,49,46,34170.322719420001,44,10.135690004732224,10.742830004732223,179738.27931851801,6742.5745466695053,887.97657218027553,48.104372180275504,1,839.8730000000005,283.06945333049498,3.2470194505368359E-2,3.2470194505368359E-2,0.24024280015831373,0.24024280015831373,6361.5123211235687,664.13167887643158,6.5212683112562952E-2,6.5212683112562952E-2,44,0.39779280377274256]
["2013-01-11T07:00:00","2013-01-11T07:00:00",53.152500000000003,53.00694,52.720680000000002,53.164090000000002,53.190089999999998,52.744639999999997,52.775660000000002,53.01905,52.817900000000002,52.651179999999997,53.03586,52.935560000000002,52.929920000000003,53.177,52.910780000000003,43.821539999999999,42.677660000000003,43.092320000000001,42.899810000000002,42.786580000000001,42.973889999999997,42.443489999999997,42.625210000000003,42.647269999999999,42.895760000000003,42.506,802.82320000000004,6228.9210000000003,7031.7449999999999,51.098689999999998,39.969929999999998,21,21,314100.30960000004,168415.51517212176,4273.6285994000018,51,47,34660.083433979999,44,10.213237845098719,10.820377845098719,200178.02495583016,6787.286061415517,836.88026543921012,34.057065439210078,1,802.82399999999961,244.45893858448289,3.5040633488282694E-2,3.5040633488282694E-2,0.24868434096663256,0.24868434096663256,6406.4460465546299,625.29895344536999,7.1787582010588102E-2,7.1787582010588102E-2,44,0.40623434458106139]
["2013-01-11T08:00:00","2013-01-11T08:00:00",53.138109999999998,52.991070000000001,52.706560000000003,53.155659999999997,53.181550000000001,52.733829999999998,52.766979999999997,53.002200000000002,52.801769999999998,52.640520000000002,53.023710000000001,52.926769999999998,52.927070000000001,53.174790000000002,52.336440000000003,43.019480000000001,42.721260000000001,43.08914,42.902389999999997,42.763939999999998,43.021279999999997,42.464869999999998,42.878810000000001,42.565390000000001,42.91433,42.527430000000003,754.26170000000002,6277.5320000000002,7031.7929999999997,51.106819999999999,40.021180000000001,21,21,314100.30960000004,168154.83704317853,4001.6147674779986,48,45,34795.229920239995,44,10.096152340280184,10.703292340280184,197883.16553308809,6892.7703837072586,792.70094836285864,38.439248362858621,1,754.26099999999951,139.02261629274108,3.6502429708518289E-2,3.6502429708518289E-2,0.25661525111832628,0.25661525111832628,6501.7807257853792,530.01227421462045,7.736055970145507E-2,7.736055970145507E-2,44,0.41416525473275512]
["2013-01-11T09:00:00","2013-01-11T09:00:00",53.164090000000002,52.994660000000003,52.708030000000001,53.157170000000001,53.183309999999999,52.737369999999999,52.75291,53.001640000000002,52.800890000000003,52.653289999999998,53.00385,52.922550000000001,52.922420000000002,53.162289999999999,51.14038,42.861919999999998,42.72992,43.09552,42.885620000000003,42.789439999999999,43.115699999999997,42.548990000000003,43.731349999999999,42.531399999999998,42.93862,42.536529999999999,472.92680000000001,6549.5360000000001,7022.4629999999997,51.67324,39.890509999999999,21,21,314100.30960000004,179078.23063886596,2513.0289713040002,52,48,38585.707156639997,44,10.407948614041425,11.015088614041424,203994.3286350093,7414.6613492276083,482.90572225033054,9.9789222503305268,1,472.92699999999968,-392.19834922760856,3.2378539079986834E-2,3.2378539079986834E-2,0.26158798806920941,0.26158798806920941,7005.9730808616614,16.489919138338337,7.7533948047259577E-2,7.7533948047259577E-2,44,0.41913799168363824]
["2013-01-11T10:00:00","2013-01-11T10:00:00",53.193060000000003,52.9923,52.7072,53.15305,53.173729999999999,52.74776,52.739669999999997,53.000630000000001,52.81026,52.658990000000003,52.965949999999999,52.92351,52.907589999999999,53.150840000000002,49.969990000000003,42.801920000000003,42.687080000000002,43.087479999999999,42.91019,42.868229999999997,43.164969999999997,42.604590000000002,43.671259999999997,42.609659999999998,43.007640000000002,42.561410000000002,576.97270000000003,7287.6490000000003,7021.2610000000004,51.909109999999998,40.27037,21,21,314100.30960000004,183213.60495659013,3067.0859029775006,57,50,42409.525961129992,44,10.660034835274534,11.267174835274535,208935.18310744662,7956.7330907390606,575.43637527869532,-1.5363247213047089,0,-266.38799999999992,-935.47209073906015,2.2542228968409319E-2,2.2542228968409319E-2,0.25878696919976052,0.25878696919976052,7527.9786780900959,-506.71767809009543,7.2205908579214148E-2,7.2205908579214148E-2,44,0.41633697281418935]
["2013-01-11T11:00:00","2013-01-11T11:00:00",53.159550000000003,52.941879999999998,52.683190000000003,53.062600000000003,53.130540000000003,52.744340000000001,52.69012,52.940399999999997,52.792279999999998,52.653190000000002,52.900860000000002,52.910150000000002,52.896900000000002,53.112349999999999,52.230899999999998,42.825710000000001,42.674210000000002,43.076999999999998,42.887309999999999,42.90005,43.168349999999997,42.628570000000003,43.036209999999997,42.579169999999998,43.148119999999999,42.528619999999997,1498.5129999999999,8527.1749999999993,7028.6620000000003,52.205190000000002,40.803440000000002,21,21,314100.30960000004,189659.41069084298,7965.2934035450053,62,53,48612.358778125003,44,11.054092434334063,11.661232434334062,216658.65661261205,8795.3595588064363,1441.1483259909726,-57.36467400902734,0,-1498.512999999999,-1766.6975588064361,3.9657420439753489E-3,3.9657420439753489E-3,0.24303039161700732,0.24303039161700732,8337.4307221586751,-1308.7687221586748,5.8444455786629802E-2,5.8444455786629802E-2,43,0.40058039523143613]
["2013-01-11T12:00:00","2013-01-11T12:00:00",53.183439999999997,52.914969999999997,52.61721,53.00703,53.043750000000003,52.712879999999998,52.639299999999999,52.866259999999997,52.744929999999997,52.63261,52.824309999999997,52.857320000000001,52.851149999999997,53.048189999999998,53.319229999999997,45.767049999999998,42.691609999999997,43.098030000000001,42.889150000000001,42.909260000000003,43.207120000000003,42.688600000000001,42.79307,43.045110000000001,43.087620000000001,42.597830000000002,1411.2159999999999,8445.768,7034.5519999999997,52.692509999999999,40.784059999999997,19,19,284185.99440000003,179011.04045446697,7469.2911008799974,67,55,50288.002969800007,44,11.23292590127018,11.840065901270179,199195.78955789653,8953.6783936433894,1329.8923480008705,-81.323651999129424,0,-1411.2160000000003,-1919.1263936433897,-1.621350492455376E-2,0,0.22819172529244244,0.22819172529244244,8494.5478157186953,-1459.9958157186957,4.3092879029626899E-2,4.3092879029626899E-2,43,0.38574172890687125]
["2013-01-11T13:00:00","2013-01-11T13:00:00",53.169980000000002,52.931840000000001,52.63214,53.010159999999999,53.04072,52.71593,52.63449,52.873600000000003,52.736400000000003,52.632339999999999,52.812469999999998,52.863399999999999,52.853679999999997,53.05368,53.34498,50.842529999999996,42.6706,43.148760000000003,42.93177,42.928310000000003,43.199579999999997,42.683109999999999,42.780619999999999,42.911000000000001,43.171860000000002,42.712420000000002,1396.1410000000001,8422.9689999999991,7026.8280000000004,53.149009999999997,40.791420000000002,19,19,284185.99440000003,185074.20093521391,7300.114137980001,69,57,52043.798742354971,44,11.414492537114306,12.021632537114304,202415.54812322737,9118.8983782037067,1279.0956959748542,-117.04530402514592,0,-1396.1409999999987,-2092.0703782037062,-2.1997719888146822E-2,0,0.2135115697095662,0.2135115697095662,8658.357936275379,-1631.5299362753785,2.593765380334764E-2,2.593765380334764E-2,42,0.37106157332399498]
["2013-01-11T14:00:00","2013-01-11T14:00:00",53.111319999999999,52.944450000000003,52.642670000000003,53.013100000000001,53.039000000000001,52.711570000000002,52.629359999999998,52.877189999999999,52.734999999999999,52.635840000000002,52.80254,52.86739,52.853209999999997,53.05444,53.348599999999998,52.553359999999998,43.587400000000002,43.216050000000003,42.989069999999998,43.00638,43.326880000000003,42.812049999999999,42.872259999999997,42.486289999999997,43.286589999999997,42.809730000000002,1491.68,8518.1200000000008,7026.44,53.500419999999998,40.780079999999998,19,19,284185.99440000003,189580.20859266122,7683.3378855999981,68,58,54176.691280400002,44,11.548071172661642,12.155211172661641,204784.32559134095,9382.8121545796057,1330.6703380542319,-161.00966194576813,0,-1491.6800000000012,-2356.3721545796061,-2.4776802515208689E-2,0,0.19782683981490307,0.19782683981490307,8914.1505665074947,-1887.7105665074951,6.0887382484219425E-3,6.0887382484219425E-3,41,0.35537684342933185]
["2013-01-11T15:00:00","2013-01-11T15:00:00",53.250030000000002,52.942149999999998,52.636139999999997,53.011960000000002,53.031019999999998,52.714260000000003,52.629809999999999,52.867899999999999,52.725810000000003,52.631210000000003,52.785330000000002,52.860709999999997,52.844149999999999,53.047150000000002,53.324480000000001,52.778709999999997,49.503770000000003,43.285530000000001,43.055689999999998,43.057400000000001,43.347369999999998,42.851100000000002,42.91377,42.520060000000001,43.183079999999997,42.829839999999997,1581.701,8622.7999999999993,7041.0990000000002,53.588810000000002,40.833599999999997,17,17,254271.67920000001,170707.76538581535,8240.8124715950034,69,59,54992.812394000022,44,11.636747902635403,12.243887902635402,184635.07480892335,9451.5775118829661,1416.3428718308294,-165.35812816917064,0,-1581.7009999999991,-2410.4785118829659,-2.5345720513631494E-2,0,0.18119555632305592,0.18119555632305592,8982.9003387336215,-1941.8013387336214,-1.432893143082032E-2,0,41,0.33874555993748473]
["2013-01-11T16:00:00","2013-01-11T16:00:00",53.487250000000003,52.936610000000002,52.631239999999998,53.00394,53.021180000000001,52.704450000000001,52.623939999999997,52.867559999999997,52.721800000000002,52.623519999999999,52.774479999999997,52.851750000000003,52.840440000000001,53.043680000000002,53.324150000000003,52.776000000000003,51.778419999999997,43.568199999999997,43.097149999999999,43.089210000000001,43.349939999999997,42.852640000000001,42.928519999999999,42.547319999999999,42.99371,42.852629999999998,1277.9179999999999,8311.384,7033.4650000000001,54.31709,40.767029999999998,17,17,254271.67920000001,181901.45970804492,6795.0861605800037,71,59,56309.875941520004,44,11.681659769605833,12.288799769605832,185347.67131675145,{"$f":"AO262*1000/(500*AQ262)","v":9640.7320624130862},1163.3768307924768,{"$f":"AU262-AC262","v":-114.54116920752313},0,{"$f":"AE262-AD262","v":-1277.9189999999999},{"$f":"AE262-AT262","v":-2607.267062413086},-2.7414914483804186E-2,0,0.16775848245851527,0.16775848245851527,{"$f":"AO262*1000/(500*AR262)","v":9164.4224004353146},{"$f":"AE262-BD262","v":-2130.9574004353144},-2.2406609489207731E-2,0,41,0.3253084860729441]
["2013-01-11T17:00:00","2013-01-11T17:00:00",53.761629999999997,52.92698,52.628830000000001,52.998669999999997,53.020449999999997,52.695360000000001,52.61768,52.866300000000003,52.718760000000003,52.617559999999997,52.781599999999997,52.847140000000003,52.83746,53.049550000000004,53.32188,52.773249999999997,52.491199999999999,45.698520000000002,43.130789999999998,43.138649999999998,43.369790000000002,42.855260000000001,42.946210000000001,42.56438,43.00694,43.095700000000001,989.96579999999994,8009.143,7019.1769999999997,54.379559999999998,40.68092,15,15,{"$f":"3.1416*(138/2)^2*AI263","v":224357.364},{"$f":"62.4*AJ263*(AF263-AB263)/1000","v":157972.90612553046},{"$f":"500*AC263*(C263-AB263)/1000","v":5279.4529625969972},70,58,54857.183332759989,44,{"$f":"19.5286-0.30357*AP263+0.0000341*AO263+0.060847*AN263","v":11.571275951647117},{"$f":"19.5286-0.30357*42+0.0000341*AO263+0.060847*AN263","v":12.178415951647116},{"$f":"62.4*AJ263*AQ263/1000","v":161996.70056719583},9481.6135337177457,{"$f":"AL263*1000/(500*AQ263)","v":912.51007834542099},-77.455721654578952,0,-989.96600000000035,-2462.436533717746,-2.5892049175502363E-2,{"$f":"IF(AZ263>1,1,IF(AZ263<0,0,AZ263))","v":0},0.1573491793138059,{"$f":"IF(BB263>1,1,BB263)","v":0.1573491793138059},9008.9193127519393,-1989.7423127519396,-2.0921759851641426E-2,{"$f":"IF(BF263>1,1,IF(BF263<0,0,BF263))","v":0},41,0.31489918292823471]
["2013-01-11T18:00:00","2013-01-11T18:00:00",53.903030000000001,53.008650000000003,52.639310000000002,53.007539999999999,53.027389999999997,52.691560000000003,52.630209999999998,52.875639999999997,52.711880000000001,52.617019999999997,52.796590000000002,52.843490000000003,52.841410000000003,53.05254,53.327030000000001,52.779679999999999,52.646099999999997,48.623539999999998,43.136139999999997,43.163139999999999,43.366250000000001,42.852829999999997,42.938009999999998,42.560180000000003,42.995420000000003,43.026319999999998,736.89620000000002,7846.7669999999998,7109.8710000000001,54.173870000000001,40.647469999999998,15,15,224357.364,156064.57982283173,4007.5031337510013,66,58,53069.254574400009,44,11.510307580987041,12.11744758098704,161143.14950444686,9221.1705379725699,696.33293559777258,-40.563264402227446,0,-736.89599999999973,-2111.2995379725699,{"$f":"IF(AZ263>1,1+AY264*60/$BK$7,IF(AZ263<0,AY264*60/$BK$7,AZ263+AY264*60/$BK$7))","v":-2.2199910825261987E-2},0,{"$f":"IF(BB263>1,1+AX264*60/$BK$7,BB263+AX264*60/$BK$7)","v":0.1496008588158052},0.1496008588158052,8759.1473731924652,-1649.2763731924651,{"$f":"IF(BF263>1,1+BE264*60/$BK$7,IF(BF263<0,BE264*60/$BK$7,BF263+BE264*60/$BK$7))","v":-1.7341825616200141E-2},0,41,0.30715086243023404]
["2013-01-11T19:00:00","2013-01-11T19:00:00",53.966250000000002,53.126390000000001,52.659350000000003,53.00806,53.029960000000003,52.692959999999999,52.634300000000003,52.877659999999999,52.716749999999998,52.618479999999998,52.805750000000003,52.844189999999998,52.843809999999998,53.05003,53.331409999999998,52.775440000000003,52.64772,50.404899999999998,43.151769999999999,43.17069,43.39678,42.867730000000002,42.933860000000003,42.538849999999996,42.97343,42.779170000000001,670.10799999999995,7976.0519999999997,7305.9440000000004,54.247729999999997,40.519579999999998,15,15,224357.364,160558.68756569235,3748.2759023200006,66,60,54748.219131899998,44,11.68925427239779,12.296394272397791,163648.38520248854,9367.2731991430319,641.31993623766471,-28.788063762335241,0,-670.10799999999927,-2061.3291991430315,-2.1674482270018166E-2,0,0.14255480136363524,0.14255480136363524,8904.7598701020052,-1598.8158701020047,-1.6811243077503715E-2,0,41,0.30010480497806408]
["2013-01-11T20:00:00","2013-01-11T20:00:00",54.020800000000001,53.273330000000001,52.686230000000002,53.011850000000003,53.033650000000002,52.690910000000002,52.63908,52.879159999999999,52.71669,52.613120000000002,52.805579999999999,52.832230000000003,52.836390000000002,53.0501,53.326639999999998,52.772280000000002,52.653759999999998,51.849299999999999,43.219839999999998,43.183869999999999,43.420659999999998,42.90607,42.936259999999997,42.53246,42.966700000000003,42.663780000000003,1069.7139999999999,8367.9120000000003,7298.1970000000001,53.149590000000003,40.657229999999998,15,15,224357.364,146800.28631870201,6074.3816461399992,65,60,52267.484576160023,44,11.604661224047058,12.211801224047058,162464.09102602917,9008.0155839193103,1046.886510319272,-22.827489680727922,0,-1069.7150000000001,-1709.8185839193102,-1.7978415382421006E-2,0,0.13130695273707355,0.13130695273707355,8560.1597368350031,-1261.9627368350029,-1.3269296809226413E-2,0,41,0.28885695635150238]
["2013-01-11T21:00:00","2013-01-11T21:00:00",54.269620000000003,53.415410000000001,52.645449999999997,53.009,53.033349999999999,52.685899999999997,52.634010000000004,52.876609999999999,52.70872,52.6051,52.813209999999998,52.834980000000002,52.827480000000001,53.046219999999998,53.318309999999997,52.766170000000002,52.645200000000003,52.499429999999997,43.825449999999996,43.219239999999999,43.466859999999997,42.957610000000003,43.010089999999998,42.573659999999997,42.997230000000002,42.656140000000001,1012.588,8308.1659999999993,7295.5780000000004,52.999870000000001,40.630360000000003,15,15,224357.364,144811.18059580974,5879.8352431200019,65,61,51383.971209329982,44,11.635380418238153,12.242520418238152,162894.15665784327,8832.3663451152752,1010.6820803045707,-1.9059196954292474,0,-1012.5879999999988,-1536.7883451152748,-1.6159035515927959E-2,0,0.12065978358914831,0.12065978358914831,8394.3451926420821,-1098.7671926420817,-1.1553326875541893E-2,0,41,0.27820978720357714]
["2013-01-11T22:00:00","2013-01-11T22:00:00",54.20729,53.700180000000003,52.733460000000001,53.022210000000001,53.032510000000002,52.68385,52.634079999999997,52.87144,52.707529999999998,52.597430000000003,52.810850000000002,52.830840000000002,52.833129999999997,53.044530000000002,53.332949999999997,52.767249999999997,52.667020000000001,52.708260000000003,47.734940000000002,43.266080000000002,43.515799999999999,42.945270000000001,43.025739999999999,42.615090000000002,43.013039999999997,42.66084,1007.5890000000001,8238.7170000000006,7456.2550000000001,53.04815,40.679690000000001,13,13,194443.04880000002,126031.79005439742,5817.0380045250004,64,60,50950.120832910005,44,11.559739120402233,12.166879120402232,140257.16127718717,8815.0987322864676,1006.4306718234295,-1.1583281765705351,0,-782.46200000000044,-1358.8437322864675,-1.4287981946509418E-2,0,0.11243234531630299,0.11243234531630299,8375.2160810858131,-918.96108108581302,-9.6627000030426041E-3,0,41,0.26998234893073181]
["2013-01-11T23:00:00","2013-01-11T23:00:00",54.001739999999998,53.320700000000002,52.662100000000002,53.006860000000003,53.030239999999999,52.680100000000003,52.629890000000003,52.873159999999999,52.703659999999999,52.603659999999998,52.813020000000002,52.827390000000001,52.828290000000003,53.049349999999997,53.331290000000003,52.746600000000001,52.390050000000002,49.493780000000001,44.671039999999998,43.364409999999999,43.487110000000001,42.933979999999998,42.926310000000001,42.204520000000002,42.519869999999997,42.147379999999998,5565.7709999999997,8315.93,13881.7,52.963999999999999,40.131970000000003,15,15,224357.364,151431.59307679604,32989.326555780004,64,62,53355.131618949985,44,11.763443988206195,12.370583988206194,164687.03376874872,9071.3453768203981,5608.7871186116035,43.016118611603815,1,5565.77,4810.3546231796026,5.0579958812959923E-2,5.0579958812959923E-2,0.17095535233243189,0.17095535233243189,8626.1298043515872,5255.5701956484136,5.5261315403563216E-2,5.5261315403563216E-2,44,0.3285053559468607]
["2013-01-12","2013-01-12",53.275599999999997,52.952849999999998,52.631959999999999,53.000509999999998,53.027709999999999,52.683880000000002,52.630699999999997,52.86853,52.700969999999998,52.604480000000002,52.811120000000003,52.825850000000003,52.832360000000001,53.046210000000002,53.194310000000002,51.951149999999998,46.756570000000004,43.75235,43.17154,43.194020000000002,43.459350000000001,42.898670000000003,42.164729999999999,41.323970000000003,41.71895,41.39461,5450.0780000000004,8350.3829999999998,13800.46,53.007289999999998,40.122120000000002,17,17,254271.67920000001,184253.20016140473,32376.161108609995,65,63,53798.052260054981,44,11.839394582067875,12.446534582067876,187850.37904425192,9087.9735255277865,5469.2257926173716,19.147792617371124,1,5450.0769999999993,4712.4864744722126,0.10013085276095809,0.10013085276095809,0.2282618695815174,0.2282618695815174,8644.6636058141958,5155.7963941858034,0.10947352836792715,0.10947352836792715,44,0.38581187319594623]
["2013-01-12T01:00:00","2013-01-12T01:00:00",53.130699999999997,52.916440000000001,52.625810000000001,52.987870000000001,53.015039999999999,52.66751,52.620249999999999,52.85575,52.701140000000002,52.607840000000003,52.807699999999997,52.82255,52.816670000000002,52.850439999999999,50.105179999999997,44.69482,43.056800000000003,43.369,43.156829999999999,43.126629999999999,43.209049999999998,41.764740000000003,41.335239999999999,40.912529999999997,41.313099999999999,41.017769999999999,5481.7619999999997,8461.402,13943.16,53.092950000000002,40.101030000000002,21,21,314100.30960000004,236671.8292520855,33200.099691329997,66,63,54964.928935919997,44,11.879185076714872,12.486325076714872,232830.3563284509,9253.9898285885229,5589.6257995689575,107.8637995689578,1,5481.7579999999998,4689.170171411477,0.14943658024185225,0.14943658024185225,0.28590150648615426,0.28590150648615426,8804.0201737853786,5139.1398262146213,0.16351060070588322,0.16351060070588322,44,0.44345151010058309]
["2013-01-12T02:00:00","2013-01-12T02:00:00",53.122779999999999,52.909149999999997,52.614719999999998,52.985030000000002,53.011830000000003,52.664920000000002,52.613819999999997,52.854410000000001,52.697360000000003,52.597000000000001,52.80095,52.794029999999999,51.847749999999998,47.277380000000001,44.14987,43.237789999999997,42.915939999999999,43.385129999999997,42.972650000000002,42.529980000000002,42.298769999999998,41.051789999999997,41.088470000000001,40.678019999999997,41.09299,40.792319999999997,5604.0839999999998,8389.0490000000009,13993.13,52.91133,40.094560000000001,23,23,344014.62479999999,260152.88071328081,34550.466799320006,66,64,53760.255775864993,44,11.898952721956999,12.506092721956996,255429.01838419528,9036.1323440947581,5807.3122243043172,203.22822430431734,1,5604.0809999999983,4956.9976559052411,0.20155846249632503,0.20155846249632503,0.34482734633975126,0.34482734633975126,8597.4503741648896,5395.6796258351096,0.22024513996990813,0.22024513996990813,44,0.50237734995418004]
["2013-01-12T03:00:00","2013-01-12T03:00:00",53.12359,52.908929999999998,52.625610000000002,52.986719999999998,53.019919999999999,52.667400000000001,52.612850000000002,52.857660000000003,52.69265,52.588839999999998,52.613100000000003,49.922550000000001,44.625540000000001,43.498629999999999,43.637529999999998,43.049160000000001,42.867139999999999,43.099110000000003,42.018099999999997,41.730040000000002,41.558349999999997,40.857120000000002,40.942570000000003,40.527299999999997,40.939770000000003,40.651310000000002,5577.8580000000002,8408.1,13985.96,52.923830000000002,40.10765,27,27,403843.25520000001,309265.28420156328,34784.303388119995,66,64,53879.861529000016,44,11.903031278138901,12.510171278138902,299954.23524212831,9053.1328146563355,5844.6126159484811,266.75461594848093,1,5577.8599999999988,4932.8271853436636,0.25342619687579426,0.25342619687579426,0.4034774773934931,0.4034774773934931,8613.7688015756012,5372.191198424398,0.27673270291221025,0.27673270291221025,44,0.56102748100792188]
["2013-01-12T04:00:00","2013-01-12T04:00:00",53.123759999999997,52.907820000000001,52.624270000000003,52.984969999999997,53.019379999999998,52.665979999999998,52.611629999999998,52.852449999999997,52.624130000000001,51.748759999999997,47.224209999999999,43.730899999999998,43.18121,43.332380000000001,43.536409999999997,42.792940000000002,42.295839999999998,41.896450000000002,41.488810000000001,41.405850000000001,41.346269999999997,40.801990000000004,40.889609999999998,40.483499999999999,40.89931,40.598500000000001,5514.6049999999996,8495.9760000000006,14010.58,52.969259999999998,40.089709999999997,29,29,433757.57040000003,334832.83401993377,34535.930711149987,65,63,54712.173845400008,44,11.870566128128141,12.477706128128141,321294.3503957864,9218.1237617228144,5818.750401350223,304.14540135022344,1,5514.6039999999994,4792.4562382771855,0.30381795759482982,0.30381795759482982,0.46146248370585824,0.46146248370585824,8769.5884617868815,5240.9915382131185,0.33184072652122004,0.33184072652122004,44,0.61901248732028702]
["2013-01-12T05:00:00","2013-01-12T05:00:00",53.114690000000003,52.908969999999997,52.619300000000003,52.982840000000003,53.013689999999997,52.663670000000003,52.611289999999997,52.61542,49.932850000000002,44.630580000000002,43.451369999999997,43.193339999999999,43.09066,43.17794,43.179209999999998,42.077579999999998,41.282470000000004,41.522179999999999,41.275570000000002,41.090009999999999,41.268889999999999,40.749769999999998,40.8429,40.44867,40.861440000000002,40.544040000000003,5358.2,8648.5169999999998,14006.72,53.30939,40.118789999999997,33,33,493586.20079999999,393169.95796305418,33678.028415000001,64,63,57039.56417010002,44,11.949930138200411,12.557070138200411,368055.20648456103,9546.4263824875961,5636.523063401225,278.32306340122523,1,5358.2029999999995,4460.2936175124032,0.35071709188742067,0.35071709188742067,0.51780296341717269,0.51780296341717269,9084.8523648167702,4921.8676351832291,0.38359322332692453,0.38359322332692453,44,0.67535296703160153]
["2013-01-12T06:00:00","2013-01-12T06:00:00",53.110500000000002,52.913029999999999,52.608359999999998,52.968870000000003,53.009720000000002,52.631140000000002,51.937359999999998,47.685609999999997,43.655369999999998,43.104320000000001,43.151940000000003,43.107979999999998,42.924950000000003,42.634799999999998,42.285559999999997,41.396599999999999,40.929969999999997,41.41283,41.141089999999998,40.93703,41.241500000000002,40.729810000000001,40.828879999999998,40.434649999999998,40.855029999999999,40.525109999999998,5236.6530000000002,8762.6880000000001,13999.34,53.674250000000001,40.138120000000001,35,35,523500.516,429535.49027726945,32952.660149835006,63,62,59306.441958719995,44,11.966383670792352,12.573523670792351,390899.06084197928,9912.174570079289,5507.5386276082945,270.88562760829427,1,5236.652,4087.1654299207112,0.39369285465363796,0.39369285465363796,0.57286535761187085,0.57286535761187085,9433.543612994632,4565.7963870053682,0.43160169906180601,0.43160169906180601,44,0.73041536122629969]
["2013-01-12T07:00:00","2013-01-12T07:00:00",53.097679999999997,52.897539999999999,52.604900000000001,52.968260000000001,52.841200000000001,50.498199999999997,45.349539999999998,43.603859999999997,43.071649999999998,42.879579999999997,43.010359999999999,42.819470000000003,42.042839999999998,41.745399999999997,41.842289999999998,40.993139999999997,40.785980000000002,41.302889999999998,41.058340000000001,40.924039999999998,41.232489999999999,40.713549999999998,40.827829999999999,40.439010000000003,40.852139999999999,40.519150000000003,5095.5690000000004,8774.3819999999996,13745.3,53.512920000000001,40.149160000000002,39,39,583329.14639999997,472969.83318735857,32047.383766784984,63,62,58629.367598159995,44,11.943295435097257,12.550435435097256,434732.83347675781,9817.9548378026975,5366.5898061281632,271.0208061281628,1,4970.9179999999997,3927.3451621973018,0.43498813787267732,0.43498813787267732,0.62513360962203324,0.62513360962203324,9343.0013486549069,4402.2986513450924,0.4778910273775222,0.4778910273775222,44,0.78268361323646207]
["2013-01-12T08:00:00","2013-01-12T08:00:00",53.0991,52.896949999999997,52.609369999999998,52.968350000000001,52.552639999999997,46.828400000000002,43.659050000000001,43.401980000000002,43.055900000000001,42.827539999999999,42.870469999999997,42.557720000000003,41.686500000000002,41.507510000000003,41.706159999999997,41.029170000000001,40.76146,41.280259999999998,41.035339999999998,41.008220000000001,41.325220000000002,40.764850000000003,40.85163,40.439239999999998,40.844889999999999,40.500979999999998,1497.6479999999999,8607.6509999999998,7110.0029999999997,54.299819999999997,40.796810000000001,39,39,583329.14639999997,502274.17085103487,9433.7746108800002,63,62,58114.598764754977,44,11.925741817878146,12.532881817878144,434093.8863961217,9746.0769572646768,1582.0860043670605,84.438004367060557,1,-1497.6480000000001,-2636.0739572646771,0.40727032439924321,0.40727032439924321,0.60938612734883624,0.60938612734883624,9273.940281133835,-2163.9372811338353,0.45513764075064789,0.45513764075064789,44,0.76693613096326507]
["2013-01-12T09:00:00","2013-01-12T09:00:00",53.112549999999999,52.893520000000002,52.611539999999998,52.976039999999998,52.899380000000001,50.490220000000001,43.869129999999998,43.467579999999998,43.119709999999998,42.904710000000001,43.05086,42.737020000000001,42.005899999999997,41.677100000000003,41.755609999999997,41.036630000000002,40.833419999999997,41.258040000000001,41.047020000000003,41.072859999999999,41.450429999999997,40.898940000000003,40.851849999999999,40.443519999999999,40.856490000000001,40.511879999999998,1706.1379999999999,8775.8089999999993,7069.6710000000003,54.581539999999997,40.789909999999999,39,39,583329.14639999997,512131.94809534505,10749.240956230002,64,63,60516.355339334987,44,12.068488717071324,12.675628717071323,439289.83623203612,10028.820800691037,1781.3731624946217,75.235162494621818,1,-1706.137999999999,-2959.1498006910369,0.37615543022510056,0.37615543022510056,0.59144641260236197,0.59144641260236197,9548.4581775155002,-2478.7871775154999,0.42907366768290883,0.42907366768290883,44,0.74899641621679081]
["2013-01-12T10:00:00","2013-01-12T10:00:00",53.147300000000001,52.895420000000001,52.607379999999999,52.977229999999999,52.987009999999998,51.993729999999999,45.885579999999997,43.695729999999998,43.134010000000004,42.936869999999999,43.079940000000001,42.954909999999998,42.302500000000002,41.927019999999999,41.915939999999999,41.048670000000001,40.81568,41.301839999999999,41.056109999999997,41.115459999999999,41.491729999999997,40.976640000000003,40.872419999999998,40.438549999999999,40.85915,40.5184,1571.6369999999999,8727.0910000000003,7155.4539999999997,54.685780000000001,40.451180000000001,37,37,553414.83120000002,489243.34438176645,9924.023254650001,65,64,62113.324774300003,44,12.18379237480363,12.790932374803631,420743.94338981464,10196.057658164271,1629.0532453873909,57.416245387390973,1,-1571.6370000000006,-3040.6036581642711,0.34418406431885312,0.34418406431885312,0.57492095014562949,0.57492095014562949,9712.0871183174513,-2556.6331183174516,0.4021911594367974,0.4021911594367974,44,0.73247095376005833]
["2013-01-12T11:00:00","2013-01-12T11:00:00",53.316310000000001,52.908029999999997,52.61468,52.977490000000003,53.035400000000003,52.28951,48.584229999999998,44.057980000000001,43.304870000000001,42.96754,43.145919999999997,42.923299999999998,42.617229999999999,42.023510000000002,41.917470000000002,41.173079999999999,40.882730000000002,41.317149999999998,41.042140000000003,41.191740000000003,41.517000000000003,40.920650000000002,40.867800000000003,40.473050000000001,40.854790000000001,40.529829999999997,701.13070000000005,7905.7820000000002,7204.6509999999998,54.446080000000002,40.366950000000003,37,37,553414.83120000002,480571.05062846898,4482.4968364680017,64,63,55653.266264830003,44,11.902657379630703,12.509797379630704,411035.48457377701,9351.4018743529887,753.19261800125469,52.061918001254639,1,-701.13100000000031,-2146.7508743529888,0.32161138947213097,0.32161138947213097,0.56754869178205614,0.56754869178205614,8897.5487893110712,-1692.8977893110714,0.38439066297333574,0.38439066297333574,44,0.72509869539648497]
["2013-01-12T12:00:00","2013-01-12T12:00:00",53.256970000000003,52.934019999999997,52.634819999999998,52.994,53.076189999999997,52.341500000000003,48.854399999999998,44.025550000000003,43.32687,42.993650000000002,43.248820000000002,42.995939999999997,42.603140000000003,42.20476,41.905029999999996,41.237870000000001,40.94623,41.340600000000002,41.049819999999997,41.072859999999999,41.457940000000001,40.88382,40.870640000000002,40.483899999999998,40.905140000000003,40.538339999999998,251.04480000000001,6968.3509999999997,7184.7089999999998,53.556350000000002,39.999549999999999,37,37,553414.83120000002,449552.05193869863,1596.4729623120006,56,55,47234.27041840001,44,11.128793621267441,11.73593362126744,384311.58126649755,8488.6596024449536,286.90853953138196,35.863739531381952,1,216.35800000000017,-1303.9506024449538,0.30790059828680144,0.30790059828680144,0.56982365477046482,0.56982365477046482,8049.5121977860799,-864.80319778608009,0.37529742275471273,0.37529742275471273,44,0.72737365838489365]
["2013-01-12T13:00:00","2013-01-12T13:00:00",53.181350000000002,52.926180000000002,52.635770000000001,53.004620000000003,53.075159999999997,52.247230000000002,47.460290000000001,43.918419999999998,43.29692,42.98612,43.259779999999999,43.011209999999998,42.4604,42.174239999999998,41.896299999999997,41.212060000000001,40.987029999999997,41.326500000000003,41.062609999999999,41.028089999999999,41.430759999999999,40.939929999999997,41.05827,40.514919999999996,40.90316,40.562800000000003,391.8793,6819.174,7208.9790000000003,52.981400000000001,39.907170000000001,37,37,553414.83120000002,428852.5751789959,2472.4742705074996,53,50,44577.724643009999,44,10.733970410326641,11.341110410326642,370677.11757877085,8305.9153209745946,460.6821476103288,68.802847610328797,1,389.80500000000029,-1096.9363209745943,0.29636652267666252,0.29636652267666252,0.57392237978963057,0.57392237978963057,7861.2627917668051,-652.28379176680482,0.36843878344297765,0.36843878344297765,44,0.7314723834040594]
["2013-01-12T14:00:00","2013-01-12T14:00:00",53.101399999999998,52.92042,52.633659999999999,53.005139999999997,53.068060000000003,52.012129999999999,45.831339999999997,43.927810000000001,43.260629999999999,42.950119999999998,43.237220000000001,42.935690000000001,42.497810000000001,41.914619999999999,41.984969999999997,41.102989999999998,40.971769999999999,41.328859999999999,41.180120000000002,41.207940000000001,41.56767,41.062919999999998,41.077179999999998,40.658290000000001,40.939010000000003,40.58222,441.50330000000002,6757.866,7199.37,52.554699999999997,39.888420000000004,39,39,583329.14639999997,435795.14401432278,2763.629641647,53,49,42798.511479239976,44,10.612452241442085,11.219592241442083,386290.48892997747,8065.7157281914433,520.82771799997488,79.324417999974855,1,441.50399999999991,-866.34572819144341,0.2872570630458583,0.2872570630458583,0.57856470990561615,0.57856470990561615,7629.2454410516048,-429.87544105160487,0.36391872540020465,0.36391872540020465,44,0.73611471352004498]
["2013-01-12T15:00:00","2013-01-12T15:00:00",53.074680000000001,52.91142,52.634450000000001,52.996220000000001,53.049950000000003,51.729669999999999,45.026850000000003,43.869190000000003,43.32423,42.963200000000001,43.22099,42.88064,42.328029999999998,41.831719999999997,41.846989999999998,41.20926,40.963799999999999,41.409129999999998,41.323560000000001,41.281730000000003,41.623179999999998,41.099139999999998,41.18544,40.774479999999997,41.061300000000003,40.603920000000002,579.05470000000003,6617.2280000000001,7196.2830000000004,52.3994,39.863689999999998,39,39,583329.14639999997,429352.39025816403,3610.6260952860002,52,48,41475.825605940008,44,10.506501653162555,11.113641653162556,382433.91519774491,7895.2684680643242,687.31271635010262,108.25801635010259,1,579.05500000000029,-698.98546806432387,0.27990736454022463,0.27990736454022463,0.58465336247798705,0.58465336247798705,7463.9487038233638,-267.6657038233634,0.36110427171943238,0.36110427171943238,44,0.74220336609241588]
["2013-01-12T16:00:00","2013-01-12T16:00:00",52.998570000000001,52.901809999999998,52.614780000000003,52.991370000000003,53.009720000000002,50.534660000000002,44.195500000000003,43.695680000000003,43.302999999999997,42.963799999999999,43.235219999999998,42.718339999999998,42.194070000000004,41.794780000000003,41.779249999999998,41.182259999999999,40.975369999999998,41.592329999999997,41.446399999999997,41.354100000000003,41.704859999999996,41.177990000000001,41.273850000000003,40.890799999999999,41.22457,40.621609999999997,918.13009999999997,6275.3509999999997,7193.4809999999998,51.822429999999997,39.893920000000001,39,39,583329.14639999997,407706.92162179493,5681.8297612480019,50,46,37427.793578504985,44,10.246769761027021,10.853909761027019,372979.7421827708,7305.2863392831123,1108.9992053609917,190.86910536099174,1,918.13000000000011,-111.80533928311252,0.27873175278204809,0.27873175278204809,0.59430732382236862,0.59430732382236862,6896.6472732059083,296.83372679409149,0.3642254215829363,0.3642254215829363,44,0.75185732743679745]
["2013-01-12T17:00:00","2013-01-12T17:00:00",52.95411,52.899509999999999,52.611890000000002,52.998910000000002,52.792020000000001,47.762949999999996,43.918230000000001,43.555109999999999,43.195219999999999,42.905679999999997,43.245159999999998,42.53022,41.934139999999999,41.678660000000001,41.78163,41.114629999999998,41.291310000000003,41.772620000000003,41.52102,41.339030000000001,41.681640000000002,41.162399999999998,41.294119999999999,40.95581,41.358139999999999,40.6556,1175.681,6021.3180000000002,7196.9989999999998,51.231000000000002,39.893630000000002,39,39,583329.14639999997,384941.79702192615,7229.5622676550001,44,41,34132.955026830001,44,9.8301807664149052,10.437320766414903,357816.01161886344,6944.5223517040949,1470.8910119649086,295.21001196490852,1,1175.6809999999996,252.47664829590485,0.28138649644907526,0.28138649644907526,0.60666938467140286,0.60666938467140286,6540.5587872057458,656.44021279425397,0.37112776486679949,0.37112776486679949,44,0.76421938828583169]
["2013-01-12T18:00:00","2013-01-12T18:00:00",52.929369999999999,52.89434,52.601050000000001,52.994010000000003,52.138640000000002,45.087800000000001,43.71866,43.466050000000003,43.141629999999999,42.801189999999998,43.111660000000001,42.27908,41.674579999999999,41.579799999999999,41.699739999999998,41.228679999999997,41.353729999999999,41.783949999999997,41.529319999999998,41.29298,41.643659999999997,41.154040000000002,41.331949999999999,40.979109999999999,41.312570000000001,40.745730000000002,1328.08,5869.5720000000001,7197.652,51.01117,39.906599999999997,41,41,613243.46160000004,392821.35113189922,8090.4243055999978,42,39,32589.53657202001,44,9.6558561971058836,10.262996197105883,369494.77837116143,6750.2116657014749,1675.754928501299,347.67492850129906,1,1328.08,447.44033429852516,0.28609124598480018,0.28609124598480018,0.62063389185692808,0.62063389185692808,6350.8815449449557,846.77045505504429,0.38003139424462806,0.38003139424462806,44,0.77818389547135691]
["2013-01-12T19:00:00","2013-01-12T19:00:00",52.903440000000003,52.886980000000001,52.596730000000001,52.871600000000001,49.97495,44.061590000000002,43.398310000000002,43.42886,43.129300000000001,42.744439999999997,42.946930000000002,41.893329999999999,41.518320000000003,41.518909999999998,41.648479999999999,41.37003,41.38514,41.815959999999997,41.541339999999998,41.27525,41.682189999999999,41.181800000000003,41.43139,41.094639999999998,41.48516,40.936909999999997,1453.23,5743.8829999999998,7197.1130000000003,50.53519,39.904940000000003,41,41,613243.46160000004,367291.54504261748,8695.0601959500054,39,36,30529.456130374991,44,9.4030664540457884,10.010206454045788,359821.42696867388,6493.5106605014589,1849.4094960285736,396.17949602857357,1,1453.2300000000005,703.60233949854137,0.29348949001052133,0.29348949001052133,0.63591432735570885,0.63591432735570885,6099.6656303798836,1097.4473696201167,0.39157084343352921,0.39157084343352921,44,0.79346433097013769]
["2013-01-12T20:00:00","2013-01-12T20:00:00",52.892690000000002,52.882179999999998,52.585079999999998,52.291200000000003,46.243319999999997,43.662689999999998,43.287059999999997,43.379260000000002,43.0717,42.631050000000002,42.653680000000001,41.622920000000001,41.34957,41.402169999999998,41.699330000000003,41.475549999999998,41.438949999999998,41.873739999999998,41.597769999999997,41.305950000000003,41.722239999999999,41.254600000000003,41.480029999999999,41.142270000000003,41.557340000000003,41.135640000000002,1557.5139999999999,5644.1189999999997,7201.6329999999998,50.126060000000003,39.917529999999999,41,41,613243.46160000004,344030.93599916319,9155.8849868499983,38,36,28809.079067535011,44,9.3444015962029461,9.9515415962029437,357576.53452161013,6166.0618437549692,1959.6514324834775,402.1374324834776,1,1557.5140000000001,1035.5711562450306,0.30437832265050263,0.30437832265050263,0.65229128916866896,0.65229128916866896,5789.8726120036008,1411.760387996399,0.40641523389375417,0.40641523389375417,44,0.8098412927830978]
["2013-01-12T21:00:00","2013-01-12T21:00:00",52.893009999999997,52.881570000000004,52.515830000000001,50.497990000000001,44.782130000000002,43.345149999999997,43.249870000000001,43.31962,43.01191,42.496250000000003,42.333179999999999,41.434629999999999,41.266820000000003,41.350320000000004,41.911549999999998,41.497369999999997,41.458950000000002,41.892589999999998,41.630490000000002,41.369309999999999,41.741500000000002,41.265149999999998,41.492800000000003,41.143749999999997,41.555210000000002,41.137900000000002,1636.4059999999999,5557.8670000000002,7194.2719999999999,50.296559999999999,39.887689999999999,43,43,643157.77679999999,367564.91641378624,9618.0662673299958,38,35,28925.557540145001,44,9.2875265121189461,9.8946665121189454,372736.72197874193,6228.9044348678035,2071.179286493501,434.77328649350102,1,1636.4049999999997,965.36756513219643,0.31452897795738288,0.31452897795738288,0.66949777475758632,0.66949777475758632,5846.6968047315395,1347.5751952684604,0.42058472932878965,0.42058472932878965,44,0.82704777837201515]
["2013-01-12T22:00:00","2013-01-12T22:00:00",52.892130000000002,52.871670000000002,52.040889999999997,46.948810000000002,44.269370000000002,43.218850000000003,43.216639999999998,43.28022,42.88364,42.203569999999999,42.012929999999997,41.294930000000001,41.201729999999998,41.394640000000003,41.986739999999998,41.50468,41.453110000000002,41.89913,41.636690000000002,41.382669999999997,41.755319999999998,41.249650000000003,41.485509999999998,41.146389999999997,41.565809999999999,41.163130000000002,1272.424,5452.6530000000002,6725.0780000000004,50.291980000000002,39.860340000000001,43,43,643157.77679999999,366368.55033421842,7462.1305479999992,38,35,28440.056570460001,44,9.2709709290526874,9.8781109290526867,372072.29601403413,6135.2919317946826,1609.7840463754928,337.36004637549286,1,1272.4250000000002,589.78606820531786,0.32073046565946095,0.32073046565946095,0.68287708026293381,0.68287708026293381,5758.1974478165548,966.88055218344562,0.43075129340513313,0.43075129340513313,44,0.84042708387736265]
["2013-01-12T23:00:00","2013-01-12T23:00:00",52.880330000000001,52.862340000000003,51.42756,45.417079999999999,44.093209999999999,43.169249999999998,43.179220000000001,43.248460000000001,42.869900000000001,41.9679,41.865299999999998,41.258200000000002,41.150970000000001,41.494,41.949339999999999,41.495489999999997,41.443359999999998,41.8992,41.654649999999997,41.37914,41.736109999999996,41.26943,41.501570000000001,41.159320000000001,41.560360000000003,41.149729999999998,589.37429999999995,5403.8760000000002,5993.2510000000002,49.976179999999999,39.953330000000001,45,45,673072.09200000006,370708.23918544425,3456.8570817900004,37,35,27081.119283299995,44,9.2246311675605313,9.8317711675605306,387431.72818761028,5871.4801256301371,749.48407562275929,160.10977562275934,1,589.375,121.77087436986312,0.32201086311302218,0.32201086311302218,0.6890742456614557,0.6890742456614557,5508.8994285491262,484.35157145087396,0.43584415753970795,0.43584415753970795,44,0.84662424927588453]
["2013-01-13","2013-01-13",52.862749999999998,52.860840000000003,50.619869999999999,44.816580000000002,44.068559999999998,43.164650000000002,43.173920000000003,43.222529999999999,42.804369999999999,41.824080000000002,41.824370000000002,41.213729999999998,41.067160000000001,41.542610000000003,41.897289999999998,41.402520000000003,41.40099,41.879089999999998,41.606969999999997,41.311259999999997,41.73095,41.300829999999998,41.543680000000002,41.187939999999998,41.574829999999999,41.142650000000003,566.29830000000004,5380.491,5946.79,49.715040000000002,40.046840000000003,45,45,673072.09200000006,360037.79577416851,3318.5363529149986,36,33,26009.831543099997,44,9.0664062556197109,9.6735462556197103,380786.32958445122,5737.627635421276,732.05110367915415,165.75280367915411,1,566.29899999999998,209.16236457872401,0.32421016537124536,0.32421016537124536,0.69502877133359575,0.69502877133359575,5377.5173769371186,569.27262306288139,0.44182995028960581,0.44182995028960581,44,0.85257877494802459]
["2013-01-13T01:00:00","2013-01-13T01:00:00",52.830739999999999,52.829700000000003,49.891120000000001,44.551760000000002,43.997239999999998,43.166919999999998,43.223109999999998,43.279730000000001,42.705539999999999,41.72598,41.765509999999999,41.196669999999997,41.165570000000002,41.55097,42.000329999999998,41.502499999999998,41.453589999999998,41.905659999999997,41.63888,41.329529999999998,41.762210000000003,41.27223,41.510890000000003,41.16225,41.60304,41.142539999999997,524.45159999999998,5294.4040000000005,5818.8549999999996,49.424880000000002,40.011389999999999,45,45,673072.09200000006,347855.78321240976,3064.9475955600001,35,32,24919.409554980011,44,8.9683758658248198,9.5755158658248192,376669.0827652287,5557.1733227503782,683.50114701133066,159.04954701133067,1,524.45099999999911,261.68167724962132,0.32696169815712617,0.32696169815712617,0.70054327328976995,0.70054327328976995,5204.8181850792635,614.03681492073611,0.44828642995509105,0.44828642995509105,44,0.85809327690419879]
["2013-01-13T02:00:00","2013-01-13T02:00:00",52.807189999999999,52.810859999999998,48.603870000000001,44.443980000000003,43.927669999999999,43.178870000000003,43.204560000000001,43.254840000000002,42.620840000000001,41.664749999999998,41.70082,41.165059999999997,41.402099999999997,41.608150000000002,42.139789999999998,41.645069999999997,41.550269999999998,41.997590000000002,41.7104,41.41357,41.832279999999997,41.35718,41.528619999999997,41.175289999999997,41.574779999999997,41.146270000000001,535.27089999999998,5253.393,5788.6639999999998,49.341259999999998,39.899709999999999,45,45,673072.09200000006,344187.1095448705,3120.8755716139995,35,32,24800.086339574998,44,8.9643069441795085,9.5714469441795078,376498.18928273948,5533.0738882558244,696.28931518021534,161.01841518021536,1,535.27099999999973,255.59011174417537,0.32964917929681709,0.32964917929681709,0.70617154547646299,0.70617154547646299,5182.097646094393,606.56635390560677,0.45466435915183573,0.45466435915183573,44,0.86372154909089183]
["2013-01-13T03:00:00","2013-01-13T03:00:00",52.793590000000002,52.795020000000001,47.393929999999997,44.285649999999997,43.883270000000003,43.197830000000003,43.201770000000003,43.276029999999999,42.507289999999998,41.577350000000003,41.604109999999999,41.11824,41.388129999999997,41.758699999999997,42.14264,41.649970000000003,41.586449999999999,42.028190000000002,41.750250000000001,41.459879999999998,41.890779999999999,41.43638,41.585940000000001,41.189540000000001,41.538089999999997,41.179119999999998,608.78030000000001,5192.2340000000004,5801.0150000000003,49.305419999999998,39.922179999999997,45,45,673072.09200000006,341302.15025210311,3535.3302654705017,35,31,24359.98887908,44,8.8884526207766292,9.4955926207766286,373312.33056680218,5481.2665192451796,795.48835242856978,186.70805242856977,1,608.78099999999995,319.74848075482078,0.33301127341544057,0.33301127341544057,0.71257276125330715,0.71257276125330715,5130.7990668807024,670.21593311929792,0.46171155150011134,0.46171155150011134,44,0.87012276486773599]
["2013-01-13T04:00:00","2013-01-13T04:00:00",52.763210000000001,52.628279999999997,46.04607,44.148150000000001,43.792769999999997,43.200209999999998,43.174399999999999,43.237990000000003,42.400910000000003,41.371519999999997,41.604619999999997,41.271470000000001,41.617019999999997,41.9133,42.218139999999998,41.701390000000004,41.625360000000001,42.051569999999998,41.770699999999998,41.478180000000002,41.91751,41.472619999999999,41.676409999999997,41.275219999999997,41.578560000000003,41.154330000000002,737.40309999999999,5062.0389999999998,5799.442,49.454859999999996,39.916550000000001,47,47,702986.40720000002,364113.9691834827,4280.2120497639999,35,31,24141.648607044986,44,8.881007217500235,9.4881472175002344,389577.38702362019,5436.6915859438323,963.90239191107526,226.49929191107526,1,737.40300000000025,362.75041405616776,0.33682552463798709,0.33682552463798709,0.72032641275933673,0.72032641275933673,5088.8014390243397,710.64056097566026,0.46918380107850288,0.46918380107850288,44,0.87787641637376557]
["2013-01-13T05:00:00","2013-01-13T05:00:00",52.725380000000001,51.662320000000001,44.984659999999998,44.035339999999998,43.760860000000001,43.196359999999999,43.1935,43.183549999999997,42.236739999999998,41.280070000000002,41.548659999999998,41.554510000000001,41.718240000000002,41.961039999999997,42.263249999999999,41.772150000000003,41.686259999999997,42.116819999999997,41.815779999999997,41.49409,41.944920000000003,41.493679999999998,41.683079999999997,41.322650000000003,41.645560000000003,41.148229999999998,623.89620000000002,5175.6220000000003,5799.518,49.435690000000001,39.915509999999998,47,47,702986.40720000002,363540.63596533576,3611.4699459150015,34,30,24636.426525980012,44,8.8370321445359199,9.4441721445359192,387648.3610021288,5575.7240944773775,817.34905720537222,193.4528572053722,1,623.89599999999973,223.79390552262248,0.33917867475074193,0.33917867475074193,0.72688655987021888,0.72688655987021888,5217.2760404910277,582.24195950897229,0.47530596392055857,0.47530596392055857,44,0.88443656348464772]
["2013-01-13T06:00:00","2013-01-13T06:00:00",52.681179999999998,51.057780000000001,44.553049999999999,43.938029999999998,43.741,43.193280000000001,43.210760000000001,43.118949999999998,42.0657,41.218739999999997,41.5167,41.686,41.735599999999998,41.980870000000003,42.287039999999998,41.798270000000002,41.722349999999999,42.161470000000001,41.859090000000002,41.525950000000002,41.968209999999999,41.514719999999997,41.719670000000001,41.363959999999999,41.672499999999999,41.210760000000001,590.74639999999999,5218.3900000000003,5809.1360000000004,49.381210000000003,39.937339999999999,47,47,702986.40720000002,358407.83414013189,3388.0546607439992,34,30,24640.898384650012,44,8.8371846349165661,9.4443246349165655,387655.05019881373,5576.6399374052799,766.77240562734642,176.02600562734642,1,590.74600000000009,232.49606259472057,0.34162332638069665,0.34162332638069665,0.73309814107151716,0.73309814107151716,5218.1387949224591,590.99720507754137,0.48152018649520062,0.48152018649520062,44,0.890648144685946]
["2013-01-13T07:00:00","2013-01-13T07:00:00",52.633589999999998,50.098219999999998,44.176340000000003,43.863190000000003,43.753329999999998,43.178060000000002,43.166159999999998,42.970239999999997,41.997100000000003,41.117310000000003,41.64432,41.664679999999997,41.760620000000003,41.999000000000002,42.303789999999999,41.807899999999997,41.740850000000002,42.193480000000001,41.888030000000001,41.542900000000003,41.99774,41.551850000000002,41.770650000000003,41.391840000000002,41.708100000000002,41.244259999999997,587.47069999999997,5217.2269999999999,5804.6970000000001,49.533580000000001,39.929139999999997,47,47,702986.40720000002,363622.2273797011,3345.4488338155002,33,29,25054.271843940009,44,8.7904336698783556,9.397573669878355,385604.25591902423,5700.3494445995211,761.15672092018542,173.68602092018546,1,587.47000000000025,104.347555400479,0.34272052096775613,0.34272052096775613,0.73927527575939778,0.73927527575939778,5332.0724527535031,472.62454724649706,0.48648974321322913,0.48648974321322913,44,0.89682527937382661]
["2013-01-13T08:00:00","2013-01-13T08:00:00",52.576920000000001,48.749679999999998,43.965969999999999,43.785730000000001,43.753630000000001,43.165050000000001,43.137309999999999,42.850720000000003,41.89228,41.036580000000001,41.992280000000001,41.660150000000002,41.774940000000001,42.021819999999998,42.334350000000001,41.850459999999998,41.776090000000003,42.231580000000001,41.912410000000001,41.554070000000003,42.021380000000001,41.573230000000002,41.760150000000003,41.407850000000003,41.779919999999997,41.290730000000003,621.99170000000004,5188.1440000000002,5810.1360000000004,49.585129999999999,39.903239999999997,47,47,702986.40720000002,363845.06844689185,3509.9582523114996,32,28,25115.519756080008,44,8.7316752236823305,9.3388152236823281,383026.7372464228,5752.7379598272018,803.95987308178348,181.96817308178345,1,621.99200000000019,57.398040172798574,0.34332405038196923,0.34332405038196923,0.74581540267444746,0.74581540267444746,5378.7379136465815,431.39808635341888,0.49102581158012276,0.49102581158012276,44,0.90336540628887629]
["2013-01-13T09:00:00","2013-01-13T09:00:00",52.554839999999999,47.487870000000001,43.816679999999998,43.705759999999998,43.74532,43.164999999999999,43.15419,42.708680000000001,41.72296,40.97363,41.943539999999999,41.667900000000003,41.80303,42.048389999999998,42.356929999999998,41.867310000000003,41.798769999999998,42.251710000000003,41.937260000000002,41.586100000000002,42.045639999999999,41.613300000000002,41.838839999999998,41.436070000000001,41.80124,41.339199999999998,578.30589999999995,5226.9690000000001,5805.2749999999996,49.44294,39.971939999999996,47,47,702986.40720000002,355481.50981093477,3243.0353921379997,32,28,24752.311699500009,44,8.7192898289529523,9.3264298289529499,382483.43516392709,5677.5981037603296,743.87603939240455,165.5701393924046,1,578.30599999999959,127.67689623966999,0.34466654852587952,0.34466654852587952,0.75189617965507538,0.75189617965507538,5307.9929090677297,497.28209093226997,0.49625463765389594,0.49625463765389594,44,0.90944618326950422]
["2013-01-13T10:00:00","2013-01-13T10:00:00",52.518090000000001,46.546840000000003,43.749209999999998,43.64967,43.74559,43.068069999999999,43.135370000000002,42.558630000000001,41.72148,41.175899999999999,41.971710000000002,41.717199999999998,41.848460000000003,42.090560000000004,42.391419999999997,41.880070000000003,41.81438,42.262680000000003,41.962319999999998,41.630180000000003,42.077080000000002,41.63673,41.864570000000001,41.471299999999999,41.818449999999999,41.361150000000002,530.24270000000001,5286.5159999999996,5816.759,49.540219999999998,39.982149999999997,47,47,702986.40720000002,358785.9620927276,2957.9429946690002,34,29,25264.444992060002,44,8.7976005742292465,9.4047405742292476,385918.64186666388,5743.4853466903178,672.44312121504652,142.2004212150465,1,530.24300000000039,73.273653309682231,0.34543700697578672,0.34543700697578672,0.757471583383446,0.757471583383446,5372.7042851749302,444.05471482506982,0.50092378804840609,0.50092378804840609,44,0.91502158699787484]
["2013-01-13T11:00:00","2013-01-13T11:00:00",51.749310000000001,45.63232,43.676859999999998,43.605460000000001,43.727679999999999,43.085250000000002,43.034030000000001,42.496000000000002,41.689860000000003,41.472709999999999,42.060470000000002,41.751379999999997,41.836869999999998,42.12283,42.426960000000001,41.915999999999997,41.845170000000003,42.295319999999997,41.998899999999999,41.693080000000002,42.121609999999997,41.668610000000001,41.888269999999999,41.535530000000001,41.839419999999997,41.369239999999998,470.60059999999999,5332.7529999999997,5803.3540000000003,49.977110000000003,39.961979999999997,49,49,732900.72239999997,393663.76241869817,2442.4335850210009,34,29,26704.107276445015,44,8.8466930581267746,9.4538330581267758,404585.85854869592,6037.0823540473148,552.1687186326252,81.568118632625215,1,470.60100000000057,-233.7283540473145,0.34297939803690147,0.34297939803690147,0.76241986288921026,0.76241986288921026,5649.3714480158769,153.98255198412335,0.50254288513113288,0.50254288513113288,44,0.9199698665036391]
["2013-01-13T12:00:00","2013-01-13T12:00:00",51.379040000000003,45.106050000000003,43.6554,43.594880000000003,43.728540000000002,43.08811,42.94059,42.413629999999998,41.469149999999999,41.582810000000002,42.100749999999998,41.857190000000003,41.90737,42.168120000000002,42.47824,41.954709999999999,41.886279999999999,42.325710000000001,42.033619999999999,41.762500000000003,42.15475,41.700809999999997,41.897100000000002,41.55903,41.869639999999997,41.392789999999998,426.3218,5365.5929999999998,5791.915,50.356189999999998,39.888280000000002,49,49,732900.72239999997,409923.21771399397,2128.6780376250013,37,31,28083.272310314991,44,9.0154165857817432,9.6225565857817426,412302.09249567811,6230.0553819343759,472.23065453950289,45.908854539502897,1,426.32200000000012,-438.14038193437591,0.33837243572153541,0.33837243572153541,0.76690255717897249,0.76690255717897249,5836.966934922626,-45.05193492262606,0.50206917265225448,0.50206917265225448,44,0.92445256079340132]
["2013-01-13T13:00:00","2013-01-13T13:00:00",50.815190000000001,44.788699999999999,43.540370000000003,43.594589999999997,43.733150000000002,43.113419999999998,42.862690000000001,42.284979999999997,41.457450000000001,41.636099999999999,42.116619999999998,41.918010000000002,41.949359999999999,42.206110000000002,42.514850000000003,41.977710000000002,41.919649999999997,42.359020000000001,42.097529999999999,41.878819999999997,42.24512,41.775539999999999,41.943719999999999,41.556139999999999,41.903509999999997,41.410730000000001,321.29559999999998,5480.5230000000001,5801.8190000000004,50.555959999999999,39.96217,49,49,732900.72239999997,418238.85002728296,1510.805809188,39,32,29029.754876084993,44,9.1085386412744995,9.7156786412744989,416560.84393237985,6374.1849311676297,331.73396275488659,10.438362754886612,1,321.29600000000028,-572.36593116762924,0.33235411742855597,0.33235411742855597,0.77028092316647356,0.77028092316647356,5975.8573637377704,-174.03836373776994,0.50023919254490168,0.50023919254490168,44,0.9278309267809024]
["2013-01-13T14:00:00","2013-01-13T14:00:00",50.021999999999998,44.552100000000003,43.513420000000004,43.603000000000002,43.704819999999998,43.121279999999999,42.822299999999998,42.244280000000003,41.592199999999998,41.684829999999998,42.122,41.981850000000001,41.978470000000002,42.216009999999997,42.515250000000002,41.99879,41.915860000000002,42.354570000000002,42.130499999999998,41.933439999999997,42.30444,41.835859999999997,41.966839999999998,41.554160000000003,41.941589999999998,41.464100000000002,194.28120000000001,5624.36,5815.2380000000003,50.836880000000001,40.034320000000001,49,49,732900.72239999997,428645.39533272723,831.31954073999975,42,34,30378.7431808,44,9.27623314246528,9.8833731424652811,424230.01740685024,6549.8015658382756,179.23644823766594,-15.044751762334073,0,190.87800000000061,-734.56356583827528,0.32463032202965408,0.32463032202965408,0.7722879688283002,0.7722879688283002,6147.4443477750565,-332.2063477750562,0.49674610633730737,0.49674610633730737,44,0.92983797244272903]
["2013-01-13T15:00:00","2013-01-13T15:00:00",49.409120000000001,44.412190000000002,43.470210000000002,43.601649999999999,43.705590000000001,43.129559999999998,42.721580000000003,42.076009999999997,41.658149999999999,41.651479999999999,42.109139999999996,41.967550000000003,41.976230000000001,42.233840000000001,42.54871,42.028410000000001,41.942419999999998,42.398200000000003,42.155050000000003,41.961329999999997,42.327550000000002,41.863210000000002,41.996670000000002,41.580300000000001,41.949460000000002,41.514130000000002,118.2411,5720.8829999999998,5812.5219999999999,51.24588,40.134079999999997,49,49,732900.72239999997,445062.17216549075,466.75615104450003,43,35,31784.653859700007,44,9.3850216966157713,9.9921616966157707,429205.2449062168,6773.4854296951744,99.468315819197684,-18.772784180802319,0,91.639000000000124,-960.96342969517445,0.31452597536453963,0.31452597536453963,0.77325153538601832,0.77325153538601832,6361.9174358367518,-549.39543583675186,0.4909693184092932,0.4909693184092932,44,0.93080153900044715]
["2013-01-13T16:00:00","2013-01-13T16:00:00",49.163629999999998,44.371130000000001,43.448970000000003,43.61618,43.722670000000001,43.093290000000003,42.65249,42.004980000000003,41.779820000000001,41.684420000000003,42.134160000000001,41.971060000000001,41.983249999999998,42.258740000000003,42.571779999999997,42.052390000000003,41.974290000000003,42.417999999999999,42.163849999999996,41.958770000000001,42.326180000000001,41.858400000000003,42.019460000000002,41.617930000000001,41.978879999999997,41.538449999999997,142.43969999999999,5769.7709999999997,5823.1469999999999,51.121270000000003,40.23545,49,49,732900.72239999997,438251.15571926028,543.06417582299991,43,35,31404.344273610008,44,9.3720531397301023,9.9791931397301017,428612.15382831328,6701.7000022077118,115.89011878749103,-26.549581212508954,0,53.376000000000204,-878.55300220771187,0.30528815858227176,0.30528815858227176,0.77381277381708768,0.77381277381708768,6293.9646189590385,-470.81761895903855,0.4860187611966062,0.4860187611966062,44,0.93136277743151652]
["2013-01-13T17:00:00","2013-01-13T17:00:00",48.874859999999998,44.413670000000003,43.428579999999997,43.626100000000001,43.700380000000003,43.034419999999997,42.579889999999999,42.13165,41.862000000000002,41.709490000000002,42.180520000000001,41.977139999999999,42.003050000000002,42.273690000000002,42.585749999999997,42.077649999999998,41.994230000000002,42.422809999999998,42.180419999999998,41.947189999999999,42.336590000000001,41.860520000000001,42.013500000000001,41.64282,42.012120000000003,41.585160000000002,136.24969999999999,5761.3069999999998,5805.7070000000003,51.10548,40.253450000000001,49,49,732900.72239999997,435392.84290189994,496.60971904499968,40,33,31260.938201604997,44,9.2454689926747307,9.85260899267473,422823.08038826601,6762.4342748590307,107.42769662382041,-28.82200337617958,0,44.400000000000546,-956.72727485903033,0.29522835427503358,0.29522835427503358,0.77427963132494659,0.77427963132494659,6345.7178144077461,-540.01081440774578,0.48034065076797366,0.48034065076797366,44,0.93182963493937543]
["2013-01-13T18:00:00","2013-01-13T18:00:00",48.325870000000002,44.324289999999998,43.373440000000002,43.624000000000002,43.715150000000001,42.961649999999999,42.636069999999997,41.891860000000001,41.904820000000001,41.727179999999997,42.227060000000002,41.995620000000002,42.037260000000003,42.290970000000002,42.592190000000002,42.086860000000001,42.005879999999998,42.434249999999999,42.182499999999997,41.931849999999997,42.331310000000002,41.855420000000002,42.032409999999999,41.693640000000002,42.07582,41.54542,241.04570000000001,5570.3729999999996,5805.6589999999997,50.807270000000003,40.093679999999999,49,49,732900.72239999997,423572.23307945154,817.19915828250021,38,32,29839.346234535009,44,9.1361457065976452,9.7432857065976446,417823.39799098525,6532.1520021263668,178.89363513376586,-62.152064866234156,0,235.28600000000006,-726.49300212636717,0.28758941930995058,0.28758941930995058,0.77675361861310199,0.77675361861310199,6125.1095642878181,-319.45056428781845,0.4769816891840199,0.4769816891840199,44,0.93430362222753083]
["2013-01-13T19:00:00","2013-01-13T19:00:00",47.774439999999998,44.181480000000001,43.334569999999999,43.621540000000003,43.723990000000001,42.964109999999998,42.458849999999998,41.85754,41.906350000000003,41.740029999999997,42.267960000000002,42.017809999999997,42.058399999999999,42.31353,42.615969999999997,42.118070000000003,42.035409999999999,42.469670000000001,42.206719999999997,41.937739999999998,42.349299999999999,41.877969999999998,42.0503,41.713270000000001,42.084739999999996,41.554720000000003,314.01519999999999,5494.6049999999996,5808.3959999999997,50.658839999999998,39.990789999999997,49,49,732900.72239999997,416358.76618853613,976.54330987199933,36,30,29308.360435125,44,8.9963450908377638,9.6034850908377631,411429.89572056464,6515.6149834611842,217.0977880487377,-96.917411951262295,0,313.79100000000017,-707.21898346118451,0.28015314696469762,0.28015314696469762,0.7800530709610427,0.7800530709610427,6103.6925986560318,-295.29659865603207,0.4738767019288897,0.4738767019288897,44,0.93760307457547154]
["2013-01-13T20:00:00","2013-01-13T20:00:00",46.925849999999997,44.18882,43.331189999999999,43.626739999999998,43.696330000000003,42.915860000000002,42.294460000000001,41.975230000000003,41.948140000000002,41.750050000000002,42.295349999999999,42.031109999999998,42.09545,42.372599999999998,42.678879999999999,42.164969999999997,42.081679999999999,42.521740000000001,42.247169999999997,41.97139,42.38644,41.934350000000002,42.117660000000001,41.740729999999999,42.101230000000001,41.625129999999999,406.69420000000002,5384.7449999999999,5791.4390000000003,50.58578,40.023820000000001,49,49,732900.72239999997,409797.45195003017,1077.8860399119997,35,30,28436.730650099995,44,8.9666225151684102,9.5737625151684096,410070.59301655402,6342.7964324348277,240.42186187465589,-166.27233812534413,0,406.69400000000041,-551.35743243482739,0.27435572901771488,0.27435572901771488,0.78432938058494339,0.78432938058494339,5940.5548456096776,-149.11584560967731,0.47230877733286236,0.47230877733286236,44,0.94187938419937223]
["2013-01-13T21:00:00","2013-01-13T21:00:00",46.081789999999998,44.095239999999997,43.29748,43.630519999999997,43.650269999999999,42.821440000000003,42.223689999999998,42.136310000000002,42.057470000000002,41.812240000000003,42.383020000000002,42.075940000000003,42.12856,42.380760000000002,42.685540000000003,42.197690000000001,42.120399999999997,42.561430000000001,42.267440000000001,41.9773,42.404249999999998,41.972749999999998,42.148690000000002,41.762419999999999,42.137169999999998,41.636490000000002,491.3931,5306.3370000000004,5797.73,50.317500000000003,39.952030000000001,51,51,762815.03760000004,413213.11010029295,1092.1948737149992,35,30,27501.338491695005,44,8.9347256425668,9.5418656425667994,425289.88800356933,6156.0566248779232,244.4831363397588,-246.9099636602412,0,491.39299999999912,-358.32662487792368,0.27058799309226406,0.27058799309226406,0.78949628399393745,0.78949628399393745,5764.3524907770625,33.377509222937078,0.472659735458411,0.472659735458411,44,1]
["2013-01-13T22:00:00","2013-01-13T22:00:00",45.396380000000001,43.995150000000002,43.276820000000001,43.634259999999998,43.675170000000001,42.727989999999998,41.961620000000003,42.261290000000002,42.098010000000002,41.818719999999999,42.410069999999997,42.085650000000001,42.161679999999997,42.410220000000002,42.714790000000001,42.226880000000001,42.15005,42.612270000000002,42.297580000000004,42.000630000000001,42.441249999999997,42.002780000000001,42.186669999999999,41.829009999999997,42.165010000000002,41.654679999999999,635.09230000000002,5183.0609999999997,5818.1530000000002,50.144640000000003,39.941519999999997,51,51,762815.03760000004,404119.19537324394,1188.1624294550006,32,28,26441.696675160012,44,8.7768978566229574,9.3840378566229568,417777.33931509894,6025.2943823898731,270.74769442791802,-364.344605572082,0,635.09200000000055,-207.14138238987289,0.26840994107521465,0.26840994107521465,0.79617415490342303,0.79617415490342303,5635.4624904882066,182.69050951179361,0.47458069122372987,0.47458069122372987,44,1]
["2013-01-13T23:00:00","2013-01-13T23:00:00",44.785170000000001,43.861429999999999,43.205199999999998,43.607300000000002,43.616050000000001,42.63485,41.766919999999999,42.301819999999999,42.104930000000003,41.831679999999999,42.446959999999997,42.101140000000001,42.194330000000001,42.445689999999999,42.742919999999998,42.258519999999997,42.202030000000001,42.67154,42.349229999999999,42.009010000000004,42.455509999999997,42.01332,42.21978,41.844459999999998,42.189970000000002,41.720410000000001,759.47860000000003,5053.7719999999999,5813.2510000000002,49.744570000000003,39.914020000000001,51,51,762815.03760000004,381947.27451556519,1163.8098170679998,31,27,24840.679167300004,44,8.6614561596049313,9.2685961596049307,412282.35397813068,5735.912924930868,268.73306188299955,-490.74553811700048,0,759.47900000000027,77.338075069132174,0.26922313614254312,0.26922313614254312,0.80415993132709895,0.80415993132709895,5360.1815721700032,453.06942782999704,0.47934462960129282,0.47934462960129282,44,1]
["2013-01-14","2013-01-14",44.591810000000002,43.823270000000001,43.212519999999998,43.611170000000001,43.587479999999999,42.543379999999999,41.923029999999997,42.319110000000002,42.118630000000003,41.829360000000001,42.469349999999999,42.120869999999996,42.212690000000002,42.458849999999998,42.75629,42.27731,42.227539999999998,42.694000000000003,42.366540000000001,42.016489999999997,42.473269999999999,42.034199999999998,42.258659999999999,41.894309999999997,42.240340000000003,41.775599999999997,1792.434,5039.7839999999997,4559.549,49.509309999999999,43.032400000000003,51,51,762815.03760000004,368121.9537488998,2523.9352775700045,31,27,16321.11369371999,44,8.370938976955852,8.9780789769558513,398453.83534032234,3899.4702359317102,603.02321747132146,-1189.4107825286785,0,-480.23499999999967,660.07876406828973,0.27616373809712735,0.27616373809712735,0.7991103521539763,0.7991103521539763,3635.7696865023354,923.77931349766459,0.48905799239658954,0.48905799239658954,44,1]
["2013-01-14T01:00:00","2013-01-14T01:00:00",44.473010000000002,43.809199999999997,43.212339999999998,43.618049999999997,43.591430000000003,42.431570000000001,41.952080000000002,42.307899999999997,42.116889999999998,41.824939999999998,42.474879999999999,42.115690000000001,42.2151,42.474769999999999,42.77261,42.292760000000001,42.222209999999997,42.690359999999998,42.356960000000001,41.999569999999999,42.465299999999999,42.033560000000001,42.252099999999999,41.906889999999997,42.27167,41.791690000000003,742.92859999999996,5092.1679999999997,5835.0959999999995,49.472099999999998,42.240630000000003,51,51,762815.03760000004,365584.89195904491,996.01465687599978,30,26,18411.930063479987,44,8.3813888151646676,8.988528815164667,398951.24406883545,4393.5272469800693,237.67293913721892,-505.25566086278104,0,742.92799999999988,1441.5687530199302,0.29132155781429453,0.29132155781429453,0.80692209797826986,0.80692209797826986,4096.761648561881,1738.3343514381186,0.50733624562041857,0.50733624562041857,44,1]
["2013-01-14T02:00:00","2013-01-14T02:00:00",44.230879999999999,43.706650000000003,43.164029999999997,43.58287,43.56033,42.327889999999996,41.991619999999998,42.315829999999998,42.11157,41.818809999999999,42.478070000000002,42.100679999999997,42.205150000000003,42.460149999999999,42.763820000000003,42.29607,42.235370000000003,42.70129,42.366909999999997,41.991819999999997,42.466709999999999,42.033290000000001,42.270110000000003,41.916849999999997,42.284080000000003,41.808109999999999,654.21690000000001,5142.3739999999998,5796.59,49.859319999999997,42.209130000000002,51,51,762815.03760000004,383234.84527383081,792.50853940649995,29,25,19670.069075529984,44,8.3634443554755737,8.9705843554755731,398097.09391842672,4703.8201581748854,189.51726243928246,-464.69963756071752,0,654.21600000000035,1092.7698418251148,0.30281182369307597,0.30281182369307597,0.81380105409001424,0.81380105409001424,4385.459920127395,1411.1300798726052,0.52217400851127738,0.52217400851127738,44,1]
["2013-01-14T03:00:00","2013-01-14T03:00:00",44.097549999999998,43.648139999999998,43.16142,43.571759999999998,43.536079999999998,42.263399999999997,42.096409999999999,42.314709999999998,42.105580000000003,41.83099,42.493639999999999,42.108640000000001,42.216549999999998,42.474110000000003,42.771909999999998,42.304569999999998,42.235900000000001,42.69462,42.373629999999999,41.994059999999998,42.471530000000001,42.03416,42.270310000000002,41.9373,42.305239999999998,41.777859999999997,644.54489999999998,5151.692,5796.2370000000001,49.917149999999999,42.355649999999997,51,51,762815.03760000004,387427.42318096786,747.57217954050054,29,25,19477.259529000006,44,8.3568695499389012,8.9640095499389005,397784.13542118814,4661.3769456632017,178.91201366089678,-465.63288633910321,0,644.54500000000007,1134.8600543367984,0.31474466010605689,0.31474466010605689,0.82057832148647702,0.82057832148647702,4345.6579158001377,1450.5790841998623,0.53742657013744566,0.53742657013744566,44,1]
["2013-01-14T04:00:00","2013-01-14T04:00:00",43.986910000000002,43.612549999999999,43.177140000000001,43.570030000000003,43.50553,42.062069999999999,42.084789999999998,42.311630000000001,42.10615,41.827800000000003,42.484850000000002,42.115589999999997,42.226480000000002,42.473419999999997,42.773780000000002,42.30274,42.231439999999999,42.693860000000001,42.364310000000003,41.992269999999998,42.461170000000003,42.029800000000002,42.280720000000002,41.950069999999997,42.32687,41.768239999999999,664.50019999999995,5136.5370000000003,5801.0370000000003,50.079920000000001,42.295020000000001,51,51,762815.03760000004,395633.12828327622,737.15332936700099,30,26,19993.713445649999,44,8.4353276284966654,9.0424676284966647,401518.71315504017,4740.4711058539542,174.77764037918598,-489.72255962081397,0,664.5,1060.565894146046,0.32589630763446287,0.32589630763446287,0.82756541189125798,0.82756541189125798,4422.1808176877066,1378.8561823122936,0.55192497916830663,0.55192497916830663,44,1]
["2013-01-14T05:00:00","2013-01-14T05:00:00",43.936729999999997,43.608989999999999,43.193129999999996,43.575560000000003,43.460839999999997,42.024799999999999,42.14893,42.318719999999999,42.105989999999998,41.819299999999998,42.48066,42.106279999999998,42.222830000000002,42.475960000000001,42.771500000000003,42.303330000000003,42.235900000000001,42.694470000000003,42.368409999999997,41.985579999999999,42.453090000000003,42.038760000000003,42.295839999999998,41.96855,42.340919999999997,41.767180000000003,502.38749999999999,5295.0330000000004,5797.42,50.314010000000003,42.638770000000001,51,51,762815.03760000004,406826.18794339441,544.97740031249839,29,25,20320.324541460006,44,8.3856180668637865,8.9927580668637859,399152.55500477372,4846.4703208358242,129.97906557800565,-372.40843442199434,0,502.38699999999972,950.9496791641759,0.3358953616280182,0.3358953616280182,0.83284791510749079,0.83284791510749079,4519.2641435191417,1278.1558564808583,0.56536454353344123,0.56536454353344123,44,1]
["2013-01-14T06:00:00","2013-01-14T06:00:00",43.911250000000003,43.57497,43.18356,43.585360000000001,43.455399999999997,41.909239999999997,42.144950000000001,42.317740000000001,42.100589999999997,41.813000000000002,42.478079999999999,42.103940000000001,42.218769999999999,42.473320000000001,42.76793,42.298470000000002,42.233609999999999,42.689680000000003,42.36186,41.983159999999998,42.454909999999998,42.037950000000002,42.296939999999999,41.963999999999999,42.33943,41.79466,386.25,5415.83,5802.08,50.82779,43.021659999999997,51,51,762815.03760000004,429973.90179717093,408.76644375000046,29,25,21138.336518950007,44,8.4135122752961955,9.0206522752961948,400480.30979599524,5024.8542647323438,97.169037228417167,-289.08096277158285,0,386.25,777.22573526765609,0.34406774157871411,0.34406774157871411,0.83690925998160159,0.83690925998160159,4686.6536640236309,1115.426335976369,0.57709303811484147,0.57709303811484147,44,1]
["2013-01-14T07:00:00","2013-01-14T07:00:00",43.952210000000001,43.591560000000001,43.1785,43.519190000000002,43.424019999999999,41.925930000000001,42.134410000000003,42.317920000000001,42.105879999999999,41.816450000000003,42.463239999999999,42.10369,42.216900000000003,42.475470000000001,42.767910000000001,42.294939999999997,42.229979999999998,42.68779,42.367609999999999,41.986179999999997,42.461370000000002,42.03481,42.294260000000001,41.96049,42.348469999999999,41.802639999999997,354.75240000000002,5369.5320000000002,5724.2849999999999,50.901440000000001,42.935989999999997,51,51,762815.03760000004,433099.7713607687,381.28255823400076,29,25,21385.369334700012,44,8.4219360943132706,9.02907609431327,400881.28070317861,5078.4924262581417,90.545108384627497,-264.20729161537253,0,354.7529999999997,645.79257374185818,0.35085812697445606,0.35085812697445606,0.84063941992496838,0.84063941992496838,4737.0005770953758,987.28442290462408,0.5874741449892833,0.5874741449892833,44,1]
["2013-01-14T08:00:00","2013-01-14T08:00:00",43.964179999999999,43.603879999999997,43.19585,43.583370000000002,43.442709999999998,41.934100000000001,42.139589999999998,42.319270000000003,42.104819999999997,41.821159999999999,42.451630000000002,42.094230000000003,42.204619999999998,42.463230000000003,42.763550000000002,42.289700000000003,42.22466,42.682110000000002,42.358370000000001,41.993569999999998,42.46275,42.04522,42.297330000000002,41.96763,42.33549,41.811010000000003,184.67609999999999,5432.6019999999999,5596.9809999999998,51.337200000000003,43.272530000000003,51,51,762815.03760000004,453443.38934136799,198.81951911849958,30,26,21906.07118567,44,8.5005390274313477,9.1076790274313471,404622.75346461142,{"$f":"AO326*1000/(500*AQ326)","v":5154.0428471603573},46.778096889363475,{"$f":"AU326-AC326","v":-137.89800311063652},0,{"$f":"AE326-AD326","v":164.37899999999991},{"$f":"AE326-AT326","v":442.9381528396425},0.35551553693324806,0.35551553693324806,0.84236783367011137,0.84236783367011137,{"$f":"AO326*1000/(500*AR326)","v":4810.4618354887734},{"$f":"AE326-BD326","v":786.51916451122634},0.59574424357097289,0.59574424357097289,44,1]
["2013-01-14T09:00:00","2013-01-14T09:00:00",44.029389999999999,43.650359999999999,43.21687,43.614089999999997,43.50141,42.031269999999999,42.117179999999998,42.323599999999999,42.101179999999999,41.83023,42.446460000000002,42.105589999999999,42.210740000000001,42.468589999999999,42.770440000000001,42.291339999999998,42.215339999999998,42.670299999999997,42.354010000000002,41.996400000000001,42.46199,42.042900000000003,42.284129999999998,41.955880000000001,42.32976,41.834330000000001,89.773009999999999,5598.9470000000001,5600.1120000000001,51.45102,43.207230000000003,51,51,{"$f":"3.1416*(138/2)^2*AI327","v":762815.03760000004},{"$f":"62.4*AJ327*(AF327-AB327)/1000","v":457751.15842170268},{"$f":"500*AC327*(C327-AB327)/1000","v":98.528571665299907},31,26,23078.271644564989,44,{"$f":"19.5286-0.30357*AP327+0.0000341*AO327+0.060847*AN327","v":8.5405110630796663},{"$f":"19.5286-0.30357*42+0.0000341*AO327+0.060847*AN327","v":9.1476510630796657},{"$f":"62.4*AJ327*AQ327/1000","v":406525.4087048751},5404.4240383532924,{"$f":"AL327*1000/(500*AQ327)","v":23.073226165875603},-66.699783834124389,0,1.1649999999999636,195.68796164670766,0.3575731584218152,{"$f":"IF(AZ327>1,1,IF(AZ327<0,0,AZ327))","v":0.3575731584218152},0.84238008342228832,{"$f":"IF(BB327>1,1,BB327)","v":0.84238008342228832},5045.7262712413549,554.3857287586452,0.60157350347459515,{"$f":"IF(BF327>1,1,IF(BF327<0,0,BF327))","v":0.60157350347459515},44,1]
["2013-01-14T10:00:00","2013-01-14T10:00:00",44.194240000000001,43.732500000000002,43.276220000000002,43.660240000000002,43.531790000000001,42.244149999999998,42.100560000000002,42.32958,42.112839999999998,41.84516,42.426679999999998,42.125540000000001,42.213920000000002,42.471200000000003,42.777329999999999,42.285029999999999,42.214959999999998,42.646590000000003,42.335320000000003,42.013530000000003,42.456060000000001,42.04072,42.27946,41.950899999999997,42.323810000000002,41.782919999999997,208.63319999999999,5799.1570000000002,5601.5290000000005,51.477020000000003,43.41093,51,51,762815.03760000004,461435.84797428548,251.54070391200034,34,29,23388.26114306501,44,8.7336227049785187,9.3407627049785162,415717.45688194194,5355.9128744439013,57.602832732541088,-151.0303672674589,0,-197.6279999999997,245.61612555609918,{"$f":"IF(AZ327>1,1+AY328*60/$BK$7,IF(AZ327<0,AY328*60/$BK$7,AZ327+AY328*60/$BK$7))","v":0.36015576500440738},0.36015576500440738,{"$f":"IF(BB327>1,1+AX328*60/$BK$7,BB327+AX328*60/$BK$7)","v":0.84030206280149666},0.84030206280149666,5007.7840282998177,593.74497170018276,{"$f":"IF(BF327>1,1+BE328*60/$BK$7,IF(BF327<0,BE328*60/$BK$7,BF327+BE328*60/$BK$7))","v":0.60781661828972422},0.60781661828972422,44,1]
["2013-01-14T11:00:00","2013-01-14T11:00:00",44.51746,43.892490000000002,43.302129999999998,43.65549,43.564709999999998,42.440390000000001,41.992350000000002,42.346760000000003,42.132680000000001,41.874209999999998,42.407260000000001,42.138950000000001,42.212290000000003,42.481369999999998,42.786929999999998,42.276890000000002,42.18338,42.628329999999998,42.33569,42.057169999999999,42.474299999999999,42.042340000000003,42.270899999999997,41.939369999999997,42.325690000000002,41.774619999999999,613.60860000000002,5930.0469999999996,5509.0590000000002,51.976430000000001,43.283569999999997,51,51,762815.03760000004,485602.67051325476,841.51510621200021,36,30,25774.534182210009,44,8.8758416156133624,9.4829816156133617,422487.02843853494,5807.7949784210668,189.61922545614229,-423.98937454385771,0,-420.98799999999937,-298.73597842106665,0.3570146133288789,0.3570146133288789,0.83587545450152989,0.83587545450152989,5435.9557419732282,73.103258026771982,0.60858528506582221,0.60858528506582221,44,1]
["2013-01-14T12:00:00","2013-01-14T12:00:00",45.071040000000004,43.929639999999999,43.345709999999997,43.664999999999999,43.606720000000003,42.62388,41.973840000000003,42.35069,42.149880000000003,41.912489999999998,42.38306,42.163519999999998,42.211649999999999,42.485469999999999,42.784100000000002,42.272669999999998,42.165030000000002,42.613199999999999,42.334949999999999,42.104550000000003,42.494779999999999,42.065869999999997,42.262140000000002,41.920960000000001,42.3264,41.794719999999998,126.30549999999999,6095.6869999999999,5998.1239999999998,52.303919999999998,40.823749999999997,51,51,762815.03760000004,500234.32949230541,206.90861788000035,39,32,34989.761513395002,44,9.3117748676067702,9.9189148676067695,443237.30229518644,7515.1648339599014,44.440210555300546,-81.865289444699442,0,-97.563000000000102,-1517.0408339599016,0.3410632191157531,0.3410632191157531,0.83484959821686222,0.83484959821686222,7055.1591540854342,-1057.0351540854344,0.59747076259384857,0.59747076259384857,44,1]
["2013-01-14T13:00:00","2013-01-14T13:00:00",45.3962,44.00376,43.348529999999997,43.671509999999998,43.620359999999998,42.74091,41.919730000000001,42.35577,42.168379999999999,41.94811,42.378680000000003,42.197400000000002,42.22052,42.490299999999998,42.792819999999999,42.281149999999997,42.176400000000001,42.610849999999999,42.340470000000003,42.120660000000001,42.508090000000003,42.09601,42.264600000000002,41.924340000000001,42.331760000000003,41.831490000000002,162.34719999999999,5852.232,6001.1120000000001,51.960239999999999,40.718470000000003,51,51,762815.03760000004,482125.03947447822,289.36034365599983,42,33,32894.723065319988,44,9.3011810565274118,9.9083210565274111,442733.04050722439,7073.2357246685415,62.220129228197663,-100.12707077180232,0,148.88000000000011,-1072.1237246685414,0.32979004321000505,0.32979004321000505,0.83641504294141267,0.83641504294141267,6639.8177607798807,-638.70576077988062,0.59075489368094647,0.59075489368094647,44,1]
["2013-01-14T14:00:00","2013-01-14T14:00:00",45.750639999999997,44.044400000000003,43.383299999999998,43.668559999999999,43.63897,42.825530000000001,41.909280000000003,42.348979999999997,42.182870000000001,41.965249999999997,42.365839999999999,42.226709999999997,42.225180000000002,42.486159999999998,42.791330000000002,42.292430000000003,42.153820000000003,42.592329999999997,42.353720000000003,42.143349999999998,42.52111,42.085169999999998,42.267200000000003,41.920380000000002,42.328510000000001,41.846269999999997,143.49950000000001,5891.1769999999997,5993.4740000000002,52.054789999999997,40.741039999999998,51,51,762815.03760000004,485922.06422075798,280.13757140749999,44,35,33325.651891874993,44,9.4375697295129388,10.044709729512938,449225.09474363254,7062.3376244118917,59.366463917391911,-84.133036082608101,0,102.29700000000048,-1068.8636244118916,0.31855114663491441,0.31855114663491441,0.83749067633063445,0.83749067633063445,6635.4634009898728,-641.98940098987259,0.58400449791928,0.58400449791928,44,1]
["2013-01-14T15:00:00","2013-01-14T15:00:00",46.45729,44.139609999999998,43.406970000000001,43.69267,43.732430000000001,42.889240000000001,41.949170000000002,42.342529999999996,42.197400000000002,41.982930000000003,42.369399999999999,42.226230000000001,42.226990000000001,42.494590000000002,42.80247,42.292569999999998,42.175220000000003,42.61739,42.36797,42.171370000000003,42.533320000000003,42.078609999999998,42.26717,41.91657,42.33079,41.861429999999999,195.14490000000001,6003.4679999999998,5808.6819999999998,52.340600000000002,40.882669999999997,49,49,732900.72239999997,479243.93482071033,448.42932005700015,45,36,34393.658050620012,44,9.5348357395261445,10.141975739526142,436056.69129135669,7214.3157973960615,94.061257541765656,-101.08364245823435,0,-194.78600000000006,-1405.6337973960617,0.3037711761030531,0.3037711761030531,0.83544253879626929,0.83544253879626929,6782.4374528087692,-973.75545280876941,0.5737656455777852,0.5737656455777852,44,0.99795186246563483]
["2013-01-14T16:00:00","2013-01-14T16:00:00",47.46857,44.305070000000001,43.462890000000002,43.718420000000002,43.799430000000001,42.97636,42.105910000000002,42.320489999999999,42.213540000000002,41.987870000000001,42.382260000000002,42.22343,42.234639999999999,42.504100000000001,42.810459999999999,42.309080000000002,42.188029999999998,42.625599999999999,42.373919999999998,42.186430000000001,42.541370000000001,42.075299999999999,42.266539999999999,41.919589999999999,42.32452,41.862560000000002,167.95429999999999,5968.03,5801.4790000000003,52.241370000000003,40.811129999999999,49,49,732900.72239999997,474654.17043110629,470.77674267149979,45,36,34108.007613600013,44,9.5250950596237622,10.13223505962376,435611.22072792018,7161.7149015512859,98.849773094043073,-69.104526905956916,0,-166.55099999999948,-1360.2359015512857,0.28946855576299657,0.28946855576299657,0.8336912868865527,0.8336912868865527,6732.5732995512544,-931.09429955125415,0.56397536710323171,0.56397536710323171,44,0.99620061055591824]
["2013-01-14T17:00:00","2013-01-14T17:00:00",47.733800000000002,44.394779999999997,43.486260000000001,43.725090000000002,43.835209999999996,43.037089999999999,42.330350000000003,42.335680000000004,42.2408,42.0092,42.421480000000003,42.2273,42.244729999999997,42.512270000000001,42.816079999999999,42.310400000000001,42.212229999999998,42.627160000000003,42.376800000000003,42.199710000000003,42.558030000000002,42.074190000000002,42.269860000000001,41.917560000000002,42.339039999999997,41.866459999999996,163.89779999999999,5945.2809999999999,5799.8639999999996,52.088160000000002,40.901519999999998,49,49,732900.72239999997,467469.05800333957,480.82205892600041,44,36,33253.859122920017,44,9.4959685960915738,10.103108596091573,434279.18002330541,7003.784561083512,101.26867081761432,-62.629129182385668,0,-145.41700000000037,-1203.9205610835124,0.27680956133039297,0.27680956133039297,0.83216225494465346,0.83216225494465346,6582.8965029207748,-783.03250292077519,0.55574193010129136,0.55574193010129136,44,0.994671578614019]
["2013-01-14T18:00:00","2013-01-14T18:00:00",47.670029999999997,44.374740000000003,43.48948,43.738379999999999,43.836379999999998,43.067950000000003,42.495699999999999,42.294339999999998,42.262390000000003,42.012050000000002,42.443179999999998,42.215949999999999,42.242539999999998,42.515929999999997,42.816020000000002,42.319249999999997,42.211509999999997,42.627749999999999,42.375599999999999,42.181800000000003,42.559690000000003,42.067770000000003,42.263579999999997,41.93694,42.34216,41.895069999999997,110.2564,5754.0510000000004,5800.0789999999997,51.698549999999997,40.806100000000001,49,49,732900.72239999997,448342.60061971861,318.36314987200001,41,35,31337.856407474992,44,9.3697859034948987,9.9769259034948981,428508.46630205627,6689.1296621379743,67.955266673329561,-42.301133326670438,0,46.027999999999338,-889.05066213797454,0.26746136366178741,0.26746136366178741,0.83264623056113385,0.83264623056113385,6282.0665825527285,-481.98758255272878,0.55067392285783356,0.55067392285783356,44,0.9951555542304994]
["2013-01-14T19:00:00","2013-01-14T19:00:00",48.32526,44.935079999999999,43.462060000000001,43.730310000000003,43.76153,43.081400000000002,42.574080000000002,42.292430000000003,42.263359999999999,41.999890000000001,42.451149999999998,42.211390000000002,42.243119999999998,42.516100000000002,42.813279999999999,42.318390000000001,42.215980000000002,42.639989999999997,42.38156,42.164279999999998,42.555309999999999,42.068150000000003,42.258009999999999,41.94023,42.355580000000003,41.91122,170.1054,5637.7939999999999,5799.723,51.387740000000001,40.725589999999997,49,49,732900.72239999997,433389.73727949418,545.53141990799998,37,32,30055.502648550013,44,9.143516640315557,9.7506566403155563,418160.49294013443,6574.1669930427888,119.3263907898729,-50.7790092101271,0,161.92900000000009,-774.44399304278886,0.25931823319853758,0.25931823319853758,0.83434888302487464,0.83434888302487464,6164.8161261839568,-365.09312618395688,0.54683503846534087,0.54683503846534087,44,0.99685820669424019]
["2013-01-14T20:00:00","2013-01-14T20:00:00",49.401119999999999,45.619720000000001,43.800890000000003,43.731000000000002,43.781309999999998,43.067,42.661760000000001,42.277270000000001,42.264310000000002,42.006309999999999,42.479649999999999,42.204529999999998,42.242139999999999,42.51408,42.807459999999999,42.322450000000003,42.221820000000001,42.667850000000001,42.389800000000001,42.141599999999997,42.538699999999999,42.071820000000002,42.265860000000004,41.942340000000002,42.362569999999998,41.939239999999998,289.83539999999999,5514.0450000000001,5803.1469999999999,51.126379999999997,40.696210000000001,49,49,732900.72239999997,420155.52027009195,1081.358487276,36,32,28756.213368824992,44,9.099210875876933,9.7063508758769323,416134.25719008874,6320.5949968828745,237.68181703378411,-52.153582966215879,0,289.10199999999986,-517.44799688287458,0.25387736648071446,0.25387736648071446,0.83738873525994306,0.83738873525994306,5925.2367314048852,-122.08973140488524,0.54555128829104238,0.54555128829104238,44,0.99989805892930861]
["2013-01-14T21:00:00","2013-01-14T21:00:00",49.877679999999998,45.712380000000003,43.986930000000001,43.798209999999997,43.887569999999997,43.119709999999998,42.64676,42.327419999999996,42.268140000000002,41.998060000000002,42.486919999999998,42.203009999999999,42.241669999999999,42.516480000000001,42.805019999999999,42.3185,42.231270000000002,42.674720000000001,42.387520000000002,42.127850000000002,42.531230000000001,42.068049999999999,42.27149,41.945300000000003,42.359769999999997,41.918500000000002,341.02460000000002,5457.625,5798.6490000000003,51.018219999999999,40.658610000000003,49,49,732900.72239999997,416157.54096619406,1357.1380879139995,37,32,28269.433263124993,44,9.0826116742725631,9.6897516742725625,415375.12581882934,6224.9569346229091,298.84313820401098,-42.181461795989037,0,341.02400000000034,-426.30793462290876,0.2493948200857021,0.2493948200857021,0.84097453739417938,0.84097453739417938,5834.9138787908641,-36.264878790863804,0.54516997002673806,0.54516997002673806,44,1]
["2013-01-14T22:00:00","2013-01-14T22:00:00",50.128970000000002,45.545859999999998,43.584479999999999,43.828949999999999,43.981589999999997,43.206629999999997,42.680860000000003,42.410400000000003,42.284109999999998,41.986660000000001,42.501309999999997,42.191960000000002,42.23265,42.508740000000003,42.801920000000003,42.318390000000001,42.235599999999998,42.671599999999998,42.382399999999997,42.109749999999998,42.520699999999998,42.063110000000002,42.270980000000002,41.946640000000002,42.359839999999998,41.920589999999997,489.411,5306.6719999999996,5796.0829999999996,50.617820000000002,40.624130000000001,49,49,732900.72239999997,397750.46375244675,2008.6357320900013,37,32,26516.617449840003,44,9.0228406550395448,9.6299806550395441,412641.61749274284,5877.6650200576523,445.23355978100176,-44.177440218998242,0,489.41100000000006,-81.582020057652699,0.2485370007485351,0.2485370007485351,0.84612060045225956,0.84612060045225956,5507.0967221441661,288.98627785583358,0.54820860546559413,0.54820860546559413,44,1]
["2013-01-14T23:00:00","2013-01-14T23:00:00",49.903700000000001,45.386060000000001,43.500059999999998,43.866140000000001,43.998989999999999,43.204030000000003,42.672759999999997,42.3917,42.28152,41.967669999999998,42.511119999999998,42.184480000000001,42.231999999999999,42.513100000000001,42.793930000000003,42.315980000000003,42.245260000000002,42.684620000000002,42.377279999999999,42.076090000000001,42.506749999999997,42.058109999999999,42.266939999999998,41.95241,42.355319999999999,41.918170000000003,642.65920000000006,5157.9650000000001,5800.6239999999998,50.308219999999999,40.624290000000002,49,49,732900.72239999997,383702.19925266004,2565.9871606879992,34,29,24974.686001224993,44,8.7877197926417736,9.3948597926417712,401888.83389881824,5683.9968935143015,583.99385079086812,-58.665349209131932,0,642.65899999999965,116.62710648569828,0.24976331246661423,0.24976331246661423,0.85287803691944708,0.85287803691944708,5316.6702968330892,483.9537031669106,0.55329728609126116,0.55329728609126116,44,1]
["2013-01-15","2013-01-15",49.692279999999997,45.169040000000003,43.498890000000003,43.871200000000002,43.977040000000002,43.284689999999998,42.703270000000003,42.396189999999997,42.284550000000003,41.974310000000003,42.51699,42.168700000000001,42.230580000000003,42.505569999999999,42.789810000000003,42.313310000000001,42.247259999999997,42.692779999999999,42.377969999999998,42.070030000000003,42.494790000000002,42.046660000000003,42.270359999999997,41.944690000000001,42.356479999999998,41.915260000000004,670.03330000000005,5127.2460000000001,5797.2790000000005,49.95937,40.521810000000002,49,49,732900.72239999997,367881.32347605977,2605.4311873829979,33,29,24194.345879879991,44,8.7611101945039085,9.3682501945039078,400671.89701206214,5523.1232897990003,594.77192491368464,-75.261375086315411,0,670.03300000000036,274.15571020100015,0.25264600732313991,0.25264600732313991,0.85992330576096188,0.85992330576096188,5165.1792762909226,632.09972370907781,0.55994369378786368,0.55994369378786368,44,1]
["2013-01-15T01:00:00","2013-01-15T01:00:00",49.57817,44.977829999999997,43.510240000000003,43.893520000000002,44.029719999999998,43.349829999999997,42.678199999999997,42.409500000000001,42.282249999999998,41.97184,42.510590000000001,42.164740000000002,42.232759999999999,42.505339999999997,42.792079999999999,42.310209999999998,42.251060000000003,42.697580000000002,42.379930000000002,42.070070000000001,42.494480000000003,42.04298,42.270319999999998,41.942779999999999,42.362139999999997,41.91254,769.40390000000002,5043.0739999999996,5794.6229999999996,49.734319999999997,40.622810000000001,49,49,732900.72239999997,357713.50445712142,2948.9828089785001,32,28,22975.009590869988,44,8.6586838270486677,9.265823827048667,395987.6314291351,5306.8133794420055,681.16191048949941,-88.241989510500616,0,751.54899999999998,487.80962055799409,0.25777523218267429,0.25777523218267429,0.86782569975136481,0.86782569975136481,4959.0862118059385,835.53678819406105,0.56872920330724996,0.56872920330724996,44,1]
["2013-01-15T02:00:00","2013-01-15T02:00:00",49.246319999999997,44.778170000000003,43.557859999999998,43.930419999999998,44.06521,43.250149999999998,42.572360000000003,42.414700000000003,42.286389999999997,41.979649999999999,42.512770000000003,42.170900000000003,42.237549999999999,42.508789999999998,42.792490000000001,42.313029999999998,42.254869999999997,42.69699,42.37612,42.061900000000001,42.503270000000001,42.057270000000003,42.267009999999999,41.94473,42.36157,41.876809999999999,787.74369999999999,5008.4799999999996,5796.2240000000002,49.59854,40.610750000000003,49,49,732900.72239999997,353137.91729909176,2902.6425372934991,34,29,22507.583229599994,44,8.7035915881293597,9.3107315881293609,398041.39829466923,5172.0219180085605,666.99879191306502,-120.74490808693497,0,787.7440000000006,624.20208199143963,0.26433859768715384,0.26433859768715384,0.87610867724395136,0.87610867724395136,4834.7614828239375,961.46251717606265,0.57883879778176828,0.57883879778176828,44,1]
["2013-01-15T03:00:00","2013-01-15T03:00:00",48.985340000000001,44.6526,43.56765,43.945410000000003,44.085299999999997,43.306130000000003,42.547440000000002,42.467059999999996,42.286720000000003,41.975200000000001,42.521059999999999,42.173470000000002,42.235849999999999,42.50676,42.790469999999999,42.31015,42.252429999999997,42.694029999999998,42.369810000000001,42.069180000000003,42.503959999999999,42.049109999999999,42.265940000000001,41.9405,42.36374,41.843629999999997,837.95889999999997,4963.5219999999999,5801.4809999999998,49.59937,40.60033,49,49,732900.72239999997,354693.2968017864,2992.2297278595011,34,29,22333.466509440001,44,8.6976542079719046,9.3047942079719039,397769.86405777972,5135.5149274548266,688.05442394271074,-149.90447605728923,0,837.95899999999983,665.96607254517312,0.27134110356433977,0.27134110356433977,0.88491965585719412,0.88491965585719412,4800.4213763923444,1001.0596236076553,0.58936474825689644,0.58936474825689644,44,1]
["2013-01-15T04:00:00","2013-01-15T04:00:00",48.621369999999999,44.494140000000002,43.602400000000003,43.973489999999998,44.098210000000002,43.393439999999998,42.453980000000001,42.484699999999997,42.293259999999997,41.968769999999999,42.522860000000001,42.186360000000001,42.239490000000004,42.505000000000003,42.794789999999999,42.315069999999999,42.249279999999999,42.694890000000001,42.375079999999997,42.072119999999998,42.504530000000003,42.047829999999998,42.264189999999999,41.945360000000001,42.360419999999998,41.805100000000003,838.96469999999999,4968.6149999999998,5807.58,49.754919999999998,40.651330000000002,49,49,732900.72239999997,363569.15842727775,2859.3049578344981,33,29,22616.116913924991,44,8.7072925867648436,9.3144325867648412,398210.65608405857,5194.752947271274,656.76096888731297,-182.20373111268702,0,838.96500000000015,612.8270527287259,0.27778486281176051,0.27778486281176051,0.89374121236802484,0.89374121236802484,4856.1448490294342,951.4351509705657,0.59936890689364253,0.59936890689364253,44,1]
["2013-01-15T05:00:00","2013-01-15T05:00:00",48.320450000000001,44.261090000000003,43.607779999999998,43.975070000000002,44.095680000000002,43.400100000000002,42.456890000000001,42.474420000000002,42.288379999999997,41.967410000000001,42.521639999999998,42.170789999999997,42.238880000000002,42.503489999999999,42.793100000000003,42.314900000000002,42.250660000000003,42.701079999999997,42.384700000000002,42.061279999999996,42.493569999999998,42.050130000000003,42.264609999999998,41.942909999999998,42.36157,41.777810000000002,731.57619999999997,5067.2879999999996,5798.8649999999998,49.770940000000003,40.551139999999997,49,49,732900.72239999997,365549.85487719579,2393.2198545839992,33,29,23359.690951200017,44,8.7326484614359217,9.339788461435921,399370.25642914197,5349.9670928832857,548.10859847448353,-183.46760152551644,0,731.57700000000023,448.89790711671412,0.28250493844688684,0.28250493844688684,0.90143360459836108,0.90143360459836108,5002.1884430578721,796.67655694212772,0.60774580851399507,0.60774580851399507,44,1]
["2013-01-15T06:00:00","2013-01-15T06:00:00",48.107799999999997,44.143160000000002,43.599330000000002,44.020769999999999,44.158969999999997,43.284509999999997,42.407420000000002,42.436279999999996,42.276919999999997,41.954210000000003,42.528840000000002,42.164549999999998,42.237819999999999,42.492519999999999,42.787979999999997,42.317869999999999,42.249070000000003,42.708779999999997,42.381349999999998,42.01952,42.464410000000001,42.042070000000002,42.26981,41.944400000000002,42.361310000000003,41.721910000000001,747.45460000000003,5054.4120000000003,5801.8670000000002,49.858040000000003,40.625120000000003,49,49,732900.72239999997,372089.67460331548,2386.5814277969985,33,29,23333.490821520001,44,8.7317550370138335,9.3388950370138311,399329.39744551008,5344.5133819282682,546.64415519681904,-200.81044480318099,0,747.45499999999993,457.35361807173194,0.2873139242654284,0.2873139242654284,0.90929295096180063,0.90929295096180063,4997.05601766374,804.81098233626017,0.61620824206154057,0.61620824206154057,44,1]
["2013-01-15T07:00:00","2013-01-15T07:00:00",47.81982,44.113329999999998,43.588180000000001,44.007359999999998,44.153959999999998,43.197130000000001,42.441929999999999,42.431179999999998,42.279409999999999,41.94829,42.533839999999998,42.139560000000003,42.235939999999999,42.486350000000002,42.782679999999999,42.323529999999998,42.247100000000003,42.713120000000004,42.37406,41.993940000000002,42.450629999999997,42.030410000000003,42.263660000000002,41.943510000000003,42.348469999999999,41.617449999999998,824.33910000000003,4973.0550000000003,5797.3940000000002,49.580739999999999,40.54851,49,49,732900.72239999997,364185.18200567545,2556.4280518335008,30,29,22458.888281324998,44,8.7019310903931846,9.3090710903931821,397965.45874326909,5161.81708359408,587.55419349522617,-236.78490650477386,0,824.33899999999994,635.5769164059202,0.29399689397817491,0.29399689397817491,0.91796071788006506,0.91796071788006506,4825.1620517759775,972.23194822402274,0.62643107504371898,0.62643107504371898,44,1]
["2013-01-15T08:00:00","2013-01-15T08:00:00",47.521859999999997,44.05639,43.622920000000001,44.039470000000001,44.155670000000001,43.254730000000002,42.334470000000003,42.427140000000001,42.282170000000001,41.940530000000003,42.537219999999998,42.140389999999996,42.238979999999998,42.488120000000002,42.781869999999998,42.3232,42.250790000000002,42.705460000000002,42.371540000000003,41.996079999999999,42.45485,42.038879999999999,42.264899999999997,41.946539999999999,42.344000000000001,41.587470000000003,808.8809,4993.326,5802.2079999999996,49.638159999999999,40.567410000000002,49,49,732900.72239999997,368182.24664947146,2400.1073620754973,30,29,22646.605907249992,44,8.7083322614372261,9.3154722614372254,398258.20353112981,5201.1350112432174,551.22089741655827,-257.66000258344172,0,808.88199999999961,601.07298875678225,0.30031706149106507,0.30031706149106507,0.92646595739970394,0.92646595739970394,4862.1487503105909,940.05924968940872,0.63631561825429905,0.63631561825429905,44,1]
["2013-01-15T09:00:00","2013-01-15T09:00:00",47.262749999999997,43.992240000000002,43.625500000000002,44.087150000000001,44.226669999999999,43.278440000000003,42.271529999999998,42.477490000000003,42.286830000000002,41.954569999999997,42.521790000000003,42.154249999999998,42.24044,42.490569999999998,42.785290000000003,42.320300000000003,42.258009999999999,42.709359999999997,42.38317,42.017240000000001,42.464129999999997,42.04325,42.267090000000003,41.944780000000002,42.322710000000001,41.629620000000003,723.83749999999998,5072.625,5796.4629999999997,49.720379999999999,40.659950000000002,49,49,732900.72239999997,370014.76816293731,2038.7353681874979,31,30,22980.081864374992,44,8.7805507915751893,9.3876907915751886,401560.97393663769,5234.3144319429357,464.37528045362137,-259.46221954637861,0,723.83799999999974,562.14856805706404,0.30622794616515514,0.30622794616515514,0.93407697552523572,0.93407697552523572,4895.790109533229,900.6728904667707,0.64578602143086294,0.64578602143086294,44,1]
["2013-01-15T10:00:00","2013-01-15T10:00:00",47.104509999999998,44.052840000000003,43.669930000000001,44.074910000000003,44.236750000000001,43.189680000000003,42.297730000000001,42.47278,42.286459999999998,41.967289999999998,42.521720000000002,42.158000000000001,42.24044,42.492280000000001,42.796250000000001,42.310119999999998,42.256630000000001,42.70975,42.38561,42.05133,42.484780000000001,42.048110000000001,42.264600000000002,41.942880000000002,42.320950000000003,41.579709999999999,711.98599999999999,5085.8040000000001,5797.7910000000002,49.956519999999998,40.57011,49,49,732900.72239999997,383096.69426543068,1966.7901263999997,33,31,23868.720761819997,44,8.8717003779780637,9.478840377978063,405729.51843443606,5380.8671945388396,443.3851556308415,-268.60084436915849,0,711.98700000000008,416.92380546116055,0.31061182023688189,0.31061182023688189,0.94156338265244233,0.94156338265244233,5036.2111418762906,761.57985812370953,0.65379388797589022,0.65379388797589022,44,1]
["2013-01-15T11:00:00","2013-01-15T11:00:00",46.96763,44.017659999999999,43.700290000000003,44.095570000000002,44.243639999999999,43.246160000000003,42.345410000000001,42.469239999999999,42.289459999999998,41.976019999999998,42.507840000000002,42.169980000000002,42.245190000000001,42.498959999999997,42.796729999999997,42.306469999999997,42.248179999999998,42.705840000000002,42.392499999999998,42.067169999999997,42.498330000000003,42.058160000000001,42.259909999999998,41.93768,42.316670000000002,41.530630000000002,652.90099999999995,5145.6559999999999,5798.5569999999998,50.630540000000003,40.651110000000003,49,49,732900.72239999997,416166.230237159,1774.9113684999991,35,32,25675.356928040001,44,8.9941536712461652,9.6012936712461645,411329.67551725457,5709.3436173150485,394.68113029340316,-258.2198697065968,0,652.90099999999984,89.213382684951284,0.31154988189246663,0.31154988189246663,0.94842851179069954,0.94842851179069954,5348.3119686115306,450.24503138846922,0.65852812836507713,0.65852812836507713,44,1]
["2013-01-15T12:00:00","2013-01-15T12:00:00",46.931429999999999,44.012450000000001,43.69529,44.082799999999999,44.215560000000004,43.2318,42.374400000000001,42.46067,42.294110000000003,41.977969999999999,42.514879999999998,42.170749999999998,42.242010000000001,42.497419999999998,42.797530000000002,42.30874,42.250030000000002,42.70194,42.388919999999999,42.053089999999997,42.494639999999997,42.057670000000002,42.265610000000002,41.937249999999999,42.309570000000001,41.514569999999999,611.31870000000004,5188.451,5799.7690000000002,50.834980000000002,40.662529999999997,49,49,732900.72239999997,426250.35785680515,1655.7139066410002,35,32,26389.629187475013,44,9.0185103552928982,9.6256503552928976,412443.57987244125,5852.3255277934304,367.1812397862966,-244.13746021370343,0,611.31800000000021,-52.556527793430178,0.31099726005491346,0.31099726005491346,0.95485640363730584,0.95485640363730584,5483.1888160084764,316.58018399152388,0.66185690844921707,0.66185690844921707,44,1]
["2013-01-15T13:00:00","2013-01-15T13:00:00",46.978149999999999,44.01811,43.674430000000001,44.069209999999998,44.199249999999999,43.281469999999999,42.403329999999997,42.450209999999998,42.303359999999998,41.96998,42.531489999999998,42.164650000000002,42.245710000000003,42.49474,42.792569999999998,42.318800000000003,42.255580000000002,42.708309999999997,42.389420000000001,42.030079999999998,42.48142,42.057160000000003,42.27599,41.936320000000002,42.31561,41.5107,550.12829999999997,5251.33,5801.4579999999996,50.842599999999997,40.715899999999998,49,49,732900.72239999997,426775.83008514839,1503.8994869174996,36,33,26589.321755500001,44,9.0861668718625506,9.6933068718625499,415537.7156882647,5852.7038145953675,331.03056726256654,-219.09773273743343,0,550.1279999999997,-51.245814595367847,0.3104584201159451,0.3104584201159451,0.96064089433738309,0.96064089433738309,5486.119877764876,315.33812223512359,0.66517262849155068,0.66517262849155068,44,1]
["2013-01-15T14:00:00","2013-01-15T14:00:00",47.183309999999999,44.0137,43.6783,44.065640000000002,44.211469999999998,43.31767,42.458480000000002,42.462859999999999,42.302849999999999,41.975549999999998,42.526960000000003,42.176699999999997,42.253050000000002,42.510210000000001,42.804729999999999,42.325670000000002,42.262500000000003,42.714309999999998,42.391930000000002,42.063249999999996,42.499549999999999,42.068300000000001,42.2697,41.930199999999999,42.321809999999999,41.53613,428.09480000000002,5372.95,5801.0439999999999,51.176450000000003,40.688330000000001,49,49,732900.72239999997,440880.80351123138,1208.764196332,37,33,28176.072177000005,44,9.1402750612357018,9.7474150612357011,418012.24578761542,6165.2569508539054,264.49186446443406,-163.60293553556596,0,428.09400000000005,-364.21295085390557,0.30662879059870163,0.30662879059870163,0.96514222086822476,0.96514222086822476,5781.2398466651657,19.804153334834155,0.66538086537603625,0.66538086537603625,44,1]
["2013-01-15T15:00:00","2013-01-15T15:00:00",47.3825,43.991880000000002,43.655290000000001,44.038310000000003,44.218429999999998,43.30527,42.520110000000003,42.45626,42.313549999999999,42.010100000000001,42.534739999999999,42.201909999999998,42.25929,42.516820000000003,42.816009999999999,42.325569999999999,42.261850000000003,42.71481,42.38879,42.085140000000003,42.510730000000002,42.078380000000003,42.263109999999998,41.934170000000002,42.33961,41.537199999999999,420.9101,5377.8050000000003,5798.7160000000003,51.0092,40.694629999999997,49,49,732900.72239999997,433183.02409654274,1230.1729037650005,38,34,27734.873059425008,44,9.186077171326394,9.7932171713263934,420106.91392096516,6038.458537230058,267.83421929109994,-153.07588070890006,0,420.91100000000006,-239.74253723005768,0.30410794367394922,0.30410794367394922,0.96956801952791893,0.96956801952791893,5664.0984416500169,134.61755834998348,0.66679634325453463,0.66679634325453463,44,1]
["2013-01-15T16:00:00","2013-01-15T16:00:00",47.45429,44.020629999999997,43.670470000000002,44.057479999999998,44.200360000000003,43.319479999999999,42.546520000000001,42.45993,42.310229999999997,42.037779999999998,42.542760000000001,42.209150000000001,42.265590000000003,42.523090000000003,42.824460000000002,42.3279,42.262970000000003,42.713200000000001,42.395589999999999,42.099939999999997,42.517679999999999,42.084310000000002,42.273319999999998,41.950189999999999,42.33455,41.540999999999997,342.25819999999999,5455.1279999999997,5797.3869999999997,51.223990000000001,40.705300000000001,49,49,732900.72239999997,442832.23083789943,1011.9359957390006,39,34,28690.400171159996,44,9.2186606458365574,9.8258006458365568,421597.05412618956,6224.4183343743116,219.5407846357862,-122.71741536421379,0,342.25900000000001,-427.03133437431188,0.29961779086891149,0.29961779086891149,0.97316680745094364,0.97316680745094364,5839.8091321579695,-42.422132157969827,0.66635028264873886,0.66635028264873886,44,1]
["2013-01-15T17:00:00","2013-01-15T17:00:00",47.696170000000002,43.986490000000003,43.67183,44.0685,44.20729,43.364510000000003,42.560079999999999,42.472479999999997,42.312579999999997,42.04251,42.558819999999997,42.221359999999997,42.262340000000002,42.530439999999999,42.825319999999998,42.328429999999997,42.262059999999998,42.70778,42.39676,42.113199999999999,42.535919999999997,42.09355,42.265120000000003,41.946190000000001,42.339959999999998,41.546410000000002,426.40910000000002,5379.8180000000002,5800.8950000000004,51.005339999999997,40.657620000000001,49,49,732900.72239999997,432585.29372017615,1311.1568134080001,38,33,27834.425157479986,44,9.1286248978700684,9.7357648978700677,417479.44880725822,6098.2733914227192,287.26272096335674,-139.14637903664328,0,421.07700000000023,-297.37839142271878,0.29649091396101251,0.29649091396101251,0.97759435156888785,0.97759435156888785,5717.9739752280657,82.921024771934754,0.6672221813643725,0.6672221813643725,44,1]
["2013-01-15T18:00:00","2013-01-15T18:00:00",48.166049999999998,44.053489999999996,43.764769999999999,44.174720000000001,44.334470000000003,43.606879999999997,42.602319999999999,42.486899999999999,42.314169999999997,42.049210000000002,42.562930000000001,42.242100000000001,42.261710000000001,42.531280000000002,42.82985,42.327730000000003,42.265079999999998,42.708309999999997,42.398060000000001,42.120010000000001,42.533580000000001,42.095590000000001,42.281680000000001,41.938079999999999,42.345930000000003,41.55303,422.80549999999999,5378.701,5800.9179999999997,51.120919999999998,40.668559999999999,49,49,732900.72239999997,437568.36195344903,1398.0106138049998,38,33,28110.059592179994,44,9.1380240320933392,9.7451640320933386,417909.29946041759,6152.3277884705985,305.97656755882781,-116.82893244117219,0,422.21699999999964,-351.40978847059887,0.29279590724743987,0.29279590724743987,0.98203388256879065,0.98203388256879065,5769.027488835759,31.890511164240706,0.66755750398974378,0.66755750398974378,44,1]
["2013-01-15T19:00:00","2013-01-15T19:00:00",48.723640000000003,44.248040000000003,43.896210000000004,44.29374,44.42333,43.88794,42.654899999999998,42.497210000000003,42.313279999999999,42.048119999999997,42.563650000000003,42.248150000000003,42.282969999999999,42.530239999999999,42.829120000000003,42.332889999999999,42.262030000000003,42.710639999999998,42.405439999999999,42.120440000000002,42.53978,42.098129999999998,42.290039999999998,41.939279999999997,42.343530000000001,41.56503,464.80739999999997,5330.03,5794.8370000000004,50.866149999999998,40.69943,49,49,732900.72239999997,425368.16818885494,1663.6874508570006,38,33,27094.461300799994,44,9.10339213035728,9.7105321303572794,416325.47852246987,5952.6077560577678,365.5093457545492,-99.298054245450771,0,464.8070000000007,-157.77075605776736,0.29113697792342741,0.29113697792342741,0.986921239272741,0.986921239272741,5580.4277123179872,214.4092876820132,0.66981197664084824,0.66981197664084824,44,1]
["2013-01-15T20:00:00","2013-01-15T20:00:00",48.656930000000003,44.417000000000002,43.998420000000003,44.399740000000001,44.53398,43.991759999999999,42.69858,42.493389999999998,42.295369999999998,42.052390000000003,42.570860000000003,42.254579999999997,42.283029999999997,42.528799999999997,42.834919999999997,42.334319999999998,42.257660000000001,42.71293,42.407060000000001,42.116230000000002,42.54148,42.093969999999999,42.29045,41.938980000000001,42.353749999999998,41.549199999999999,484.66109999999998,5313.6940000000004,5798.3549999999996,50.767560000000003,40.663829999999997,49,49,732900.72239999997,421583.30468861986,1722.4201201515009,37,32,26844.064739310015,44,9.0340066076104719,9.6411466076104713,413152.27005836705,5942.8924297433887,381.31920751540991,-103.34189248459006,0,484.66099999999915,-144.53742974338911,0.28961719449454593,0.28961719449454593,0.99201735698932725,0.99201735698932725,5568.6456874579635,229.70931254203606,0.6722273261270052,0.6722273261270052,44,1]
["2013-01-15T21:00:00","2013-01-15T21:00:00",48.24503,44.345100000000002,44.034320000000001,44.441589999999998,44.580640000000002,44.012369999999997,42.849449999999997,42.484119999999997,42.316510000000001,42.059100000000001,42.566679999999998,42.249490000000002,42.301949999999998,42.532760000000003,42.829039999999999,42.337919999999997,42.263100000000001,42.71987,42.403210000000001,42.1,42.530589999999997,42.088169999999998,42.295580000000001,41.935229999999997,42.361350000000002,41.57423,593.55870000000004,5205.5159999999996,5799.0749999999998,50.760899999999999,40.628070000000001,49,49,732900.72239999997,420134.02575770539,1979.7556879800002,36,32,26373.304345139994,44,9.017953678169274,9.6250936781692733,412418.1213547198,5849.0662707626634,439.06982861812804,-154.488871381872,0,593.5590000000002,-49.991270762663589,0.28909154584402885,0.28909154584402885,0.99825851634759866,0.99825851634759866,5480.1137998183704,318.96120018162947,0.67558114214098031,0.67558114214098031,44,1]
["2013-01-15T22:00:00","2013-01-15T22:00:00",48.114730000000002,44.441989999999997,44.121259999999999,44.52028,44.6539,44.062730000000002,42.94679,42.474780000000003,42.340589999999999,42.061410000000002,42.576479999999997,42.23798,42.301690000000001,42.533259999999999,42.826970000000003,42.347320000000003,42.270339999999997,42.730310000000003,42.402520000000003,42.076740000000001,42.520530000000001,42.084449999999997,42.296140000000001,41.942050000000002,42.355469999999997,41.6066,752.96140000000003,5045.8860000000004,5798.8469999999998,50.434739999999998,40.626629999999999,49,49,732900.72239999997,403737.37144717603,2450.1853380910006,33,29,24745.302467729998,44,8.779897814149594,9.3870378141495934,401531.11131671729,5636.8087628197036,558.13527445440354,-194.82612554559648,0,752.96099999999933,162.03823718029616,0.29079534691582731,0.29079534691582731,1.0061757572479362,1,5272.2281421792195,526.61885782078025,0.68111843870750588,0.68111843870750588,44,1]
["2013-01-15T23:00:00","2013-01-15T23:00:00",48.171930000000003,44.482149999999997,44.143700000000003,44.561309999999999,44.703699999999998,44.132899999999999,42.937959999999997,42.47175,42.3401,42.053440000000002,42.598190000000002,42.232190000000003,42.297370000000001,42.529679999999999,42.824910000000003,42.34552,42.274540000000002,42.72663,42.40605,42.064320000000002,42.514769999999999,42.078850000000003,42.299250000000001,41.942740000000001,42.341479999999997,41.618000000000002,785.18349999999998,5017.5069999999996,5802.69,50.368130000000001,40.5702,49,49,732900.72239999997,400169.73972106003,2573.0188480775,33,29,24580.591180255004,44,8.7742811592466978,9.3814211592466954,401274.24480952311,5602.8729269407941,586.49108716238197,-198.69241283761801,0,785.18299999999999,199.81707305920554,0.29289638522114469,0.29289638522114469,1.0082560490674148,1,5240.2702667340363,562.41973326596326,0.68703217463190325,0.68703217463190325,44,1]
["2013-01-16","2013-01-16",48.099069999999998,44.598379999999999,44.18591,44.59966,44.746850000000002,44.166310000000003,42.898609999999998,42.479309999999998,42.330959999999997,42.042000000000002,42.602150000000002,42.229559999999999,42.284529999999997,42.525419999999997,42.822859999999999,42.33728,42.271230000000003,42.734479999999998,42.40231,42.06203,42.508540000000004,42.076770000000003,42.297530000000002,41.94905,42.329560000000001,41.557380000000002,864.90430000000003,4932.2030000000004,5797.107,49.872210000000003,40.64358,49,49,732900.72239999997,380262.16261071118,2828.9679051334983,32,28,22758.738285945004,44,8.6513089755507266,9.2584489755507242,395650.35730813199,5261.3398389221738,653.99765818753724,-210.90664181246279,0,864.90399999999954,535.76716107782613,0.29852987444667306,0.29852987444667306,1.0090943001346224,1,4916.3176998750459,880.78930012495402,0.69629350565904669,0.69629350565904669,44,1]
["2013-01-16T01:00:00","2013-01-16T01:00:00",47.866529999999997,44.469650000000001,44.134360000000001,44.573799999999999,44.710509999999999,44.13729,42.904760000000003,42.484090000000002,42.34299,42.035510000000002,42.591500000000003,42.231850000000001,42.299129999999998,42.519730000000003,42.818530000000003,42.34149,42.274299999999997,42.73554,42.407069999999997,42.039960000000001,42.496879999999997,42.06841,42.297699999999999,41.946579999999997,42.331850000000003,41.682389999999998,904.30529999999999,4889.0510000000004,5793.357,49.727200000000003,40.592979999999997,49,49,732900.72239999997,367913.33657961467,2796.1752889710001,31,27,22328.833712610012,44,8.5758022296000025,9.1829422296000018,392197.20691216242,5207.4040689838739,652.10815597397959,-252.1971440260204,0,904.30599999999959,585.95293101612606,0.3046910574443496,0.3046910574443496,1.0095086046284212,1,4863.111006107818,930.24599389218201,0.70607486436184574,0.70607486436184574,44,1]
["2013-01-16T02:00:00","2013-01-16T02:00:00",47.46904,44.453330000000001,44.133809999999997,44.551209999999998,44.707920000000001,44.130420000000001,42.809629999999999,42.495510000000003,42.353479999999998,42.042569999999998,42.590020000000003,42.231679999999997,42.280549999999998,42.52505,42.816859999999998,42.339550000000003,42.274590000000003,42.731879999999997,42.400590000000001,42.03857,42.501649999999998,42.067700000000002,42.296410000000002,41.945160000000001,42.337400000000002,41.842529999999996,856.45140000000004,4942.5600000000004,5799.0110000000004,49.618499999999997,40.615769999999998,49,49,732900.72239999997,355618.47549450945,2409.4161833070016,30,27,22248.2665944,44,8.5730548908690398,9.1801948908690392,392071.56285602896,5190.2774163025852,562.0904599300336,-294.36094006996643,0,856.45100000000002,608.73358369741527,0.31109177464784116,0.31109177464784116,1.0090054184563808,1,4847.0140032710951,951.99699672890529,0.71608493069927959,0.71608493069927959,44,1]
["2013-01-16T03:00:00","2013-01-16T03:00:00",47.18571,44.451349999999998,44.117789999999999,44.53884,44.694240000000001,44.115989999999996,42.782649999999997,42.506070000000001,42.344799999999999,42.028680000000001,42.608890000000002,42.210009999999997,42.27834,42.519840000000002,42.809240000000003,42.346020000000003,42.28096,42.738570000000003,42.399169999999998,42.016559999999998,42.487090000000002,42.057099999999998,42.29721,41.946190000000001,42.331699999999998,41.746189999999999,813.41390000000001,4983.777,5797.1909999999998,49.524039999999999,40.613390000000003,49,49,732900.72239999997,355704.45354405564,2212.290588664001,30,27,22204.346262524992,44,8.571557207552102,9.1786972075521014,392003.06929729058,5180.9363747724892,516.193390557979,-297.22050944202101,0,813.41399999999976,616.25462522751059,0.31757157416451387,0.31757157416451387,1.0085528926328284,1,4838.2348301577213,958.95616984227854,0.72616817141095824,0.72616817141095824,44,1]
["2013-01-16T04:00:00","2013-01-16T04:00:00",46.683880000000002,44.432729999999999,44.095910000000003,44.524529999999999,44.673110000000001,44.07817,42.69558,42.540260000000004,42.32497,42.017960000000002,42.607979999999998,42.202500000000001,42.281059999999997,42.518070000000002,42.808459999999997,42.349420000000002,42.279330000000002,42.741529999999997,42.40551,42.005070000000003,42.480049999999999,42.052979999999998,42.289679999999997,41.94838,42.315730000000002,41.542760000000001,900.12689999999998,4897.8559999999998,5797.9830000000002,49.445689999999999,40.647959999999998,49,49,732900.72239999997,361424.7378191817,2313.8302040640006,29,25,21545.00733344,44,8.4273797500703047,9.0345197500703041,385409.40090217703,5113.0975397804441,549.12209314993731,-351.00480685006266,0,900.12700000000041,684.88546021955608,0.32477301378448986,0.32477301378448986,1.0094646632427151,1,4769.4859116938333,1028.4970883061669,0.73698262157958006,0.73698262157958006,44,1]
["2013-01-16T05:00:00","2013-01-16T05:00:00",46.119529999999997,44.425939999999997,44.085349999999998,44.513910000000003,44.66433,44.054499999999997,42.637169999999998,42.541820000000001,42.329540000000001,42.00817,42.620249999999999,42.197290000000002,42.275350000000003,42.519759999999998,42.809060000000002,42.344329999999999,42.27516,42.748719999999999,42.403840000000002,41.994599999999998,42.473050000000001,42.053530000000002,42.290410000000001,41.949150000000003,42.298220000000001,41.448030000000003,803.41129999999998,4995.43,5798.8410000000003,49.340110000000003,40.587690000000002,51,51,762815.03760000004,375660.31164119375,1876.5679439749977,28,24,21861.050720300002,44,8.3773098295622308,8.9844498295622301,398757.08574776025,5219.1099923643105,448.01206643996369,-355.39923356003629,0,803.41100000000006,579.73100763568982,0.33086877444785379,0.33086877444785379,1.0084477130010465,1,4866.4194547269644,932.42154527303592,0.74678685578904314,0.74678685578904314,44,1]
["2013-01-16T06:00:00","2013-01-16T06:00:00",45.841639999999998,44.401240000000001,44.059719999999999,44.48695,44.646619999999999,44.026809999999998,42.597050000000003,42.531109999999998,42.347320000000003,42.017719999999997,42.605530000000002,42.201779999999999,42.272770000000001,42.52187,42.808929999999997,42.343670000000003,42.278350000000003,42.745080000000002,42.404290000000003,41.990929999999999,42.470750000000002,42.05603,42.29251,41.946159999999999,42.274619999999999,41.440809999999999,688.93179999999995,5114.2110000000002,5803.1440000000002,49.6843,40.539990000000003,51,51,762815.03760000004,392387.30758064601,1515.9358666969997,27,24,23382.965394704996,44,8.4292071199594414,9.0363471199594407,401227.37903976301,5548.081821203963,359.68646756998749,-329.24533243001247,0,688.93299999999999,255.06217879603719,0.33355070447356983,0.33355070447356983,1.0072439987266169,1,5175.313671396445,627.83032860355524,0.75338837161269456,0.75338837161269456,44,1]
["2013-01-16T07:00:00","2013-01-16T07:00:00",45.69314,44.377609999999997,44.054360000000003,44.484940000000002,44.630499999999998,44.015070000000001,42.580579999999998,42.550870000000003,42.345039999999997,42.020569999999999,42.603230000000003,42.197330000000001,42.276829999999997,42.522640000000003,42.812109999999997,42.339730000000003,42.275660000000002,42.742019999999997,42.403840000000002,41.998089999999998,42.474110000000003,42.05921,42.293999999999997,41.943440000000002,42.264870000000002,41.451320000000003,763.47450000000003,5037.9520000000002,5801.4269999999997,49.595170000000003,40.584620000000001,51,51,762815.03760000004,387644.47762302659,1619.260701794999,28,24,22697.359196800004,44,8.4058279486108809,9.0129679486108802,400114.53847115336,5400.3863356615329,385.27096002782037,-378.20353997217967,0,763.47499999999945,401.04066433846674,0.33776757035427152,0.33776757035427152,1.0080277935993831,1,5036.6004464263578,764.82655357364183,0.76143037653940049,0.76143037653940049,44,1]
["2013-01-16T08:00:00","2013-01-16T08:00:00",45.48001,44.374600000000001,44.042929999999998,44.471020000000003,44.618600000000001,43.988059999999997,42.545180000000002,42.546639999999996,42.349769999999999,42.0246,42.60716,42.192419999999998,42.271059999999999,42.529600000000002,42.812109999999997,42.337060000000001,42.278179999999999,42.743160000000003,42.410409999999999,42.019500000000001,42.478999999999999,42.057589999999998,42.288089999999997,41.932459999999999,42.258560000000003,41.448680000000003,697.86360000000002,5097.8090000000002,5795.6729999999998,49.941960000000002,40.623280000000001,51,51,762815.03760000004,404277.22623895318,1406.659233293999,28,24,23752.42538606,44,8.4418057056646472,9.0489457056646465,401827.06741497666,5627.3328750320734,333.26027211218525,-364.60332788781477,0,697.86399999999958,168.34012496792639,0.33953763457082986,0.33953763457082986,1.0073379064834342,1,5249.7663614427402,545.90663855725961,0.76717048043130365,0.76717048043130365,44,1]
["2013-01-16T09:00:00","2013-01-16T09:00:00",45.53416,44.392420000000001,44.064430000000002,44.476140000000001,44.627600000000001,43.992319999999999,42.559739999999998,42.564689999999999,42.35868,42.046590000000002,42.589880000000001,42.216819999999998,42.271169999999998,42.52975,42.818489999999997,42.342359999999999,42.26914,42.744210000000002,42.414650000000002,42.063549999999999,42.505580000000002,42.071599999999997,42.289340000000003,41.928359999999998,42.266770000000001,41.443420000000003,503.81970000000001,5296.0259999999998,5799.8459999999995,49.975679999999997,40.585419999999999,51,51,762815.03760000004,406132.66092128941,1030.4976997889992,32,27,24865.530553379995,44,8.6623035918702591,9.2694435918702585,412322.69146443187,5741.0896050137935,237.92694145611367,-265.89275854388632,0,503.81999999999971,58.756394986206033,0.34015544682610094,0.34015544682610094,1.0052975709371508,1,5365.0535346454326,434.79246535456696,0.77174224004417036,0.77174224004417036,44,1]
["2013-01-16T10:00:00","2013-01-16T10:00:00",45.834299999999999,44.410429999999998,44.096640000000001,44.489310000000003,44.631439999999998,44.044420000000002,42.627160000000003,42.557839999999999,42.36224,42.085970000000003,42.561279999999996,42.225560000000002,42.282640000000001,42.548659999999998,42.82929,42.344670000000001,42.275449999999999,42.747630000000001,42.422319999999999,42.116959999999999,42.534990000000001,42.098109999999998,42.284820000000003,41.917470000000002,42.28387,41.445030000000003,318.84339999999997,5492.3950000000004,5803.4870000000001,50.515650000000001,40.624339999999997,51,51,762815.03760000004,431758.41298857133,699.74488515899941,36,29,27163.49079372501,44,8.8623580360660235,9.4694980360660228,421845.21465879719,6130.0820127512725,157.91392816930565,-160.92947183069433,0,311.09199999999964,-326.59501275127241,0.33672136273303288,0.33672136273303288,1.0032710728791634,1,5737.0497760850103,66.437223914989772,0.77244081474655824,0.77244081474655824,44,1]
["2013-01-16T11:00:00","2013-01-16T11:00:00",46.391330000000004,44.442700000000002,44.139009999999999,44.508890000000001,44.652509999999999,44.033659999999998,42.70937,42.609119999999997,42.366320000000002,42.130270000000003,42.5657,42.271549999999998,42.297820000000002,42.567619999999998,42.84581,42.340350000000001,42.279400000000003,42.754060000000003,42.430439999999997,42.153379999999999,42.560490000000001,42.117100000000001,42.279690000000002,41.916350000000001,42.277650000000001,41.477429999999998,181.0574,5663.1809999999996,5801.1610000000001,51.268320000000003,40.700530000000001,51,51,762815.03760000004,466043.01890561794,444.84897893000044,40,31,29923.653769995006,44,9.0781735935568317,9.6853135935568311,432117.96146116301,6592.439208528267,98.00406972735766,-83.053330272642341,0,137.98000000000047,-791.27820852826699,0.32840122371374003,0.32840122371374003,1.0014508333093328,1,6179.1811862244213,-378.0201862244212,0.76846600479022686,0.76846600479022686,44,1]
["2013-01-16T12:00:00","2013-01-16T12:00:00",47.867959999999997,44.528170000000003,44.263420000000004,44.648380000000003,44.810459999999999,44.300080000000001,42.855159999999998,42.65504,42.383020000000002,42.160200000000003,42.560720000000003,42.315669999999997,42.309010000000001,42.575369999999999,42.859940000000002,42.351039999999998,42.277290000000001,42.742240000000002,42.432929999999999,42.197859999999999,42.590789999999998,42.129710000000003,42.292360000000002,41.915579999999999,42.288690000000003,41.553730000000002,128.51740000000001,5849.7629999999999,5797.6570000000002,51.602249999999998,40.788960000000003,49,49,732900.72239999997,459549.01618397271,405.74421130099967,43,33,31627.591875134985,44,9.2579718829421047,9.8651118829421041,423394.87513235054,6832.5098142518882,87.652936611005913,-40.864463388994096,0,-52.105999999999767,-1034.852814251888,0.31751994430242336,0.31751994430242336,0.99945211537602485,0.99945211537602485,6412.0087537623722,-614.35175376237203,0.76200621360305842,0.76200621360305842,44,0.99945211537602485]
["2013-01-16T13:00:00","2013-01-16T13:00:00",48.330379999999998,44.602179999999997,44.300750000000001,44.707479999999997,44.839370000000002,44.365070000000003,43.356879999999997,42.685029999999998,42.387860000000003,42.183700000000002,42.574269999999999,42.355159999999998,42.330869999999997,42.595869999999998,42.868749999999999,42.365479999999998,42.283700000000003,42.736330000000002,42.436999999999998,42.234940000000002,42.602310000000003,42.135190000000001,42.300179999999997,41.918660000000003,42.306260000000002,41.602370000000001,118.8625,5844.1509999999998,5802.6490000000003,51.856909999999999,40.715229999999998,49,49,732900.72239999997,468970.92989009293,399.85404431249987,45,35,32556.830156840006,44,9.4113529083482454,10.018492908348245,430409.45034608163,6918.6291224847801,84.97270226851515,-33.889797731484848,0,-41.501999999999498,-1115.9801224847797,0.30578562676180687,0.30578562676180687,0.99901572978388153,0.99901572978388153,6499.3468488081544,-696.69784880815405,0.75468056897636315,0.75468056897636315,44,0.99901572978388153]
["2013-01-16T14:00:00","2013-01-16T14:00:00",48.735460000000003,44.658729999999998,44.420589999999997,44.823399999999999,44.934379999999997,44.454149999999998,43.829569999999997,42.700940000000003,42.399360000000001,42.207079999999998,42.572920000000003,42.392040000000001,42.342190000000002,42.592739999999999,42.875770000000003,42.376809999999999,42.253070000000001,42.686439999999997,42.440190000000001,42.251620000000003,42.611699999999999,42.144489999999998,42.298920000000003,41.925280000000001,42.316029999999998,41.591900000000003,192.3186,5970.607,5794.85,52.171050000000001,40.800980000000003,49,49,732900.72239999997,483816.32066838461,686.91972910800007,47,36,33943.10976624499,44,9.519472043028955,10.126612043028954,435354.0632814375,7131.3008983730997,144.31887104727133,-47.999728952728674,0,-175.75699999999961,-1336.4508983730993,0.29173310118094375,0.29173310118094375,0.99716767854494537,0.99716767854494537,6703.7444748584103,-908.89447485840992,0.7451237174124179,0.7451237174124179,44,0.99716767854494537]
["2013-01-16T15:00:00","2013-01-16T15:00:00",48.689430000000002,44.75018,44.48948,44.856250000000003,44.955910000000003,44.463679999999997,44.200960000000002,42.77702,42.394570000000002,42.227379999999997,42.572009999999999,42.400359999999999,42.36683,42.610999999999997,42.88693,42.378059999999998,42.282150000000001,42.717970000000001,42.44547,42.266370000000002,42.625050000000002,42.149720000000002,42.312539999999998,41.936259999999997,42.324330000000003,41.702590000000001,285.13580000000002,6076.8239999999996,5792.6419999999998,52.679490000000001,40.767119999999998,49,49,732900.72239999997,502006.62343806372,996.09910643600028,48,37,36194.687956440008,44,9.6570978593146055,10.264237859314605,441648.10543646,7495.976220543107,206.2936755839599,-78.842124416040122,0,-284.18199999999979,-1703.3342205431072,0.27382286763919539,0.27382286763919539,0.99417955916885592,0.99417955916885592,7052.5816826417376,-1259.9396826417378,0.73187569263109531,0.73187569263109531,44,0.99417955916885592]
["2013-01-16T16:00:00","2013-01-16T16:00:00",48.921250000000001,44.882179999999998,44.572780000000002,44.932560000000002,45.036929999999998,44.552210000000002,44.469270000000002,42.905769999999997,42.436970000000002,42.259410000000003,42.592469999999999,42.410559999999997,42.382829999999998,42.629559999999998,42.90419,42.390169999999998,42.299100000000003,42.739310000000003,42.454410000000003,42.281669999999998,42.630339999999997,42.165239999999997,42.318300000000001,41.948549999999997,42.33276,41.813879999999997,317.9178,6116.6239999999998,5799.6419999999998,52.849670000000003,40.872839999999997,49,49,732900.72239999997,504699.84010709327,1129.7797170930005,49,37,36628.882910960019,44,9.6719039072637365,10.279043907263736,442325.23050249921,7574.2859445597278,233.6209556930192,-84.296844306980802,0,-316.98199999999997,-1774.643944559728,0.25516282598842654,0.25516282598842654,0.99084655406624,0.99084655406624,7126.9046501642124,-1327.2626501642126,0.71791977972276344,0.71791977972276344,44,0.99084655406624]
["2013-01-16T17:00:00","2013-01-16T17:00:00",48.53051,44.875889999999998,44.60586,44.988480000000003,44.978900000000003,44.447319999999998,44.42897,44.058700000000002,42.789740000000002,42.358379999999997,42.628790000000002,42.430630000000001,42.396680000000003,42.650269999999999,42.914909999999999,42.39658,42.302909999999997,42.756129999999999,42.464559999999999,42.28595,42.636589999999998,42.165489999999998,42.327449999999999,41.954929999999997,42.345739999999999,41.852670000000003,231.69,6027.0439999999999,5802.375,52.796880000000002,40.94659,49,49,732900.72239999997,500511.61150207161,773.59437479999951,49,37,35711.109621380005,44,9.6406078380890587,10.247747838089058,440893.96721201972,7408.4767726551527,160.48663897386365,-71.203361026136349,0,-224.66899999999987,-1606.1017726551527,0.23827497303911055,0.23827497303911055,0.98848420250243008,0.98848420250243008,6969.5527613683371,-1167.1777613683371,0.70564712880157399,0.70564712880157399,44,0.98848420250243008]
["2013-01-16T18:00:00","2013-01-16T18:00:00",46.904649999999997,44.975720000000003,44.724739999999997,45.164319999999996,45.119030000000002,44.808810000000001,44.931359999999998,44.849670000000003,43.337879999999998,42.394170000000003,42.685470000000002,42.428159999999998,42.40175,42.655970000000003,42.925609999999999,42.405920000000002,42.306519999999999,42.754899999999999,42.474960000000003,42.285269999999997,42.631239999999998,42.168909999999997,42.326610000000002,41.96725,42.349850000000004,41.871989999999997,134.2473,5883.8370000000004,5793.6329999999998,52.664999999999999,40.797539999999998,51,51,762815.03760000004,513743.58852755191,337.81050840899997,45,34,34913.100122010001,44,9.4308547141605423,10.037994714160542,448905.46230706869,7404.0161109867495,71.639425830995648,-62.607874169004347,0,-90.204000000000633,-1610.3831109867497,0.22134210263610557,0.22134210263610557,0.98753572469524742,0.98753572469524742,6956.1901786535682,-1162.5571786535684,0.69342306242387719,0.69342306242387719,44,1]
["2013-01-16T19:00:00","2013-01-16T19:00:00",45.404620000000001,45.20073,45.041449999999998,45.63335,45.709859999999999,45.469569999999997,45.342080000000003,45.109299999999998,43.607300000000002,42.625500000000002,42.770020000000002,42.467820000000003,42.438119999999998,42.666919999999998,42.933799999999998,42.410449999999997,42.308759999999999,42.755969999999998,42.479340000000001,42.285820000000001,42.634909999999998,42.175849999999997,42.332099999999997,41.97804,42.354860000000002,41.860120000000002,129.59389999999999,5812.7740000000003,5803.7950000000001,52.142339999999997,40.79871,51,51,762815.03760000004,489430.15904087562,229.67278927499996,43,33,32968.978764809995,44,9.3037131758800218,9.9108531758800211,442853.56852330052,7087.2732513470928,49.372285007759949,-80.221614992240035,0,-8.9790000000002692,-1283.4782513470927,0.20784657430693732,0.20784657430693732,0.98744131222761078,0.98744131222761078,6653.1060807249942,-849.3110807249941,0.6844927188530604,0.6844927188530604,44,1]
["2013-01-16T20:00:00","2013-01-16T20:00:00",46.029249999999998,45.603540000000002,45.410960000000003,45.751739999999998,45.904980000000002,45.489400000000003,45.650889999999997,45.60313,44.105919999999998,42.718559999999997,42.780830000000002,42.472059999999999,42.43994,42.671370000000003,42.937989999999999,42.412849999999999,42.316980000000001,42.771070000000002,42.48856,42.275919999999999,42.628749999999997,42.178179999999998,42.334539999999997,41.983139999999999,42.368229999999997,41.89038,154.46190000000001,5675.9949999999999,5805.3069999999998,51.849469999999997,40.791849999999997,51,51,762815.03760000004,474049.28143945517,319.64886202649984,41,32,31381.49791595,44,9.188733078933895,9.7958730789338944,437380.55519204738,6830.4297548690956,69.574088022934802,-84.887811977065212,0,129.3119999999999,-1025.1227548690958,0.19706760460901637,0.19706760460901637,0.98880100317482378,0.98880100317482378,6407.0854456936904,-601.77844569369063,0.67816513359540742,0.67816513359540742,44,1]
["2013-01-16T21:00:00","2013-01-16T21:00:00",46.21022,45.933590000000002,45.750570000000003,46.253990000000002,46.408140000000003,45.734769999999997,45.709049999999998,45.67051,44.102600000000002,42.997230000000002,43.10857,42.692549999999997,42.565190000000001,42.7117,42.954169999999998,42.411929999999998,42.322690000000001,42.777990000000003,42.48807,42.286189999999998,42.630519999999997,42.18045,42.345419999999997,41.987839999999998,42.375140000000002,41.905349999999999,523.80909999999994,5600.299,6115.5519999999997,51.64029,40.889600000000002,51,51,762815.03760000004,463379.81802114571,1127.4650401585002,43,33,30103.539228154998,44,9.2060016876800859,9.8131416876800852,438202.53506848088,6539.9812534123266,244.94130642346681,-278.86779357653313,0,515.2529999999997,-424.42925341232694,0.19260481218760839,0.19260481218760839,0.99421878992024826,0.99421878992024826,6135.3519976071484,-19.799997607148725,0.67795694040760368,0.67795694040760368,44,1]
["2013-01-16T22:00:00","2013-01-16T22:00:00",46.184959999999997,46.182949999999998,45.949809999999999,46.384590000000003,46.538310000000003,45.936920000000001,45.691189999999999,45.513489999999997,43.875149999999998,42.735720000000001,42.890349999999998,42.580350000000003,42.502389999999998,42.68477,42.922719999999998,42.40699,42.319279999999999,42.767299999999999,42.499499999999998,42.308570000000003,42.648969999999998,42.180869999999999,42.337710000000001,41.95729,42.331429999999997,41.587429999999998,1894.4059999999999,5503.8519999999999,7398.2569999999996,51.658360000000002,40.682740000000003,51,51,762815.03760000004,479372.827228899,4354.7942085899986,43,34,30204.09404412,44,9.270277606904493,9.8774176069044923,441262.04686345323,6516.3300010830362,939.51754052037302,-954.88845947962693,0,1894.4049999999997,881.92699891696338,0.20187810589994845,0.20187810589994845,1.0141380961629405,1,6115.787596751361,1282.4694032486386,0.69144186089197346,0.69144186089197346,44,1]
["2013-01-16T23:00:00","2013-01-16T23:00:00",46.231400000000001,46.227670000000003,45.979770000000002,46.37632,46.53022,45.835479999999997,45.492370000000001,44.956099999999999,43.539340000000003,42.681789999999999,42.913400000000003,42.595469999999999,42.496079999999999,42.677869999999999,42.919379999999997,42.406059999999997,42.317489999999999,42.77581,42.504840000000002,42.303440000000002,42.642620000000001,42.180010000000003,42.345640000000003,41.963940000000001,42.276699999999998,40.990969999999997,1958.395,5446.5990000000002,7404.9949999999999,51.197539999999996,40.403489999999998,51,51,762815.03760000004,485829.24488698272,5131.4159549250035,43,34,29395.430967974993,44,9.2427021960079472,9.8498421960079483,439949.46672602044,6360.7872123525285,1110.3713710783268,-848.02362892167321,0,1958.3959999999997,1044.2077876474714,0.21285775106724594,0.21285775106724594,1.0205921593684897,1,5968.7110479574376,1436.2839520425623,0.70654411193765809,0.70654411193765809,44,1]
["2013-01-17","2013-01-17",46.225450000000002,46.182639999999999,45.934359999999998,46.39526,46.432319999999997,45.754069999999999,45.353700000000003,44.461530000000003,43.208120000000001,42.556420000000003,42.88223,42.51961,42.449120000000001,42.656869999999998,42.912089999999999,42.399439999999998,42.308300000000003,42.75741,42.484380000000002,42.292879999999997,42.648589999999999,42.177680000000002,42.323560000000001,41.924250000000001,42.032130000000002,40.556959999999997,1971.5229999999999,5431.1639999999998,7402.6880000000001,50.832099999999997,39.586289999999998,51,51,762815.03760000004,489093.15345978452,5587.7792051350052,42,34,30538.919211419994,44,9.2816951451094241,9.8888351451094216,441805.5177811631,{"$f":"AO390*1000/(500*AQ390)","v":6580.4615932707329},1204.0428214407013,{"$f":"AU390-AC390","v":-767.48017855929857},0,{"$f":"AE390-AD390","v":1971.5240000000003},{"$f":"AE390-AT390","v":822.22640672926718},0.2215033044713326,0.2215033044713326,1.0207301977775702,1,{"$f":"AO390*1000/(500*AR390)","v":6176.4441945466524},{"$f":"AE390-BD390","v":1226.2438054533477},0.71943783101516778,0.71943783101516778,44,1]
["2013-01-17T01:00:00","2013-01-17T01:00:00",46.208030000000001,46.181449999999998,46.050899999999999,46.377270000000003,46.355400000000003,45.690660000000001,44.879420000000003,43.74718,42.983139999999999,42.595619999999997,42.899349999999998,42.471400000000003,42.388109999999998,42.65513,42.919220000000003,42.395420000000001,42.303620000000002,42.757510000000003,42.493789999999997,42.297699999999999,42.643590000000003,42.164520000000003,42.29683,41.912469999999999,41.567920000000001,40.144979999999997,2126.252,5273.1580000000004,7399.4110000000001,50.597079999999998,39.582729999999998,51,51,{"$f":"3.1416*(138/2)^2*AI391","v":762815.03760000004},{"$f":"62.4*AJ391*(AF391-AB391)/1000","v":497516.38900073519},{"$f":"500*AC391*(C391-AB391)/1000","v":6445.7860943000051},39,33,29040.203908650001,44,{"$f":"19.5286-0.30357*AP391+0.0000341*AO391+0.060847*AN391","v":9.1697419532849658},{"$f":"19.5286-0.30357*42+0.0000341*AO391+0.060847*AN391","v":9.7768819532849651},{"$f":"62.4*AJ391*AQ391/1000","v":436476.58409954782},6333.9195490112234,{"$f":"AL391*1000/(500*AQ391)","v":1405.8816763084305},-720.37032369156941,0,2126.2529999999997,1065.4914509887767,0.23270674328785601,{"$f":"IF(AZ391>1,1,IF(AZ391<0,0,AZ391))","v":0.23270674328785601},1.0223571436184149,{"$f":"IF(BB391>1,1,BB391)","v":1},5940.5859756530435,1458.8250243469565,0.73477709712482764,{"$f":"IF(BF391>1,1,IF(BF391<0,0,BF391))","v":0.73477709712482764},44,1]
["2013-01-17T02:00:00","2013-01-17T02:00:00",46.184849999999997,46.20384,45.987110000000001,46.309600000000003,46.256599999999999,45.28989,44.399990000000003,43.459769999999999,42.864100000000001,42.428289999999997,42.791269999999997,42.462679999999999,42.38993,42.630479999999999,42.906269999999999,42.396949999999997,42.312049999999999,42.75703,42.482779999999998,42.253610000000002,42.624339999999997,42.162939999999999,42.284860000000002,41.450099999999999,40.529609999999998,39.933590000000002,2141.835,5258.7839999999997,7400.6189999999997,50.232289999999999,39.702330000000003,51,51,762815.03760000004,490214.60141042172,6694.5837310499946,41,33,27687.39258431999,44,9.1236110871253118,9.7307510871253111,434280.77063113212,6069.3934276507607,1467.5293953502658,-674.30560464973428,0,2141.835,1331.225572349239,{"$f":"IF(AZ391>1,1+AY392*60/$BK$7,IF(AZ391<0,AY392*60/$BK$7,AZ391+AY392*60/$BK$7))","v":0.2467043255649973},0.2467043255649973,{"$f":"IF(BB391>1,1+AX392*60/$BK$7,BB391+AX392*60/$BK$7)","v":1.0225209853681325},1,5690.6999955949932,1709.9190044050065,{"$f":"IF(BF391>1,1+BE392*60/$BK$7,IF(BF391<0,BE392*60/$BK$7,BF391+BE392*60/$BK$7))","v":0.75275656840944882},0.75275656840944882,44,1]
["2013-01-17T03:00:00","2013-01-17T03:00:00",46.185789999999997,46.246699999999997,45.954700000000003,46.253689999999999,46.172820000000002,44.962789999999998,43.467869999999998,43.25864,42.844970000000004,42.441409999999998,42.762,42.401449999999997,42.351100000000002,42.623980000000003,42.907899999999998,42.39781,42.312690000000003,42.753300000000003,42.472270000000002,42.231900000000003,42.599350000000001,42.131599999999999,42.262779999999999,40.980119999999999,40.243819999999999,39.865209999999998,2196.4160000000002,5201.433,7397.8490000000002,50.418959999999998,39.607230000000001,51,51,762815.03760000004,502354.89427163039,6941.3115206399998,40,33,28118.244604544994,44,9.1383031410149851,9.7454431410149844,434980.10737668513,6153.9312431743028,1519.1685838228898,-677.24741617711038,0,2196.4160000000002,1243.9177568256973,0.25978388286078885,0.25978388286078885,1.0230948941437281,1,5770.5420261918407,1627.3069738081595,0.76986738999308779,0.76986738999308779,44,1]
["2013-01-17T04:00:00","2013-01-17T04:00:00",46.192019999999999,46.18683,45.866399999999999,46.127740000000003,45.892829999999996,44.247329999999998,43.31044,43.183459999999997,42.756439999999998,42.416420000000002,42.712519999999998,42.36889,42.348869999999998,42.619590000000002,42.903489999999998,42.39349,42.31485,42.744689999999999,42.455440000000003,42.22627,42.591529999999999,42.101179999999999,41.945329999999998,39.913170000000001,40.176609999999997,39.907600000000002,2118.9639999999999,5284.0389999999998,7403.0029999999997,50.23742,39.642310000000002,5,5,74785.788,48205.480664525174,6658.2298704399973,38,32,27992.487224644996,44,9.0731678143603958,9.6803078143603951,42341.145890358428,6170.3889528727523,1467.6747981894046,-651.28920181059539,0,2118.9639999999999,1232.6140471272474,0.27274458381109884,0.27274458381109884,1.0222805011775413,1,5783.3878346552438,1619.615165344756,0.78689733368190351,0.78689733368190351,44,1]
["2013-01-17T05:00:00","2013-01-17T05:00:00",46.174529999999997,46.176380000000002,45.826120000000003,45.963839999999998,45.520789999999998,43.556579999999997,43.029240000000001,43.053330000000003,42.718850000000003,42.306629999999998,42.653739999999999,42.336620000000003,42.324939999999998,42.614440000000002,42.90014,42.389670000000002,42.299259999999997,42.710799999999999,42.451009999999997,42.20984,42.571289999999998,42.071370000000002,41.674840000000003,39.81391,40.211840000000002,39.939509999999999,2063.6759999999999,5334.4520000000002,7398.1270000000004,50.424660000000003,39.671010000000003,51,51,762815.03760000004,499089.55770907854,6433.5305667599987,39,33,28682.414874900001,44,9.1575413472340905,9.7646813472340899,435895.83941990905,6264.217389215094,1405.0781367649863,-658.59786323501362,0,2063.6750000000002,1133.9096107849064,0.28466742649191767,0.28466742649191767,1.0216991479173609,1,5874.7262414301904,1523.40075856981,0.80291560128587514,0.80291560128587514,44,1]
["2013-01-17T06:00:00","2013-01-17T06:00:00",46.176340000000003,46.174289999999999,45.79898,45.89143,44.86101,43.387230000000002,43.050559999999997,43.04278,42.707569999999997,42.309350000000002,42.688650000000003,42.341650000000001,42.346229999999998,42.61504,42.896479999999997,42.39096,42.296840000000003,42.71217,42.452190000000002,42.202820000000003,42.531239999999997,42.00235,40.818040000000003,39.860199999999999,40.239820000000002,40.002859999999998,733.37099999999998,5352.3519999999999,6085.7219999999998,50.329659999999997,39.714419999999997,51,51,762815.03760000004,491552.15180995117,2263.7256005400018,36,31,28408.250522240003,44,9.0264983428083845,9.6336383428083838,429658.23718058062,6294.4121725504983,501.57337088386288,-231.7976291161371,0,733.36999999999989,-208.69017255049857,0.28247308924255776,0.28247308924255776,1.0077112452823991,1,5897.7199498976561,188.00205010234367,0.80489240688459485,0.80489240688459485,44,1]
["2013-01-17T07:00:00","2013-01-17T07:00:00",46.170540000000003,46.156939999999999,45.742739999999998,45.898960000000002,45.098559999999999,43.16901,42.977110000000003,42.967910000000003,42.63926,42.306420000000003,42.70431,42.344940000000001,42.321660000000001,42.603279999999998,42.892499999999998,42.394120000000001,42.295769999999997,42.720390000000002,42.445799999999998,42.182789999999997,42.531010000000002,41.975119999999997,40.811369999999997,39.820419999999999,40.229109999999999,39.861449999999998,452.67430000000002,5348.8670000000002,5801.5410000000002,50.633229999999998,39.721119999999999,51,51,762815.03760000004,512733.04778086109,1427.981449693501,36,32,29183.712539684995,44,9.1137885976032589,9.7209285976032582,433813.22348577291,6404.2987671141982,313.36725323407899,-139.30704676592103,0,452.67399999999998,-602.75776711419803,0.27613520660747753,0.27613520660747753,1.0047597805295618,1,6004.3055036697579,-202.76450366975769,0.80276037691014623,0.80276037691014623,44,1]
["2013-01-17T08:00:00","2013-01-17T08:00:00",46.179189999999998,46.16339,45.710659999999997,45.88897,45.106659999999998,43.200839999999999,42.992829999999998,42.989490000000004,42.688780000000001,42.354489999999998,42.731960000000001,42.422649999999997,42.383090000000003,42.648180000000004,42.89743,42.400880000000001,42.324109999999997,42.731949999999998,42.451329999999999,42.186329999999998,42.545349999999999,41.986899999999999,40.883000000000003,39.833779999999997,40.227170000000001,39.946379999999998,414.34829999999999,5388.3149999999996,5802.6629999999996,50.532499999999999,39.961280000000002,51,51,762815.03760000004,503895.69521229819,1291.2771138615001,37,34,28480.53164714999,44,9.2115041291678157,9.818644129167815,438464.44940336706,6183.6875384917139,280.36183792671358,-133.98646207328642,0,414.34799999999996,-381.02453849171434,0.27212880646168136,0.27212880646168136,1.0043567899699626,1,5801.3166120450642,1.3463879549353805,0.80277453392197629,0.80277453392197629,44,1]
["2013-01-17T09:00:00","2013-01-17T09:00:00",46.239780000000003,46.170140000000004,45.668840000000003,45.821190000000001,45.128529999999998,43.277459999999998,42.980730000000001,43.013860000000001,42.712940000000003,42.374650000000003,42.77675,42.43,42.375320000000002,42.65034,42.905929999999998,42.413760000000003,42.318330000000003,42.731850000000001,42.45758,42.228560000000002,42.562519999999999,42.004939999999998,40.879860000000001,39.824599999999997,40.210560000000001,40.035980000000002,175.67670000000001,5688.2640000000001,5804.5630000000001,50.881979999999999,40.67427,51,51,762815.03760000004,516265.89442331885,544.93155573000013,42,37,29032.074657719997,44,9.4128527458282534,10.019992745828251,448048.57476489194,6168.602748106714,115.78457040486734,-59.892129595132673,0,116.29899999999998,-364.03974810671389,0.26830099813819708,0.26830099813819708,1.0012228617411372,1,5794.8294762603064,9.7335237396937373,0.80287688006242219,0.80287688006242219,44,1]
["2013-01-17T10:00:00","2013-01-17T10:00:00",46.216320000000003,45.90701,45.132750000000001,45.290680000000002,45.221670000000003,43.634399999999999,43.059489999999997,43.162089999999999,42.827680000000001,42.455179999999999,42.70299,42.407780000000002,42.378390000000003,42.681269999999998,42.943899999999999,42.420059999999999,42.309080000000002,42.71969,42.458770000000001,42.292859999999997,42.607729999999997,42.083599999999997,41.239109999999997,39.832929999999998,40.221249999999998,39.911009999999997,189.62200000000001,5963.1210000000001,5798.7240000000002,51.87547,40.688360000000003,51,51,762815.03760000004,569504.20829725463,597.8127464100005,48,41,33355.045285154993,44,9.8036540442237872,10.410794044223785,466650.58304978634,6804.6149190275519,121.95712817145473,-67.664871828545287,0,-164.39699999999993,-1005.8909190275517,0.25772424751578371,0.25772424751578371,0.99827139698829981,0.99827139698829981,6407.7812208111736,-609.05722081117347,0.79647275987657973,0.79647275987657973,44,1]
["2013-01-17T11:00:00","2013-01-17T11:00:00",46.094580000000001,45.574809999999999,45.586559999999999,45.589199999999998,45.416249999999998,43.748840000000001,42.98171,43.159190000000002,42.853569999999998,42.531950000000002,42.684710000000003,42.459560000000003,42.398560000000003,42.665190000000003,42.969520000000003,42.439500000000002,42.319040000000001,42.726210000000002,42.476019999999998,42.347540000000002,42.640630000000002,42.122,41.663699999999999,39.913530000000002,40.232619999999997,39.83379,396.06310000000002,6189.8829999999998,5799.8990000000003,52.076079999999997,40.589700000000001,51,51,762815.03760000004,582728.82137559028,1239.8339479245001,51,42,35549.67414676999,44,9.9393378884048573,10.546477888404857,473109.08767590969,7153.3284301043677,249.48018909204791,-146.58291090795211,0,-389.98399999999947,-1353.4294301043674,0.24349319592115562,0.24349319592115562,0.99417078981837037,0.99417078981837037,6741.5253742397672,-941.62637423976685,0.78657173865108787,0.78657173865108787,44,1]
["2013-01-17T12:00:00","2013-01-17T12:00:00",46.00074,45.818550000000002,45.500070000000001,45.749760000000002,45.649810000000002,44.291649999999997,42.887270000000001,43.114109999999997,42.787350000000004,42.548679999999997,42.737639999999999,42.480879999999999,42.387270000000001,42.648609999999998,42.962760000000003,42.417940000000002,42.296219999999998,42.727510000000002,42.487160000000003,42.360639999999997,42.651350000000001,42.133360000000003,41.992420000000003,39.988210000000002,40.227130000000002,39.835970000000003,573.84659999999997,6376.0410000000002,5802.1940000000004,52.820929999999997,40.67221,5,5,74785.788,60596.045062705125,1768.8161521409993,54,44,38730.36840875999,44,10.169493562738717,10.776633562738716,47457.295994181368,7616.9709277695092,347.86710689743421,-225.97949310256575,0,-573.84699999999975,-1814.7769277695088,0.22441116362794841,0.22441116362794841,0.98813689836989438,0.98813689836989438,7187.8417658505332,-1385.6477658505328,0.7720019174183107,0.7720019174183107,44,0.99396610855152401]
["2013-01-17T13:00:00","2013-01-17T13:00:00",46.588920000000002,46.131990000000002,45.751019999999997,46.406039999999997,46.179029999999997,44.633319999999998,43.239840000000001,43.040410000000001,42.769289999999998,42.5413,42.755119999999998,42.538969999999999,42.370170000000002,42.628570000000003,42.947560000000003,42.403840000000002,42.300690000000003,42.727519999999998,42.488639999999997,42.362520000000004,42.66,42.155630000000002,42.165959999999998,40.702959999999997,40.258310000000002,39.833759999999998,807.93079999999998,6605.9430000000002,5798.0129999999999,53.010170000000002,40.662779999999998,51,51,762815.03760000004,627192.61422998039,2728.850911464001,57,45,40783.077269385016,44,10.300337934886031,10.90747793488603,490292.56655139034,7918.7843209022376,529.85657921410609,-278.07422078589389,0,-807.93000000000029,-2120.7713209022377,0.20211165881679621,0.20211165881679621,0.97964166894817173,0.97964166894817173,7478.003166790023,-1679.9901667900231,0.75433714213688874,0.75433714213688874,44,1]
["2013-01-17T14:00:00","2013-01-17T14:00:00",47.175400000000003,46.801929999999999,46.284910000000004,46.619549999999997,46.353279999999998,45.344740000000002,43.687240000000003,42.918999999999997,42.762239999999998,42.554310000000001,42.734999999999999,42.568019999999997,42.390189999999997,42.613720000000001,42.927370000000003,42.395899999999997,42.137650000000001,42.647669999999998,42.500500000000002,42.396050000000002,42.678420000000003,42.201990000000002,42.254710000000003,41.878070000000001,40.363790000000002,39.854770000000002,970.61670000000004,6780.9639999999999,5810.348,53.473460000000003,40.611220000000003,51,51,762815.03760000004,648244.99112335523,3552.7628662605011,59,46,43609.193199679998,44,10.457555488109088,11.064695488109088,497776.06837083964,8340.2269773784992,679.4633545669866,-291.15334543301344,0,-970.61599999999999,-2529.8789773784993,0.17551046524554212,0.17551046524554212,0.96943582735249545,0.96943582735249545,7882.5835282219114,-2072.2355282219114,0.73254798190259907,0.73254798190259907,44,1]
["2013-01-17T15:00:00","2013-01-17T15:00:00",47.573819999999998,46.966670000000001,46.663460000000001,47.050400000000003,47.088320000000003,46.54081,44.419750000000001,43.628439999999998,42.923479999999998,42.686070000000001,42.8613,42.676470000000002,42.490850000000002,42.61027,42.922620000000002,42.389870000000002,42.20149,42.70946,42.542400000000001,42.467410000000001,42.748959999999997,42.222810000000003,42.285089999999997,41.736559999999997,40.803759999999997,39.881869999999999,1116.318,6916.2749999999996,5799.9579999999996,53.567839999999997,40.633099999999999,39,39,583329.14639999997,498165.73233997478,4293.3311200499993,60,46,44730.109446749993,44,10.495778732134175,11.102918732134174,382043.60367383197,8523.4474903330447,818.1062557855596,-298.21174421444039,0,-1116.317,-2723.4894903330451,0.14687349416137693,0.14687349416137693,0.95769796760923909,0.95769796760923909,8057.3605059886968,-2257.4025059886972,0.70881182631294959,0.70881182631294959,44,0.98826214025674364]
["2013-01-17T16:00:00","2013-01-17T16:00:00",48.851660000000003,47.012039999999999,46.668340000000001,47.04,47.102130000000002,46.763809999999999,45.831200000000003,43.893650000000001,43.142040000000001,42.868429999999996,43.028219999999997,42.98283,42.685720000000003,42.778579999999998,43.005180000000003,42.439799999999998,42.285690000000002,42.762619999999998,42.579369999999997,42.500320000000002,42.771859999999997,42.228499999999997,42.284100000000002,41.851109999999998,42.29,39.956789999999998,1075.4179999999999,6875.6139999999996,5800.1959999999999,53.773859999999999,40.631259999999997,1,1,14957.1576,12895.839438158479,4782.8516528300024,60,46,45181.72227820001,44,10.511178729686621,11.118318729686621,9810.3630656734931,8596.8897380830749,910.05048545542093,-165.36751454457897,0,-1075.4179999999997,-2796.693738083075,0.11746679441348948,0.11746679441348948,0.94639015302845853,0.94639015302845853,8127.4378575893725,-2327.2418575893726,0.68434132329900332,0.68434132329900332,44,0.97695432567596308]
["2013-01-17T17:00:00","2013-01-17T17:00:00",51.37444,47.046930000000003,46.716749999999998,47.062750000000001,47.136589999999998,46.771639999999998,46.67801,44.829680000000003,43.591230000000003,43.044849999999997,43.161929999999998,42.987389999999998,42.703800000000001,42.936970000000002,43.10642,42.50788,42.355069999999998,42.814540000000001,42.60042,42.459829999999997,42.738460000000003,42.217309999999998,42.310870000000001,41.930720000000001,42.135739999999998,40.146680000000003,954.72559999999999,6755.3180000000002,5800.5929999999998,53.737270000000002,40.728340000000003,49,49,732900.72239999997,621538.52147975424,5359.7149513279983,58,45,43939.72949487,44,10.407979775775068,11.015119775775068,475988.19193474454,8443.4694227867803,1029.9241671862046,75.198567186204627,1,-954.72500000000036,-2642.8764227867805,8.9677454316160199E-2,8.9677454316160199E-2,0.93635140225839908,0.93635140225839908,7978.0756613294707,-2177.4826613294708,0.66144550959012138,0.66144550959012138,44,0.96691557490590363]
["2013-01-17T18:00:00","2013-01-17T18:00:00",51.938429999999997,46.904069999999997,46.604810000000001,46.967959999999998,47.070219999999999,46.642890000000001,46.5745,45.383670000000002,44.096960000000003,43.453110000000002,43.357309999999998,43.246479999999998,43.028460000000003,43.129959999999997,43.357140000000001,42.681339999999999,42.434840000000001,42.878300000000003,42.656219999999998,42.480179999999997,42.696060000000003,42.21237,42.34328,41.959330000000001,42.282299999999999,41.131250000000001,759.3057,6550.7920000000004,5791.4859999999999,53.579940000000001,40.746470000000002,49,49,732900.72239999997,569316.00298146007,4102.9766874629977,53,43,42034.69630412,44,10.221324143970492,10.828464143970493,467451.86897763336,8224.9023144258772,802.82684115508141,43.521141155081409,1,-759.30600000000049,-2433.4163144258773,6.40905471959759E-2,6.40905471959759E-2,0.92836744489663447,0.92836744489663447,7763.7411446803872,-1972.2551446803873,0.64070762396607894,0.64070762396607894,44,0.95893161754413903]
["2013-01-17T19:00:00","2013-01-17T19:00:00",52.472000000000001,47.463929999999998,46.599760000000003,46.931780000000003,47.01932,46.549160000000001,46.507539999999999,46.443829999999998,44.011020000000002,43.542169999999999,43.498860000000001,43.137099999999997,42.912840000000003,43.118429999999996,43.348059999999997,42.737290000000002,42.5473,42.960560000000001,42.666609999999999,42.447769999999998,42.70478,42.232799999999997,42.35286,41.967460000000003,42.349339999999998,41.894240000000003,631.1087,6431.4979999999996,5800.3890000000001,53.154330000000002,40.826990000000002,35,35,523500.516,367826.96653288178,3337.8581812559992,50,41,39641.631277659995,44,10.018026626568208,10.625166626568205,327253.18755855621,7914.0598753308968,666.3703952241184,35.261695224118398,1,-631.10899999999947,-2113.6708753308967,4.1865702211943613E-2,4.1865702211943613E-2,0.92173145447034266,0.92173145447034266,7461.8371025892784,-1661.4481025892783,0.62323781494329034,0.62323781494329034,44,0.95229562711784721]
["2013-01-17T20:00:00","2013-01-17T20:00:00",53.084670000000003,51.296750000000003,46.601030000000002,46.948929999999997,47.070999999999998,46.63091,46.600450000000002,46.758279999999999,43.9833,43.493229999999997,43.690309999999997,43.227130000000002,42.975200000000001,43.226430000000001,43.365549999999999,42.637219999999999,42.525669999999998,43.010379999999998,42.761450000000004,42.452080000000002,42.722540000000002,42.255679999999998,42.366019999999999,41.983600000000003,42.376069999999999,41.746969999999997,466.64819999999997,6267.9120000000003,5801.2640000000001,53.096310000000003,40.88335,35,35,523500.516,370742.4456065892,2645.3586485700012,48,40,38274.879269760007,44,9.9105733830988179,10.517713383098817,323743.07346626522,7724.0494147458285,533.84573148538777,67.197531485387799,1,-466.64800000000014,-1922.7854147458283,2.1647981336362979E-2,2.1647981336362979E-2,0.91682474000351011,0.91682474000351011,7278.1749940561967,-1476.9109940561966,0.60770837832134073,0.60770837832134073,44,0.94738891265101466]
["2013-01-17T21:00:00","2013-01-17T21:00:00",53.139049999999997,51.846969999999999,46.585700000000003,46.949770000000001,47.063499999999998,46.62527,46.626399999999997,46.855370000000001,44.357860000000002,43.52796,43.550759999999997,43.272750000000002,43.17015,43.37762,43.601419999999997,42.956479999999999,42.81756,43.191040000000001,42.849690000000002,42.672449999999998,42.895600000000002,42.312249999999999,42.406480000000002,42.00909,42.397790000000001,41.84639,402.63889999999998,6204.1450000000004,5805.6710000000003,52.715269999999997,40.89141,35,35,523500.516,355047.53159254568,2273.4321002369993,47,40,36678.470949849987,44,9.8561358593898856,10.463275859389885,321964.7937889786,7442.7689457844899,461.32320671515771,58.684306715157732,1,-398.47400000000016,-1637.0979457844896,4.4342095550576263E-3,4.4342095550576263E-3,0.91263486210741573,0.91263486210741573,7010.8962896040302,-1205.22528960403,0.59503566491789206,0.59503566491789206,43,0.94319903475492028]
["2013-01-17T22:00:00","2013-01-17T22:00:00",53.121960000000001,51.9968,46.60624,46.96123,47.077620000000003,46.641500000000001,46.64949,46.872250000000001,46.022390000000001,42.809820000000002,43.087479999999999,42.853059999999999,42.824890000000003,43.078859999999999,43.398319999999998,42.838230000000003,42.711840000000002,43.211300000000001,42.810180000000003,42.551760000000002,42.814349999999997,42.329300000000003,42.417189999999998,42.033369999999998,42.400939999999999,41.899009999999997,207.25550000000001,5997.4669999999996,5802.9979999999996,52.37762,40.868630000000003,33,33,493586.20079999999,322738.87149284914,1163.0090568625005,46,39,34512.393864164995,44,9.721425630768028,10.328565630768027,299417.76031131332,7100.2742138836666,239.26718179720694,32.011681797206933,1,-194.46900000000005,-1297.276213883667,-9.2064017111231494E-3,0,0.91059005776741975,0.91059005776741975,6682.9015950395169,-879.90359503951731,0.58578364691031815,0.58578364691031815,43,0.9411542304149243]
["2013-01-17T23:00:00","2013-01-17T23:00:00",53.047130000000003,52.273989999999998,46.685569999999998,46.959699999999998,47.07882,46.63326,46.63982,46.88261,46.281849999999999,42.677900000000001,43.025919999999999,42.836829999999999,42.811050000000002,43.089489999999998,43.404850000000003,42.888370000000002,42.806980000000003,43.244169999999997,43.042259999999999,42.950920000000004,43.13111,42.454999999999998,42.4968,42.07058,42.417319999999997,41.94511,149.72149999999999,5922.348,5791.6819999999998,51.945399999999999,40.868760000000002,33,33,493586.20079999999,308006.72123508964,831.10554371500029,42,37,32799.858375359996,44,9.541334170599777,10.148474170599776,293870.98315096472,6875.3190673119807,174.21159952157009,24.490099521570102,1,-130.66600000000017,-1083.6370673119809,-1.1394236501550801E-2,0,0.90921612976917876,0.90921612976917876,6463.9980008781004,-672.31600087810057,0.57871437275122695,0.57871437275122695,43,0.93978030241668331]
["2013-01-18","2013-01-18",52.767440000000001,51.834629999999997,48.440559999999998,47.034149999999997,47.111660000000001,46.658439999999999,46.674239999999998,46.912599999999998,46.668140000000001,42.57009,42.984059999999999,42.798520000000003,42.817529999999998,43.10342,43.412239999999997,42.901850000000003,42.81438,43.26746,43.03013,42.891820000000003,43.184269999999998,42.599029999999999,42.614550000000001,42.170529999999999,42.480829999999997,41.892749999999999,106.46469999999999,5790.076,5796.7160000000003,51.579689999999999,40.818600000000004,33,33,493586.20079999999,298355.61050739925,578.88530422150006,40,36,31153.764471419985,44,9.4243553684754211,10.031495368475422,290268.06190604769,6611.3305904464714,122.84878521408015,16.384085214080159,1,6.6400000000003274,-814.61459044647108,-8.5655166117428131E-3,0,0.90928594809918295,0.90928594809918295,6211.1905208714079,-414.47452087140755,0.57435625243850041,0.57435625243850041,43,0.9398501207466875]
["2013-01-18T01:00:00","2013-01-18T01:00:00",52.356169999999999,52.178890000000003,48.822620000000001,47.111980000000003,47.236930000000001,46.735950000000003,46.764609999999998,46.977089999999997,46.61692,42.489730000000002,42.879689999999997,42.727910000000001,42.7804,43.123420000000003,43.437820000000002,42.935360000000003,42.81109,43.228580000000001,42.960299999999997,42.76446,43.084339999999997,42.574069999999999,42.628619999999998,42.180770000000003,42.4803,41.866340000000001,118.111,5753.9579999999996,5795.1189999999997,51.308759999999999,40.81944,33,33,493586.20079999999,290824.44856345514,619.48215556499986,41,37,30177.553364279996,44,9.451913569721949,10.059053569721948,291116.84841214697,6385.4907562739691,131.08079141760996,12.969791417609954,1,41.161000000000058,-590.37175627396937,-6.2076461000986115E-3,0,0.90971874814154741,0.90971874814154741,6000.0780699916613,-204.95906999166164,0.57220114701891944,0.57220114701891944,43,0.94028292078905196]
["2013-01-18T02:00:00","2013-01-18T02:00:00",52.253720000000001,51.999290000000002,49.637079999999997,47.14958,47.219029999999997,46.743780000000001,46.784190000000002,46.982880000000002,46.753010000000003,42.516640000000002,42.946330000000003,42.748489999999997,42.78331,43.05453,43.399749999999997,42.908230000000003,42.816800000000001,43.24344,42.958680000000001,42.712690000000002,43.047699999999999,42.583599999999997,42.654290000000003,42.191070000000003,42.579410000000003,41.935020000000002,135.73570000000001,5707.299,5803.6689999999999,51.109760000000001,40.768880000000003,33,33,493586.20079999999,282579.96373949421,700.30798379500004,41,37,29509.247041559993,44,9.4291243241171969,10.036264324117196,290414.94468554098,6259.170210765632,148.54146784421923,12.805767844219218,1,96.369999999999891,-455.50121076563209,-4.7895081100175346E-3,0,0.91073206025939346,0.91073206025939346,5880.5240851716353,-76.855085171635437,0.5713930304979844,0.5713930304979844,43,0.94129623290689801]
["2013-01-18T03:00:00","2013-01-18T03:00:00",52.274619999999999,52.174770000000002,50.39902,47.178519999999999,47.25271,46.773209999999999,46.817819999999998,47.01773,46.822539999999996,42.484340000000003,42.943689999999997,42.754730000000002,42.774700000000003,43.033099999999997,43.36497,42.825150000000001,42.716880000000003,43.118949999999998,42.827970000000001,42.616779999999999,42.944429999999997,42.47166,42.610700000000001,42.23751,42.55753,41.99248,168.80279999999999,5659.3329999999996,5796.3670000000002,50.992759999999997,40.77599,33,33,493586.20079999999,277206.63430738024,867.82701099599979,40,37,28910.051807204993,44,9.4086917666256902,10.015831766625691,289785.6264318297,6145.3924784217306,184.47347038710251,15.670670387102518,1,137.03400000000056,-349.02547842173044,-3.6699361494425169E-3,0,0.91217294655966252,0.91217294655966252,5772.8708869767115,23.496113023288672,0.57164008763245344,0.57164008763245344,43,0.94273711920716707]
["2013-01-18T04:00:00","2013-01-18T04:00:00",52.277419999999999,52.076309999999999,51.027230000000003,47.107810000000001,47.21564,46.718380000000003,46.753480000000003,46.965919999999997,46.748019999999997,42.456890000000001,42.900179999999999,42.674399999999999,42.720329999999997,43.008380000000002,43.300469999999997,42.765630000000002,42.62303,43.046570000000003,42.777859999999997,42.585419999999999,42.922699999999999,42.51014,42.6661,42.252229999999997,42.56747,41.944839999999999,144.3349,5686.808,5801.9120000000003,51.023009999999999,40.821240000000003,33,33,493586.20079999999,279605.62908823189,745.675950521,37,34,29007.753625079989,44,9.2294823986152288,9.8366223986152281,284266.0175149368,6285.8895812905494,161.58564875379781,17.250748753797808,1,115.10400000000027,-483.9775812905491,-5.0889316995700326E-3,0,0.9133832431043607,0.9133832431043607,5897.9093533495025,-95.997353349502191,0.57063069382286324,0.57063069382286324,43,0.94394741575186525]
["2013-01-18T05:00:00","2013-01-18T05:00:00",52.183039999999998,51.991549999999997,51.243989999999997,46.982520000000001,47.09187,46.614890000000003,46.679549999999999,46.907519999999998,45.75027,42.60915,43.061520000000002,42.864049999999999,42.881929999999997,43.140909999999998,43.45046,42.929340000000003,42.80659,43.225110000000001,42.950009999999999,42.763390000000001,43.084800000000001,42.606619999999999,42.693019999999997,42.193359999999998,42.542920000000002,42.024610000000003,113.9224,5773.7809999999999,5797.18,51.11007,40.816749999999999,33,33,493586.20079999999,279830.15947663086,578.63636291599971,38,35,29715.687721460003,44,9.3144699513017883,9.9216099513017859,286883.61534947774,6380.5429352009342,124.24461422737848,10.322214227378481,1,23.399000000000342,-583.36293520093386,-6.1339496870538666E-3,0,0.91362927911396408,0.91362927911396408,5990.0939196992103,-192.91391969921006,0.56860224085479849,0.56860224085479849,43,0.94419345176146863]
["2013-01-18T06:00:00","2013-01-18T06:00:00",52.058799999999998,51.962820000000001,51.391039999999997,46.990430000000003,47.105550000000001,46.643610000000002,46.709679999999999,46.900860000000002,46.524929999999998,42.743819999999999,43.16863,42.952190000000002,42.937350000000002,43.167009999999998,43.492690000000003,43.029209999999999,42.876240000000003,43.35295,43.143590000000003,42.981079999999999,43.316510000000001,42.910969999999999,43.090490000000003,42.707540000000002,43.01314,41.995379999999997,701.74929999999995,5717.7870000000003,6382.6880000000001,51.458280000000002,40.901760000000003,33,33,493586.20079999999,291455.22803594009,3530.9989703030001,39,35,30179.966410619996,44,9.3303018546021441,9.9374418546021417,287371.23447116866,6469.2368759181809,756.88847484850555,55.139174848505604,1,664.90099999999984,-86.548875918180784,-9.1004487655755868E-4,0,0.92062058595704799,0.92062058595704799,6073.9910436091377,308.6969563908624,0.57184813030849857,0.57184813030849857,43,0.95118475860455254]
["2013-01-18T07:00:00","2013-01-18T07:00:00",51.900689999999997,50.939709999999998,47.42315,47.026719999999997,47.157800000000002,46.675899999999999,46.716769999999997,45.663600000000002,43.209269999999997,42.89228,43.37809,43.18056,43.207270000000001,43.450130000000001,43.751930000000002,43.242989999999999,43.145650000000003,43.564279999999997,43.306849999999997,43.098219999999998,43.451689999999999,43.022170000000003,43.168059999999997,42.57002,42.028060000000004,41.293610000000001,5855.0119999999997,5743.6809999999996,11598.69,51.380719999999997,40.640189999999997,35,35,523500.516,329509.89489280246,31052.290342479988,31,29,30845.089045465,44,8.9879005364503577,9.595040536450357,293602.6434799186,6863.6916753524347,6909.7983931948684,1054.7863931948687,1,5855.0090000000009,4734.9983246475658,4.9787601746875652E-2,4.9787601746875652E-2,0.9821848857370421,0.9821848857370421,6429.3817057444148,5169.3082942555857,0.62620241831775025,0.62620241831775025,44,1]
["2013-01-18T08:00:00","2013-01-18T08:00:00",49.04421,46.938130000000001,46.5929,46.976480000000002,47.106079999999999,46.594090000000001,44.776919999999997,43.404710000000001,43.215420000000002,42.993980000000001,43.470500000000001,43.2438,43.253869999999999,43.485460000000003,43.798969999999997,43.2836,43.178339999999999,43.61974,43.35812,43.149000000000001,43.491280000000003,42.933709999999998,42.566600000000001,40.382689999999997,40.517249999999997,40.043170000000003,5748.7879999999996,5859.8209999999999,11608.61,51.352559999999997,40.577240000000003,5,5,74785.788,52776.774520037528,25872.535369759989,32,30,31570.723208859981,44,9.0734916614221266,9.6806316614221259,42342.657165799093,6958.8917666810894,5702.8840352083098,-45.903964791689759,0,5748.7890000000007,4649.7182333189112,9.8678499644479237E-2,9.8678499644479237E-2,1.0426323025331448,1,6522.4510782020825,5086.1589217979181,0.6796824065791276,0.6796824065791276,44,1]
["2013-01-18T09:00:00","2013-01-18T09:00:00",46.917400000000001,46.827910000000003,46.509709999999998,46.828420000000001,45.992699999999999,43.711379999999998,43.294029999999999,43.492429999999999,43.300429999999999,43.065959999999997,43.525089999999999,43.312800000000003,43.335850000000001,43.593510000000002,43.909030000000001,43.386690000000002,43.316890000000001,43.756329999999998,43.506039999999999,43.330300000000001,43.557079999999999,41.482669999999999,40.26276,39.746769999999998,40.151620000000001,39.773629999999997,5589.3869999999997,6015.84,11605.23,51.57499,40.446759999999998,9,9,134614.4184,99130.712474291111,19964.647584495007,41,38,33472.825581600009,44,9.6251293523325607,10.23226935233256,80850.506242834614,6955.2988549682577,4148.4424476138101,-1440.9445523861896,0,5589.3899999999994,4649.9311450317418,0.14757163626802078,0.14757163626802078,1.0587713667984628,1,6542.6005569271902,5062.6294430728094,0.73291498687206291,0.73291498687206291,44,1]
["2013-01-18T10:00:00","2013-01-18T10:00:00",47.000689999999999,46.86497,46.293109999999999,44.727089999999997,43.773600000000002,43.283410000000003,43.27561,43.494869999999999,43.31138,43.117570000000001,43.534680000000002,43.384390000000003,43.381659999999997,43.659669999999998,43.971440000000001,43.450710000000001,43.351880000000001,43.796579999999999,43.542230000000004,42.720199999999998,41.138249999999999,39.907820000000001,40.045439999999999,39.663919999999997,40.080109999999998,39.694490000000002,5375.4080000000004,6226.0519999999997,11601.46,52.130980000000001,40.461309999999997,51,51,762815.03760000004,591972.67502643028,19636.902964799992,48,41,36327.986121420014,44,9.9050313267404242,10.512171326740422,471476.10706164851,7335.2592077818153,3965.0360139269064,-1410.3719860730939,0,5375.4079999999994,4266.2007922181838,0.19242992162569805,0.19242992162569805,1.0565213869956098,1,6911.6046518401772,4689.8553481598219,0.78222791885541598,0.78222791885541598,44,1]
["2013-01-18T11:00:00","2013-01-18T11:00:00",46.98386,46.747300000000003,44.686889999999998,43.717179999999999,43.746830000000003,43.346220000000002,43.331949999999999,43.577579999999998,43.404240000000001,43.226050000000001,43.585630000000002,43.4895,43.46904,43.72907,44.038290000000003,43.512729999999998,43.425980000000003,43.84845,43.467289999999998,41.022930000000002,40.440559999999998,39.895470000000003,40.013249999999999,39.605980000000002,40.018039999999999,39.65802,2916.0830000000001,8193.3130000000001,8320.4750000000004,58.272590000000001,41.341839999999998,13,13,194443.04880000002,225855.16155702341,10681.378742359999,53,44,69359.467037375012,44,11.21394582597449,11.821085825974487,136061.56608598409,12370.216177916607,1905.0170043837875,-1011.0659956162126,0,127.16200000000026,-4049.7411779166068,0.14984766771137537,0.14984766771137537,1.0013370841084315,1,11734.872423474224,-3414.3974234742236,0.74632618300038889,0.74632618300038889,44,1]
["2013-01-18T12:00:00","2013-01-18T12:00:00",46.895200000000003,46.192320000000002,43.645530000000001,43.690170000000002,43.751190000000001,43.360489999999999,43.338290000000001,43.597329999999999,43.429839999999999,43.252279999999999,43.565939999999998,43.518360000000001,43.483690000000003,43.729959999999998,44.044530000000002,43.53913,43.429519999999997,43.730820000000001,42.773850000000003,40.511200000000002,40.53651,39.986609999999999,40.070659999999997,39.633830000000003,40.03678,39.67136,3433.0349999999999,8158.473,11591.51,57.331690000000002,40.32009,13,13,194443.04880000002,214277.1326600801,12399.847777200004,57,46,69394.339643400002,44,11.33682898183994,11.943968981839941,137552.53767547704,12242.283932228371,2187.5337093049347,-1245.5012906950651,0,3433.0370000000003,-650.77393222837054,0.14300490428390447,0.14300490428390447,1.0360977274371075,1,11619.979882551565,-28.469882551564297,0.74602682763063533,0.74602682763063533,44,1]
["2013-01-18T13:00:00","2013-01-18T13:00:00",46.512050000000002,44.101010000000002,43.416730000000001,43.739640000000001,43.83005,43.439190000000004,43.371519999999997,43.639789999999998,43.490029999999997,43.341299999999997,43.602719999999998,43.57403,43.533000000000001,43.751300000000001,44.067450000000001,43.508020000000002,43.355490000000003,42.82573,40.448410000000003,40.122219999999999,40.425510000000003,39.916400000000003,40.030079999999998,39.630989999999997,40.087380000000003,39.698680000000003,3834.9650000000001,7771.9470000000001,11606.91,55.469200000000001,40.311920000000001,15,15,224357.364,220785.69527721903,13064.517741025,59,46,58900.788412080001,44,10.978998884851929,11.586138884851929,153704.88114785348,10729.719354165756,2379.9105689045155,-1455.0544310954847,0,3834.9629999999997,877.1906458342437,0.15222839614947564,0.15222839614947564,1.0403239024529571,1,10167.457683264729,1439.4523167352709,0.76116239342506831,0.76116239342506831,44,1]
["2013-01-18T14:00:00","2013-01-18T14:00:00",43.957520000000002,43.673659999999998,43.3735,43.716549999999998,43.818820000000002,43.420780000000001,43.346530000000001,43.613109999999999,43.469540000000002,43.317349999999998,43.560310000000001,43.531559999999999,43.495710000000003,43.72672,44.038539999999998,43.447240000000001,42.244320000000002,40.409570000000002,40.15484,40.114240000000002,40.407789999999999,39.892620000000001,40.030450000000002,39.634529999999998,40.053750000000001,39.716439999999999,3776.393,7822.4009999999998,11598.79,54.333889999999997,40.409640000000003,51,51,762815.03760000004,695785.6258932458,8007.9924122200064,61,47,54460.533562124976,44,10.888433194468464,11.495573194468463,518285.6999825575,10003.373780130642,1470.9173063188234,-2305.4756936811764,0,3776.389000000001,1595.4162198693593,0.16900389255501527,0.16900389255501527,1.0397080080460803,1,9475.0444611723669,2123.7455388276339,0.7834931715688439,0.7834931715688439,44,1]
["2013-01-18T15:00:00","2013-01-18T15:00:00",43.85971,43.643279999999997,43.37332,43.71564,43.825589999999998,43.444189999999999,43.362630000000003,43.613669999999999,43.464820000000003,43.33464,43.5471,43.518419999999999,43.50817,43.736969999999999,43.994509999999998,42.501309999999997,39.889740000000003,40.321330000000003,40.136200000000002,40.109279999999998,40.403919999999999,39.884120000000003,40.001260000000002,39.620690000000003,40.039009999999998,39.705750000000002,3715.9389999999999,7893.0870000000004,11609.03,53.873089999999998,40.361310000000003,19,19,284185.99440000003,251232.35940834065,7717.9309842199964,62,47,53324.827532429976,44,10.849705618855863,11.456845618855864,192400.06532708963,9829.7279955238555,1422.6986897795439,-2293.2403102204562,0,3715.9430000000002,1779.3020044761452,0.187712912814884,0.187712912814884,1.0390724299172505,1,9308.8148878722968,2300.2151121277038,0.80767949352351598,0.80767949352351598,44,1]
["2013-01-18T16:00:00","2013-01-18T16:00:00",43.84657,43.61262,43.335810000000002,43.688000000000002,43.801679999999998,43.422260000000001,43.335529999999999,43.588090000000001,43.448830000000001,43.3217,43.541150000000002,43.500520000000002,43.48921,43.682749999999999,42.849870000000003,40.136879999999998,39.829979999999999,40.331609999999998,40.1449,40.124870000000001,40.42689,39.902799999999999,39.999609999999997,39.601489999999998,40.024929999999998,39.707630000000002,3758.864,7839.1710000000003,11598.04,53.876809999999999,40.347760000000001,21,21,314100.30960000004,277713.93466615514,7778.8562820799962,62,48,53028.268208774993,44,10.900439945919228,11.507579945919229,213647.08945566084,9729.5647647005408,1427.2554723797452,-2331.6085276202548,0,3758.8690000000006,1868.4752352994601,0.20735957254119203,0.20735957254119203,1.0395237885970332,1,9216.2328583395429,2381.807141660458,0.83272374006307137,0.83272374006307137,44,1]
["2013-01-18T17:00:00","2013-01-18T17:00:00",43.808410000000002,43.591079999999998,43.31409,43.659820000000003,43.782089999999997,43.39105,43.324260000000002,43.575319999999998,43.429279999999999,43.293030000000002,43.538440000000001,43.507399999999997,43.484780000000001,42.187139999999999,40.579230000000003,39.978580000000001,39.802109999999999,40.292169999999999,40.100149999999999,40.075290000000003,40.379710000000003,39.887689999999999,39.999789999999997,39.626550000000002,40.047049999999999,39.709629999999997,4035.16,7567.5169999999998,11602.68,53.611199999999997,40.289259999999999,51,51,762815.03760000004,661709.98247633956,8269.6165524000098,60,47,50407.00371148999,44,10.750207826561809,11.35734782656181,511706.21969541733,9377.8659026374262,1538.5035686412109,-2496.6564313587887,0,4035.1630000000005,2224.8140973625741,0.23075306724714151,0.23075306724714151,1.0424289671618165,1,8876.544855587048,2726.1351444129523,0.86138852969386726,0.86138852969386726,44,1]
["2013-01-18T18:00:00","2013-01-18T18:00:00",43.813420000000001,43.62124,43.357709999999997,43.715899999999998,43.844459999999998,43.433819999999997,43.387,43.651200000000003,43.490690000000001,43.331330000000001,43.580120000000001,43.454239999999999,41.640239999999999,40.241030000000002,40.520299999999999,39.9739,39.836089999999999,40.303199999999997,40.104210000000002,40.043500000000002,40.355420000000002,39.843170000000001,39.959609999999998,39.576430000000002,40.025689999999997,39.733669999999996,4446.6660000000002,7158.5029999999997,11605.17,53.218620000000001,40.29016,51,51,762815.03760000004,641879.01281612937,9070.6428067500092,54,44,46274.209847689999,44,10.42673855580623,11.033878555806229,496309.19292194437,8876.0660104825893,1739.8811254740694,-2706.7848745259307,0,4446.6670000000004,2729.1039895174108,0.25944907371637627,0.25944907371637627,1.0467558530157353,1,8387.6598085882797,3217.5101914117204,0.89522003396128302,0.89522003396128302,44,1]
["2013-01-18T19:00:00","2013-01-18T19:00:00",43.828229999999998,43.643389999999997,43.363700000000001,43.726700000000001,43.836649999999999,43.41075,43.38505,43.646709999999999,43.470860000000002,43.294879999999999,43.25179,40.708399999999997,39.924610000000001,40.143509999999999,40.440730000000002,39.915900000000001,39.802990000000001,40.255549999999999,40.044699999999999,39.967440000000003,40.305750000000003,39.813420000000001,39.957250000000002,39.60013,40.018839999999997,39.72242,4528.9290000000001,7073.3429999999998,11602.27,52.634929999999997,40.357909999999997,29,29,433757.57040000003,349496.0954388199,9297.4609887449969,51,43,43419.786738930001,44,10.268555727797514,10.875695727797513,277933.58012200275,8456.843959348711,1810.860501750268,-2718.0684982497323,0,4528.9270000000006,3145.4260406512894,0.29252262692568065,0.29252262692568065,1.0476208011823227,1,7984.7373125660524,3617.532687433948,0.93325769826429461,0.93325769826429461,44,1]
["2013-01-18T20:00:00","2013-01-18T20:00:00",43.829799999999999,43.655079999999998,43.372990000000001,43.737909999999999,43.843730000000001,43.415379999999999,43.4054,43.663429999999998,43.496319999999997,42.322000000000003,40.169600000000003,39.854050000000001,39.833950000000002,40.085929999999998,40.4114,39.88796,39.781230000000001,40.23507,40.023110000000003,39.941110000000002,40.276330000000002,39.8005,39.947850000000003,39.541939999999997,39.976689999999998,39.693829999999998,4530.8609999999999,7067.5630000000001,11598.42,52.320770000000003,40.350920000000002,31,31,463671.88560000004,365336.84173946333,9369.7525850850016,49,42,42298.834487775006,44,10.16948425603313,10.776624256033129,294234.96589184221,8318.7767290520915,1842.7193256189603,-2688.1416743810396,0,4530.857,3279.6432709479086,0.32700744864057085,0.32700744864057085,1.0476410947631822,1,7850.1084352262997,3748.3115647737004,0.97267047744918522,0.97267047744918522,44,1]
["2013-01-18T21:00:00","2013-01-18T21:00:00",43.83146,43.665399999999998,43.375979999999998,43.73751,43.849130000000002,43.414090000000002,43.419409999999999,43.456470000000003,41.390149999999998,39.699440000000003,39.937620000000003,39.786960000000001,39.781869999999998,40.054929999999999,40.377969999999998,39.856340000000003,39.750320000000002,40.201349999999998,39.989179999999998,39.900370000000002,40.236420000000003,39.743479999999998,39.900620000000004,39.527920000000002,39.968130000000002,39.643439999999998,5359.8130000000001,6246.6890000000003,11606.5,52.748530000000002,40.553919999999998,35,35,523500.516,428096.53393892996,11223.502020130005,52,44,38087.968073145013,44,10.147587711294246,10.754727711294246,331485.48594831047,7506.8024355686375,2212.0532168720783,-3147.7597831279218,0,5359.8109999999997,4099.6975644313625,0.37011498440421597,0.37011498440421597,1.0563573875237613,1,7083.0185748257181,4523.4814251742819,1.0202340194537602,1,44,1]
["2013-01-18T22:00:00","2013-01-18T22:00:00",43.830509999999997,43.661720000000003,43.37406,43.741410000000002,43.862609999999997,43.396459999999998,41.877209999999998,40.136150000000001,39.695369999999997,39.496519999999997,39.846339999999998,39.722430000000003,39.722230000000003,40.001280000000001,40.327419999999996,39.811839999999997,39.711930000000002,40.160870000000003,39.95805,39.846130000000002,40.195450000000001,39.707009999999997,39.867069999999998,39.48169,39.912619999999997,39.60904,5067.3230000000003,5930.0780000000004,10950.72,52.604550000000003,40.655209999999997,51,51,762815.03760000004,618581.83603514556,10695.776012404991,46,40,35430.259124260017,44,9.8135718361372675,10.420711836137267,467122.66655641707,7220.6653634087561,2179.7926771207026,-2887.5303228792977,0,5020.6419999999989,3730.0546365912433,0.40933579548116911,0.40933579548116911,1.0527910903597295,1,6799.9690772359463,4150.750922764053,1.0436443520618215,1,44,1]
["2013-01-18T23:00:00","2013-01-18T23:00:00",43.815370000000001,43.664949999999997,43.383369999999999,43.7376,43.863030000000002,43.182510000000001,39.737850000000002,39.861040000000003,39.670099999999998,39.478079999999999,39.842640000000003,39.707940000000001,39.70758,39.98001,40.306100000000001,39.784480000000002,39.688020000000002,40.140459999999997,39.918120000000002,39.790210000000002,40.151670000000003,39.675260000000002,39.844760000000001,39.471469999999997,39.891939999999998,39.620379999999997,1085.81,5855.9480000000003,6941.7579999999998,52.22701,40.759369999999997,39,39,583329.14639999997,458878.03833335149,2277.4810459500027,45,40,33576.951761360011,44,9.7503740550623768,10.357514055062376,354911.06817630318,6887.3156192252782,467.15767684164655,-618.6523231583534,0,1085.8099999999995,54.442380774721642,0.40990824670212395,0.40990824670212395,1.0114170844731605,1,6483.5927970474377,458.16520295256214,1.0048175194783362,1,44,1]
["2013-01-19","2013-01-19",43.804349999999999,43.66977,43.388449999999999,43.739249999999998,43.865130000000001,42.656419999999997,39.706780000000002,39.895650000000003,39.710889999999999,39.516860000000001,39.89725,39.743049999999997,39.735460000000003,40.007219999999997,40.327399999999997,39.808689999999999,39.708710000000004,40.169469999999997,39.939909999999998,39.801690000000001,40.148670000000003,39.686950000000003,39.868360000000003,39.489699999999999,39.897970000000001,39.580080000000002,1062.039,5882.1729999999998,6944.2120000000004,51.896900000000002,40.692100000000003,39,39,583329.14639999997,448329.0300504567,2243.1697432649985,45,40,32954.286015199999,44,9.7291411531183218,10.336281153118321,354138.19609294599,6774.3463675902585,461.12389736395835,-600.91510263604164,0,1062.0390000000007,169.86563240974192,0.41169435133765764,0.41169435133765764,1.0111671369547075,1,6376.4298836353,567.78211636470041,1.0059701203570475,1,44,1]
["2013-01-19T01:00:00","2013-01-19T01:00:00",43.802529999999997,43.674999999999997,43.391039999999997,43.735210000000002,43.867730000000002,41.667740000000002,39.720950000000002,39.931069999999998,39.729280000000003,39.522379999999998,39.902610000000003,39.733319999999999,39.740079999999999,40.031669999999998,40.357590000000002,39.862690000000001,39.757449999999999,40.227379999999997,39.989069999999998,39.83522,40.176290000000002,39.672229999999999,39.835850000000001,39.48715,39.904710000000001,39.537480000000002,1148.0509999999999,5789.8249999999998,6937.8760000000002,51.663809999999998,40.612679999999997,41,41,613243.46160000004,464030.89734792494,2448.2474587749975,43,39,31992.054376125001,44,9.6354820542258626,10.242622054225862,368715.13343297236,6640.4678450091969,508.17332127171824,-639.87767872828169,0,1148.0510000000004,297.40815499080327,0.41482154120378234,0.41482154120378234,1.0120715366836708,1,6246.8485524028183,691.02744759718189,1.007266021442508,1,44,1]
["2013-01-19T02:00:00","2013-01-19T02:00:00",43.799210000000002,43.682470000000002,43.39902,43.760669999999998,43.880459999999999,40.273099999999999,39.718440000000001,39.932720000000003,39.749560000000002,39.56129,39.961289999999998,39.793579999999999,39.786430000000003,40.055259999999997,40.374290000000002,39.853230000000003,39.754669999999997,40.225110000000001,40.002569999999999,39.867449999999998,40.227760000000004,39.71819,39.848059999999997,39.464680000000001,39.905929999999998,39.592570000000002,1237.175,5711.42,6948.5959999999995,51.444450000000003,40.614359999999998,41,41,613243.46160000004,453528.68606247124,2602.1749210000003,43,39,30927.596313900016,44,9.5991840343039918,10.206324034303991,367326.13917367888,6443.7969317758761,542.16585736887089,-695.00914263112907,0,1237.1759999999995,504.7990682241234,0.42012940685604894,0.42012940685604894,1.0130086690122277,1,6060.4770551965121,888.11894480348747,1.0093384008390378,1,44,1]
["2013-01-19T03:00:00","2013-01-19T03:00:00",43.792110000000001,43.678089999999997,43.416539999999998,43.761620000000001,43.830710000000003,39.906280000000002,39.710140000000003,39.958129999999997,39.778700000000001,39.59572,40.003300000000003,39.84834,39.841209999999997,40.118180000000002,40.437890000000003,39.911470000000001,39.792610000000003,40.24935,40.004519999999999,39.85089,40.1982,39.714480000000002,39.886429999999997,39.477980000000002,39.889009999999999,39.627800000000001,1319.8689999999999,5619.8729999999996,6939.741,51.415520000000001,40.573399999999999,41,41,613243.46160000004,451073.51435150485,2748.1718376950002,46,41,30465.668725380005,44,9.705126303535458,10.312266303535459,371380.16757786652,6278.2632131807977,566.33406959245337,-753.53493040754654,0,1319.8680000000004,661.47778681920227,0.4270847192672757,0.4270847192672757,1.0138781595761888,1,5908.6272267687937,1031.1137732312063,1.0108419641101298,1,44,1]
["2013-01-19T04:00:00","2013-01-19T04:00:00",43.783589999999997,43.669559999999997,43.399180000000001,43.746389999999998,43.388359999999999,39.780419999999999,39.74915,39.99006,39.807899999999997,39.612319999999997,40.028080000000003,39.870690000000003,39.865780000000001,40.14273,40.46931,39.940649999999998,39.842930000000003,40.30818,40.046619999999997,39.865600000000001,40.206699999999998,39.719290000000001,39.898350000000001,39.494120000000002,39.877929999999999,39.59695,1382.56,5559.0150000000003,6941.576,51.44773,40.606499999999997,41,41,613243.46160000004,453486.593031267,2894.140499199998,44,40,30133.280094225007,44,9.6329448512130735,10.240084851213073,368618.04382789164,6256.2966070402317,600.88385097222681,-781.67614902777314,0,1382.5609999999997,685.2793929597683,0.4342903010146697,0.4342903010146697,1.0145373644802473,1,5885.3575008522175,1056.2184991477825,1.0111059355015013,1,44,1]
["2013-01-19T05:00:00","2013-01-19T05:00:00",43.763849999999998,43.675690000000003,43.39781,43.712829999999997,41.9236,39.782310000000003,39.786810000000003,40.01867,39.822119999999998,39.616149999999998,40.04945,39.876469999999998,39.877249999999997,40.158740000000002,40.475320000000004,39.947130000000001,39.866720000000001,40.314129999999999,40.057720000000003,39.872529999999998,40.229149999999997,39.760530000000003,39.92989,39.527990000000003,39.931919999999998,39.656399999999998,1055.1869999999999,5642.6639999999998,6697.8509999999997,51.455120000000001,40.647350000000003,41,41,613243.46160000004,451494.44466354721,2167.0639215750002,43,39,30492.307349639992,44,9.5843406806227254,10.191480680622725,366758.13758305984,6362.9431310362834,452.20928466290684,-602.97771533709306,0,1055.1869999999999,334.90786896371628,0.43781179320085784,0.43781179320085784,1.0110950894852515,1,5983.881695937599,713.96930406240062,1.0075072506752785,1,44,1]
["2013-01-19T06:00:00","2013-01-19T06:00:00",43.752450000000003,43.673439999999999,43.378799999999998,43.703710000000001,41.51099,39.767339999999997,39.780250000000002,40.005180000000003,39.817270000000001,39.601390000000002,40.047179999999997,39.867330000000003,39.874459999999999,40.155549999999998,40.473570000000002,39.951300000000003,39.858600000000003,40.318190000000001,40.060169999999999,39.860370000000003,40.240580000000001,39.781599999999997,39.94415,39.535449999999997,39.91771,39.542549999999999,779.65700000000004,5625.6409999999996,6405.2969999999996,51.815640000000002,40.671289999999999,43,43,643157.77679999999,492556.47660125804,1641.1390021500017,41,38,31347.056139175009,44,9.5526406143458686,10.159780614345868,383376.55824574549,6563.0138104638718,343.59902531775111,-436.05797468224893,0,779.65599999999995,-157.71681046387221,0.43615343110444732,0.43615343110444732,1.0081979337195333,1,6170.8135892052969,234.48341079470265,1.0024655482161686,1,44,1]
["2013-01-19T07:00:00","2013-01-19T07:00:00",43.753590000000003,43.668979999999998,43.3795,43.704720000000002,40.7012,39.838349999999998,39.790709999999997,39.993969999999997,39.811070000000001,39.601149999999997,40.047170000000001,39.856749999999998,39.862130000000001,40.13532,40.455880000000001,39.942030000000003,39.854210000000002,40.316400000000002,40.060429999999997,39.854849999999999,40.249830000000003,39.803260000000002,39.958779999999997,39.556289999999997,39.947929999999999,39.560560000000002,715.9425,5659.0479999999998,6374.991,51.802230000000002,40.648650000000004,43,43,643157.77679999999,491295.4963188016,1500.9841903874999,40,38,31559.322295919996,44,9.5598788902908733,10.167018890290873,383667.05230193993,6602.4523235272409,314.01740704307821,-401.92509295692179,0,715.94300000000021,-227.46132352724089,0.43376171879282061,0.43376171879282061,1.0075280037105645,1,6208.1761893956909,166.81481060430906,1.0017540258277633,1,44,1]
["2013-01-19T08:00:00","2013-01-19T08:00:00",43.76097,43.682160000000003,43.386710000000001,43.720880000000001,41.10718,39.774189999999997,39.783700000000003,40.019300000000001,39.820599999999999,39.60089,40.054009999999998,39.852029999999999,39.871670000000002,40.143009999999997,40.458530000000003,39.94106,39.854460000000003,40.311880000000002,40.065570000000001,39.87162,40.253959999999999,39.851489999999998,39.990319999999997,39.581389999999999,39.976100000000002,39.654400000000003,224.1028,5682.9709999999995,5902.5829999999996,51.882289999999998,40.712000000000003,43,43,643157.77679999999,490742.46295494883,460.14691769799975,42,40,31740.217065794983,44,9.6877414019436099,10.294881401943609,388798.56427073176,6552.6557220916493,94.995706141718955,-129.10709385828105,0,219.61200000000008,-650.07272209164967,0.42692632845582074,0.42692632845582074,1.0023091781760343,1,6166.2132523066521,-263.63025230665244,0.99722797832008758,0.99722797832008758,44,1]
["2013-01-19T09:00:00","2013-01-19T09:00:00",43.78378,43.689079999999997,43.385120000000001,43.722679999999997,41.565980000000003,39.766089999999998,39.767969999999998,40.023539999999997,39.840820000000001,39.622540000000001,40.052320000000002,39.894759999999998,39.910730000000001,40.174779999999998,40.504240000000003,39.978160000000003,39.904629999999997,40.347709999999999,40.11,39.914299999999997,40.264389999999999,39.82255,39.959850000000003,39.567239999999998,39.954970000000003,39.606369999999998,155.77010000000001,5798.8230000000003,5900.3969999999999,52.167900000000003,40.647539999999999,43,43,643157.77679999999,504132.45217960607,325.35778672050014,46,43,33402.26426814001,44,9.9269582115435746,10.534098211543576,398399.06332030706,6729.6071075021046,65.550348815240795,-90.219751184759218,0,101.57399999999961,-829.21010750210462,0.41820734277384131,0.41820734277384131,1.001068031182506,1,6341.7415705383919,-441.34457053839196,0.99258732457439769,0.99258732457439769,44,1]
["2013-01-19T10:00:00","2013-01-19T10:00:00",43.843389999999999,43.694499999999998,43.383710000000001,43.704329999999999,42.372729999999997,39.84243,39.77599,40.02055,39.85839,39.685169999999999,40.060020000000002,39.938270000000003,39.925930000000001,40.19144,40.524430000000002,39.989199999999997,39.896850000000001,40.330300000000001,40.091749999999998,39.968159999999997,40.306690000000003,39.829560000000001,39.94952,39.544939999999997,39.959159999999997,39.61383,220.84829999999999,6103.79,5899.5990000000002,52.669159999999998,40.595309999999998,41,41,613243.46160000004,499580.37551949237,467.04556787399986,50,45,36848.122445749999,44,10.166155975400077,10.773295975400076,389022.1097268397,7249.175112975754,91.882432062649883,-128.96586793735011,0,-204.1909999999998,-1349.5761129757539,0.40401680807181806,0.40401680807181806,0.99785297068947687,0.99785297068947687,6840.6405114812796,-941.04151148127949,0.98269245306894781,0.98269245306894781,44,0.99785297068947687]
["2013-01-19T11:00:00","2013-01-19T11:00:00",43.894710000000003,43.691479999999999,43.393189999999997,43.726759999999999,43.667189999999998,40.016800000000003,39.783880000000003,40.045079999999999,39.878300000000003,39.731180000000002,40.033619999999999,39.971380000000003,39.93045,40.190629999999999,40.533909999999999,39.984769999999997,39.882689999999997,40.299340000000001,40.090919999999997,40.018050000000002,40.333919999999999,39.829070000000002,39.951779999999999,39.550919999999998,39.945689999999999,39.619459999999997,1405.1590000000001,7302.8090000000002,5897.65,54.034590000000001,40.53069,41,41,613243.46160000004,551615.01536631433,3003.7030073750047,56,49,49308.201227550009,44,10.834432661859456,11.441572661859455,414594.64737792156,9102.1288823234991,554.47351995623467,-850.68548004376544,0,-1405.1590000000006,-3204.4788823234994,0.37032232552703898,0.37032232552703898,0.98307799256142325,0.98307799256142325,8619.1300243049918,-2721.4800243049922,0.95407661113572817,0.95407661113572817,44,0.98307799256142325]
["2013-01-19T12:00:00","2013-01-19T12:00:00",44.753779999999999,43.644280000000002,43.365070000000003,43.724850000000004,43.820279999999997,41.825319999999998,39.869219999999999,40.062260000000002,39.89246,39.759039999999999,40.000680000000003,39.987310000000001,39.943219999999997,40.187289999999997,40.53689,39.998080000000002,39.884270000000001,40.287089999999999,40.082700000000003,40.060420000000001,40.35651,39.855240000000002,39.949280000000002,39.54936,39.927990000000001,39.647350000000003,1828.9949999999999,7732.4880000000003,5903.4939999999997,53.462890000000002,40.514400000000002,51,51,762815.03760000004,657614.98386881244,4669.8174689249963,61,51,50062.021771560001,44,10.981831942410196,11.588971942410197,522731.4484745505,9117.2441964310055,850.46238066908643,-978.53261933091346,0,-1828.9940000000006,-3213.7501964310059,0.33653035688769217,0.33653035688769217,0.96384647047293281,0.96384647047293281,8639.5966821451184,-2736.1026821451187,0.92530701475211408,0.92530701475211408,44,1]
["2013-01-19T13:00:00","2013-01-19T13:00:00",49.938540000000003,43.865470000000002,43.34272,43.708240000000004,43.824330000000003,43.397379999999998,40.73706,40.105670000000003,39.899070000000002,39.774459999999998,39.983739999999997,39.991399999999999,39.935000000000002,40.178100000000001,40.535429999999998,39.980780000000003,39.865929999999999,40.283630000000002,40.07253,40.0747,40.368980000000001,39.861280000000001,39.941040000000001,39.529719999999998,39.914740000000002,39.631399999999999,1965.1420000000001,7867.107,5901.9650000000001,53.736440000000002,40.502319999999997,39,39,583329.14639999997,513419.77085180226,10127.496856940003,64,52,52057.119045420011,44,11.110711759448824,11.717851759448823,404427.00520782918,9370.6182236523873,1823.0149564139901,-142.1270435860099,0,-1965.1419999999998,-3468.6532236523872,0.30005813167099676,0.30005813167099676,0.94318337820471299,0.94318337820471299,8885.0960251213546,-2983.1310251213545,0.8939399625898421,0.8939399625898421,44,0.97933690773178017]
["2013-01-19T14:00:00","2013-01-19T14:00:00",52.943510000000003,47.391449999999999,43.3538,43.695480000000003,43.790979999999998,43.425400000000003,43.070900000000002,40.364350000000002,39.939509999999999,39.78407,39.975940000000001,39.961620000000003,39.917389999999997,40.182929999999999,40.546689999999998,39.973190000000002,39.753270000000001,40.260089999999998,40.061720000000001,40.075429999999997,40.364289999999997,39.857190000000003,39.948700000000002,39.534280000000003,39.96219,39.611719999999998,1894.0519999999999,7798.058,5904.0069999999996,53.95852,40.485019999999999,37,37,553414.83120000002,495439.27057623403,12625.551756540004,65,52,52533.567231500005,44,11.126958642594152,11.734098642594152,384248.21379114292,9442.5743671591954,2269.3625746408757,375.31057464087576,1,-1894.0510000000004,-3538.5673671591958,0.26285077260741663,0.26285077260741663,0.92326779420431304,0.92326779420431304,8954.0012968368883,-3049.9942968368887,0.8618698559140473,0.8618698559140473,44,0.95942132373138023]
["2013-01-19T15:00:00","2013-01-19T15:00:00",53.823590000000003,51.61983,44.68242,43.699919999999999,43.749479999999998,43.41827,43.320920000000001,42.491590000000002,40.108730000000001,39.870899999999999,39.972650000000002,39.965159999999997,39.92548,40.184420000000003,40.543210000000002,39.9741,39.767659999999999,40.290230000000001,40.075090000000003,40.084919999999997,40.365380000000002,39.85136,39.954709999999999,39.537970000000001,39.959879999999998,39.67848,1991.385,7887.9040000000005,5896.5190000000002,54.104930000000003,40.535240000000002,35,35,523500.516,471260.65078860772,14084.179938675003,66,53,53518.206014880008,44,11.221381825107409,11.828521825107408,366562.50856222922,9538.6124185053723,2510.239854268606,518.854854268606,1,-1991.3850000000002,-3642.093418505372,0.2245548569147835,0.2245548569147835,0.90232876181044586,0.90232876181044586,9049.0099787923482,-3152.490978792348,0.82872201623146113,0.82872201623146113,44,0.93848229133751304]
["2013-01-19T16:00:00","2013-01-19T16:00:00",54.138179999999998,52.906149999999997,50.47166,44.262419999999999,43.76249,43.419199999999996,43.337499999999999,43.546529999999997,41.22175,39.998179999999998,40.074150000000003,39.985810000000001,39.931249999999999,40.188609999999997,40.537669999999999,39.973419999999997,39.791879999999999,40.311630000000001,40.10286,40.091630000000002,40.383490000000002,39.86168,39.952460000000002,39.54054,39.947339999999997,39.711509999999997,1790.0920000000001,7688.6559999999999,5898.5630000000001,54.03154,40.508609999999997,35,35,523500.516,467784.28907405399,12912.533276820002,65,53,51986.578441040008,44,11.169153324839465,11.776293324839465,364856.38979940227,{"$f":"AO454*1000/(500*AQ454)","v":9308.9560021394409},2312.1776380494975,{"$f":"AU454-AC454","v":522.08563804949745},1,{"$f":"AE454-AD454","v":-1790.0929999999998},{"$f":"AE454-AT454","v":-3410.3930021394408},0.18869522678418821,0.18869522678418821,0.88350627629657752,0.88350627629657752,{"$f":"AO454*1000/(500*AR454)","v":8829.0223429448579},{"$f":"AE454-BD454","v":-2930.4593429448578},0.79790879673305526,0.79790879673305526,44,0.9196598058236447]
["2013-01-19T17:00:00","2013-01-19T17:00:00",54.275440000000003,53.767479999999999,52.304670000000002,47.749200000000002,43.820610000000002,43.424849999999999,43.3446,43.579270000000001,43.201819999999998,40.209139999999998,40.185540000000003,40.064660000000003,39.959099999999999,40.202480000000001,40.553789999999999,39.996789999999997,39.828139999999998,40.331069999999997,40.109189999999998,40.082949999999997,40.380000000000003,39.877600000000001,39.961930000000002,39.544460000000001,39.95505,39.694420000000001,1147.3489999999999,7045.7290000000003,5898.3789999999999,54.330120000000001,40.577109999999998,33,33,{"$f":"3.1416*(138/2)^2*AI455","v":493586.20079999999},{"$f":"62.4*AJ455*(AF455-AB455)/1000","v":450776.32448463008},{"$f":"500*AC455*(C455-AB455)/1000","v":8364.7593579900022},62,52,48449.990697145018,44,{"$f":"19.5286-0.30357*AP455+0.0000341*AO455+0.060847*AN455","v":10.987708682772647},{"$f":"19.5286-0.30357*42+0.0000341*AO455+0.060847*AN455","v":11.594848682772646},{"$f":"62.4*AJ455*AQ455/1000","v":338418.99837576004},8818.9434387004712,{"$f":"AL455*1000/(500*AQ455)","v":1522.5666423255102},375.21764232551027,1,-1147.3500000000004,-2920.5644387004713,0.15798605031136878,{"$f":"IF(AZ455>1,1,IF(AZ455<0,0,AZ455))","v":0.15798605031136878},0.87144211049383047,{"$f":"IF(BB455>1,1,BB455)","v":0.87144211049383047},8357.1579108455062,-2458.7789108455063,0.77205520676248129,{"$f":"IF(BF455>1,1,IF(BF455<0,0,BF455))","v":0.77205520676248129},44,0.90759564002089765]
["2013-01-19T18:00:00","2013-01-19T18:00:00",54.434249999999999,53.849969999999999,52.87762,50.90645,44.341999999999999,43.431179999999998,43.362720000000003,43.596969999999999,43.444290000000002,40.998339999999999,40.326210000000003,40.123080000000002,40.008420000000001,40.227249999999998,40.56729,40.010869999999997,39.871070000000003,40.353209999999997,40.112139999999997,40.0745,40.374319999999997,39.868580000000001,39.987369999999999,39.567700000000002,39.978949999999998,39.689190000000004,822.05550000000005,6728.3010000000004,5906.2460000000001,54.216639999999998,40.623910000000002,33,33,493586.20079999999,447442.24841546611,6060.6288354149983,59,51,45727.989425864987,44,10.834041439421997,11.441181439421996,333686.08125178976,8441.5385858639656,1118.8121938249365,296.75669382493641,1,-822.05500000000029,-2535.2925858639655,{"$f":"IF(AZ455>1,1+AY456*60/$BK$7,IF(AZ455<0,AY456*60/$BK$7,AZ455+AY456*60/$BK$7))","v":0.13132793368232079},0.13132793368232079,{"$f":"IF(BB455>1,1+AX456*60/$BK$7,BB455+AX456*60/$BK$7)","v":0.86279835939871807},0.86279835939871807,7993.5782275602378,-2087.3322275602377,{"$f":"IF(BF455>1,1+BE456*60/$BK$7,IF(BF455<0,BE456*60/$BK$7,BF455+BE456*60/$BK$7))","v":0.75010730762211086},0.75010730762211086,44,0.89895188892578526]
["2013-01-19T19:00:00","2013-01-19T19:00:00",54.459000000000003,53.95579,53.306759999999997,52.097490000000001,45.705179999999999,43.444629999999997,43.376739999999998,43.618519999999997,43.463239999999999,42.537239999999997,40.439520000000002,40.194760000000002,40.052700000000002,40.258879999999998,40.579419999999999,40.018790000000003,39.9161,40.389130000000002,40.125430000000001,40.055759999999999,40.36692,39.877719999999997,40.006399999999999,39.59836,40.008749999999999,39.673789999999997,614.55960000000005,6508.54,5893.98,53.6233,40.596719999999998,31,31,463671.88560000004,403602.92574551399,4543.1963717580029,56,50,42392.008496600007,44,10.65943748973406,11.266577489734061,308410.84437074012,7953.8922269448267,852.42703963196652,237.86743963196648,1,-614.5600000000004,-2059.9122269448271,0.10966835060395036,0.10966835060395036,0.85633637854219113,0.85633637854219113,7525.2681722070392,-1631.2881722070397,0.73295462449876936,0.73295462449876936,44,0.89248990806925832]
["2013-01-19T20:00:00","2013-01-19T20:00:00",54.379379999999998,54.13449,53.577509999999997,52.69258,48.267519999999998,43.517380000000003,43.392910000000001,43.630499999999998,43.465949999999999,43.199399999999997,40.640779999999999,40.256030000000003,40.073430000000002,40.277709999999999,40.59346,40.026949999999999,39.932690000000001,40.395850000000003,40.139519999999997,40.053049999999999,40.362630000000003,39.871740000000003,40.013399999999997,39.607349999999997,40.016170000000002,39.659129999999998,524.94730000000004,6426.2470000000003,5902.7929999999997,53.646259999999998,40.621250000000003,31,31,463671.88560000004,404691.38993289729,3863.6777464125003,52,47,41850.96571873498,44,10.458446931008863,11.065586931008864,302595.55927838094,8003.2849991615094,738.8626192588606,213.91531925886056,1,-523.45400000000063,-2100.4919991615097,8.7582078982188838E-2,8.7582078982188838E-2,0.85083235985032624,0.85083235985032624,7564.1655485000783,-1661.3725485000787,0.71548560991277788,0.71548560991277788,44,0.88698588937739342]
["2013-01-19T21:00:00","2013-01-19T21:00:00",54.306190000000001,54.095039999999997,53.68967,53.110729999999997,50.226149999999997,43.838610000000003,43.405430000000003,43.637999999999998,43.479230000000001,43.301229999999997,41.159289999999999,40.308590000000002,40.106819999999999,40.293759999999999,40.618830000000003,40.055619999999998,39.950749999999999,40.400190000000002,40.154800000000002,40.055390000000003,40.372390000000003,39.874459999999999,40.01923,39.599069999999998,40.0122,39.654409999999999,390.94709999999998,6291.8,5900.8530000000001,53.193939999999998,40.622430000000001,31,31,463671.88560000004,391740.92288683669,2864.0354504190004,51,47,39548.713308999984,44,10.379940123836901,10.9870801238369,300324.11196119612,7620.2199313614092,551.8404569294031,160.89335692940313,1,-390.94700000000012,-1719.3669313614091,6.9503264552673472E-2,6.9503264552673472E-2,0.84672162691958452,0.84672162691958452,7199.1307723691762,-1298.2777723691761,0.70183446745068445,0.70183446745068445,44,0.88287515644665171]
["2013-01-19T22:00:00","2013-01-19T22:00:00",54.229930000000003,54.03284,53.713079999999998,53.476030000000002,51.656039999999997,44.515129999999999,43.44012,43.646120000000003,43.479219999999998,43.319139999999997,42.229520000000001,40.412520000000001,40.171790000000001,40.321550000000002,40.643590000000003,40.078830000000004,39.975200000000001,40.426430000000003,40.17071,40.064300000000003,40.381369999999997,39.882689999999997,40.032049999999998,39.605310000000003,40.011330000000001,39.659529999999997,455.18630000000002,6359.6040000000003,5904.4170000000004,52.68497,40.606340000000003,41,41,613243.46160000004,498436.59306249779,3316.1232327600014,50,47,38407.651831259987,44,10.341029927445966,10.948169927445965,395713.90492708841,7428.2063006747203,641.35260337246109,186.16630337246107,1,-455.1869999999999,-1523.7893006747199,5.3480911502783016E-2,5.3480911502783016E-2,0.84193542267567023,0.84193542267567023,7016.2688532949878,-1111.8518532949874,0.69014355787100756,0.69014355787100756,44,0.87808895220273742]
["2013-01-19T23:00:00","2013-01-19T23:00:00",54.186700000000002,53.969430000000003,53.589109999999998,53.767209999999999,52.415280000000003,46.195619999999998,43.472209999999997,43.65466,43.485129999999998,43.322719999999997,43.195340000000002,40.564010000000003,40.230580000000003,40.331359999999997,40.655140000000003,40.09346,39.987670000000001,40.44247,40.19379,40.073349999999998,40.386400000000002,39.89837,40.028480000000002,39.611170000000001,40.019089999999998,39.674799999999998,210.69829999999999,6079.12,5900.4690000000001,52.391770000000001,40.71743,29,29,433757.57040000003,344203.51742710068,1528.8163298850004,49,46,35484.856890399999,44,10.180515619962641,10.78765561996264,275550.64497381687,6971.1315644600354,300.34163041549567,89.643330415495683,1,-178.65099999999984,-1070.6625644600354,4.2223099417159425E-2,4.2223099417159425E-2,0.84005694158025335,0.84005694158025335,6578.78933857232,-678.32033857232,0.68301114924947792,0.68301114924947792,44,0.87621047110732053]
["2013-01-20","2013-01-20",54.113199999999999,53.907069999999997,53.535800000000002,53.774749999999997,52.90164,47.8125,43.594920000000002,43.657049999999998,43.487450000000003,43.32029,43.518459999999997,40.615740000000002,40.268549999999998,40.361379999999997,40.659979999999997,40.104779999999998,40.002940000000002,40.453510000000001,40.191180000000003,40.079470000000001,40.394309999999997,39.910739999999997,40.039830000000002,39.622909999999997,40.026339999999998,39.671129999999998,202.7097,6063.134,5896.1610000000001,52.516910000000003,40.75967,29,29,433757.57040000003,347689.94973603787,1463.7738385395003,48,45,35642.860795080007,44,10.125056553112229,10.732196553112228,274049.56367197091,7040.5257705200956,289.13889633328853,86.42919633328853,1,-166.97299999999996,-1144.3647705200956,3.0190322731425322E-2,3.0190322731425322E-2,0.83830125242125031,0.83830125242125031,6642.2303428171817,-746.06934281718168,0.67516637280628877,0.67516637280628877,44,0.87445478194831749]
["2013-01-20T01:00:00","2013-01-20T01:00:00",54.040840000000003,53.80753,53.497639999999997,53.774810000000002,53.313299999999998,49.060749999999999,43.84337,43.666620000000002,43.49062,43.319850000000002,43.62341,40.874130000000001,40.307200000000002,40.394179999999999,40.652650000000001,40.102170000000001,40.007660000000001,40.455280000000002,40.193510000000003,40.08014,40.403750000000002,39.918999999999997,40.052289999999999,39.627160000000003,40.035829999999997,39.680489999999999,134.8664,5981.0990000000002,5916.7659999999996,52.006399999999999,40.756309999999999,29,29,433757.57040000003,333618.9027331096,968.3643536200002,47,45,33643.951024455004,44,10.056893729933917,10.664033729933916,272204.63650018891,6690.7241794382726,192.57722704928361,57.710827049283608,1,-64.333000000000538,-773.95817943827296,2.2052300505308108E-2,2.2052300505308108E-2,0.83762480323086541,0.83762480323086541,6309.7983139375337,-393.03231393753413,0.67103371319834026,0.67103371319834026,44,0.8737783327579326]
["2013-01-20T02:00:00","2013-01-20T02:00:00",53.92698,53.760840000000002,53.415080000000003,53.72054,53.633130000000001,50.106140000000003,43.988500000000002,43.677320000000002,43.490900000000003,43.316890000000001,43.649979999999999,41.272100000000002,40.347589999999997,40.450240000000001,40.664380000000001,40.129939999999998,40.020670000000003,40.474449999999997,40.207149999999999,40.071289999999998,40.398229999999998,39.919719999999998,40.065629999999999,39.642449999999997,40.050649999999997,39.685429999999997,143.62889999999999,5924.6390000000001,5998.5209999999997,52.056159999999998,40.699399999999997,29,29,433757.57040000003,334832.02202576213,1022.7490803975002,46,44,33642.351604820004,44,9.9959921897243618,10.603132189724363,270556.24664341827,6731.1680454099451,204.63182863405225,61.002928634052267,1,73.881999999999607,-732.64704540994535,1.4348656952147928E-2,1.4348656952147928E-2,0.83840165832986624,0.83840165832986624,6345.7384106600612,-347.21741066006143,0.66738278853559263,0.66738278853559263,44,0.87455518785693342]
["2013-01-20T03:00:00","2013-01-20T03:00:00",53.90307,53.71105,53.391159999999999,53.675240000000002,53.639479999999999,50.573390000000003,44.259509999999999,43.692790000000002,43.491819999999997,43.313740000000003,43.664180000000002,41.619819999999997,40.39002,40.461739999999999,40.672809999999998,40.134770000000003,40.019840000000002,40.48498,40.218510000000002,40.056550000000001,40.392659999999999,39.918469999999999,40.075969999999998,39.65287,40.054380000000002,39.686579999999999,227.922,5774.665,6000.6570000000002,51.622309999999999,40.722900000000003,29,29,433757.57040000003,323058.10653482442,1620.12541689,44,42,31470.22072382499,44,9.8002285266824334,10.407368526682433,265257.61486214917,6422.3442623083947,330.63013020135025,102.70813020135026,1,225.99200000000019,-421.68726230839457,9.914696042752396E-3,9.914696042752396E-3,0.84077792098563342,0.84077792098563342,6047.680668392125,-47.023668392124819,0.66688834365640492,0.66688834365640492,43,0.87693145051270061]
["2013-01-20T04:00:00","2013-01-20T04:00:00",53.847189999999998,53.685789999999997,53.36168,53.683999999999997,53.733649999999997,51.031750000000002,44.498429999999999,43.710560000000001,43.491140000000001,43.303080000000001,43.687660000000001,41.891739999999999,40.48189,40.459069999999997,40.684229999999999,40.139899999999997,40.032829999999997,40.495379999999997,40.225110000000001,40.05247,40.384059999999998,39.906779999999998,40.074719999999999,39.655419999999999,40.06127,39.691949999999999,266.93239999999997,5730.0770000000002,5996.8990000000003,51.991799999999998,40.729599999999998,39,39,583329.14639999997,447711.3264841176,1889.2460928879998,43,42,32266.636594700001,44,9.8273863078792711,10.43452630787927,357714.29405825952,6566.6771578582775,384.48597291291281,117.55357291291284,1,266.82200000000012,-569.77815785827715,3.9235876911717597E-3,3.9235876911717597E-3,0.84358350328207354,0.84358350328207354,6184.5905875640892,-187.69158756408888,0.6649148025118945,0.6649148025118945,43,0.87973703280914073]
["2013-01-20T05:00:00","2013-01-20T05:00:00",53.793410000000002,53.642299999999999,53.313450000000003,53.638030000000001,53.688270000000003,51.335000000000001,44.917380000000001,43.735100000000003,43.492539999999998,43.294460000000001,43.703800000000001,42.29177,40.520159999999997,40.493119999999998,40.711530000000003,40.152900000000002,40.045200000000001,40.511119999999998,40.235230000000001,40.045279999999998,40.372990000000001,39.902369999999998,40.080159999999999,39.662379999999999,40.072139999999997,39.700040000000001,135.4419,5880.9949999999999,5998.1049999999996,51.82347,40.654710000000001,39,39,583329.14639999997,441289.68457642541,954.4164051015,41,40,32841.710858099999,44,9.7253023402612104,10.33244234026121,353998.46430789324,6753.8693829888498,196.27490677598109,60.83300677598109,1,117.10999999999967,-755.76438298885023,-4.0231302451060255E-3,0,0.84481489253309516,0.84481489253309516,6357.0082999891665,-358.90329998916695,0.66114100295794642,0.66114100295794642,43,0.88096842206016235]
["2013-01-20T06:00:00","2013-01-20T06:00:00",53.765790000000003,53.58623,53.250959999999999,53.591709999999999,53.671239999999997,51.879710000000003,45.485990000000001,43.775199999999998,43.494300000000003,43.293660000000003,43.717410000000001,42.672339999999998,40.574579999999997,40.534529999999997,40.717030000000001,40.17653,40.055390000000003,40.518859999999997,40.250999999999998,40.041980000000002,40.371110000000002,39.906359999999999,40.089689999999997,39.676380000000002,40.079929999999997,39.704940000000001,179.4744,5833.7280000000001,6000.3410000000003,52.309780000000003,40.731769999999997,27,27,403843.25520000001,317639.68809301063,1261.7813086200003,42,41,33771.480560640011,44,9.8178544871178257,10.424994487117825,247408.15726583358,6879.6050308042659,257.03809529375383,77.563695293753824,1,166.61300000000028,-879.26403080426553,-9.2452931119661446E-3,0,0.84656679636095333,0.84656679636095333,6478.9445409053142,-478.60354090531382,0.65610857826516433,0.65610857826516433,43,0.88272032588802052]
["2013-01-20T07:00:00","2013-01-20T07:00:00",53.71593,53.538179999999997,53.236310000000003,53.587989999999998,53.679560000000002,52.444569999999999,46.19764,43.838189999999997,43.492809999999999,43.293770000000002,43.72222,42.968490000000003,40.652250000000002,40.567990000000002,40.73509,40.177570000000003,40.062449999999998,40.528680000000001,40.244140000000002,40.037909999999997,40.3795,39.904809999999998,40.091659999999997,39.693399999999997,40.094119999999997,39.713610000000003,191.98070000000001,5841.74,5999.4780000000001,51.940730000000002,40.619579999999999,27,27,403843.25520000001,308121.21241331188,1344.0875976119999,39,38,33067.607400500005,44,9.6113114123570522,10.218451412357052,242203.30914044817,6880.9772114938878,279.68870010474029,87.708000104740279,1,157.73800000000028,-881.49921149388774,-9.2687956094069449E-3,0,0.84822538126128344,0.84822538126128344,6472.136738941037,-472.65873894103697,0.65113866202800741,0.65113866202800741,43,0.88437891078835063]
["2013-01-20T08:00:00","2013-01-20T08:00:00",53.658949999999997,53.559170000000002,53.230490000000003,53.557029999999997,53.636609999999997,52.791159999999998,47.044289999999997,43.913829999999997,43.498390000000001,43.301699999999997,43.724400000000003,43.206719999999997,40.712029999999999,40.592030000000001,40.755940000000002,40.190019999999997,40.070810000000002,40.532389999999999,40.272260000000003,40.050809999999998,40.389569999999999,39.914029999999997,40.097819999999999,39.704270000000001,40.11007,39.728259999999999,162.63900000000001,5898.6559999999999,6000.8779999999997,52.148989999999998,40.705649999999999,27,27,403843.25520000001,313000.14939400245,1132.8367454549998,42,41,33750.163075519995,44,9.8171275608752318,10.424267560875233,247389.83885600336,6875.7715260880341,230.78782228923254,68.148822289232527,1,102.22199999999975,-874.89352608803438,-9.1993380907971021E-3,0,0.84930022603985,0.84930022603985,6475.3063711051363,-474.42837110513665,0.64615013844711267,0.64615013844711267,43,0.88545375556691719]
["2013-01-20T09:00:00","2013-01-20T09:00:00",53.676259999999999,53.52317,53.201509999999999,53.536580000000001,53.622340000000001,52.987659999999998,48.286290000000001,44.07582,43.52008,43.314369999999997,43.724269999999997,43.400959999999998,40.920470000000002,40.636650000000003,40.763300000000001,40.209249999999997,40.07846,40.537199999999999,40.25956,40.074460000000002,40.411450000000002,39.93065,40.114789999999999,39.710450000000002,40.10915,39.732129999999998,197.91380000000001,6156.8429999999998,5997.5209999999997,52.37218,40.647539999999999,27,27,403843.25520000001,318526.97372438345,1379.8678779970003,46,44,36093.383855760003,44,10.079572389481417,10.686712389481416,254003.4010670344,7161.6894965555121,273.79492396660947,75.881123966609465,1,-159.32200000000012,-1164.1684965555123,-1.2241009077247979E-2,0,0.84762498568248279,0.84762498568248279,6754.8152397711283,-757.29423977112856,0.63818733435937647,0.63818733435937647,43,0.88377851520954998]
["2013-01-20T10:00:00","2013-01-20T10:00:00",53.72439,53.497610000000002,53.165999999999997,53.51079,53.604149999999997,53.133000000000003,49.816040000000001,44.359259999999999,43.561300000000003,43.33426,43.710799999999999,43.521970000000003,41.426009999999998,40.717689999999997,40.791980000000002,40.232080000000003,40.089910000000003,40.545639999999999,40.287529999999997,40.115409999999997,40.434019999999997,39.940049999999999,40.111089999999997,39.708320000000001,40.105069999999998,39.7425,398.52589999999998,6401.74,6003.2139999999999,52.778860000000002,40.61683,27,27,403843.25520000001,328513.91404160619,2786.0726479754999,50,47,38929.076966100009,44,10.358810524544012,10.965950524544011,261040.15156326891,7516.1287821342103,537.91362268365094,139.38772268365096,1,-398.52599999999984,-1512.9147821342103,-1.5908009567345671E-2,0,0.84343456101633418,0.84343456101633418,7099.9913557824057,-1096.7773557824057,0.62665493023782903,0.62665493023782903,43,0.87958809054340137]
["2013-01-20T11:00:00","2013-01-20T11:00:00",53.730449999999998,53.462949999999999,53.167009999999998,53.518180000000001,53.595910000000003,53.155520000000003,52.294469999999997,46.356990000000003,43.714770000000001,43.393250000000002,43.691119999999998,43.582850000000001,42.763680000000001,40.932369999999999,40.916870000000003,40.25647,40.108730000000001,40.558199999999999,40.323540000000001,40.149630000000002,40.453130000000002,39.966239999999999,40.108690000000003,39.713549999999998,40.106789999999997,39.745600000000003,1945.9570000000001,7939.4390000000003,5993.482,52.523330000000001,40.485379999999999,35,35,523500.516,417402.85069446155,13606.958375724995,56,50,47787.284855025006,44,10.843416413556355,11.450556413556352,354215.72707245639,8814.0643193010128,2509.7179443765863,563.76094437658617,1,-1945.9570000000003,-2820.5823193010128,-2.9657883610358007E-2,0,0.82297319535370617,0.82297319535370617,8346.7183827764875,-2353.2363827764875,0.60191109976336854,0.60191109976336854,43,0.85912672488077335]
["2013-01-20T12:00:00","2013-01-20T12:00:00",53.731859999999998,53.433520000000001,53.114060000000002,53.521039999999999,53.602339999999998,53.198120000000003,53.131239999999998,51.465960000000003,44.904040000000002,43.557479999999998,43.70299,43.612769999999998,43.56035,42.349200000000003,41.156689999999998,40.311779999999999,40.158499999999997,40.575569999999999,40.365609999999997,40.226280000000003,40.4801,39.99306,40.117179999999998,39.74051,40.109180000000002,39.754739999999998,2061.2739999999999,8066.66,6005.3860000000004,53.134909999999998,40.546349999999997,35,35,523500.516,437082.41610806569,14405.33702544,59,51,50773.816704800003,44,11.006104149633682,11.61324414963368,359530.15497253754,9226.4830524050449,2617.6995655487153,556.42556554871544,1,-2061.2739999999994,-3221.0970524050445,-3.3869219424721562E-2,0,0.80129929349211937,0.80129929349211937,8744.1228395084727,-2738.7368395084723,0.57311380571889936,0.57311380571889936,43,0.83745282301918655]
["2013-01-20T13:00:00","2013-01-20T13:00:00",53.949330000000003,53.587359999999997,53.150829999999999,53.529269999999997,53.571809999999999,53.211959999999998,53.120820000000002,53.21846,49.758920000000003,44.238570000000003,43.764449999999997,43.660179999999997,43.586669999999998,43.712269999999997,42.125889999999998,40.547020000000003,40.216450000000002,40.611789999999999,40.394170000000003,40.310920000000003,40.520809999999997,40.014499999999998,40.144019999999998,39.730699999999999,40.131950000000003,39.769840000000002,2286.413,8287.6550000000007,6001.2420000000002,53.683169999999997,40.53105,33,33,493586.20079999999,428527.48817902367,16210.085134685003,63,53,54500.116539299997,44,11.254864973990131,11.86200497399013,346647.35308499582,9684.721525357998,2880.5472428405551,594.13424284055509,1,-2286.4130000000005,-3683.4795253579978,-3.8731082690498041E-2,0,0.77725809810661683,0.77725809810661683,9189.0227088595293,-3187.7807088595291,0.53959490127432719,0.53959490127432719,43,0.81341162763368402]
["2013-01-20T14:00:00","2013-01-20T14:00:00",54.158059999999999,53.631259999999997,53.13879,53.502690000000001,53.530500000000004,53.21564,53.118380000000002,53.326729999999998,53.121589999999998,48.758400000000002,44.189570000000003,43.722589999999997,43.563720000000004,43.789700000000003,43.927190000000003,41.218249999999998,40.222180000000002,40.617310000000003,40.435589999999998,40.394829999999999,40.603380000000001,40.027140000000003,40.149540000000002,39.760350000000003,40.12923,39.790840000000003,2135.0410000000002,8362.4840000000004,6227.4430000000002,53.875999999999998,40.573799999999999,21,21,314100.30960000004,276067.15448616934,15337.301878009996,66,53,55619.717332399996,44,11.29304336103484,11.90018336103484,221342.06116010153,9850.2618920792429,2716.2389070300283,581.19790703002809,1,-2135.0410000000002,-3622.8188920792427,-3.8093247733793856E-2,0,0.75480855034903382,0.75480855034903382,9347.707618441822,-3120.2646184418218,0.50678591560707009,0.50678591560707009,43,0.79096207987610101]
["2013-01-20T15:00:00","2013-01-20T15:00:00",54.234270000000002,53.635829999999999,53.25047,53.539909999999999,53.546469999999999,53.22992,53.114840000000001,53.324680000000001,53.130180000000003,52.602130000000002,46.280729999999998,43.93215,43.643140000000002,43.778170000000003,44.116480000000003,42.80547,40.600940000000001,40.681539999999998,40.491599999999998,40.459049999999998,40.698920000000001,40.051360000000003,40.162930000000003,39.7761,40.16957,39.803460000000001,1410.5229999999999,8406.2450000000008,6995.7240000000002,54.305120000000002,40.556100000000001,19,19,284185.99440000003,257160.92485516396,10177.494706815001,69,54,57788.815314950007,44,11.427856602239796,12.034996602239795,202652.53584377081,10113.675263237679,1781.1729812605925,370.64998126059254,1,-1410.5210000000006,-3117.9512632376791,-3.2784661179748112E-2,0,0.7399771918165402,0.7399771918165402,9603.4618413095541,-2607.7378413095539,0.47936605097321283,0.47936605097321283,43,0.77613072134360739]
["2013-01-20T16:00:00","2013-01-20T16:00:00",54.208840000000002,53.811059999999998,53.381599999999999,53.530790000000003,53.537889999999997,53.233199999999997,53.122309999999999,53.34496,53.200220000000002,53.043469999999999,50.370100000000001,44.424799999999998,43.73565,43.806399999999996,44.122340000000001,43.487369999999999,41.2547,40.849460000000001,40.52402,40.505020000000002,40.750279999999997,40.07761,40.17895,39.785420000000002,40.17521,39.822769999999998,1109.232,8107.71,6998.4780000000001,54.96472,40.590530000000001,19,19,284185.99440000003,268515.31935727701,7978.744599120002,69,54,58270.882002449995,44,11.444295076283547,12.051435076283546,202944.04269114541,10183.393841916395,1394.3619149867363,285.12991498673637,1,-1109.232,-3184.915841916395,-3.3488780916612303E-2,0,0.72831382949317525,0.72831382949317525,9670.3640078721201,-2671.88600787212,0.45127168063721318,0.45127168063721318,43,0.76446735902024243]
["2013-01-20T17:00:00","2013-01-20T17:00:00",54.319609999999997,53.949370000000002,53.484679999999997,53.53819,53.548659999999998,53.235050000000001,53.14181,53.367060000000002,53.20814,53.073320000000002,52.606110000000001,46.14687,43.92557,43.860469999999999,44.13832,43.527949999999997,42.554340000000003,41.106830000000002,40.550040000000003,40.53978,40.773569999999999,40.106020000000001,40.220149999999997,39.812559999999998,40.178199999999997,39.853490000000001,950.16769999999997,7949.2120000000004,6999.0439999999999,55.066299999999998,40.660220000000002,27,27,403843.25520000001,383360.0603750805,6872.6199841619982,68,54,57258.49200447998,44,11.409772577352769,12.016912577352768,287524.20520074177,10036.745538317255,1204.6900913351149,254.52239133511489,1,-950.16800000000057,-3037.7015383172547,-3.1940850671128389E-2,0,0.71832299470652372,0.71832299470652372,9529.6510873167354,-2530.6070873167355,0.42466283112922004,0.42466283112922004,43,0.75447652423359091]
["2013-01-20T18:00:00","2013-01-20T18:00:00",54.464410000000001,54.04345,53.461350000000003,53.648949999999999,53.58164,53.232860000000002,53.151449999999997,53.361330000000002,53.198270000000001,53.068440000000002,53.151620000000001,48.772590000000001,44.21275,43.91198,44.164169999999999,43.546509999999998,43.21913,41.52993,40.616630000000001,40.551780000000001,40.797289999999997,40.125010000000003,40.243980000000001,39.833300000000001,40.184600000000003,39.857909999999997,541.76009999999997,7536.9229999999998,6995.1629999999996,54.773249999999997,40.598689999999998,27,27,403843.25520000001,375863.87018012156,3956.609450325001,62,50,53416.28363944,44,11.035365272104904,11.642505272104906,278089.2088296116,9680.9271505430261,717.07811255264608,175.31801255264611,1,-541.76000000000022,-2685.7641505430265,-2.8240296351789061E-2,0,0.71262649192594563,0.71262649192594563,9176.0806443307047,-2180.9176443307051,0.40173089923107025,0.40173089923107025,43,0.74878002145301281]
["2013-01-20T19:00:00","2013-01-20T19:00:00",54.759610000000002,54.001570000000001,53.546860000000002,53.700319999999998,53.585479999999997,53.225709999999999,53.162039999999998,53.37612,53.202719999999999,53.099589999999999,53.203670000000002,50.77787,44.689160000000001,43.972740000000002,44.197400000000002,43.571040000000004,43.386020000000002,42.025069999999999,40.725020000000001,40.574620000000003,40.822580000000002,40.1511,40.263710000000003,39.841709999999999,40.228740000000002,39.850740000000002,280.04390000000001,7270.4049999999997,6999.8419999999996,54.496670000000002,40.613509999999998,27,27,403843.25520000001,369074.78690979542,2087.5690496965003,61,49,50468.097939900013,44,10.873985139750591,11.48112513975059,274022.45868399827,9282.3555102002938,383.95657578475988,103.91267578475987,1,-270.5630000000001,-2282.5135102002941,-2.400019299609233E-2,0,0.70978157373002582,0.70978157373002582,8791.4899150722704,-1791.6479150722707,0.38289206408261689,0.38289206408261689,43,0.745935103257093]
["2013-01-20T20:00:00","2013-01-20T20:00:00",54.913049999999998,54.18627,53.589260000000003,53.72287,53.613329999999998,53.235669999999999,53.177219999999998,53.382750000000001,53.215290000000003,53.100059999999999,53.191099999999999,51.840980000000002,45.46284,44.14152,44.221429999999998,43.583280000000002,43.443950000000001,42.755420000000001,40.922350000000002,40.598350000000003,40.842970000000001,40.200609999999998,40.287329999999997,39.87032,40.225290000000001,39.86253,202.97040000000001,7163.9290000000001,7012.9620000000004,54.110080000000004,40.687800000000003,27,27,403843.25520000001,359035.68296698516,1527.4050323040001,54,46,48078.130469060001,44,10.609946248994946,11.217086248994946,267368.72639512771,9062.8414773758777,287.91946659459984,84.949066594599827,1,-150.96699999999964,-2049.8794773758773,-2.1554090635561136E-2,0,0.70819418459964423,0.70819418459964423,8572.302896105095,-1559.3408961050945,0.36649589280653194,0.36649589280653194,43,0.74434771412671141]
["2013-01-20T21:00:00","2013-01-20T21:00:00",54.903239999999997,54.198009999999996,53.610770000000002,53.769010000000002,53.65249,53.240470000000002,53.179780000000001,53.367910000000002,53.210680000000004,53.0976,53.301639999999999,52.428620000000002,46.268389999999997,44.213720000000002,44.242179999999998,43.60136,43.486730000000001,43.183450000000001,41.019710000000003,40.595930000000003,40.854680000000002,40.25,40.30612,39.88156,40.22927,39.870109999999997,401.55270000000002,7000.8050000000003,7402.357,53.892440000000001,40.630580000000002,15,15,224357.364,196311.21094653872,3018.2969704755001,55,46,46421.847898649998,44,10.553467013343965,11.160607013343965,147747.47770690781,8797.4592311613815,572.00102424333522,170.44832424333521,1,401.55199999999968,-1395.1022311613815,-1.4669233127217728E-2,0,0.71241642707702657,0.71241642707702657,8318.8751011744462,-916.5181011744462,0.35685888027000218,0.35685888027000218,43,0.74856995660409376]
["2013-01-20T22:00:00","2013-01-20T22:00:00",54.861879999999999,54.192120000000003,53.654600000000002,53.793039999999998,53.671590000000002,53.2361,53.204230000000003,53.395650000000003,53.242620000000002,53.109250000000003,53.333880000000001,52.563079999999999,46.278559999999999,44.214239999999997,44.244819999999997,43.607959999999999,43.493389999999998,43.149760000000001,41.049509999999998,40.577469999999998,40.843649999999997,40.296979999999998,40.293979999999998,39.867449999999998,40.233359999999998,39.874589999999998,745.72479999999996,6662.1880000000001,7407.9120000000003,53.502690000000001,40.66386,15,15,224357.364,190792.03056129219,5588.1969188960002,51,44,42767.349580020003,44,10.307154620678684,10.914294620678682,144299.1289606395,8298.5753399329424,1084.3335769281473,338.60877692814734,1,745.72400000000016,-890.66333993294211,-9.3651546671717247E-3,0,0.72025757230654486,0.72025757230654486,7836.9424807336945,-429.03048073369428,0.35234770682336114,0.35234770682336114,43,0.75641110183361204]
["2013-01-20T23:00:00","2013-01-20T23:00:00",54.893120000000003,54.194070000000004,53.642180000000003,53.782550000000001,53.703740000000003,53.241050000000001,53.226059999999997,53.42013,53.24953,53.09187,53.289589999999997,52.432290000000002,45.983440000000002,44.19388,44.238759999999999,43.617930000000001,43.503369999999997,43.005119999999998,41.019289999999998,40.584209999999999,40.866880000000002,40.271059999999999,40.304510000000001,39.859490000000001,40.221760000000003,39.875929999999997,735.19880000000001,6669.3509999999997,7404.55,52.672730000000001,40.73272,27,27,403843.25520000001,322477.04537214577,5520.3100336860025,50,44,39816.058816755001,44,10.206515605651347,10.813655605651347,257202.34715359641,7802.0865014322517,1081.7227439753106,346.52394397531054,1,735.19900000000052,-397.5365014322515,-4.1800202779645928E-3,0,0.7279880491741213,0.7279880491741213,7364.0330834924407,40.516916507559472,0.35277373445099286,0.35277373445099286,43,0.76414157870118848]
["2013-01-21","2013-01-21",54.88156,54.220170000000003,53.641379999999998,53.799979999999998,53.716369999999998,53.238979999999998,53.2331,53.420569999999998,53.233699999999999,53.074399999999997,53.343330000000002,52.337960000000002,46.055929999999996,44.246290000000002,44.235550000000003,43.624490000000002,43.505429999999997,42.987450000000003,41.031309999999998,40.576639999999998,40.87238,40.255609999999997,40.312420000000003,39.887309999999999,40.236719999999998,39.879890000000003,379.67989999999998,7018.0290000000005,7397.7079999999996,51.683529999999998,40.640549999999998,27,27,403843.25520000001,297449.59301047702,2847.9162827164992,50,45,38749.97694321,44,10.231009213763462,10.838149213763462,257819.58164772761,7575.0057757901041,556.72245488456508,177.04255488456511,1,379.67899999999918,-177.29777579010442,-1.8642522016735024E-3,0,0.73198030124003077,0.73198030124003077,7150.6631213382925,247.04487866170712,0.35537136409922082,0.35537136409922082,43,0.76813383076709796]
["2013-01-21T01:00:00","2013-01-21T01:00:00",54.740670000000001,54.248629999999999,53.64687,53.795279999999998,53.719619999999999,53.237369999999999,53.237839999999998,53.421680000000002,53.236530000000002,53.077660000000002,53.334690000000002,52.30209,46.007179999999998,44.26361,44.23706,43.632899999999999,43.505009999999999,42.985860000000002,41.053910000000002,40.5456,40.859769999999997,40.275419999999997,40.308070000000001,39.894930000000002,40.257379999999998,39.894550000000002,912.71939999999995,6485.6030000000001,7398.3220000000001,52.148769999999999,40.686230000000002,27,27,403843.25520000001,308804.12751158525,6775.1708693639994,47,44,37170.741905809991,44,10.116310298988122,10.723450298988121,254929.18974161489,7348.6757142133092,1339.4549334932287,426.73553349322879,1,912.71900000000005,49.646285786690896,5.2202119947810483E-4,5.2202119947810483E-4,0.74157736695434417,0.74157736695434417,6932.6086043999239,465.71339560007618,0.36026825137954477,0.36026825137954477,43,0.77773089648141136]
["2013-01-21T02:00:00","2013-01-21T02:00:00",54.660719999999998,54.167760000000001,53.608550000000001,53.767589999999998,53.721469999999997,53.225189999999998,53.245449999999998,53.424129999999998,53.228439999999999,53.056669999999997,53.353000000000002,51.657490000000003,45.376240000000003,44.20973,44.228459999999998,43.640459999999997,43.479559999999999,42.527900000000002,40.85575,40.553489999999996,40.872259999999997,40.290770000000002,40.314570000000003,39.912059999999997,40.268940000000001,39.904609999999998,1126.8399999999999,6270.1239999999998,7396.9629999999997,52.001350000000002,40.613140000000001,27,27,403843.25520000001,304835.65999586228,8313.8874961999991,44,42,35702.744419020004,44,9.9445575846885834,10.551697584688583,250601.05240712801,7180.3585257509558,1672.0477357385325,545.20773573853262,1,1126.8389999999999,216.60447424904396,2.7995758174737661E-3,2.7995758174737661E-3,0.75342586351511609,0.75342586351511609,6767.2038802225989,629.75911977740088,0.36689004807348002,0.36689004807348002,43,0.78957939304218328]
["2013-01-21T03:00:00","2013-01-21T03:00:00",54.624270000000003,54.104329999999997,53.594499999999996,53.724609999999998,53.72484,53.223849999999999,53.246209999999998,53.427140000000001,53.228450000000002,53.047870000000003,53.360439999999997,50.705640000000002,44.893819999999998,44.146889999999999,44.21801,43.641919999999999,43.426319999999997,42.074979999999996,40.74532,40.53349,40.866990000000001,40.229680000000002,40.363909999999997,39.958739999999999,40.320839999999997,39.916289999999996,1163.7070000000001,6226.7169999999996,7390.424,51.842010000000002,40.725670000000001,27,27,403843.25520000001,300525.98692919378,8557.889640930005,44,42,34609.151627890009,44,9.9072660705110493,10.51440607051105,249661.31299497615,6986.6199982059734,1727.5986291319134,563.89162913191331,1,1163.7070000000003,403.80400179402659,7.0454976629924894E-3,7.0454976629924894E-3,0.76566202004435069,0.76566202004435069,6583.1871806731233,807.23681932687668,0.37537798883300555,0.37537798883300555,43,0.80181554957141787]
["2013-01-21T04:00:00","2013-01-21T04:00:00",54.530990000000003,54.036769999999997,53.553609999999999,53.702840000000002,53.71152,53.214680000000001,53.241480000000003,53.422669999999997,53.208599999999997,53.026429999999998,53.270650000000003,49.324669999999998,44.551609999999997,44.08287,44.208320000000001,43.645850000000003,43.347859999999997,41.697780000000002,40.71396,40.529870000000003,40.85913,40.247709999999998,40.383139999999997,39.982570000000003,40.340719999999997,39.923960000000001,1305.7670000000001,6087.8040000000001,7393.5709999999999,51.711100000000002,40.657400000000003,27,27,403843.25520000001,297033.79599492322,9536.6888710050007,45,43,33646.379537399996,44,9.935282542225341,10.54242254222534,250367.32301468245,6773.1097519172836,1919.761985725861,613.99498572586094,1,1305.7669999999998,620.46124808271634,1.3569529014410334E-2,1.3569529014410334E-2,0.77939191030255928,0.77939191030255928,6383.0451497531758,1010.5258502468241,0.38600347487069209,0.38600347487069209,44,0.81554543982962646]
["2013-01-21T05:00:00","2013-01-21T05:00:00",54.431550000000001,53.988619999999997,53.504150000000003,53.6631,53.710790000000003,53.205269999999999,53.249450000000003,53.412559999999999,53.210479999999997,53.017330000000001,53.150489999999998,47.881169999999997,44.343600000000002,44.015909999999998,44.19361,43.642989999999998,43.15531,41.577530000000003,40.72213,40.503100000000003,40.813299999999998,40.263109999999998,40.431739999999998,40.018540000000002,40.39931,39.939819999999997,1294.412,6099.3010000000004,7393.7129999999997,51.957430000000002,40.705019999999998,27,27,403843.25520000001,302841.59830854228,9379.1346063800029,44,41,34315.917782705015,44,9.836419796390242,10.443559796390241,247875.9997014885,6977.318677533106,1907.0220264128918,612.61002641289178,1,1294.4119999999994,416.39432246689375,1.7947835673723649E-2,1.7947835673723649E-2,0.79300240490757556,0.79300240490757556,6571.6898168316366,822.02318316836318,0.39464689141790527,0.39464689141790527,44,0.82915593443464275]
["2013-01-21T06:00:00","2013-01-21T06:00:00",54.29777,53.94556,53.44462,53.642139999999998,53.711390000000002,53.186970000000002,53.24879,53.402940000000001,53.205649999999999,53.010339999999999,52.659309999999998,46.468589999999999,44.15578,43.97334,44.185890000000001,43.617570000000001,42.717939999999999,41.325490000000002,40.718040000000002,40.47475,40.75853,40.257950000000001,40.44567,40.054139999999997,40.428489999999996,39.959510000000002,1391.106,6008.13,7399.2359999999999,51.747669999999999,40.759650000000001,27,27,403843.25520000001,297059.4998104301,9973.0197577799991,41,37,33008.726301299997,44,9.5484565668743304,10.15559656687433,240619.37840318642,6913.9396655611199,2088.9281294693365,697.82212946933646,1,1391.1059999999998,485.29633443887997,2.30506338104178E-2,2.30506338104178E-2,0.80762961842846825,0.80762961842846825,6500.5981842501169,898.63781574988298,0.40409589617305847,0.40409589617305847,44,0.84378314795553544]
["2013-01-21T07:00:00","2013-01-21T07:00:00",54.196910000000003,53.906109999999998,53.403060000000004,53.618920000000003,53.709159999999997,53.174950000000003,53.244720000000001,53.399839999999998,53.199010000000001,52.991149999999998,51.804859999999998,45.456380000000003,44.026699999999998,43.938809999999997,44.176929999999999,43.575130000000001,42.05518,41.073900000000002,40.699440000000003,40.465949999999999,40.781799999999997,40.278260000000003,40.471269999999997,40.07667,40.461689999999997,39.980150000000002,1153.365,6027.4679999999998,7180.8329999999996,51.728029999999997,40.688969999999998,29,29,433757.57040000003,317973.66969580681,8198.5566987000002,41,35,33268.790450039996,44,9.4356307543463647,10.042770754346364,255389.23932268022,7051.7364055848175,1737.7866752412865,584.42167524128649,1,1153.3649999999998,129.09659441518215,2.4408059809105861E-2,2.4408059809105861E-2,0.81975703080575968,0.81975703080575968,6625.4206660331765,555.4123339668231,0.40993595063409172,0.40993595063409172,44,0.85591056033282686]
["2013-01-21T08:00:00","2013-01-21T08:00:00",54.140090000000001,53.885069999999999,53.380299999999998,53.613990000000001,53.711730000000003,53.174950000000003,53.24512,53.392330000000001,53.19838,52.995139999999999,51.459989999999998,45.300930000000001,44.01153,43.935839999999999,44.182639999999999,43.55968,41.917450000000002,41.04927,40.704360000000001,40.44585,40.774839999999998,40.293509999999998,40.484990000000003,40.095170000000003,40.485610000000001,40.00403,372.37479999999999,5999.1289999999999,6033.2820000000002,51.491869999999999,40.715850000000003,29,29,433757.57040000003,310935.30421474157,2631.9562576439998,40,34,32323.367043289985,44,9.3425448161761899,9.9496848161761893,252869.73134702441,6919.6065267620761,563.43454795890034,191.05974795890035,1,34.153000000000247,-886.32452676207595,1.5088526932565132E-2,1.5088526932565132E-2,0.82011614306850533,0.82011614306850533,6497.3650201941437,-464.0830201941435,0.40505620643932833,0.40505620643932833,44,0.85626967259557252]
["2013-01-21T09:00:00","2013-01-21T09:00:00",54.01238,53.763579999999997,53.364649999999997,53.66216,53.7316,53.188319999999997,53.254989999999999,53.392490000000002,53.195889999999999,53.027270000000001,52.367559999999997,46.245449999999998,44.150939999999999,43.97925,44.189140000000002,43.618720000000003,42.490049999999997,41.157359999999997,40.722169999999998,40.480620000000002,40.772590000000001,40.309109999999997,40.490569999999998,40.110799999999998,40.498240000000003,40.038800000000002,292.71660000000003,6092.84,5802.6760000000004,51.840409999999999,40.649360000000001,27,27,403843.25520000001,297398.43737765437,2045.149413714,41,35,34092.638540999993,44,9.4637239742481007,10.0708639742481,238484.13239505718,7204.9097445720199,432.20817075373088,139.49157075373085,1,-290.16399999999976,-1402.2337445720195,3.4430730583944955E-4,3.4430730583944955E-4,0.81706512410655974,0.81706512410655974,6770.5489078548253,-967.87290785482492,0.3948792079329026,0.3948792079329026,43,0.85321865363362692]
["2013-01-21T10:00:00","2013-01-21T10:00:00",53.903170000000003,53.708069999999999,53.353679999999997,53.670229999999997,53.733519999999999,53.207949999999997,53.25291,53.411799999999999,53.204909999999998,53.057949999999998,52.96508,47.661670000000001,44.35004,44.04683,44.214709999999997,43.679099999999998,43.010939999999998,41.481749999999998,40.760449999999999,40.51782,40.814300000000003,40.316299999999998,40.48901,40.108930000000001,40.503959999999999,40.070329999999998,374.84789999999998,6178.5590000000002,5803.71,52.028269999999999,40.728409999999997,27,27,403843.25520000001,301337.9251013844,2592.605512518001,43,35,34908.425850870008,44,9.4915423215146681,10.098682321514667,239185.14971451665,7355.6909232216949,546.29804613340661,171.45014613340663,1,-374.84900000000016,-1551.9809232216949,-1.5974475263077603E-2,0,0.8131236585668431,0.8131236585668431,6913.461526856745,-1109.7515268567449,0.38321038288400605,0.38321038288400605,43,0.84927718809391028]
["2013-01-21T11:00:00","2013-01-21T11:00:00",53.926070000000003,53.68535,53.308210000000003,53.623150000000003,53.697139999999997,53.21264,53.240519999999997,53.417149999999999,53.226999999999997,53.059690000000003,53.285179999999997,49.48883,44.690089999999998,44.15943,44.260759999999998,43.698419999999999,43.303989999999999,41.828380000000003,40.79354,40.578769999999999,40.888030000000001,40.334330000000001,40.484580000000001,40.103650000000002,40.49691,40.100749999999998,451.32859999999999,6256.4170000000004,5805.0879999999997,52.226840000000003,40.686680000000003,27,27,403843.25520000001,305575.27468716586,3119.8811600760009,45,36,36100.026603359998,44,9.5930229071745767,10.200162907174576,241742.44211779264,7526.3088502292558,650.44797458841811,199.11937458841811,1,-451.32900000000063,-1721.220850229256,-1.8098308031822032E-2,0,0.8083780204550306,0.8083780204550306,7078.3235389246602,-1273.2355389246604,0.36982255471689307,0.36982255471689307,43,0.84453154998209778]
["2013-01-21T12:00:00","2013-01-21T12:00:00",53.937309999999997,53.592239999999997,53.2697,53.599049999999998,53.670549999999999,53.214869999999998,53.22213,53.421860000000002,53.228870000000001,53.093429999999998,53.375830000000001,51.205590000000001,45.461979999999997,44.335540000000002,44.30753,43.682960000000001,43.468049999999998,42.46848,40.822609999999997,40.646169999999998,40.960070000000002,40.369199999999999,40.500059999999998,40.09816,40.487740000000002,40.125489999999999,579.10839999999996,6383.0860000000002,5803.9790000000003,52.654969999999999,40.680860000000003,27,27,403843.25520000001,315740.62972378969,3999.2704906439985,48,38,38215.88695172999,44,9.7868677450539945,10.394007745053994,246627.29697056813,7809.6257040038608,817.27281798921138,238.16441798921142,1,-579.10699999999997,-2005.6467040038606,-2.108899148371092E-2,0,0.80228882111260547,0.80228882111260547,7353.4459255940201,-1549.4669255940198,0.35353020635219268,0.35353020635219268,42,0.83844235063967265]
["2013-01-21T13:00:00","2013-01-21T13:00:00",53.895659999999999,53.550530000000002,53.208019999999998,53.604059999999997,53.680680000000002,53.252090000000003,53.261620000000001,53.481099999999998,53.277639999999998,53.161290000000001,53.442990000000002,52.619869999999999,47.259680000000003,44.565640000000002,44.386560000000003,43.710009999999997,43.587879999999998,43.257060000000003,41.00047,40.706299999999999,41.021450000000002,40.407859999999999,40.524479999999997,40.097369999999998,40.495539999999998,40.155949999999997,740.56370000000004,6544.4830000000002,5803.9189999999999,52.895299999999999,40.665489999999998,15,15,224357.364,178349.61986858016,5087.5652372635013,50,40,40018.891819115001,44,9.9700442110318228,10.577184211031822,139579.61710059491,8027.8263510274537,1020.5702461447715,280.00654614477151,1,-740.56400000000031,-2223.9073510274538,-2.3383960441664013E-2,0,0.79450193229616273,0.79450193229616273,7567.0218123602262,-1763.1028123602264,0.33499151749909345,0.33499151749909345,42,0.83065546182322991]
["2013-01-21T14:00:00","2013-01-21T14:00:00",53.914299999999997,53.524009999999997,53.175669999999997,53.610709999999997,53.725360000000002,53.335909999999998,53.324599999999997,53.545160000000003,53.349069999999998,53.19182,53.440480000000001,53.19265,49.86768,45.105989999999998,44.541629999999998,43.761429999999997,43.483550000000001,43.662419999999997,41.67154,40.804360000000003,41.083750000000002,40.446660000000001,40.552250000000001,40.104210000000002,40.498530000000002,40.15175,948.1635,6748.8429999999998,5800.6790000000001,53.360700000000001,40.781370000000003,25,25,373928.94,308206.62113361119,6524.5737884624996,53,42,42447.961607594996,44,10.174569490818991,10.78170949081899,237404.91744267696,8343.9327130052734,1282.5257706185878,334.36227061858779,1,-948.16399999999976,-2543.2537130052733,-2.6741826358258333E-2,0,0.78453216918621738,0.78453216918621738,7874.068883740737,-2073.3898837407369,0.31319021943731046,0.31319021943731046,42,0.82068569871328456]
["2013-01-21T15:00:00","2013-01-21T15:00:00",53.8583,53.558570000000003,53.248730000000002,53.629010000000001,53.741019999999999,53.355690000000003,53.316130000000001,53.554819999999999,53.404139999999998,53.276420000000002,53.502540000000003,53.41957,52.551229999999997,47.58623,44.957709999999999,43.90943,43.555120000000002,43.954839999999997,42.913499999999999,41.028680000000001,41.148470000000003,40.525919999999999,40.593269999999997,40.120980000000003,40.501370000000001,40.183430000000001,2255.0610000000001,8058.7529999999997,5803.692,52.637709999999998,40.727849999999997,23,23,344014.62479999999,267349.95838849852,15418.833008534997,55,44,47989.310002290011,44,10.48522347107809,11.092363471078089,225081.18162485797,9153.7028532889726,2941.0594921635243,685.99849216352413,1,-2255.0609999999997,-3350.0108532889726,-3.5224723384390394E-2,0,0.7608206340841922,0.7608206340841922,8652.6753522666222,-2848.9833522666222,0.28323370439742668,0.28323370439742668,42,0.79697416361125939]
["2013-01-22","2013-01-22",53.665300000000002,53.575699999999998,53.22437,51.611820000000002,47.120570000000001,44.115169999999999,43.732520000000001,43.756010000000003,43.314320000000002,41.708449999999999,40.480249999999998,39.705719999999999,39.697899999999997,39.969000000000001,40.30959,39.789940000000001,39.678719999999998,40.153019999999998,39.907240000000002,39.713659999999997,40.0886,39.619750000000003,39.799030000000002,39.41771,39.819139999999997,39.438049999999997,5808.009,5792.6930000000002,11600.7,51.50132,40.662730000000003,41,41,613243.46160000004,461617.81866816303,41315.998022625012,41,35,31392.31221143499,44,9.3716428464099337,9.9787828464099331,358618.95888070541,6699.4256451974543,8817.2369988368155,3009.2279988368155,1,5808.0070000000005,4901.2743548025464,0.33143869066356585,0.33143869066356585,1.0610700827398052,1,6291.8118761806718,5308.8881238193289,0.61966508384114682,0.61966508384114682,44,1]
["2013-01-22T03:00:00","2013-01-22T03:00:00",44.917999999999999,43.996589999999998,43.471069999999997,43.662320000000001,42.610579999999999,40.050849999999997,39.606589999999997,39.801839999999999,39.627690000000001,39.424689999999998,39.875619999999998,39.676079999999999,39.69012,39.970149999999997,40.308430000000001,39.799140000000001,39.692549999999997,40.162230000000001,39.912199999999999,39.660080000000001,40.057780000000001,39.608919999999998,39.818179999999998,39.442430000000002,39.844529999999999,39.442349999999998,6002.5159999999996,5596.7619999999997,11599.28,50.94706,40.69059,41,41,613243.46160000004,440243.74275049818,16433.838367700006,38,34,28701.510775070001,44,9.2190395174298878,9.8261795174298889,352779.38007286406,6226.5728920688025,3565.1953409310213,-2437.3206590689783,0,6002.5180000000009,5372.7071079311982,0.49689713784634792,0.49689713784634792,1.0631153287017681,1,5841.8453935547668,5757.4346064452338,0.79751559440969666,0.79751559440969666,44,1]
["2013-01-22T10:00:00","2013-01-22T10:00:00",45.248989999999999,43.757550000000002,42.326929999999997,40.263500000000001,40.296390000000002,39.71658,39.701450000000001,39.93,39.759639999999997,39.578400000000002,39.956710000000001,39.835920000000002,39.816310000000001,40.09449,40.427190000000003,39.882109999999997,39.776679999999999,40.238460000000003,40.000019999999999,39.819189999999999,40.184809999999999,39.713360000000002,39.8887,39.520130000000002,39.921529999999997,39.576160000000002,2124.9960000000001,7926.7879999999996,5801.7920000000004,51.308900000000001,40.382280000000002,45,45,673072.09200000006,492771.54305758583,6027.3705293399971,47,41,43306.50014828,44,10.142998655056349,10.75013865505635,426002.88581210654,8539.1907503983421,1188.4790157859902,-936.51698421400988,0,-2124.9959999999992,-2737.3987503983417,{"$f":"IF(AZ519>1,1+AY520*60/$BK$7,IF(AZ519<0,AY520*60/$BK$7,AZ519+AY520*60/$BK$7))","v":0.49466074423390249},0.49466074423390249,{"$f":"IF(BB519>1,1+AX520*60/$BK$7,BB519+AX520*60/$BK$7)","v":0.9661650699175941},0.9661650699175941,8056.9193640885169,-2255.1273640885165,{"$f":"IF(BF519>1,1+BE520*60/$BK$7,IF(BF519<0,BE520*60/$BK$7,BF519+BE520*60/$BK$7))","v":0.82641306949709015},0.82641306949709015,44,0.9661650699175941]
["2013-01-22T19:00:00","2013-01-22T19:00:00",55.188029999999998,54.700589999999998,53.269930000000002,52.940019999999997,52.412649999999999,50.871029999999998,48.317920000000001,43.916899999999998,43.384070000000001,41.148589999999999,40.306220000000003,40.176340000000003,39.954239999999999,40.180790000000002,40.532609999999998,39.972859999999997,39.83408,40.292430000000003,40.06953,40.014339999999997,40.319580000000002,39.807110000000002,39.945509999999999,39.536250000000003,39.938470000000002,39.582949999999997,1311.6410000000001,7114.2089999999998,5802.5690000000004,54.301929999999999,40.564839999999997,33,33,493586.20079999999,453341.33007391391,10234.131368140001,57,50,48864.264655905012,44,10.880141424766361,11.487281424766362,335105.95060906868,8982.2848340327182,1881.2496949431459,569.60869494314579,1,-1311.6399999999994,-3179.7158340327178,0.16240912323874052,0.16240912323874052,0.78242037499976758,0.78242037499976758,8507.542010863348,-2704.9730108633476,0.54016001004045433,0.54016001004045433,44,0.78242037499976758]
["2013-01-22T22:00:00","2013-01-22T22:00:00",54.95243,54.729990000000001,54.373719999999999,54.109769999999997,53.261279999999999,52.362380000000002,51.30301,50.019710000000003,45.116109999999999,43.429960000000001,42.672849999999997,40.529200000000003,40.197719999999997,40.29128,40.60201,40.027610000000003,39.89667,40.363610000000001,40.116779999999999,40.018729999999998,40.324939999999998,39.823650000000001,39.966949999999997,39.560600000000001,39.96058,39.617240000000002,835.19949999999994,6627.6130000000003,5792.4139999999998,53.482399999999998,40.572760000000002,29,29,433757.57040000003,375280.97036397317,6403.9715102024993,53,49,42780.048944659982,44,10.611822669012906,11.218962669012907,287224.60530982492,8062.7146304621238,1206.9503439597499,371.75084395975,1,-835.19900000000052,-2270.300630462124,7.994578378589251E-2,7.994578378589251E-2,0.75082519381131496,0.75082519381131496,7626.3822613154243,-1833.9682613154246,0.47195898365868555,0.47195898365868555,44,0.75082519381131496]
["2013-01-23T05:00:00","2013-01-23T05:00:00",53.851779999999998,53.604129999999998,53.270220000000002,53.580840000000002,53.6922,53.249740000000003,53.227020000000003,53.396889999999999,53.196890000000003,52.84348,51.651679999999999,49.8157,45.308950000000003,43.953569999999999,43.127839999999999,40.6541,40.18336,40.5535,40.314140000000002,40.226860000000002,40.478230000000003,39.939459999999997,40.054459999999999,39.637500000000003,40.020560000000003,39.676780000000001,1895.116,7700.9709999999995,5805.8549999999996,51.656529999999997,40.498429999999999,21,21,314100.30960000004,234801.41467726938,13431.634649999996,52,49,42964.102257549996,44,10.618098886982455,11.225238886982455,208113.24442051133,8092.616713190153,2529.9509437545116,634.83494375451164,1,-1895.116,-2286.7617131901534,-2.4044862038000547E-2,0,0.64332066421439438,0.64332066421439438,7654.9109894443436,-1849.055989444344,0.3555202411279843,0.3555202411279843,43,0.64332066421439438]
["2013-01-23T08:00:00","2013-01-23T08:00:00",53.574620000000003,53.394440000000003,53.066589999999998,53.377580000000002,53.50385,53.04945,53.053649999999998,53.259140000000002,53.079410000000003,52.90728,53.236440000000002,53.064880000000002,52.226700000000001,50.186660000000003,46.199579999999997,43.770910000000001,42.661360000000002,41.126829999999998,40.45984,40.308619999999998,40.601939999999999,39.986109999999996,40.110860000000002,39.694319999999998,40.085250000000002,39.728000000000002,1670.586,7474.6670000000004,5804.0820000000003,52.003660000000004,40.528460000000003,21,21,314100.30960000004,240601.20904836661,11565.984759660001,48,47,42886.649379200004,44,10.493763743830721,11.10090374383072,205676.29310632465,8173.7402186918962,2204.3539462110798,533.76794621107979,1,-1670.585,-2369.6582186918959,-2.4916502938197829E-2,0,0.588203719191976,0.588203719191976,7726.6951175996055,-1922.6131175996052,0.29434158939907989,0.29434158939907989,42,0.588203719191976]
["2013-01-23T15:00:00","2013-01-23T15:00:00",54.665520000000001,54.343649999999997,53.939720000000001,54.179679999999998,53.962919999999997,53.391860000000001,53.080829999999999,53.239750000000001,53.081710000000001,52.997489999999999,53.072659999999999,53.198549999999997,53.144129999999997,53.341529999999999,53.64226,53.074480000000001,52.920720000000003,53.351129999999998,52.75309,50.882719999999999,47.789439999999999,44.221870000000003,43.235810000000001,41.149940000000001,40.807250000000003,40.039569999999998,4188.9139999999998,9432.5329999999994,13148.86,55.235720000000001,40.651949999999999,5,5,74785.788,70914.857664530893,30633.423359150005,73,61,68780.945894705015,44,12.228617255009443,12.835757255009442,57066.470920135755,11249.177966794072,5010.1205590682866,821.20655906828688,1,3716.3270000000011,1899.6820332059287,1.9974793237543878E-2,1.9974793237543878E-2,0.42292928472499364,0.42292928472499364,10717.084240255745,2431.775759744256,8.3460614921862825E-2,8.3460614921862825E-2,44,0.42292928472499364]
["2013-01-24","2013-01-24",53.509900000000002,53.323560000000001,52.991779999999999,53.305660000000003,53.389899999999997,53.032530000000001,52.989640000000001,53.189749999999997,53.028480000000002,52.92304,53.106589999999997,52.826270000000001,51.580489999999998,49.34552,45.785739999999997,43.537930000000003,42.363689999999998,41.384749999999997,40.397939999999998,40.146250000000002,40.14132,39.643219999999999,39.755629999999996,39.340560000000004,39.75027,39.41048,3186.82,8414.4650000000001,11601.29,52.277119999999996,40.301430000000003,21,21,314100.30960000004,252184.33390873278,22466.156822200002,59,56,50384.512177924968,44,11.297063865267242,11.904203865267242,221420.86247744819,8919.9304843857462,3977.3443949931225,790.52439499312231,1,3186.8250000000007,2681.3595156142546,0.23817238157960335,0.23817238157960335,0.70093758913216231,0.70093758913216231,8464.9948452128374,3136.2951547871635,0.34690288247011059,0.34690288247011059,44,0.70093758913216231]
["2013-01-24T03:00:00","2013-01-24T03:00:00",53.485199999999999,53.310209999999998,52.998359999999998,53.314430000000002,53.420459999999999,53.028559999999999,52.995089999999998,53.17109,52.899749999999997,52.109009999999998,50.504530000000003,46.951050000000002,43.958629999999999,43.262230000000002,42.440249999999999,40.47128,40.017960000000002,40.248890000000003,39.822980000000001,39.803229999999999,40.114040000000003,39.618429999999996,39.732999999999997,39.319180000000003,39.726990000000001,39.39864,3622.5129999999999,7970.25,11592.76,51.647300000000001,40.262920000000001,27,27,403843.25520000001,308664.01651725324,25514.373362639999,54,52,45368.177347500001,44,10.882618847549752,11.489758847549751,274240.02655891073,8337.7315668304891,4689.0135031026321,1066.5005031026321,1,3622.51,3255.0284331695111,0.33612527485635668,0.33612527485635668,0.81000730058341497,0.81000730058341497,7897.150488441278,3695.6095115587223,0.45876924522956036,0.45876924522956036,44,0.81000730058341497]
["2013-01-24T10:00:00","2013-01-24T10:00:00",53.516300000000001,53.305250000000001,52.953360000000004,52.96772,51.754840000000002,48.802889999999998,44.917319999999997,43.624960000000002,42.443680000000001,40.859059999999999,40.355559999999997,40.059809999999999,39.782359999999997,39.972439999999999,40.294939999999997,39.688310000000001,39.562339999999999,40.050510000000003,39.826529999999998,39.796219999999998,40.098210000000002,39.61036,39.71754,39.301560000000002,39.713479999999997,39.378149999999998,2697.32,9234.1010000000006,6536.78,52.943089999999998,40.617449999999998,39,39,583329.14639999997,493760.27196083422,19067.557379000005,61,58,56908.10232482,44,11.641212289276362,12.248352289276362,423737.0858925216,9777.0061932883982,3275.8714307726582,578.55143077265802,1,-2697.3210000000008,-3240.2261932883985,0.49470709500941618,0.49470709500941618,0.97163818558658521,0.97163818558658521,9292.3686355174486,-2755.5886355174489,0.65101954017483243,0.65101954017483243,44,0.97163818558658521]
["2013-01-24T19:00:00","2013-01-24T19:00:00",56.338149999999999,56.120019999999997,55.777450000000002,56.08381,56.025970000000001,55.597149999999999,55.350740000000002,55.156660000000002,53.808410000000002,53.445030000000003,53.386339999999997,53.210619999999999,53.121470000000002,53.298279999999998,53.336539999999999,51.458730000000003,48.736179999999997,45.574289999999998,43.802100000000003,42.773260000000001,41.587609999999998,40.531880000000001,40.296120000000002,39.606990000000003,39.980449999999998,39.522060000000003,2468.4380000000001,8267.375,5798.9369999999999,54.914819999999999,40.466180000000001,17,17,254271.67920000001,244230.03900188967,20754.737783709996,66,56,59726.16255999999,44,11.615614143296,12.222754143296001,184299.75490088094,10283.771795996028,3573.5928428181614,1105.1548428181613,1,-2468.4380000000001,-4484.8347959960283,-3.0302358388819589E-2,0,0.62054167698431739,0.62054167698431739,9772.9467286648978,-3974.0097286648979,0.17701399890720931,0.17701399890720931,43,0.62054167698431739]
["2013-01-24T22:00:00","2013-01-24T22:00:00",56.055109999999999,55.819319999999998,55.482869999999998,55.794350000000001,55.878909999999998,55.485050000000001,55.430999999999997,55.612630000000003,55.424869999999999,55.197839999999999,54.368749999999999,53.621259999999999,53.437269999999998,53.484850000000002,53.723689999999998,53.079680000000003,52.75179,52.17212,49.786389999999997,46.1327,44.256079999999997,42.88232,41.658000000000001,40.222200000000001,40.375520000000002,39.738109999999999,1564.5160000000001,7360.9679999999998,5796.4530000000004,53.719639999999998,40.559289999999997,13,13,194443.04880000002,169641.34637353264,12764.103786,58,51,48436.457609400008,44,10.92640020448054,11.53354020448054,132572.70425369192,8865.9497552611847,2336.3785962673928,771.86259626739275,1,-1564.5149999999994,-3069.4967552611843,-3.2275171295999508E-2,0,0.56110029605841583,0.56110029605841583,8399.2350571741099,-2602.7820571741095,8.1279056412559864E-2,8.1279056412559864E-2,42,0.56110029605841583]
["2013-01-25T05:00:00","2013-01-25T05:00:00",55.691549999999999,55.524290000000001,55.17671,55.417749999999998,54.966790000000003,53.652349999999998,53.318899999999999,53.38073,53.097929999999998,52.881210000000003,52.853610000000003,51.625030000000002,49.68486,46.40428,44.637320000000003,43.476599999999998,43.29325,43.688330000000001,43.276519999999998,42.78284,41.48133,40.264960000000002,40.404649999999997,39.98762,40.39734,40.033709999999999,5770.5990000000002,7020.6360000000004,12791.23,52.319369999999999,40.530859999999997,25,25,373928.94,286663.34243042493,45177.557923079999,50,49,41381.418846180008,44,10.564129382654739,11.171269382654739,246494.5830097259,7834.3263978050527,8553.0110975840762,2782.412097584076,1,5770.5939999999991,4956.9036021949469,0.24928618664274749,0.24928618664274749,0.84391314253593352,0.84391314253593352,7408.5437256452824,5382.6862743547172,0.36108254640133902,0.36108254640133902,44,0.84391314253593352]
["2013-01-25T09:00:00","2013-01-25T09:00:00",53.851900000000001,53.564219999999999,53.083579999999998,53.324170000000002,53.351179999999999,52.414230000000003,51.064889999999998,48.826790000000003,45.254330000000003,43.308900000000001,43.60163,43.30124,43.209139999999998,43.305889999999998,42.980960000000003,40.706389999999999,40.432969999999997,40.735019999999999,40.016599999999997,39.789560000000002,40.141039999999997,39.683689999999999,39.852820000000001,39.453049999999998,39.871769999999998,39.495469999999997,4783.2309999999998,6814.2920000000004,11597.52,52.116410000000002,40.481769999999997,21,21,314100.30960000004,247368.64847404481,34335.060512665012,45,44,39640.917137440018,44,10.200543274386705,10.807683274386704,199929.21315575906,7772.3148799294468,6732.0062449770567,1948.7752449770569,1,4783.2280000000001,3825.2051200705537,0.4151894246779228,0.4151894246779228,1.0502947275585848,1,7335.6918649504905,4261.8281350495099,0.54521851646138664,0.54521851646138664,44,1]
["2013-01-25T14:00:00","2013-01-25T14:00:00",53.251559999999998,53.0503,52.354840000000003,52.056480000000001,50.600729999999999,47.077629999999999,43.991120000000002,43.593609999999998,43.291809999999998,43.060470000000002,43.31176,42.955640000000002,41.615160000000003,40.919069999999998,40.93338,40.12809,39.92266,40.35483,40.059759999999997,39.910179999999997,40.139000000000003,39.649650000000001,39.799320000000002,39.39864,39.811489999999999,39.446559999999998,1250.787,7051.84,5801.0529999999999,51.98621,40.015219999999999,39,39,583329.14639999997,456439.98383285705,8633.5572675000003,48,44,42208.753060800002,44,10.28810647937328,10.895246479373281,374484.38793075172,8205.3491855716547,1678.3569036361548,427.56990363615478,1,-1250.7870000000003,-2404.2961855716549,0.43447578735919451,0.43447578735919451,0.97250946366803137,0.97250946366803137,7748.1043023136708,-1947.0513023136709,0.58777914241829743,0.58777914241829743,44,0.97250946366803137]
["2013-01-25T23:00:00","2013-01-25T23:00:00",52.62133,52.403500000000001,52.068719999999999,52.404490000000003,52.486199999999997,51.946339999999999,51.942459999999997,51.788249999999998,49.797550000000001,45.830280000000002,43.834339999999997,43.485419999999998,43.334609999999998,43.516750000000002,43.688360000000003,42.239739999999998,40.919879999999999,40.893920000000001,40.349530000000001,40.150880000000001,40.44153,39.863619999999997,39.987290000000002,39.542230000000004,39.914259999999999,39.529850000000003,770.60519999999997,6571.4589999999998,5800.8540000000003,51.292589999999997,40.123620000000003,33,33,493586.20079999999,362289.79161012697,5044.1812818479984,48,43,36698.214213614985,44,10.039350104684271,10.646490104684272,309209.76382434473,7310.8744751300046,1004.8820350421745,234.27683504217453,1,-770.60499999999956,-1510.0204751300043,0.22883025617660896,0.22883025617660896,0.86893515928028908,0.86893515928028908,6893.9554449909092,-1093.1014449909089,0.42438509311490008,0.42438509311490008,44,0.86893515928028908]
["2013-01-26T02:00:00","2013-01-26T02:00:00",52.372669999999999,52.264859999999999,51.912930000000003,52.223030000000001,52.342440000000003,51.82743,51.826320000000003,51.987209999999997,51.626600000000003,49.388449999999999,45.47898,43.689190000000004,43.467739999999999,43.574480000000001,43.849960000000003,43.050939999999997,41.806339999999999,41.236400000000003,40.598959999999998,40.207230000000003,40.523699999999998,39.956229999999998,40.052410000000002,39.597479999999997,39.971080000000001,39.57038,710.86350000000004,6507.6,5796.7359999999999,50.70881,40.064300000000003,31,31,463671.88560000004,322269.59486115311,4550.3403387075005,47,43,34635.10663799999,44,9.9689981363558005,10.5761381363558,288434.27579784358,6948.5631683869424,912.89822236257169,202.03472236257164,1,-710.86400000000049,-1151.8271683869425,0.18829896883490177,0.18829896883490177,0.84592262763338655,0.84592262763338655,6549.6698684259327,-752.93386842593281,0.39667668595207656,0.39667668595207656,44,0.84592262763338655]
["2013-01-26T09:00:00","2013-01-26T09:00:00",52.117359999999998,51.981400000000001,51.648879999999998,51.97954,52.116239999999998,51.625340000000001,51.596600000000002,51.605409999999999,51.245899999999999,50.89705,50.9893,49.534559999999999,46.60474,44.093760000000003,44.073689999999999,43.377180000000003,43.140039999999999,43.180700000000002,41.766440000000003,40.784709999999997,40.808540000000001,40.228430000000003,40.225909999999999,39.742089999999997,40.10369,39.663629999999998,814.69709999999998,6615.6279999999997,5800.9309999999996,51.511800000000001,40.127319999999997,25,25,373928.94,276455.31570008356,5073.0088575914997,46,45,37657.742326720014,44,10.193764013341154,10.800904013341153,237852.78642021332,7388.3880924524456,995.316126791275,180.61902679127502,1,-814.69700000000012,-1587.457092452446,8.5493800790414701E-2,8.5493800790414701E-2,0.79194070363992841,0.79194070363992841,6973.0723058376598,-1172.1413058376602,0.32408357545672406,0.32408357545672406,44,0.79194070363992841]
["2013-01-26T18:00:00","2013-01-26T18:00:00",51.809989999999999,51.649439999999998,51.347290000000001,51.69529,51.838230000000003,51.391489999999997,51.394039999999997,51.634700000000002,51.444299999999998,51.2836,51.602719999999998,51.492820000000002,51.45187,51.670769999999997,51.883479999999999,50.736330000000002,46.932110000000002,44.585209999999996,43.651009999999999,43.355139999999999,43.425469999999997,42.149279999999997,41.361739999999998,40.29842,40.539079999999998,39.961500000000001,1122.692,6925.4160000000002,5802.7240000000002,52.478230000000003,40.215449999999997,17,17,254271.67920000001,198597.35720404427,6651.1024675399985,52,49,42462.426408240019,44,10.600991740520985,11.208131740520985,168201.19499337036,8011.0290522975556,1254.8075935418342,132.11559354183419,1,-1122.692,-2208.3050522975554,-2.321990525468403E-2,0,0.6820349176868763,0.6820349176868763,7577.0748223318524,-1774.3508223318522,0.15477289593324767,0.15477289593324767,42,0.6820349176868763]
["2013-01-26T19:00:00","2013-01-26T19:00:00",51.805410000000002,51.693359999999998,51.377450000000003,51.716459999999998,51.850700000000003,51.394910000000003,51.404530000000001,51.631639999999997,51.43412,51.287379999999999,51.628039999999999,51.515680000000003,51.475059999999999,51.687899999999999,51.853819999999999,51.020150000000001,48.558480000000003,45.466169999999998,43.80124,43.423999999999999,43.49879,42.479190000000003,41.634230000000002,40.538809999999998,40.677070000000001,40.015749999999997,1049.3050000000001,6847.9170000000004,5798.6120000000001,52.376489999999997,40.215510000000002,17,17,254271.67920000001,196122.33363556754,6185.4745931500029,51,49,41638.690839329982,44,10.572902357621153,11.180042357621153,167755.5133169741,7876.4920796447168,1170.0618021297421,120.75680212974203,1,-1049.3050000000003,-2077.8800796447167,-2.1848511612898525E-2,0,0.67100167630660745,0.67100167630660745,7448.7536822158709,-1650.1416822158708,0.13742197175816925,0.13742197175816925,42,0.67100167630660745]
["2013-01-27T04:00:00","2013-01-27T04:00:00",51.848619999999997,51.680990000000001,51.36477,51.702170000000002,51.659770000000002,49.144410000000001,46.46866,44.644779999999997,43.551920000000003,42.987229999999997,42.879240000000003,42.315150000000003,41.858690000000003,41.817590000000003,41.635579999999997,40.711950000000002,40.447429999999997,40.890889999999999,40.650570000000002,40.554499999999997,40.874659999999999,40.402999999999999,40.551690000000001,40.152740000000001,40.577330000000003,40.206209999999999,7531.6589999999997,6466.2389999999996,13997.9,51.615969999999997,39.979230000000001,39,39,583329.14639999997,415312.28303316102,43843.331029094996,51,50,37622.971010429988,44,10.496813311455664,11.103953311455662,382081.26209083514,7168.4557768347231,8353.6459548626462,821.9869548626466,1,7531.6610000000001,6829.4442231652765,0.44034611128493312,0.44034611128493312,1.0791939748760917,1,6776.5002166598342,7221.3997833401654,0.56811256633295992,0.56811256633295992,44,1]
["2013-01-27T07:00:00","2013-01-27T07:00:00",47.18909,44.9876,43.656269999999999,43.543619999999997,43.183450000000001,42.227420000000002,41.72175,41.661140000000003,41.020899999999997,40.506210000000003,40.633600000000001,40.46893,40.40916,40.703719999999997,41.049979999999998,40.488250000000001,40.395330000000001,40.862290000000002,40.632599999999996,40.563299999999998,40.87229,40.388280000000002,40.532989999999998,40.125970000000002,40.543089999999999,40.179259999999999,5955.1450000000004,8041.348,13996.49,51.578220000000002,40.026879999999998,49,49,732900.72239999997,521308.69556118321,20872.277037675005,53,52,46444.17240316001,44,10.919310278947757,11.526450278947758,499372.87243275472,8506.7959819227017,3823.0028279197081,-2132.1421720802923,0,5955.1419999999998,5489.6940180772981,0.63067683330499713,0.63067683330499713,1.0626171791231123,1,8058.7121410634109,5937.7778589365889,0.77189061624903743,0.77189061624903743,44,1]
["2013-01-27T14:00:00","2013-01-27T14:00:00",54.170119999999997,53.324309999999997,51.402589999999996,47.556609999999999,44.307949999999998,43.569249999999997,43.136200000000002,42.844000000000001,41.872430000000001,41.454259999999998,41.234990000000003,40.836289999999998,40.625010000000003,40.798099999999998,41.125210000000003,40.519509999999997,40.377929999999999,40.907670000000003,40.708350000000003,40.756210000000003,41.002389999999998,40.461399999999998,40.525779999999997,40.095050000000001,40.516689999999997,40.23659,3008.5320000000002,10209.18,7200.65,53.994210000000002,41.166690000000003,43,43,643157.77679999999,552135.18629937514,20959.735438979995,69,63,65479.2303168,44,12.237722753802881,12.844862753802881,491137.08130847162,10701.211595343959,3425.4306721349344,416.89867213493426,1,-3008.5300000000007,-3500.5615953439592,0.48775637015342455,0.48775637015342455,0.85685889093268752,0.85685889093268752,10195.395867100886,-2994.7458671008862,0.66411514798876692,0.66411514798876692,44,0.89253360761436329]
["2013-01-27T23:00:00","2013-01-27T23:00:00",55.413130000000002,55.100270000000002,54.75461,55.09111,55.125990000000002,54.791600000000003,54.663609999999998,54.754989999999999,54.085349999999998,53.477440000000001,53.043979999999998,51.112189999999998,46.193390000000001,44.466909999999999,44.407159999999998,43.439770000000003,42.577759999999998,42.367019999999997,41.888100000000001,41.472589999999997,41.455730000000003,40.972389999999997,40.76585,40.234749999999998,40.62809,40.3429,2998.0410000000002,9499.0300000000007,6500.9889999999996,53.515639999999998,40.816459999999999,27,27,403843.25520000001,331950.66537380265,22590.583709715003,68,64,60314.945897699989,44,12.122467655111571,12.729607655111568,305483.9922511708,9950.9353398468411,3727.0602574368495,729.01925743684933,1,-2998.0410000000011,-3449.9463398468415,0.11837440121344156,0.11837440121344156,0.56998651864297012,0.56998651864297012,9476.3244134206379,-2975.3354134206384,0.34205048890820816,0.34205048890820816,44,0.60566123532464589]
["2013-01-28T02:00:00","2013-01-28T02:00:00",55.136539999999997,54.856949999999998,54.519190000000002,54.873420000000003,54.913440000000001,54.594810000000003,54.498910000000002,54.721609999999998,54.565959999999997,54.486109999999996,54.63411,54.386710000000001,53.676119999999997,53.196539999999999,50.859310000000001,45.976880000000001,43.990670000000001,44.206969999999998,43.594110000000001,42.8705,42.38503,41.700029999999998,41.490549999999999,40.795099999999998,40.95111,40.463909999999998,2954.0419999999999,9452.0959999999995,6498.0540000000001,53.549930000000003,40.849260000000001,21,21,314100.30960000004,256484.15104614393,21671.782635229996,67,64,60023.976052160011,44,12.112545583378658,12.719685583378656,237404.18942968099,9911.0423385365702,3578.4026546771347,624.36065467713479,1,-2954.0419999999995,-3412.9883385365702,1.0651844943226706E-2,1.0651844943226706E-2,0.47671876668897339,0.47671876668897339,9437.9653740177109,-2939.9113740177108,0.24925313755786588,0.24925313755786588,44,0.51239348337064916]
["2013-01-28T09:00:00","2013-01-28T09:00:00",55.066839999999999,54.735320000000002,54.40401,54.764330000000001,54.803919999999998,54.496949999999998,54.398339999999997,54.632820000000002,54.482320000000001,54.414209999999997,54.55339,54.61842,54.587539999999997,54.774819999999998,54.242420000000003,52.864570000000001,51.021239999999999,46.748049999999999,44.572249999999997,44.242460000000001,44.110019999999999,43.003360000000001,43.529209999999999,41.527470000000001,41.494660000000003,40.572369999999999,1020.071,11017.56,12037.63,54.478070000000002,40.579689999999999,5,5,74785.788,64892.800888755854,7392.6942536849992,69,65,76563.117776400017,44,12.737377316175241,13.34451731617524,59440.667497753806,12021.80258555617,1160.7875106749002,140.71651067490018,1,1020.0699999999997,15.827414443829184,1.0048067188576586E-2,1.0048067188576586E-2,0.44909548089671825,0.44909548089671825,11474.842583267638,562.78741673236073,0.20224290475105777,0.20224290475105777,44,0.48477019757839401]
["2013-01-28T18:00:00","2013-01-28T18:00:00",55.028579999999998,54.726460000000003,54.399360000000001,54.786569999999998,54.81447,54.539090000000002,54.37086,54.605289999999997,54.430860000000003,54.305199999999999,54.30688,54.267270000000003,53.882980000000003,53.372019999999999,52.091360000000002,47.675800000000002,44.566980000000001,44.474110000000003,43.879350000000002,43.548430000000003,43.35745,42.789360000000002,41.50788,39.960120000000003,39.685809999999996,39.527569999999997,3041.5509999999999,11643.64,14685.19,54.07967,39.908659999999998,19,19,284185.99440000003,258055.38776835424,23573.556233255003,77,66,82501.069438200007,44,13.000708467842621,13.607848467842622,230544.2420635134,12691.780550616484,3626.5033235018573,584.95232350185734,1,3041.5500000000011,1993.4094493835164,6.3141927944795673E-2,6.3141927944795673E-2,0.55711505736993294,0.55711505736993294,12125.512660309578,2559.6773396904227,0.29722109839276667,0.29722109839276667,44,0.59278977405160882]
["2013-01-28T19:00:00","2013-01-28T19:00:00",55.025829999999999,54.730200000000004,54.409770000000002,54.802750000000003,54.81935,54.516330000000004,54.352240000000002,54.568339999999999,54.379040000000003,54.25159,54.13785,53.965380000000003,53.295909999999999,51.805329999999998,48.48809,44.763689999999997,43.895290000000003,44.119660000000003,43.38523,43.023380000000003,43.214280000000002,41.806229999999999,41.08549,39.380600000000001,39.655009999999997,39.487119999999997,3326.7730000000001,11356.87,14683.64,54.403320000000001,39.924230000000001,21,21,314100.30960000004,292355.42157466454,25846.880441415004,76,67,82218.571424149995,44,13.051922285563515,13.659062285563515,255815.84064008793,12598.691537581462,3960.6243242811443,633.85132428114412,1,3326.7699999999986,2084.948462418537,8.5064762250630671E-2,8.5064762250630671E-2,0.59209540762713853,0.59209540762713853,12038.684604439961,2644.9553955600386,0.32503229849117321,0.32503229849117321,44,0.6277701243088144]
["2013-01-29T04:00:00","2013-01-29T04:00:00",54.916080000000001,54.583979999999997,54.107590000000002,54.175060000000002,53.706159999999997,52.209110000000003,49.213099999999997,45.495570000000001,44.175440000000002,43.768000000000001,43.372900000000001,42.656489999999998,42.623420000000003,42.322519999999997,40.495359999999998,39.773299999999999,39.60331,40.147350000000003,39.924100000000003,39.985909999999997,40.225859999999997,39.783360000000002,39.825499999999998,39.412869999999998,39.691969999999998,39.55162,1172.623,11724.16,12896.06,52.337960000000002,39.943829999999998,37,37,553414.83120000002,441551.77202858648,9008.3595892900012,70,66,72655.381590400022,44,12.664970512232642,13.27211051223264,437360.50913444482,11473.438729324285,1422.563057780379,249.94005778037899,1,1171.8999999999996,1422.6212706757142,0.31155273243384074,0.31155273243384074,0.85745164224553727,0.85745164224553727,10948.579959974715,1947.4800400252843,0.60226162015029749,0.60226162015029749,44,0.89312635892721315]
["2013-01-29T09:00:00","2013-01-29T09:00:00",54.889060000000001,54.502780000000001,53.973660000000002,53.995820000000002,53.240459999999999,51.255200000000002,47.094450000000002,44.793680000000002,44.042610000000003,43.579120000000003,43.127409999999998,42.266060000000003,42.474310000000003,41.202010000000001,40.425510000000003,39.832149999999999,39.685789999999997,40.21311,39.985720000000001,40.045430000000003,40.25318,39.793979999999998,39.784660000000002,39.331180000000003,39.732259999999997,39.638759999999998,141.54769999999999,12406.74,12393.2,53.312370000000001,39.969670000000001,37,37,553414.83120000002,472191.94277078513,1079.322444655,72,67,82769.704899000004,44,13.070715937055901,13.677855937055901,451372.15056766191,12664.907614485786,165.15123576285305,23.603535762853056,1,-13.539999999999054,-271.7076144857856,0.31250546811011004,0.31250546811011004,0.86309189079938009,0.86309189079938009,12102.730907519097,290.46909248090378,0.63238207039893735,0.63238207039893735,44,0.89876660748105597]
["2013-01-29T13:00:00","2013-01-29T13:00:00",54.7744,54.341540000000002,53.968269999999997,54.014789999999998,53.373739999999998,51.573599999999999,47.638420000000004,45.007060000000003,44.142609999999998,43.717320000000001,43.227170000000001,42.562359999999998,42.280479999999997,41.592669999999998,40.416029999999999,39.783650000000002,39.655540000000002,40.159619999999997,39.928620000000002,39.990569999999998,40.202730000000003,39.754460000000002,39.750599999999999,39.257899999999999,39.630229999999997,39.745780000000003,692.77629999999999,13078.63,12385.85,53.659010000000002,39.947620000000001,37,37,553414.83120000002,480466.76071035879,5205.7358788529991,76,68,89663.098297850011,44,13.366627651956687,13.973767651956686,461590.89510898187,13415.964090946243,778.91537258329356,86.139072583293569,1,-692.77999999999884,-1030.1140909462429,0.2859143804148353,0.2859143804148353,0.84876493815674015,0.84876493815674015,12833.059849151688,-447.2098491516881,0.62990085274123242,0.62990085274123242,44,0.88443965483841602]
["2013-01-29T22:00:00","2013-01-29T22:00:00",45.754469999999998,44.633369999999999,43.891550000000002,43.706949999999999,43.083280000000002,42.096260000000001,41.31776,40.469790000000003,39.893540000000002,39.667470000000002,39.913640000000001,39.86356,39.815860000000001,40.088459999999998,40.374859999999998,39.787379999999999,39.704410000000003,40.158470000000001,39.871560000000002,39.84057,40.137320000000003,39.658259999999999,39.750160000000001,39.325830000000003,39.745570000000001,39.444879999999998,5257.9939999999997,7153.5029999999997,12411.5,52.417610000000003,40.323540000000001,51,51,762815.03760000004,617497.51581801835,16587.89318123,57,46,43257.483013605008,44,10.445562170763932,11.052702170763931,497205.19056277216,8282.4614523243781,3176.0651863540347,-2081.928813645965,0,5257.9970000000003,4129.0385476756219,0.49637621392726156,0.49637621392726156,1.0552868327871587,1,7827.4945520612309,4584.0054479387691,0.88775930836455186,0.88775930836455186,44,1]
["2013-01-30T01:00:00","2013-01-30T01:00:00",42.643709999999999,42.011060000000001,40.553179999999998,40.1937,40.207000000000001,39.714619999999996,39.637329999999999,39.89884,39.683190000000003,39.496850000000002,39.776809999999998,39.682870000000001,39.632759999999998,39.914479999999998,40.261659999999999,39.713189999999997,39.595309999999998,40.09695,39.849580000000003,39.806910000000002,40.10286,39.628509999999999,39.734520000000003,39.324930000000002,39.735999999999997,39.431269999999998,5293.66,7101.2610000000004,12394.92,50.929049999999997,39.952419999999996,51,51,762815.03760000004,547290.39974023122,8502.7825652000029,53,42,38973.957265215002,44,10.056105942743834,10.663245942743831,478667.20716820017,7751.3020421860947,1691.0686131614077,-3602.5913868385924,0,5293.6589999999997,4643.6179578139054,0.63782496224008878,0.63782496224008878,1.0556618118962864,1,7309.9612396610164,5084.9587603389837,1.0432425806032908,1,44,1]
["2013-01-30T08:00:00","2013-01-30T08:00:00",43.95055,41.944189999999999,40.171460000000003,40.178019999999997,40.193919999999999,39.627279999999999,39.597470000000001,39.806469999999997,39.607309999999998,39.442079999999997,39.826929999999997,39.640590000000003,39.633839999999999,39.959290000000003,40.265009999999997,39.736060000000002,39.692410000000002,40.212389999999999,39.939929999999997,39.774349999999998,40.111640000000001,39.5916,39.745609999999999,39.365259999999999,39.77608,39.615270000000002,117.5849,6201.4030000000002,6203.6390000000001,50.9542,39.988259999999997,49,49,732900.72239999997,518563.34326636506,254.88173263599987,43,37,34002.106606910012,44,9.5823308352956325,10.189470835295632,438228.78474735137,{"$f":"AO710*1000/(500*AQ710)","v":7096.8342027320514},53.198274410891031,{"$f":"AU710-AC710","v":-64.386625589108974},0,{"$f":"AE710-AD710","v":2.2359999999998763},{"$f":"AE710-AT710","v":-893.19520273205126},0.59223862266576821,0.59223862266576821,0.97533823111773332,0.97533823111773332,{"$f":"AO710*1000/(500*AR710)","v":6673.9690719029368},{"$f":"AE710-BD710","v":-470.33007190293665},0.96988693360923384,0.96988693360923384,44,1]
["2013-01-30T17:00:00","2013-01-30T17:00:00",50.364229999999999,49.956040000000002,48.359160000000003,45.831910000000001,42.512360000000001,40.722999999999999,40.008510000000001,40.098619999999997,39.786960000000001,39.692549999999997,39.876829999999998,39.842610000000001,39.767270000000003,40.030079999999998,40.391399999999997,39.85539,39.757280000000002,40.24644,39.997369999999997,39.922110000000004,40.184190000000001,39.691890000000001,39.8108,39.400979999999997,39.770699999999998,39.477310000000003,1596.24,7790.2020000000002,6193.9610000000002,50.560040000000001,39.930799999999998,43,43,643157.77679999999,444783.70483089902,8689.0685903999965,52,39,41401.963353240011,44,9.9563599503454849,10.563499950345484,399579.0446347291,8316.6867328462486,1745.4307867000102,149.19078670001022,1,-1596.241,-2122.7257328462483,0.44567408799831265,0.44567408799831265,0.94221543748656078,0.94221543748656078,7838.6829266536688,-1644.7219266536686,0.86579325916125505,0.86579325916125505,44,0.9517367334891258]
["2013-01-30T19:00:00","2013-01-30T19:00:00",50.690109999999997,50.512450000000001,49.641120000000001,48.410400000000003,45.166319999999999,41.824300000000001,40.494540000000001,40.269979999999997,39.880760000000002,39.636800000000001,40.038020000000003,39.884830000000001,39.828209999999999,40.056080000000001,40.41798,39.872300000000003,39.764400000000002,40.249650000000003,39.993029999999997,39.84046,40.154490000000003,39.684350000000002,39.80621,39.460889999999999,39.779089999999997,39.485489999999999,290.82760000000002,6435.259,6198.5959999999995,51.265000000000001,39.916249999999998,41,41,{"$f":"3.1416*(138/2)^2*AI720","v":613243.46160000004},{"$f":"62.4*AJ720*(AF720-AB720)/1000","v":450759.34727315337},1629.3063717560001,49,37,36516.072788125006,44,9.6680570820750624,10.275197082075064,369961.66221818584,{"$f":"AO720*1000/(500*AQ720)","v":7553.9630099675705},337.04939015653821,46.221790156538191,{"$f":"AJ720/$BK$7","v":0.10746896178429931},-236.66300000000047,{"$f":"AE720-AT720","v":-1355.367009967571},0.43142266312201311,{"$f":"IF(AZ720>1,1,IF(AZ720<0,0,AZ720))","v":0.43142266312201311},0.93972697130677652,{"$f":"IF(BB720>1,1,BB720)","v":0.93972697130677652},7107.6150649853298,-909.01906498533026,{"$f":"IF(BF719>1,1+BE720*60/$BK$7,IF(BF719<0,BE720*60/$BK$7,BF719+BE720*60/$BK$7))","v":0.85623509755595495},0.85623509755595495,44,0.94924826730934153]
["2013-01-31T04:00:00","2013-01-31T04:00:00",50.620559999999998,50.40663,50.00271,49.985120000000002,48.355930000000001,44.505490000000002,42.034480000000002,40.739460000000001,40.089970000000001,39.671280000000003,40.085650000000001,39.923580000000001,39.864960000000004,40.07047,40.398620000000001,39.875419999999998,39.794260000000001,40.28622,39.981520000000003,39.74324,40.101329999999997,39.654499999999999,39.867930000000001,39.483440000000002,40.031750000000002,39.575069999999997,121.3425,5752.1009999999997,5800.7389999999996,49.754570000000001,39.908459999999998,39,39,583329.14639999997,370531.14045659726,670.14368516249999,34,30,28317.909588555009,44,8.9625707169697275,9.5697107169697269,326235.23249488621,6319.1489323343112,149.54273864610079,28.200238646100786,0.10222657340457739,48.63799999999992,-518.40993233431163,0.34294857396579309,0.34294857396579309,0.92451145423712922,0.92451145423712922,5918.2373273498379,-117.49832734983829,0.80716931888293342,0.80716931888293342,44,0.93403275023969423]
["2013-01-31T07:00:00","2013-01-31T07:00:00",50.613520000000001,50.277940000000001,49.993310000000001,50.274050000000003,49.143990000000002,45.809190000000001,42.550460000000001,41.119770000000003,40.168300000000002,39.753100000000003,40.134180000000001,39.934690000000003,39.900460000000002,40.123579999999997,40.397869999999998,39.899419999999999,39.818950000000001,40.297530000000002,40.003770000000003,39.715130000000002,40.101930000000003,39.647329999999997,39.917720000000003,39.45628,39.987760000000002,39.579819999999998,157.2021,5940.4430000000002,5800.2020000000002,50.097470000000001,39.998890000000003,39,39,583329.14639999997,382839.71210995916,867.26040538500024,36,31,29995.019435469996,44,9.0806071627495282,9.6877471627495275,330531.72828252142,6606.3907176858356,191.01374827504409,33.811648275044092,0.10222657340457739,-140.24099999999999,-806.1887176858354,0.31973592089227437,0.31973592089227437,0.92115257219021507,0.92115257219021507,6192.3621522254844,-392.16015222548413,0.79685774244907148,0.79685774244907148,44,0.93067386819278008]
["2013-01-31T14:00:00","2013-01-31T14:00:00",51.923450000000003,51.46922,50.303809999999999,50.363370000000003,50.348399999999998,49.988860000000003,49.861370000000001,49.20955,46.857379999999999,43.502409999999998,41.570149999999998,40.504429999999999,40.17474,40.283299999999997,40.598190000000002,39.939610000000002,39.760829999999999,40.286140000000003,40.09487,40.157080000000001,40.417610000000003,39.824890000000003,39.863019999999999,39.427219999999998,39.824620000000003,39.653950000000002,3129.9520000000002,null,5796.701,52.092880000000001,40.038679999999999,33,33,493586.20079999999,383116.29412474972,19201.473032000002,67,47,53801.824269200006,44,10.865971207579722,11.473111207579722,334669.51105233131,9902.8100187988221,3534.2396303435307,404.28763034353051,8.6499408265411637E-2,5796.701,-4106.109018798822,0.12783941273318936,0.12783941273318936,0.89234270074696054,0.89234270074696054,9378.7680247805456,-3582.0670247805456,0.63992124810690065,0.63992124810690065,44,0.90186399674952555]
["2013-02-01T06:00:00","2013-02-01T06:00:00",51.06521,51.11777,50.831359999999997,51.247329999999998,51.37585,50.823300000000003,50.94952,51.099179999999997,50.913960000000003,50.695239999999998,51.26294,50.952120000000001,51.005040000000001,51.199249999999999,51.066330000000001,49.491779999999999,47.711069999999999,44.550040000000003,41.541229999999999,40.373040000000003,40.736559999999997,40.312269999999998,40.392200000000003,39.82358,40.191879999999998,39.815890000000003,133.3836,5864.7870000000003,5800.9080000000004,49.529670000000003,39.984670000000001,15,15,224357.364,135991.9438972174,750.2373995759998,30,26,27989.695957500004,44,8.7079906321507519,9.3151306321507512,121910.99381548066,6428.5085135850541,172.3101071804212,38.926507180421197,3.9317912847914381E-2,-63.878999999999905,-627.6005135850537,-6.5990993626873192E-3,0,0.99932832453278109,0.99932832453278109,6009.5122790645228,-208.60427906452242,0.52037788583748068,0.52037788583748068,43,0.99932832453278109]
["2013-02-01T13:00:00","2013-02-01T13:00:00",51.398650000000004,51.069040000000001,50.74492,51.176099999999998,51.250149999999998,50.838349999999998,50.823210000000003,51.073540000000001,50.888890000000004,50.76173,51.073999999999998,50.991329999999998,50.950270000000003,51.200499999999998,51.491720000000001,50.881410000000002,49.298189999999998,48.14181,44.442830000000001,41.515749999999997,41.003019999999999,40.51482,40.35528,39.983829999999998,40.260899999999999,39.90061,1063.8800000000001,6867.6620000000003,5803.7830000000004,52.258150000000001,40.104909999999997,13,13,194443.04880000002,149937.07580392022,6116.2673976000015,51,41,41732.172262440014,44,10.089314074149206,10.696454074149205,122416.13210600722,8272.5489474782025,1212.4248194971101,148.54481949710998,3.4075524468192467E-2,-1063.8789999999999,-2468.7659474782022,-2.595860175060179E-2,0,0.97434122746823593,0.97434122746823593,7802.9919023906778,-1999.2089023906774,0.4629438419842109,0.4629438419842109,43,0.97434122746823593]
["2013-02-01T16:00:00","2013-02-01T16:00:00",51.331330000000001,51.060929999999999,50.742820000000002,51.100290000000001,51.19847,50.822580000000002,50.75367,50.985289999999999,50.81803,50.696469999999998,50.912799999999997,50.915390000000002,50.876849999999997,51.128860000000003,51.450499999999998,50.902889999999999,49.762300000000003,49.071210000000001,46.380899999999997,42.773510000000002,41.291559999999997,40.609409999999997,40.40607,39.92024,40.32911,39.969099999999997,246.4085,7421.4369999999999,7201.9759999999997,53.289520000000003,39.954810000000002,13,13,194443.04880000002,161619.93594842142,1399.8750254775005,58,45,49481.35508913501,44,10.596949208539504,11.204089208539505,128575.3941942393,9338.7925364897801,264.20340381539569,17.794903815395685,3.4075524468192467E-2,-219.46100000000024,-2136.8165364897804,-2.2468217184176076E-2,0,0.96591361878149173,0.96591361878149173,8832.7313658697803,-1630.7553658697807,0.4139237378419065,0.4139237378419065,43,0.96591361878149173]
["2013-02-02T01:00:00","2013-02-02T01:00:00",51.45946,51.238930000000003,50.951740000000001,51.315489999999997,51.455089999999998,51.037759999999999,51.030679999999997,51.283329999999999,51.1145,50.981110000000001,51.294989999999999,51.213030000000003,51.18862,51.393720000000002,51.628830000000001,50.848509999999997,50.312869999999997,50.321089999999998,49.056269999999998,47.100479999999997,43.432259999999999,41.198929999999997,40.928359999999998,40.093559999999997,40.3765,39.782409999999999,958.30669999999998,6382.625,7340.9319999999998,51.073390000000003,39.879460000000002,9,9,134614.4184,94843.551246040428,{"$f":"500*AC767*(C767-AB767)/1000","v":5595.0976256174999},52,45,35723.32873312501,44,{"$f":"19.5286-0.30357*AP767+0.0000341*AO767+0.060847*AN767","v":10.127800509799565},{"$f":"19.5286-0.30357*42+0.0000341*AO767+0.060847*AN767","v":10.734940509799564},{"$f":"62.4*AJ767*AQ767/1000","v":85072.913658588455},7054.5087649701336,{"$f":"AL767*1000/(500*AQ767)","v":1104.8988613477795},146.59216134777955,2.3590747708748628E-2,958.30699999999979,286.42323502986619,3.0116855337599642E-3,3.0116855337599642E-3,0.94973616494948021,0.94973616494948021,6655.52430411969,685.4076958803098,0.32576513321232903,{"$f":"IF(BF767>1,1,IF(BF767<0,0,BF767))","v":0.32576513321232903},42,0.94973616494948021]
["2013-02-02T02:00:00","2013-02-02T02:00:00",51.460859999999997,51.252330000000001,50.946289999999998,51.31427,51.464300000000001,51.047289999999997,51.052680000000002,51.296019999999999,51.11683,50.978920000000002,51.29045,51.19914,51.175310000000003,51.384410000000003,51.644550000000002,50.728209999999997,50.208190000000002,50.090600000000002,48.812100000000001,46.469099999999997,42.83728,40.999049999999997,40.713749999999997,40.034309999999998,40.438839999999999,39.717529999999996,1511.316,6336.6559999999999,7847.9719999999998,50.91534,40.208060000000003,11,11,164528.73360000001,114963.35749974921,8873.9412611400003,51,44,33924.175027839985,44,10.005602368449345,10.612742368449343,102723.44700297462,6781.0360193431343,1773.79450718973,262.47850718972995,2.8833136088470546E-2,1511.3159999999998,1066.9359806568655,1.4230313303456182E-2,1.4230313303456182E-2,0.96562736362847479,0.96562736362847479,6393.1025271457229,1454.8694728542769,{"$f":"IF(BF767>1,1+BE768*60/$BK$7,IF(BF767<0,BE768*60/$BK$7,BF767+BE768*60/$BK$7))","v":0.34106280745459966},0.34106280745459966,44,0.96562736362847479]
["2013-02-02T11:00:00","2013-02-02T11:00:00",50.406590000000001,49.35519,47.533560000000001,44.395670000000003,41.908920000000002,40.717529999999996,39.917459999999998,40.025489999999998,39.84939,39.73265,39.956299999999999,39.95673,39.873570000000001,40.148200000000003,40.490819999999999,39.952930000000002,39.833440000000003,40.287120000000002,40.079140000000002,40.036529999999999,40.343020000000003,39.863190000000003,39.976019999999998,39.563800000000001,39.98113,39.636429999999997,981.91579999999999,8381.15,7399.2340000000004,53.064929999999997,40.154220000000002,43,43,643157.77679999999,538926.59843934921,5287.695136264002,60,50,54103.298558249982,44,11.058792480836324,11.665932480836325,443823.01929059625,9784.6665722329217,956.28797545970747,-25.627824540292522,0.11271135016402123,-981.91599999999926,-2385.4325722329213,0.48472858492338261,0.48472858492338261,0.98967534106561195,0.98967534106561195,9275.434886516905,-1876.2008865169046,0.85471804257205486,0.85471804257205486,44,0.98967534106561195]
["2013-02-02T13:00:00","2013-02-02T13:00:00",50.790039999999998,49.796959999999999,48.40757,46.566670000000002,42.726939999999999,41.123179999999998,40.39819,40.045909999999999,39.86224,39.767209999999999,39.939129999999999,39.968809999999998,39.910029999999999,40.165260000000004,40.531999999999996,39.962760000000003,39.828449999999997,40.289000000000001,40.09057,40.090969999999999,40.375979999999998,39.888809999999999,39.972610000000003,39.533340000000003,39.955350000000003,39.635150000000003,678.58979999999997,8076.1059999999998,7397.5159999999996,52.876330000000003,40.190930000000002,43,43,643157.77679999999,531408.87639893813,3784.7972870609979,63,50,51224.3175262,44,10.96061922764342,11.567759227643421,439883.02767567447,9346.9751046562815,690.61742013908929,12.027620139089322,0.11271135016402123,-678.59000000000015,-1949.4591046562819,0.44222413766095009,0.44222413766095009,0.973426092119554,0.973426092119554,8856.3941413630891,-1458.8781413630895,0.82255948744013097,0.82255948744013097,44,0.973426092119554]
["2013-02-02T20:00:00","2013-02-02T20:00:00",52.31082,50.456650000000003,49.5227,48.800409999999999,46.568809999999999,42.641190000000002,41.005510000000001,40.602069999999998,40.10772,39.931980000000003,40.128839999999997,39.988480000000003,39.921889999999998,40.212910000000001,40.565519999999999,39.99577,39.85857,40.369810000000001,40.132019999999997,40.096449999999997,40.390419999999999,39.91234,40.00985,39.586750000000002,40.010219999999997,39.65343,252.86369999999999,7152.8959999999997,7395.4179999999997,52.84151,39.966819999999998,41,41,613243.46160000004,504660.23905800219,1600.2972338714999,58,45,46045.659301120002,44,10.479791982168193,11.086931982168194,401023.82810834749,8787.513984908981,305.40629749034576,52.54259749034577,0.10746896178429931,242.52199999999993,-1392.0959849089813,0.29296399212243995,0.29296399212243995,0.949332154453434,0.949332154453434,8306.2941804239672,-910.87618042396753,0.71016985034100166,0.71016985034100166,44,0.949332154453434]
["2013-02-03T05:00:00","2013-02-03T05:00:00",50.044559999999997,49.055100000000003,46.628889999999998,43.723640000000003,41.580210000000001,40.367339999999999,40.274659999999997,40.522840000000002,40.334350000000001,40.169559999999997,40.539250000000003,40.401130000000002,40.368499999999997,40.655540000000002,41.007660000000001,40.463720000000002,40.348660000000002,40.84684,40.585819999999998,40.427810000000001,40.778599999999997,40.32114,40.410919999999997,39.961689999999997,40.344070000000002,39.90155,701.61490000000003,6356.107,7057.7219999999998,50.956569999999999,39.87979,43,43,643157.77679999999,443671.61814640299,3558.2434734244989,42,37,35202.599447729997,44,9.6232676411675939,10.230407641167593,386211.03591063118,7316.1426576428157,739.5083678651124,37.89346786511237,0.11271135016402123,701.61499999999978,-258.42065764281597,0.27263450203716177,0.27263450203716177,1.0073773475310013,1,6881.9544015183228,175.76759848167694,0.7309536626003863,0.7309536626003863,44,1]
["2013-02-03T12:00:00","2013-02-03T12:00:00",50.435279999999999,49.181719999999999,47.327379999999998,44.34863,41.89575,40.545430000000003,40.42774,40.677970000000002,40.524880000000003,40.413060000000002,40.596119999999999,40.619140000000002,40.555810000000001,40.821550000000002,41.194650000000003,40.629919999999998,40.504910000000002,40.988149999999997,40.787770000000002,40.742890000000003,41.014229999999998,40.498719999999999,40.564230000000002,40.153530000000003,40.564630000000001,40.173520000000003,1601.0940000000001,8600.9809999999998,6999.8869999999997,52.85727,40.322139999999997,43,43,643157.77679999999,509037.51297278871,8215.0211827199964,63,49,53907.20748126501,44,10.991258775111138,11.598398775111137,441112.68602131982,9809.105323465541,1494.8280903589098,-106.26590964109027,0.11271135016402123,-1601.0940000000001,-2809.2183234655413,0.1767139764007396,0.1767139764007396,0.95695987009523764,0.95695987009523764,9295.6292547802077,-2295.742254780208,0.66943877735446577,0.66943877735446577,44,0.95695987009523764]
["2013-02-03T15:00:00","2013-02-03T15:00:00",52.98028,51.36853,49.480159999999998,48.712380000000003,46.424979999999998,42.85557,40.890439999999998,40.684109999999997,40.582160000000002,40.471789999999999,40.563369999999999,40.616790000000002,40.553289999999997,40.795859999999998,41.148429999999998,40.554110000000001,40.393619999999999,40.956090000000003,40.717880000000001,40.744010000000003,41.040469999999999,40.562370000000001,40.61918,40.200270000000003,40.589350000000003,40.200499999999998,1546.377,8546.8410000000003,7000.4629999999997,53.421840000000003,40.383299999999998,41,41,613243.46160000004,505932.97925605014,9881.1789285300019,70,49,55719.16412607002,44,11.05304649669899,11.660186496698987,422960.21007935394,10082.136928078724,1787.9557335583511,241.57873355835113,0.10746896178429931,-1546.3780000000006,-3081.6739280787242,7.4480952406197884E-2,7.4480952406197884E-2,0.90263888557929262,0.90263888557929262,9557.1651691581756,-2556.7021691581758,0.58400368743434605,0.58400368743434605,44,0.90263888557929262]
["2013-02-04","2013-02-04",53.524940000000001,53.22757,52.261969999999998,50.717329999999997,49.679250000000003,47.93956,45.076929999999997,42.368780000000001,40.847270000000002,40.781419999999997,40.82714,40.720039999999997,40.618740000000003,40.885080000000002,41.247819999999997,40.658639999999998,40.511789999999998,41.045079999999999,40.789299999999997,40.776040000000002,41.070419999999999,40.588230000000003,40.676909999999999,40.261069999999997,40.631610000000002,40.297130000000003,1243.664,7701.7259999999997,6458.0619999999999,51.344169999999998,40.366019999999999,37,37,553414.83120000002,381488.37647604191,8225.4755479199994,59,45,42275.351643449998,44,10.351224491041647,10.958364491041646,357459.72003600263,8168.183711992091,1589.2758494492409,345.61184944924094,9.6984185024855479E-2,-1243.6639999999998,-1710.1217119920912,-1.798160271612868E-2,0,0.84588637257286636,0.84588637257286636,7715.6315941141911,-1257.5695941141912,0.44209047863152745,0.44209047863152745,43,0.84588637257286636]
["2013-02-04T01:00:00","2013-02-04T01:00:00",53.32846,53.011539999999997,52.587299999999999,51.795000000000002,50.040869999999998,48.633499999999998,46.420189999999998,43.498959999999997,41.247,40.626519999999999,40.927169999999997,40.754860000000001,40.64978,40.90428,41.259239999999998,40.666730000000001,40.532209999999999,41.046869999999998,40.791600000000003,40.79222,41.094239999999999,40.614490000000004,40.674439999999997,40.255679999999998,40.633049999999997,40.316249999999997,1478.8869999999999,7873.8490000000002,6394.9610000000002,51.147410000000001,40.36721,35,35,523500.516,353815.35377002228,9621.7941051350026,58,44,42440.833494900005,44,10.296020422176092,10.903160422176091,336334.25303435704,8244.1237982568055,1869.0316667226289,390.14466672262893,9.1741796645133558E-2,-1478.8879999999999,-1849.1627982568052,-1.9443593144586924E-2,0,0.83033614811154854,0.83033614811154854,7785.0516458657239,-1390.0906458657237,0.42747394136515554,0.42747394136515554,42,0.83033614811154854]
["2013-02-04T10:00:00","2013-02-04T10:00:00",52.951990000000002,52.71499,52.316800000000001,52.637099999999997,52.73104,52.33173,52.27984,52.495980000000003,52.197960000000002,50.006079999999997,48.953659999999999,47.006399999999999,43.7821,41.891500000000001,41.507980000000003,41.01567,40.764740000000003,41.238140000000001,40.995629999999998,40.989040000000003,41.188049999999997,40.713340000000002,40.774340000000002,40.335329999999999,40.74221,40.405450000000002,2444.3240000000001,8436.9709999999995,5992.6459999999997,52.772460000000002,40.54618,27,27,403843.25520000001,311646.41511063545,15333.904419479999,60,56,51576.384898940014,44,11.337706725053856,11.944846725053855,285708.15875775769,9098.2040988884401,2704.9393305606359,260.61533056063581,7.0772243126245887E-2,-2444.3249999999998,-3105.5580988884403,-3.2654349426987486E-2,0,0.64329302078222828,0.64329302078222828,8635.7549973011428,-2643.1089973011431,0.24678760153529578,0.24678760153529578,42,0.64329302078222828]
["2013-02-04T17:00:00","2013-02-04T17:00:00",55.352229999999999,54.514209999999999,54.113970000000002,54.117820000000002,53.975670000000001,53.488109999999999,52.688720000000004,52.656739999999999,52.391930000000002,52.304670000000002,52.381320000000002,52.466270000000002,52.381439999999998,52.590949999999999,52.871859999999998,51.82958,49.745669999999997,48.93242,46.531869999999998,43.523969999999998,41.99418,41.357979999999998,41.379130000000004,40.542929999999998,40.919930000000001,40.537860000000002,2169.2109999999998,9364.5120000000006,7195.3010000000004,55.213569999999997,40.735709999999997,13,13,194443.04880000002,178064.00325196996,{"$f":"500*AC831*(C831-AB831)/1000","v":16067.747181034998},71,61,67789.046852159998,44,{"$f":"19.5286-0.30357*AP831+0.0000341*AO831+0.060847*AN831","v":12.194793497658656},{"$f":"19.5286-0.30357*42+0.0000341*AO831+0.060847*AN831","v":12.801933497658657},{"$f":"62.4*AJ831*AQ831/1000","v":147962.43241548067},11117.703118986832,{"$f":"AL831*1000/(500*AQ831)","v":2635.1815115393188},465.97051153931898,3.4075524468192467E-2,-2169.2110000000002,-3922.4021189868317,-4.1243308065109632E-2,0,0.40976341932216909,0.40976341932216909,10590.438837158139,-3395.1378371581386,-2.7217655097979694E-2,{"$f":"IF(BF831>1,1,IF(BF831<0,0,BF831))","v":0},41,0.40976341932216909]
["2013-02-04T20:00:00","2013-02-04T20:00:00",54.82085,54.408909999999999,53.82394,53.933990000000001,53.738489999999999,52.905169999999998,52.437829999999998,52.555729999999997,52.327039999999997,52.245159999999998,52.396129999999999,52.41574,52.368499999999997,52.544490000000003,52.259390000000003,50.055790000000002,48.491439999999997,46.796880000000002,43.843690000000002,42.046880000000002,42.182859999999998,40.688000000000002,40.47195,40.049700000000001,40.467359999999999,40.104370000000003,5660.6490000000003,8669.616,14330.27,53.76952,40.386229999999998,15,15,224357.364,191310.72683827099,41652.413897759987,62,57,58013.992558320009,44,11.618076146238714,12.225216146238711,162651.89858869513,9986.8501166781734,7170.2773115744676,1509.6283115744673,3.9317912847914381E-2,5660.6540000000005,4343.419883321827,8.2548581847382035E-2,8.2548581847382035E-2,0.50373800826379656,0.50373800826379656,9490.8739222854492,4839.3960777145512,9.3128859046522738E-2,9.3128859046522738E-2,44,0.50373800826379656]
["2013-02-05T05:00:00","2013-02-05T05:00:00",52.71405,52.509459999999997,51.529200000000003,49.97372,48.76,45.96564,42.981929999999998,41.530410000000003,41.454169999999998,40.599490000000003,40.190089999999998,39.924619999999997,39.849420000000002,40.073239999999998,40.377940000000002,39.67662,39.549639999999997,40.058329999999998,39.834890000000001,39.811799999999998,40.121169999999999,39.631129999999999,39.72972,39.323219999999999,39.719149999999999,39.39743,3229.1680000000001,8772.4310000000005,12001.6,52.660290000000003,40.293959999999998,39,39,583329.14639999997,482764.63888365682,21500.801586080001,58,57,54241.388324115025,44,11.489430341852323,12.096570341852324,418212.26266154245,9441.9630408534667,3742.7097682570825,513.54176825708237,0.10222657340457739,3229.1689999999999,2559.6369591465336,0.47182340535562489,0.47182340535562489,0.97519501942275477,0.97519501942275477,8968.0606636821558,3033.5393363178446,0.52632422271052715,0.52632422271052715,44,0.97519501942275477]
["2013-02-05T12:00:00","2013-02-05T12:00:00",46.647530000000003,43.485280000000003,41.293979999999998,41.658169999999998,41.064729999999997,40.107669999999999,39.79016,39.731479999999998,39.550199999999997,39.450420000000001,39.661320000000003,39.647660000000002,39.608060000000002,39.885890000000003,40.250920000000001,39.656559999999999,39.54815,40.06129,39.82949,39.830170000000003,40.140779999999999,39.635590000000001,39.735990000000001,39.340620000000001,39.746169999999999,39.411160000000002,2705.1909999999998,9293.3389999999999,11998.53,53.897930000000002,40.272930000000002,47,47,702986.40720000002,635481.74940012326,9787.8814983350021,62,59,63310.8719375,44,11.920393733068751,12.527533733068751,522904.18519993039,10622.278652066207,1642.2077521117649,-1062.9832478882349,0.12319612692346506,2705.1910000000007,1376.251347933794,0.61035943522854041,0.61035943522854041,1.0284445659581638,1,10107.475786775047,1891.0542132249539,0.70155631612816882,0.70155631612816882,44,1]
["2013-02-05T15:00:00","2013-02-05T15:00:00",42.438299999999998,41.59346,40.868180000000002,40.380180000000003,40.106659999999998,39.666440000000001,39.539870000000001,39.825299999999999,39.645629999999997,39.542349999999999,39.716090000000001,39.728369999999998,39.678809999999999,39.958010000000002,40.336930000000002,39.74353,39.63015,40.1477,39.937179999999998,39.954059999999998,40.244149999999998,39.727800000000002,39.806049999999999,39.37182,39.77534,39.438099999999999,3169.4540000000002,9545.9419999999991,7877.5309999999999,54.373460000000001,40.301000000000002,51,51,762815.03760000004,710918.03327809914,4754.4979453999995,65,60,67167.443478660003,44,12.112749822622307,12.719889822622306,576562.75319030089,11090.370801387331,785.0402286886648,-2384.4137713113355,0.13368090368290891,-1668.4109999999991,-3212.8398013873311,0.60383374240527943,0.60383374240527943,0.98245697744269234,0.98245697744269234,10561.010262715137,-2683.4792627151373,0.71142314834112907,0.71142314834112907,44,1]
["2013-02-06","2013-02-06",53.916519999999998,53.654609999999998,53.309759999999997,53.614150000000002,53.683019999999999,53.164850000000001,50.497239999999998,43.306800000000003,41.438249999999996,41.066229999999997,40.618519999999997,40.199010000000001,39.97043,40.172199999999997,40.509419999999999,39.888060000000003,39.768279999999997,40.276220000000002,39.997959999999999,39.982529999999997,40.283709999999999,39.773569999999999,39.877540000000003,39.450949999999999,39.852820000000001,39.516080000000002,3166.2280000000001,9164.1470000000008,5997.9189999999999,51.223550000000003,40.00367,37,37,553414.83120000002,404295.06211093359,22797.538170159994,57,55,51410.314821180014,44,11.271196735402238,11.878336735402238,389229.20017766434,9122.4234707398755,4045.2737549250869,879.04575492508684,9.6984185024855479E-2,-3166.228000000001,-3124.5044707398756,0.22059151433891799,0.22059151433891799,0.71218920206025138,0.71218920206025138,8656.1470627375857,-2658.2280627375858,0.37493003415006987,0.37493003415006987,44,0.72973222461755904]
["2013-02-06T01:00:00","2013-02-06T01:00:00",53.669040000000003,53.383429999999997,53.022959999999998,53.333269999999999,53.42221,52.969200000000001,52.850259999999999,51.11889,43.086599999999997,41.305349999999997,41.352510000000002,40.539479999999998,40.159959999999998,40.253320000000002,40.550080000000001,39.931559999999998,39.808059999999998,40.318060000000003,40.04956,39.987200000000001,40.286340000000003,39.783810000000003,39.89517,39.469549999999998,39.866379999999999,39.533050000000003,3081.8539999999998,9083.61,6001.7569999999996,50.884569999999997,39.940890000000003,35,35,523500.516,370813.65842878132,21782.528662730001,53,52,49704.060542399973,44,11.030472464495841,11.63761246449584,360326.18087777152,9012.1362801791365,3949.5187051764415,867.66470517644166,9.1741796645133558E-2,-3081.853000000001,-3010.3792801791369,0.18893795198633556,0.18893795198633556,0.6797841072141334,0.6797841072141334,8541.9686716734523,-2540.2116716734527,0.34822019427458129,0.34822019427458129,44,0.69732712977144107]
["2013-02-06T11:00:00","2013-02-06T11:00:00",53.228000000000002,52.966380000000001,52.653979999999997,52.874360000000003,52.84843,52.392310000000002,52.285060000000001,52.532179999999997,52.380020000000002,52.282159999999998,52.485129999999998,52.485979999999998,52.453699999999998,52.700270000000003,53.036790000000003,52.438589999999998,52.332740000000001,52.769159999999999,49.849879999999999,42.315660000000001,42.12771,40.942419999999998,40.708739999999999,39.833300000000001,40.150100000000002,39.738059999999997,3391.7260000000001,10682.26,8956.9369999999999,53.058869999999999,40.350670000000001,13,13,194443.04880000002,161624.66791445695,22877.09011822001,66,62,67876.148265999989,44,12.2586106558706,12.865750655870599,148736.74171072998,11074.03606680246,3732.4115693754025,340.68556937540234,3.4075524468192467E-2,-1725.3230000000003,-2117.0990668024606,-2.2260891761664667E-2,0,0.33622494998739572,0.33622494998739572,10551.447806122114,-1594.5108061221144,4.2797545102948899E-2,4.2797545102948899E-2,42,0.35376797254470338]
["2013-02-06T16:00:00","2013-02-06T16:00:00",53.040219999999998,52.711190000000002,52.329619999999998,52.646030000000003,52.669910000000002,52.380600000000001,52.245609999999999,52.514000000000003,52.369,52.304229999999997,52.386690000000002,52.487020000000001,52.427529999999997,52.634309999999999,52.830390000000001,51.446539999999999,44.653979999999997,42.056449999999998,41.380960000000002,40.585230000000003,40.809359999999998,40.341209999999997,40.401220000000002,39.986969999999999,40.400129999999997,40.114669999999997,3957.2939999999999,10287.56,14244.86,54.511090000000003,40.525889999999997,17,17,254271.67920000001,228421.55780299226,25575.100730850005,75,63,71936.79205600002,44,12.457925609109601,13.065065609109601,197664.33423216364,11548.759289973241,4105.8361613828774,148.54216138287757,4.4560301227636302E-2,3957.3000000000011,2696.1007100267598,8.9316884155714274E-2,8.9316884155714274E-2,0.47264902048268276,0.47264902048268276,11012.082787528014,3232.7772124719868,0.16047300530114095,0.16047300530114095,44,0.49019204303999042]
["2013-02-06T19:00:00","2013-02-06T19:00:00",52.829520000000002,52.6004,52.276310000000002,52.617449999999998,52.67718,52.346130000000002,52.260849999999998,52.513129999999997,52.34431,52.261049999999997,52.422879999999999,52.249690000000001,50.079000000000001,43.467039999999997,42.198079999999997,40.816020000000002,40.193309999999997,40.769269999999999,40.521389999999997,40.556829999999998,40.866759999999999,40.38306,40.462470000000003,40.0396,40.452620000000003,40.1661,4697.8890000000001,9703.7990000000009,14401.69,53.424370000000003,39.916679999999999,25,25,373928.94,309357.41287362913,29745.670760190005,65,60,65537.954357155017,44,12.057184243578988,12.664324243578985,281332.27971177839,10871.187340785147,4934.0990664600586,236.21006646005844,6.5529854746523966E-2,4697.8909999999996,3530.5026592148533,0.18012890570117929,0.18012890570117929,0.60341255935807603,0.60341255935807603,10350.012064857516,4051.6779351424848,0.26826704418985187,0.26826704418985187,44,0.62095558191538369]
["2013-02-07T04:00:00","2013-02-07T04:00:00",52.652659999999997,51.480730000000001,43.67971,41.72495,41.13729,40.351790000000001,40.262039999999999,40.530250000000002,40.366889999999998,40.262039999999999,40.479520000000001,40.453609999999998,40.426960000000001,40.69162,41.049160000000001,40.43929,40.317680000000003,40.859439999999999,40.620199999999997,40.646459999999998,40.94782,40.464759999999998,40.547449999999998,40.134819999999998,40.545749999999998,40.244430000000001,2843.4920000000002,9159.4089999999997,12002.9,52.074350000000003,40.212200000000003,47,47,702986.40720000002,518935.43259563774,17641.351369579992,61,58,54325.141734674995,44,11.553133333152418,12.160273333152418,506793.81129158364,9404.3996841593962,3053.9509691205699,210.45896912056969,0.12319612692346506,2843.491,2598.5003158406034,0.53335723644169819,0.53335723644169819,1.0165720220298133,1,8934.8553681879785,3068.0446318120212,0.66697023672126221,0.66697023672126221,44,1]
["2013-02-07T11:00:00","2013-02-07T11:00:00",52.537300000000002,52.272030000000001,51.952860000000001,52.302199999999999,52.307510000000001,49.872309999999999,46.406280000000002,42.561239999999998,40.916690000000003,40.507269999999998,40.537239999999997,40.549599999999998,40.499229999999997,40.760919999999999,41.102649999999997,40.498359999999998,40.348779999999998,40.87227,40.6449,40.706670000000003,40.97786,40.483750000000001,40.533250000000002,40.103319999999997,40.507190000000001,40.27516,7570.94,11544.99,3974.0540000000001,51.876829999999998,40.576160000000002,37,37,553414.83120000002,400641.4616685377,46417.963105800009,70,62,65233.061071649987,44,12.168481382543265,12.775621382543264,420215.20758550463,10721.643732016129,7629.212166505934,58.272166505934365,9.6984185024855479E-2,-7570.9359999999997,-6747.5897320161293,0.32767201537566742,0.32767201537566742,0.76283763726989162,0.76283763726989162,10212.115578313096,-6238.0615783130961,0.49941464138144293,0.49941464138144293,44,0.76283763726989162]
["2013-02-07T14:00:00","2013-02-07T14:00:00",53.026200000000003,52.7059,52.354559999999999,52.720860000000002,52.755960000000002,52.454389999999997,52.222549999999998,52.325870000000002,52.111370000000001,51.962359999999997,51.874319999999997,50.967019999999998,47.647709999999996,42.775300000000001,41.728050000000003,40.758609999999997,40.498699999999999,40.961080000000003,40.80151,40.90945,41.093170000000001,40.559220000000003,40.544490000000003,40.06812,40.403489999999998,40.265999999999998,6665.5940000000001,12517.34,5851.7420000000002,52.225389999999997,40.914349999999999,25,25,373928.94,279050.43040658778,42527.156279400013,79,63,70792.066716799993,44,12.418890475042881,13.02603047504288,289772.03120167414,11400.707149976786,6848.7851414525294,183.19114145252934,6.5529854746523966E-2,-6665.598,-5548.9651499767861,0.15311704173814594,0.15311704173814594,0.55582754006988078,0.55582754006988078,10869.323060840905,-5017.5810608409047,0.34178147378610768,0.34178147378610768,44,0.55582754006988078]
["2013-02-07T23:00:00","2013-02-07T23:00:00",52.584009999999999,52.42745,52.114049999999999,52.441920000000003,52.543599999999998,52.143219999999999,52.119759999999999,52.32817,52.156370000000003,52.052019999999999,52.337859999999999,52.227609999999999,52.168570000000003,52.28848,52.366630000000001,51.099330000000002,47.983319999999999,43.747140000000002,41.275230000000001,41.12912,41.401009999999999,40.938459999999999,41.027520000000003,40.618040000000001,41.024720000000002,40.719830000000002,6084.4849999999997,8612.4629999999997,14696.95,51.179960000000001,40.360019999999999,15,15,224357.364,146440.76889919274,36093.71262364999,56,51,46593.166456110011,44,10.863543976153352,11.470683976153351,152088.52402772152,8577.8943884955079,6644.9241063283907,560.43910632839106,3.9317912847914381E-2,6084.487000000001,6119.0556115044928,0.24454413736276495,0.24454413736276495,0.52414488618755706,0.52414488618755706,8123.8689084231646,6573.0810915768361,0.42370859839623143,0.42370859839623143,44,0.52414488618755706]
["2013-02-08","2013-02-08",52.569369999999999,52.432659999999998,52.110759999999999,52.449010000000001,52.55086,52.128999999999998,52.120809999999999,52.331569999999999,52.16001,52.03049,52.285220000000002,52.110729999999997,51.957850000000001,51.799309999999998,49.947789999999998,45.220089999999999,41.379660000000001,41.396520000000002,41.129260000000002,41.102910000000001,41.390900000000002,40.922640000000001,41.026119999999999,40.617420000000003,41.022419999999997,40.703710000000001,5666.9440000000004,8350.4869999999992,14017.43,50.801180000000002,40.350540000000002,19,19,284185.99440000003,179060.51609934814,33621.015371519999,53,48,43633.966730839995,44,10.580094265521645,11.187234265521646,187618.9916448436,8248.3134149445414,6355.5228389758277,688.57883897582724,4.9802689607358223E-2,5666.9430000000011,5769.1165850554589,0.30520529482778169,0.30520529482778169,0.58373170794788898,0.58373170794788898,7800.67096034936,6216.7590396506403,0.48907663065323398,0.48907663065323398,44,0.58373170794788898]
["2013-02-08T09:00:00","2013-02-08T09:00:00",52.258800000000001,51.895029999999998,50.841540000000002,48.003889999999998,43.021090000000001,41.099679999999999,40.946330000000003,41.109909999999999,40.903399999999998,40.693869999999997,41.06944,40.92794,40.918300000000002,41.22992,41.53613,40.972659999999998,40.895899999999997,41.384270000000001,41.110660000000003,40.977519999999998,41.309629999999999,40.868929999999999,41.005699999999997,40.624110000000002,41.039679999999997,40.676070000000003,4296.5140000000001,7525.6580000000004,11822.17,51.784129999999998,40.575319999999998,43,43,643157.77679999999,445800.27486764669,24882.680801609997,47,42,42176.835323489999,44,10.16532408453101,10.772464084531009,407965.41169228795,8298.1781933882885,4895.6000998482659,599.0860998482658,0.11271135016402123,4296.5119999999997,3523.9918066117116,0.69397737042961882,0.69397737042961882,1.0070245441534971,1,7830.4898475465588,3991.6801524534412,0.92049933962135977,0.92049933962135977,44,1]
["2013-02-08T16:00:00","2013-02-08T16:00:00",53.156149999999997,52.918689999999998,52.591549999999998,52.894019999999998,52.798169999999999,52.236240000000002,51.92503,51.874279999999999,50.940530000000003,46.957529999999998,42.994399999999999,41.332180000000001,41.129959999999997,41.350230000000003,41.657769999999999,41.05095,40.898719999999997,41.483640000000001,41.286079999999998,41.277810000000002,41.521000000000001,41.005830000000003,41.061129999999999,40.649619999999999,41.047629999999998,40.709069999999997,4719.8,10519.8,5799.9970000000003,52.268250000000002,41.218429999999998,31,31,463671.88560000004,334443.2074832042,29373.864092,64,45,58120.948218000027,44,10.891559334233802,11.498699334233802,315126.85486641637,10672.658787308294,5393.8767059136426,674.0767059136424,8.125701988568973E-2,-4719.802999999999,-4872.6617873082932,0.42684157260606115,0.42684157260606115,0.7512108139068826,0.7512108139068826,10109.134351389288,-4309.1373513892877,0.69229143878805866,0.69229143878805866,44,0.7512108139068826]
["2013-02-08T19:00:00","2013-02-08T19:00:00",52.907809999999998,52.680050000000001,52.36016,52.675060000000002,52.729570000000002,52.373390000000001,52.302799999999998,52.514240000000001,52.361849999999997,52.216949999999997,52.178489999999996,51.713290000000001,50.941099999999999,48.229750000000003,43.194659999999999,41.424950000000003,41.090499999999999,41.558219999999999,41.381810000000002,41.374090000000002,41.63758,41.144240000000003,41.11853,40.69061,41.078980000000001,40.730339999999998,2961.7620000000002,8947.1949999999997,5985.4340000000002,51.563969999999998,41.197690000000001,23,23,344014.62479999999,232560.25476353426,18033.383951069998,57,44,46374.564292299983,44,10.430160642367429,11.037300642367429,223899.17471923609,8892.3969404509426,3457.9302408475269,496.1682408475267,6.0287466366802052E-2,-2961.7609999999995,-2906.9629404509424,0.31383823447613235,0.31383823447613235,0.6319699807583985,0.6319699807583985,8403.2438355965533,-2417.8098355965531,0.5954598083475372,0.5954598083475372,44,0.6319699807583985]
["2013-02-09T04:00:00","2013-02-09T04:00:00",52.80348,52.650930000000002,52.337809999999998,52.668140000000001,52.768000000000001,52.35313,52.33108,52.535240000000002,52.379019999999997,52.251060000000003,52.573459999999997,52.457970000000003,52.437730000000002,52.701450000000001,52.899079999999998,52.00864,51.311149999999998,50.127690000000001,46.05077,42.184699999999999,41.70485,41.233179999999997,41.258330000000001,40.838259999999998,41.23301,40.873809999999999,6173.2610000000004,7405.65,13437.01,51.779809999999998,41.063639999999999,13,13,194443.04880000002,132325.18354927871,36822.483276935003,49,46,39680.102180249996,44,10.323573484346525,10.930713484346525,125258.45921516788,7687.2804248289258,7133.6700092789315,960.40900927893108,3.4075524468192467E-2,6031.3600000000006,5749.7295751710744,0.19948981257068438,0.19948981257068438,0.54182455919919192,0.54182455919919192,7260.2949911868827,6176.7150088131175,0.52377337612947572,0.52377337612947572,44,0.54182455919919192]
["2013-02-09T11:00:00","2013-02-09T11:00:00",52.700339999999997,52.548169999999999,52.064320000000002,51.941749999999999,51.56373,48.907049999999998,44.918689999999998,42.521129999999999,41.417630000000003,41.213059999999999,41.489960000000004,41.211060000000003,41.109380000000002,41.279649999999997,41.519289999999998,40.91039,40.711739999999999,40.437739999999998,40.0946,40.005360000000003,40.319609999999997,39.862780000000001,39.971550000000001,39.564529999999998,39.964089999999999,39.623089999999998,6548.8810000000003,7453.857,14002.74,51.906480000000002,40.569029999999998,37,37,553414.83120000002,424183.35669301928,42820.677028624996,50,46,42253.865522325017,44,10.411338814311284,11.018478814311283,359535.65309925663,8116.8937589934985,8225.7772592635793,1676.8962592635789,9.6984185024855479E-2,6548.8829999999998,5885.8462410065013,0.62631550606535857,0.62631550606535857,1.0142351163031436,1,7669.6368408756825,6333.1031591243172,0.98320600927585133,0.98320600927585133,44,1]
["2013-02-09T14:00:00","2013-02-09T14:00:00",49.082120000000003,44.157899999999998,41.731400000000001,41.78295,41.684640000000002,41.128749999999997,41.046500000000002,41.204479999999997,40.976939999999999,40.773069999999997,40.964399999999998,40.357300000000002,40.134630000000001,40.396949999999997,40.661459999999998,39.835090000000001,39.701059999999998,40.178159999999998,39.925280000000001,39.852370000000001,40.163339999999998,39.696899999999999,39.801720000000003,39.390459999999997,39.789920000000002,39.461280000000002,3945.4029999999998,7449.3609999999999,10941.98,52.094720000000002,40.541629999999998,47,47,702986.40720000002,554182.92360143026,18979.045499260003,53,49,43031.569037745016,44,10.620399504187105,11.227539504187106,465878.18100577442,8103.5688009250052,3574.0737420993419,-371.32925790065792,0.12319612692346506,3492.6189999999997,2838.4111990749943,0.77937019630810389,0.77937019630810389,1.0367242207711898,1,7665.3605220800464,3276.6194779199532,1.0344530271095453,1,44,1]
["2013-02-09T21:00:00","2013-02-09T21:00:00",51.273290000000003,47.998519999999999,42.679519999999997,42.003740000000001,41.814979999999998,41.25468,41.053519999999999,41.265149999999998,41.065689999999996,40.877400000000002,41.076540000000001,40.720570000000002,40.451979999999999,40.457610000000003,40.683169999999997,40.014420000000001,39.847200000000001,40.3444,40.085430000000002,39.991970000000002,40.261499999999998,39.74821,39.838830000000002,39.401339999999998,39.800460000000001,39.49738,540.30520000000001,7542.1959999999999,7001.8909999999996,51.356189999999998,39.852260000000001,47,47,702986.40720000002,520202.73149940773,3181.2927038660014,53,52,43382.447415139985,44,10.814905456856275,11.422045456856274,474410.44755455939,8022.7141306421727,588.3163226081042,48.011122608104188,0.12319612692346506,-540.30500000000029,-1020.8231306421731,0.694464223444764,0.694464223444764,0.9658223397268586,0.9658223397268586,7596.2659366057669,-594.37493660576729,0.94736922948116531,0.94736922948116531,44,0.9658223397268586]
["2013-02-10","2013-02-10",51.885219999999997,50.808039999999998,46.70778,42.819710000000001,42.037309999999998,41.396599999999999,41.223230000000001,41.360439999999997,41.132730000000002,40.928870000000003,41.141210000000001,40.996319999999997,40.705199999999998,40.6357,40.822969999999998,40.129350000000002,39.91198,40.388489999999997,40.143419999999999,40.11327,40.346890000000002,39.824840000000002,39.896120000000003,39.429949999999998,39.811570000000003,39.504550000000002,1324.1780000000001,8127.6540000000005,6803.4759999999997,51.275840000000002,39.90775,45,45,673072.09200000006,494390.6314363337,8197.1054196299974,59,58,46197.951080430008,44,11.275996131842664,11.883136131842663,473588.43828461884,8194.0345740222565,1453.9035529609514,{"$f":"AU958-AC958","v":129.72555296095129},0.11795373854374315,{"$f":"AE958-AD958","v":-1324.1780000000008},-1390.5585740222568,0.66078770143835208,0.66078770143835208,0.93615040117461024,0.93615040117461024,{"$f":"AO958*1000/(500*AR958)","v":7775.3802645810993},{"$f":"AE958-BD958","v":-971.9042645810996},0.92678752110224549,0.92678752110224549,44,0.93615040117461024]
["2013-02-10T06:00:00","2013-02-10T06:00:00",52.074829999999999,51.870440000000002,51.443010000000001,51.484389999999998,49.518349999999998,44.091720000000002,42.037939999999999,41.721339999999998,41.445959999999999,41.134540000000001,41.40231,41.17051,41.084789999999998,41.31476,41.498240000000003,40.650829999999999,40.292099999999998,40.623280000000001,40.250430000000001,40.153799999999997,40.44164,39.895330000000001,39.981470000000002,39.536110000000001,39.940649999999998,39.618160000000003,279.21120000000002,7069.69,6796.2709999999997,51.73659,39.965609999999998,39,39,583329.14639999997,441107.68588274857,1739.0208893519994,55,48,41608.589798100002,44,10.511028912115211,11.118168912115213,382598.70624080888,7917.1297398185543,330.89451163959239,51.683311639592375,0.10222657340457739,-273.41899999999987,-1120.8587398185546,0.56722880630581274,0.56722880630581274,0.86020620668999259,0.86020620668999259,7484.7918082554188,-688.52080825541907,0.86003293056391972,0.86003293056391972,44,0.86020620668999259]
["2013-02-10T15:00:00","2013-02-10T15:00:00",52.469009999999997,51.890940000000001,51.483240000000002,51.78105,51.82629,51.48057,51.290619999999997,50.19061,46.094430000000003,42.421590000000002,41.800040000000003,41.70617,41.448700000000002,41.618679999999998,41.822180000000003,41.138849999999998,40.897759999999998,41.352029999999999,40.853529999999999,40.687579999999997,40.823500000000003,40.278660000000002,40.153869999999998,39.691929999999999,40.06691,39.737099999999998,1620.405,8422.3189999999995,6801.915,52.871850000000002,39.978529999999999,33,33,493586.20079999999,404547.39629976684,10315.425311774999,67,48,54295.827004540013,44,10.943663700854817,11.550803700854814,337062.42266971851,9922.7879234444918,1885.1868247686109,264.78182476861093,8.6499408265411637E-2,-1620.4039999999995,-3120.8729234444918,0.36673696987693516,0.36673696987693516,0.74287806982455107,0.74287806982455107,9401.2206268420723,-2599.3056268420723,0.70541716368425744,0.70541716368425744,44,0.74287806982455107]
["2013-02-10T18:00:00","2013-02-10T18:00:00",53.009720000000002,52.419580000000003,51.681640000000002,51.85087,51.876719999999999,51.526719999999997,51.3979,51.593220000000002,50.76155,47.971110000000003,43.639339999999997,42.106160000000003,41.782060000000001,41.811309999999999,42.055050000000001,41.302079999999997,41.022770000000001,41.528129999999997,41.211770000000001,41.077179999999998,41.042189999999998,40.514629999999997,40.296140000000001,39.789479999999998,40.148310000000002,39.845529999999997,1321.4870000000001,8123.8860000000004,6802.3990000000003,53.028320000000001,39.987769999999998,31,31,463671.88560000004,381419.31963837473,8698.152975265004,66,46,52969.970788650011,44,10.776758003892967,11.383898003892966,311805.29354956455,9830.4092510039263,1614.2429795905052,292.75597959050515,8.125701988568973E-2,-1321.4870000000001,-3028.010251003926,0.26202645821056031,{"$f":"IF(AZ976>1,1,IF(AZ976<0,0,AZ976))","v":0.26202645821056031},0.69270075062030756,{"$f":"IF(BB976>1,1,BB976)","v":0.69270075062030756},9306.1218170675475,-2503.7228170675471,0.61760025620433412,0.61760025620433412,44,0.69270075062030756]
["2013-02-11T03:00:00","2013-02-11T03:00:00",53.059019999999997,52.800910000000002,52.412019999999998,52.290300000000002,52.063800000000001,51.573619999999998,51.519449999999999,51.719279999999998,51.50891,51.160229999999999,50.007010000000001,45.81635,42.682400000000001,42.22287,42.337159999999997,41.654879999999999,41.368850000000002,41.744219999999999,41.386150000000001,41.241900000000001,41.415370000000003,40.815629999999999,40.688139999999997,40.14423,40.385829999999999,39.989269999999998,360.22199999999998,6775.8689999999997,6426.5609999999997,50.751199999999997,39.983939999999997,27,27,403843.25520000001,271198.68943031511,2354.0057422499995,51,42,36478.771624470006,44,9.9710201123944273,10.578160112394428,251267.90331889183,7316.95878922664,472.16949032604282,111.94749032604284,7.0772243126245887E-2,-349.30799999999999,-890.39778922664027,0.11444803323533903,0.11444803323533903,0.64263000951740767,0.64263000951740767,6896.9974431995652,-470.43644319956547,0.51397272173357389,0.51397272173357389,44,0.64263000951740767]
["2013-02-11T10:00:00","2013-02-11T10:00:00",52.282789999999999,52.107500000000002,51.771320000000003,52.077710000000003,52.060760000000002,51.540619999999997,51.477789999999999,51.631030000000003,50.825360000000003,48.510420000000003,44.89087,42.707120000000003,41.88711,41.953279999999999,42.102159999999998,41.45787,41.310519999999997,41.719850000000001,41.109470000000002,40.236660000000001,40.471980000000002,40.004019999999997,40.104750000000003,39.710410000000003,40.109659999999998,39.792490000000001,6004.1490000000003,6900.5969999999998,12904.75,51.231020000000001,40.138910000000003,29,29,433757.57040000003,309600.6564610448,37496.811127349996,52,41,38271.090494835,44,9.9712911858738735,10.578431185873875,269887.67760462058,7676.2557188286464,7520.9539924921601,1516.8049924921597,7.6014631505967808E-2,6004.1530000000002,5228.4942811713536,0.14009924405605331,0.14009924405605331,0.72952494619295505,0.72952494619295505,7235.6835947358777,5669.0664052641223,0.57354907836268776,0.57354907836268776,44,0.72952494619295505]
["2013-02-11T13:00:00","2013-02-11T13:00:00",52.120849999999997,51.802849999999999,51.458770000000001,51.70458,51.133719999999997,47.996139999999997,43.885509999999996,42.476640000000003,41.803310000000003,41.490659999999998,41.603050000000003,41.397930000000002,41.2654,41.52628,41.385750000000002,40.457920000000001,40.243020000000001,40.497709999999998,39.99212,39.916339999999998,40.224989999999998,39.752719999999997,39.850259999999999,39.445659999999997,39.834150000000001,39.53481,3998.3739999999998,8902.2379999999994,12900.61,50.276589999999999,40.51585,39,39,583329.14639999997,390997.98555271525,25161.847549479993,53,42,43446.21526805999,44,10.208609940640848,10.815749940640845,371590.73469052574,8511.6809282915237,4929.5345195450682,931.16051954506838,0.10222657340457739,3998.3720000000012,4388.9290717084768,0.28837427835291574,0.28837427835291574,0.87770947275547129,0.87770947275547129,8033.8793900565624,4866.7306099434381,0.73648913234092206,0.73648913234092206,44,0.87770947275547129]
["2013-02-11T20:00:00","2013-02-11T20:00:00",49.135680000000001,44.263840000000002,42.22784,42.058929999999997,41.980289999999997,41.399279999999997,41.293170000000003,41.417029999999997,41.135680000000001,40.699779999999997,40.54768,40.16422,40.078429999999997,40.259239999999998,40.482590000000002,39.864139999999999,39.731450000000002,40.197339999999997,39.9255,39.837049999999998,40.235900000000001,39.877029999999998,39.901539999999997,39.29813,39.677320000000002,39.36439,1014.155,7424.3729999999996,6410.2169999999996,52.023739999999997,40.841270000000002,47,47,702986.40720000002,555319.50077680859,4954.8013049749998,49,44,41511.414170654985,44,10.264327223219336,10.871467223219335,450258.58905930951,8088.4822293565212,965.44102642529765,-48.713973574702322,0.12319612692346506,-1014.1559999999999,-1678.2652293565216,0.41927303827667811,0.41927303827667811,0.96224247845955779,0.96224247845955779,7636.7638918130006,-1226.5468918130009,0.90173398835362617,0.90173398835362617,44,0.96224247845955779]
["2013-02-11T23:00:00","2013-02-11T23:00:00",51.890630000000002,49.93235,44.341250000000002,42.614699999999999,42.226260000000003,41.586680000000001,41.388809999999999,41.54768,41.247439999999997,40.944899999999997,41.05762,40.573839999999997,40.24147,40.354120000000002,40.574950000000001,39.956290000000003,39.786949999999997,40.243569999999998,39.958210000000001,39.832160000000002,40.227789999999999,39.921840000000003,39.906370000000003,39.370359999999998,39.765470000000001,39.44444,2202.4079999999999,7053,4857.1890000000003,51.568260000000002,41.261159999999997,47,47,702986.40720000002,531827.75339238509,13705.794212760002,48,43,36347.988150000019,44,10.027407395915002,10.634547395915,439865.78056418372,7249.7280134060538,2733.6665743417411,531.25857434174122,0.12319612692346506,-2195.8109999999997,-2392.5390134060535,0.36574794004325495,0.36574794004325495,0.92284711773642081,0.92284711773642081,6835.8317090132496,-1978.6427090132493,0.86171981212095117,0.86171981212095117,44,0.92284711773642081]
["2013-02-12T08:00:00","2013-02-12T08:00:00",51.891010000000001,51.673279999999998,50.914200000000001,46.58023,43.201149999999998,41.919820000000001,41.65699,41.769530000000003,41.445160000000001,41.099350000000001,41.39134,41.077979999999997,40.72925,40.660089999999997,40.804589999999997,40.12914,39.925510000000003,40.518189999999997,40.265470000000001,40.111930000000001,40.45205,39.991329999999998,40.112859999999998,39.637659999999997,39.88494,39.547699999999999,1112.665,6953.1729999999998,5993.3019999999997,51.826120000000003,41.41675,43,43,643157.77679999999,492770.38573255949,6866.984510575001,47,45,36189.075215505014,44,10.143682464848721,10.750822464848723,407096.86758981226,7135.2933889467367,1353.9431137304261,241.27811373042618,0.11271135016402123,-959.87100000000009,-1141.9913889467371,0.31902098844410598,0.31902098844410598,0.89054581456733162,0.89054581456733162,6732.3361229022466,-739.03412290224696,0.8531015521565174,0.8531015521565174,44,0.89054581456733162]
["2013-02-12T15:00:00","2013-02-12T15:00:00",51.867719999999998,51.547730000000001,51.036389999999997,51.030070000000002,47.080689999999997,42.933250000000001,41.98751,41.939929999999997,41.587090000000003,41.28763,41.568579999999997,41.257379999999998,41.088720000000002,41.094799999999999,41.087589999999999,40.326680000000003,40.054209999999998,40.483179999999997,40.199179999999998,40.040689999999998,40.347140000000003,39.798409999999997,39.9876,39.61553,40.052570000000003,39.713799999999999,321.87119999999999,7017.9849999999997,6696.2430000000004,52.204360000000001,40.974440000000001,41,41,613243.46160000004,477968.66530748387,1955.9984075519999,48,46,39405.705055600003,44,10.314216542395961,10.92135654239596,394687.85342381505,7641.0466841810512,379.2820132313467,57.410813231346708,0.10746896178429931,-321.74199999999928,-944.80368418105081,0.25925311657252936,0.25925311657252936,0.86928467152265931,0.86928467152265931,7216.2656539285654,-520.02265392856498,0.82469215181534317,0.82469215181534317,44,0.86928467152265931]
["2013-02-12T18:00:00","2013-02-12T18:00:00",51.717300000000002,51.563189999999999,51.151240000000001,51.380360000000003,49.766440000000003,44.033729999999998,42.306170000000002,42.078319999999998,41.650880000000001,41.354999999999997,41.643889999999999,41.339799999999997,41.144190000000002,41.235819999999997,41.207839999999997,40.444479999999999,40.141080000000002,40.536180000000002,40.221209999999999,40.05545,40.377879999999998,39.836709999999997,39.968380000000003,39.643859999999997,39.911819999999999,39.781390000000002,208.8142,6899.0460000000003,6698.1239999999998,52.166840000000001,40.923749999999998,41,41,613243.46160000004,473946.48484396003,1246.193748961,48,46,38783.297546070011,44,10.292992446320989,10.900132446320987,393875.68384348304,7535.8643753658398,242.14411026920078,33.329910269200781,0.10746896178429931,-200.92200000000048,-837.74037536584001,0.23165468501317676,0.23165468501317676,0.86128346987456839,0.86128346987456839,7116.1149164128101,-417.99091641281029,{"$f":"IF(BF1023>1,1+BE1024*60/$BK$7,IF(BF1023<0,BE1024*60/$BK$7,BF1023+BE1024*60/$BK$7))","v":0.8103934099394946},0.8103934099394946,44,0.86128346987456839]
["2013-02-13T03:00:00","2013-02-13T03:00:00",51.558349999999997,51.448599999999999,51.082470000000001,51.307690000000001,51.184489999999997,47.918419999999998,43.270310000000002,42.323929999999997,41.775069999999999,41.435830000000003,41.813899999999997,41.448329999999999,41.290680000000002,41.401600000000002,41.429259999999999,40.570529999999998,40.26435,40.611289999999997,40.255499999999998,40.00421,40.392710000000001,39.864719999999998,39.988129999999998,39.588590000000003,39.964759999999998,39.642879999999998,275.39440000000002,6124.2629999999999,6396.317,50.629429999999999,41.315460000000002,39,39,583329.14639999997,399907.54960296943,1640.7268556840002,40,38,28520.600927054995,44,9.4562584916125765,10.063398491612576,344205.3385087272,6032.1111044821646,347.01396057209661,71.619560572096589,0.10222657340457739,272.05400000000009,364.20589551783542,0.21339860665432597,0.21339860665432597,0.85545125245764031,0.85545125245764031,5668.1847490836681,728.13225091633194,0.82821373644128771,0.82821373644128771,44,0.85545125245764031]
["2013-02-13T10:00:00","2013-02-13T10:00:00",51.542819999999999,51.384149999999998,51.004710000000003,51.197569999999999,51.207450000000001,49.085369999999998,44.319679999999998,42.499070000000003,41.837989999999998,41.42801,41.823270000000001,41.51708,41.342820000000003,41.457689999999999,41.524929999999998,40.59592,40.318240000000003,40.644080000000002,40.301850000000002,40.085160000000002,40.43797,39.917389999999997,40.018900000000002,39.618380000000002,39.961579999999998,39.893949999999997,1614.895,6556.9629999999997,5011.7290000000003,51.664290000000001,42.481389999999998,39,39,583329.14639999997,428437.30082635739,9405.8509593250019,41,38,30105.967766350012,44,9.5103195008325372,10.117459500832537,346173.14512010367,6331.2211043413472,1978.0304875144545,363.13548751445455,0.10222657340457739,-1545.2339999999995,-1319.4921043413469,0.20197075132462253,{"$f":"IF(AZ1040>1,1,IF(AZ1040<0,0,AZ1040))","v":0.20197075132462253},0.8516943323260413,{"$f":"IF(BB1040>1,1,BB1040)","v":0.8516943323260413},5951.2899980222664,-939.56099802226618,0.84499001363836346,0.84499001363836346,44,0.8516943323260413]
["2013-02-13T13:00:00","2013-02-13T13:00:00",51.556370000000001,51.246429999999997,50.946300000000001,51.376390000000001,51.450580000000002,50.47804,46.55639,43.184649999999998,42.032440000000001,41.58614,41.793669999999999,41.625120000000003,41.447589999999998,41.558010000000003,41.686920000000001,40.782040000000002,40.413600000000002,40.710929999999998,40.379809999999999,40.232410000000002,40.510890000000003,39.969059999999999,40.08258,39.624160000000003,39.987830000000002,39.702550000000002,492.40190000000001,7192.0110000000004,6699.6090000000004,53.092370000000003,40.920479999999998,37,37,553414.83120000002,462391.79844613915,2918.4217451290001,51,43,43770.183385395023,44,10.280504253441972,10.88764425344197,355017.53202673502,8515.182194636127,567.75848210984316,75.356582109843146,9.6984185024855479E-2,-492.40200000000004,-1815.5731946361266,0.15574331768155203,0.15574331768155203,0.84287803321957822,0.84287803321957822,8040.340475224054,-1340.7314752240536,0.81334826658231607,0.81334826658231607,44,0.84287803321957822]
["2013-02-13T20:00:00","2013-02-13T20:00:00",53.042070000000002,52.242890000000003,51.359139999999996,51.686950000000003,51.781280000000002,51.315510000000003,51.263260000000002,51.459299999999999,51.152920000000002,50.601230000000001,46.073369999999997,42.956339999999997,42.162619999999997,42.168509999999998,42.371409999999997,41.701030000000003,41.397060000000003,41.689100000000003,41.220640000000003,40.841740000000001,40.906770000000002,40.404960000000003,40.27919,39.834229999999998,40.179699999999997,39.84348,446.56990000000002,7036.085,6594.451,52.52816,40.943600000000004,29,29,433757.57040000003,343329.54103353183,2947.046508220501,49,42,40754.974423799984,44,10.11683862785158,10.723978627851579,273827.13342477614,8056.8596422210085,582.60225681712541,136.03235681712539,7.6014631505967808E-2,-441.63400000000001,-1462.4086422210084,-1.537694716618682E-2,0,0.73172654736081533,0.73172654736081533,7600.7190685654614,-1006.2680685654614,0.66887298294186048,0.66887298294186048,43,0.73172654736081533]
["2013-02-14","2013-02-14",52.955689999999997,52.489530000000002,51.486130000000003,51.712960000000002,51.789549999999998,51.282690000000002,51.290869999999998,51.46949,51.193939999999998,50.657640000000001,48.210320000000003,43.542319999999997,42.485660000000003,42.315480000000001,42.391280000000002,41.754550000000002,41.478969999999997,41.778840000000002,41.310589999999998,40.857480000000002,40.951990000000002,40.46734,40.404429999999998,39.953189999999999,40.25929,39.870109999999997,178.06630000000001,6491.7020000000002,6597.2740000000003,51.652030000000003,40.995699999999999,29,29,433757.57040000003,318895.01241606346,1165.0504069770002,42,39,34588.859386830009,44,9.7240331050909035,10.331173105090903,263195.27358717204,7114.0974147283441,239.62287959860026,61.556579598600251,7.6014631505967808E-2,105.57200000000012,-516.82341472834378,-5.4342993559285705E-3,0,0.73167162851478951,0.73167162851478951,6696.0177774556159,-98.7437774556156,0.65325552406363951,0.65325552406363951,43,0.73167162851478951]
["2013-02-14T07:00:00","2013-02-14T07:00:00",52.709040000000002,52.314100000000003,51.429279999999999,51.690370000000001,51.759079999999997,51.226179999999999,51.255220000000001,51.432960000000001,51.256410000000002,50.656210000000002,47.115879999999997,43.5411,42.60548,42.514279999999999,42.497419999999998,41.80592,41.481960000000001,41.773789999999998,41.271999999999998,40.749299999999998,41.044620000000002,40.535780000000003,40.669269999999997,40.245429999999999,40.46255,39.957439999999998,434.15839999999997,6372.4740000000002,6806.6319999999996,51.43985,40.641869999999997,29,29,433757.57040000003,310788.3332696479,2768.1071267200005,36,35,34404.923401260014,44,9.4743728879829678,10.081512887982967,256437.85221319972,7262.7336517223766,584.33569365440337,150.1772936544034,7.6014631505967808E-2,434.15799999999945,-456.10165172237703,-4.7958216318347057E-3,0,0.75467875555000197,0.75467875555000197,6825.3492870638947,-18.717287063895128,0.66434352772219551,0.66434352772219551,43,0.75467875555000197]
["2013-02-14T14:00:00","2013-02-14T14:00:00",53.540419999999997,52.653820000000003,52.25168,52.52111,52.317970000000003,51.699350000000003,51.20147,51.455730000000003,51.192439999999998,51.075229999999998,51.259369999999997,51.273589999999999,51.032069999999997,48.423259999999999,44.795990000000003,42.968339999999998,42.286380000000001,42.54956,42.15117,41.83135,41.825679999999998,41.234859999999998,41.423439999999999,40.638019999999997,41.014760000000003,40.577260000000003,2762.8539999999998,9573.5480000000007,6810.6930000000002,53.07582,40.92427,23,23,344014.62479999999,268300.49556587392,17907.659229319994,66,50,58166.723599700003,44,11.197355274749771,11.804495274749769,240368.16795234944,10389.368234277064,3198.5515847125212,435.69758471252135,6.0287466366802052E-2,-2762.8550000000005,-3578.6752342770642,-3.7629085615115854E-2,0,0.64199932077463961,0.64199932077463961,9855.0123907661982,-3044.319390766198,0.54213771495902863,0.54213771495902863,43,0.64199932077463961]
["2013-02-14T17:00:00","2013-02-14T17:00:00",53.96651,53.560130000000001,52.97278,52.968980000000002,52.687890000000003,52.387009999999997,52.08717,51.838189999999997,51.396680000000003,51.209339999999997,51.321199999999997,51.287080000000003,51.226709999999997,51.463639999999998,51.779449999999997,50.006340000000002,45.227730000000001,43.679630000000003,42.87303,42.508980000000001,42.518470000000001,41.991840000000003,41.707889999999999,41.030520000000003,41.525449999999999,40.719180000000001,1920.7,8913.9920000000002,6993.2920000000004,54.216320000000003,40.931870000000004,19,19,284185.99440000003,239347.56471325544,12722.073365499997,67,49,59208.740512199998,44,11.172041051466021,11.77918105146602,198116.10597096194,10599.449149791744,2277.4841780286115,356.78417802861145,4.9802689607358223E-2,-1920.6999999999998,-3606.1571497917439,-3.7918052700439582E-2,0,0.56718267128997124,0.56718267128997124,10053.11663917942,-3059.8246391794191,0.44163028912437363,0.44163028912437363,43,0.56718267128997124]
["2013-02-15","2013-02-15",53.79542,53.354880000000001,52.675530000000002,52.750799999999998,52.735810000000001,52.166429999999998,51.794040000000003,51.695720000000001,51.30265,51.055819999999997,51.323459999999997,51.237819999999999,51.213320000000003,51.266970000000001,50.199399999999997,45.874290000000002,43.536850000000001,42.998980000000003,42.369140000000002,42.187390000000001,42.08043,41.185609999999997,41.239800000000002,40.854480000000002,41.265610000000002,40.914090000000002,7005.3980000000001,6992.393,13997.79,51.950890000000001,40.482300000000002,19,19,284185.99440000003,195717.84853882063,45119.421709669994,50,43,40096.444217934994,44,10.155229747831584,10.762369747831585,180084.78160907398,7896.7084376395669,8885.9479952788297,1880.5499952788296,4.9802689607358223E-2,7005.3970000000008,6101.081562360434,0.12271970597437845,0.12271970597437845,0.67269477080920759,0.67269477080920759,7451.2296376016402,6546.5603623983607,0.49456463746561596,0.49456463746561596,44,0.67269477080920759]
["2013-02-15T09:00:00","2013-02-15T09:00:00",51.327620000000003,49.559919999999998,45.699339999999999,43.769880000000001,42.908679999999997,42.205550000000002,42.056190000000001,41.935209999999998,41.277450000000002,40.97166,41.251519999999999,40.974150000000002,40.905119999999997,41.273110000000003,41.720230000000001,41.151499999999999,40.899039999999999,41.399290000000001,41.107219999999998,40.958480000000002,41.243510000000001,40.794449999999998,40.931170000000002,40.537280000000003,40.955750000000002,40.591250000000002,6106.6959999999999,6521.68,12628.38,51.776179999999997,40.776310000000002,47,47,702986.40720000002,490642.07434216986,{"$f":"500*AC1087*(C1087-AB1087)/1000","v":32781.873866760005},46,41,35868.816090799977,44,{"$f":"19.5286-0.30357*AP1087+0.0000341*AO1087+0.060847*AN1087","v":9.8893736286962799},{"$f":"19.5286-0.30357*42+0.0000341*AO1087+0.060847*AN1087","v":10.496513628696281},{"$f":"62.4*AJ1087*AQ1087/1000","v":433810.742769807},7254.0117175305031,{"$f":"AL1087*1000/(500*AQ1087)","v":6629.7169259812172},523.02092598121726,0.12319612692346506,6106.6999999999989,5374.3682824694961,0.60854135715651647,0.60854135715651647,1.0642107825054565,1,6834.4247165532552,5793.955283446744,1.0197583857867047,{"$f":"IF(BF1087>1,1,IF(BF1087<0,0,BF1087))","v":1},44,1]
["2013-02-15T12:00:00","2013-02-15T12:00:00",42.811199999999999,42.305439999999997,41.523290000000003,41.643970000000003,41.59122,40.98359,40.860399999999998,41.136090000000003,41.040399999999998,40.987250000000003,41.330219999999997,41.100650000000002,40.986780000000003,41.187489999999997,41.398969999999998,40.748989999999999,40.652119999999996,41.135159999999999,40.881999999999998,40.73912,41.084609999999998,40.644799999999996,40.781849999999999,40.413440000000001,40.843060000000001,40.487769999999998,6133.0829999999996,6498.0820000000003,12631.17,51.7898,40.5916,51,51,762815.03760000004,537972.76661895495,7124.8945173450056,46,38,36383.410926200006,44,9.7243803125834223,10.331520312583422,462877.18050787342,7482.9263678878524,1465.3673115037136,-4667.715688496286,0.13368090368290891,6133.0879999999997,5148.2436321121477,0.7727761328423296,0.7727761328423296,1.0644882472783705,1,7043.1862543765819,5587.9837456234181,1.0587565803026595,1,44,1]
["2013-02-15T19:00:00","2013-02-15T19:00:00",43.142600000000002,41.493679999999998,40.923929999999999,41.251170000000002,41.540599999999998,41.256120000000003,41.463700000000003,41.440080000000002,41.376379999999997,41.088250000000002,41.33896,40.978859999999997,40.90889,41.14564,41.457920000000001,40.914749999999998,40.808459999999997,41.288359999999997,41.029559999999996,40.85577,41.164279999999998,40.707850000000001,40.822839999999999,40.43562,40.83934,40.511600000000001,247.43969999999999,6473.1270000000004,6229.6260000000002,52.059269999999998,40.73216,51,51,762815.03760000004,549665.14669512515,325.50692535000002,45,35,36660.910786484994,44,9.5513020578191394,10.158442057819139,454638.71471393009,7676.6310110510367,68.159696631837747,-179.28000336816223,0.13368090368290891,-243.5010000000002,-1447.0050110510365,0.72848652416891124,0.72848652416891124,0.97458930335073424,0.97458930335073424,7217.8215080267,-988.19550802669983,0.93197953470389439,0.93197953470389439,44,1]
["2013-02-15T22:00:00","2013-02-15T22:00:00",47.591949999999997,42.400280000000002,41.129930000000002,41.587310000000002,42.380859999999998,41.832000000000001,41.424579999999999,42.164400000000001,41.873989999999999,41.205649999999999,41.452669999999998,41.075760000000002,40.93647,41.182020000000001,41.469769999999997,40.929780000000001,40.816029999999998,41.302759999999999,41.026049999999998,40.767420000000001,41.12144,40.691510000000001,40.830449999999999,40.444809999999997,40.877180000000003,40.540199999999999,134.0213,6122.3990000000003,6221.1310000000003,51.261450000000004,40.729030000000002,49,49,732900.72239999997,490314.98068993457,472.54235113749985,40,33,32241.838837790005,44,9.2789177043686397,9.8860577043686391,424352.79049000813,6949.4826584376569,101.85290271838936,-32.168397281610638,0.12843851530318698,98.731999999999971,-728.35165843765662,0.6963922446444909,0.6963922446444909,0.97315687095668857,0.97315687095668857,6522.6887808964275,-301.55778089642718,0.9138115404132805,0.9138115404132805,44,0.99856756760595433]
["2013-02-16T07:00:00","2013-02-16T07:00:00",49.43497,48.525359999999999,42.589260000000003,42.96604,42.359610000000004,41.645119999999999,41.631250000000001,42.084679999999999,41.885899999999999,41.583350000000003,41.767539999999997,41.264159999999997,41.204430000000002,41.336590000000001,41.532710000000002,40.968820000000001,40.860590000000002,41.3506,41.051969999999997,40.695489999999999,41.116399999999999,40.697899999999997,40.892069999999997,40.481810000000003,40.923189999999998,40.620310000000003,210.2346,5893.3720000000003,6100.1310000000003,50.049480000000003,40.598599999999998,47,47,702986.40720000002,413623.28848950868,926.57325961799961,32,29,27848.775783680016,44,8.8857262542234885,9.4928662542234896,389784.39394872333,6268.2047560137626,208.55318588676724,-1.681414113232762,0.12319612692346506,206.75900000000001,-168.07375601376225,0.68234632697973163,0.68234632697973163,0.98828859551552217,0.98828859551552217,5867.3060460089728,232.82495399102754,0.93734842597178436,0.93734842597178436,44,1]
["2013-02-16T14:00:00","2013-02-16T14:00:00",49.020240000000001,44.001080000000002,43.609789999999997,44.05077,44.087989999999998,43.582160000000002,43.404339999999998,43.239370000000001,42.580669999999998,41.88785,41.89714,41.803539999999998,41.763500000000001,42.061920000000001,42.19567,41.372540000000001,41.06673,41.574539999999999,41.393839999999997,41.254950000000001,41.580770000000001,41.046900000000001,41.122480000000003,40.868200000000002,41.274160000000002,40.891590000000001,359.4597,7203.902,7093.2910000000002,52.620480000000001,40.73621,49,49,732900.72239999997,536397.38592648844,1460.9610452025001,52,40,42806.558210770003,44,10.065103634987258,10.672243634987257,460307.43564705289,8505.9349139675687,290.30223595990816,-69.157464040091838,0.12843851530318698,-110.61099999999988,-1412.6439139675686,0.60360153438802733,0.60360153438802733,0.96606390694274913,0.96606390694274913,8022.0354172641819,-928.74441726418172,0.89052933608655527,0.89052933608655527,44,0.97615583110058446]
["2013-02-16T17:00:00","2013-02-16T17:00:00",48.780450000000002,44.245820000000002,43.929279999999999,44.249009999999998,44.39555,43.995609999999999,43.926169999999999,44.144680000000001,43.906959999999998,43.526060000000001,43.344479999999997,42.730899999999998,42.261360000000003,41.819969999999998,41.883110000000002,41.328780000000002,41.16919,41.573770000000003,41.322800000000001,41.206299999999999,41.504379999999998,41.064889999999998,41.187379999999997,40.881309999999999,41.400390000000002,40.947009999999999,138.28219999999999,7334.8990000000003,7399.8710000000001,53.17897,40.786160000000002,49,49,732900.72239999997,559404.28879095719,541.61265838400016,55,42,45450.004838094988,44,10.276939164979041,10.88407916497904,469995.31101581705,8845.0469752659428,105.40349605837231,-32.878703941627677,0.12843851530318698,64.971999999999753,-1445.1759752659427,0.55903559209761133,0.55903559209761133,0.96722402682016118,0.96722402682016118,8351.6490736922187,-951.77807369221864,0.86151177215634733,0.86151177215634733,44,0.97731595097799651]
["2013-02-17","2013-02-17",44.669029999999999,44.309229999999999,44.000579999999999,44.322220000000002,44.456960000000002,44.01379,44.02516,44.253810000000001,44.044280000000001,43.880499999999998,44.277459999999998,44.165950000000002,41.956330000000001,41.739190000000001,42.087269999999997,41.566769999999998,41.433349999999997,41.894109999999998,41.627769999999998,41.450490000000002,41.761670000000002,41.293500000000002,41.36045,40.885390000000001,41.29627,40.974060000000001,425.01459999999997,6370.2849999999999,6795.3,50.982779999999998,40.75132,27,27,403843.25520000001,252217.9336675654,785.20809828099948,44,37,32588.658083049995,44,9.5341322406320046,10.141272240632006,240258.40797279976,6836.208531735183,164.71516829494891,-260.29943170505106,7.0772243126245887E-2,425.01500000000033,-40.908531735182805,0.52644735992796421,0.52644735992796421,1.0044689514347449,1,6426.9368398336301,368.36316016637011,0.86190549145496165,0.86190549145496165,44,1]
["2013-02-17T09:00:00","2013-02-17T09:00:00",44.545009999999998,44.267150000000001,43.963569999999997,44.29824,44.455570000000002,44.001449999999998,44.018329999999999,44.265430000000002,44.082599999999999,43.920189999999998,44.27272,43.280949999999997,41.866019999999999,42.133290000000002,42.469749999999998,41.93242,41.819400000000002,42.27946,42.023989999999998,41.900939999999999,42.249459999999999,41.826439999999998,41.905749999999998,41.511009999999999,41.785980000000002,41.248179999999998,290.33139999999997,6713.1859999999997,7000.098,51.6051,40.639850000000003,51,51,762815.03760000004,492985.8535193401,478.58663473099995,48,41,36805.881393249991,44,9.9213275555098264,10.528467555509824,472251.80198340421,7419.5476739017213,96.476329816409702,-193.85507018359027,0.13368090368290891,286.91200000000026,-419.44967390172133,0.5285248615660737,0.5285248615660737,1.0030168248039375,1,6991.6882393750657,8.4097606249342789,0.90280513878006141,0.90280513878006141,44,1]
["2013-02-17T12:00:00","2013-02-17T12:00:00",53.230559999999997,46.943600000000004,44.028179999999999,44.404829999999997,44.488160000000001,44.1158,44.007579999999997,44.249780000000001,44.085430000000002,43.99447,44.19135,44.203290000000003,43.924239999999998,42.453240000000001,42.570610000000002,41.962730000000001,41.791539999999998,42.235239999999997,42.047179999999997,42.098489999999998,42.358780000000003,41.919409999999999,41.962569999999999,41.56568,41.950189999999999,41.582070000000002,1279.0029999999999,8719.5640000000003,7440.5619999999999,54.542050000000003,40.901420000000002,47,47,702986.40720000002,568507.04212123272,7449.2268277349967,67,49,59470.173142660009,44,11.180955904164708,11.788095904164706,490467.74525613547,10637.761860863509,1332.4847878096525,53.481787809652587,0.12319612692346506,-1279.0020000000004,-3197.1998608635095,0.38279116584550826,0.38279116584550826,0.95194100467843157,0.95194100467843157,10089.869242012077,-2649.307242012077,0.77615807597758502,0.77615807597758502,44,0.9707112210780755]
["2013-02-17T19:00:00","2013-02-17T19:00:00",54.942129999999999,54.769179999999999,54.273609999999998,54.210299999999997,47.798760000000001,44.070830000000001,43.969630000000002,44.18777,44.029260000000001,43.95252,44.130209999999998,44.150840000000002,44.117890000000003,44.371310000000001,44.70234,44.076000000000001,42.177799999999998,42.544620000000002,42.297710000000002,42.224290000000003,42.495139999999999,42.056199999999997,42.070439999999998,41.62688,42.032150000000001,41.733699999999999,264.0498,7649.0249999999996,7427.3059999999996,53.299500000000002,40.777149999999999,41,41,613243.46160000004,442581.43663801276,1743.8416499069999,64,49,47891.884104375014,44,10.786136247959188,11.393276247959189,412746.51787123422,8880.2668543031778,323.3487153913797,59.298915391379694,0.10746896178429931,-221.71900000000005,-1452.9608543031782,0.20984949681409343,0.20984949681409343,0.87638595275030817,0.87638595275030817,8407.0434284350122,-979.73742843501259,0.64062936028133588,0.64062936028133588,44,0.89515616914995211]
["2013-02-18","2013-02-18",54.06129,54.027709999999999,54.128740000000001,54.549689999999998,54.26126,47.990360000000003,44.15361,44.373460000000001,44.217370000000003,44.110759999999999,44.377450000000003,44.322929999999999,44.291939999999997,44.557899999999997,44.881300000000003,44.285769999999999,44.15455,43.112290000000002,42.484319999999997,42.359749999999998,42.565620000000003,42.139389999999999,42.16046,41.756799999999998,42.152380000000001,41.779339999999998,1108.5219999999999,7110.1260000000002,6001.6049999999996,51.810339999999997,40.952419999999996,39,39,583329.14639999997,365125.7792543961,6807.4058889500011,58,51,38600.589648959998,44,10.590997107029537,11.198137107029536,385509.5276428287,7289.3211581258429,1285.5080253835094,{"$f":"AU1150-AC1150","v":176.98602538350951},0.10222657340457739,{"$f":"AE1150-AD1150","v":-1108.5210000000006},-1287.7161581258433,0.150986821195077,0.150986821195077,0.8548672074064233,0.8548672074064233,{"$f":"AO1150*1000/(500*AR1150)","v":6894.1091326214973},{"$f":"AE1150-BD1150","v":-892.50413262149777},0.60426969032358047,0.60426969032358047,44,0.87363742380606724]
["2013-02-18T04:00:00","2013-02-18T04:00:00",53.644289999999998,53.54918,53.298290000000001,53.678730000000002,54.155839999999998,54.01605,53.768079999999998,47.531730000000003,44.531480000000002,44.30556,44.514029999999998,44.446449999999999,44.41254,44.671660000000003,45.003509999999999,44.404829999999997,44.272869999999998,44.773020000000002,44.549639999999997,42.93797,42.890430000000002,42.28098,42.339500000000001,41.945360000000001,42.322740000000003,41.85595,1285.6659999999999,7285.5320000000002,5999.866,51.993580000000001,41.162529999999997,35,35,523500.516,331160.20304746582,7577.9339672199994,59,54,39454.980684300019,44,10.802672841334632,11.409812841334631,352884.77993295481,7304.6701059634233,1402.9738896144841,117.30788961448411,9.1741796645133558E-2,-1285.6660000000002,-1304.8041059634234,9.9452489162562399E-2,9.9452489162562399E-2,0.80473991766214359,0.80473991766214359,6915.9733350516353,-916.10733505163535,0.56910626625830474,0.56910626625830474,44,0.82351013406178752]
["2013-02-18T13:00:00","2013-02-18T13:00:00",54.023949999999999,53.701729999999998,53.429470000000002,53.881909999999998,53.428179999999998,45.353540000000002,44.345019999999998,44.376139999999999,44.183149999999998,44.127000000000002,44.217140000000001,44.314279999999997,44.239429999999999,44.456229999999998,44.747070000000001,44.114199999999997,43.927199999999999,44.36383,44.112479999999998,43.359050000000003,43.027299999999997,42.330840000000002,41.368319999999997,40.691780000000001,40.809480000000001,40.674680000000002,2020.569,10782.85,12803.42,52.20843,40.77073,41,41,613243.46160000004,441354.9987742895,13486.560567314997,77,58,61665.501722499997,44,11.803439608737252,12.410579608737249,451675.04706159153,10448.734227750594,2285.1916075940862,264.62260759408628,0.10746896178429931,2020.5699999999997,2354.685772249406,0.28716715714670693,0.28716715714670693,0.95834132669653305,0.95834132669653305,9937.5699873173508,2865.8500126826493,0.80139876719346526,0.80139876719346526,44,0.97711154309617698]
["2013-02-18T16:00:00","2013-02-18T16:00:00",54.008769999999998,53.776040000000002,50.627220000000001,45.129390000000001,44.815019999999997,44.269550000000002,44.116349999999997,44.315170000000002,44.161119999999997,44.119819999999997,44.235259999999997,44.283659999999998,44.214790000000001,44.425559999999997,44.630940000000002,43.86674,43.35951,43.350940000000001,42.767429999999997,42.435540000000003,42.011040000000001,41.250369999999997,41.000599999999999,40.411749999999998,40.520209999999999,40.297440000000002,4153.25,9048.741,13201.99,53.089390000000002,40.260539999999999,45,45,673072.09200000006,537258.04374898656,28473.29066124999,67,50,58042.470488925013,44,11.193118243672345,11.800258243672342,470107.59196576726,10371.099317518134,5087.6422532829783,934.39225328297834,0.11795373854374315,4153.2489999999998,2830.890682481866,0.37697104883893617,0.37697104883893617,1.0436706188661642,1,9837.4915684661646,3364.4984315338352,0.90771259391153258,0.90771259391153258,44,1]
["2013-02-18T23:00:00","2013-02-18T23:00:00",44.653709999999997,44.418979999999998,44.116959999999999,44.409950000000002,44.559989999999999,44.139299999999999,44.015819999999998,43.910679999999999,43.20729,42.560279999999999,42.42022,41.819499999999998,41.237139999999997,41.37256,41.27261,40.526260000000001,40.40598,40.89837,40.656619999999997,40.580730000000003,40.899509999999999,40.43891,40.546590000000002,40.156190000000002,40.552010000000003,40.261200000000002,4754.7089999999998,7644.97,12399.68,50.991810000000001,40.072760000000002,51,51,762815.03760000004,510773.36984674633,10442.553414794987,50,41,41737.904839249997,44,10.089509555018427,10.696649555018425,480257.20770000113,8273.5250136097966,2069.9823629387338,-2684.726637061266,0.13368090368290891,4754.71,4126.1549863902037,0.65577874304493711,0.65577874304493711,1.049994866243064,1,7803.9211483128947,4595.7588516871056,1.0483235253202559,1,44,1]
["2013-02-19T08:00:00","2013-02-19T08:00:00",42.94209,42.174079999999996,41.201770000000003,40.738039999999998,40.698810000000002,40.180759999999999,40.227539999999998,40.445239999999998,40.248959999999997,40.095410000000001,40.479819999999997,40.321109999999997,40.308169999999997,40.63158,40.982880000000002,40.447220000000002,40.368340000000003,40.870640000000002,40.596069999999997,40.449440000000003,40.79636,40.330979999999997,40.439529999999998,40.042059999999999,40.417850000000001,40.071309999999997,562.51610000000005,6762.4049999999997,6199.8890000000001,51.46707,40.269240000000003,51,51,762815.03760000004,542434.28259574808,807.42998477900107,44,37,37862.130790574993,44,9.7139576599586093,10.321097659958607,462381.06580387079,7795.4078277784711,166.24119911645602,-396.27490088354403,0.13368090368290891,-562.51599999999962,-1595.5188277784709,0.95248715529032968,0.95248715529032968,0.98926569463208314,0.98926569463208314,7336.841882131137,-1136.9528821311369,0.9764030123182238,0.9764030123182238,44,1]
["2013-02-19T11:00:00","2013-02-19T11:00:00",46.132820000000002,43.060209999999998,41.859659999999998,41.47972,40.942100000000003,40.26829,40.24335,40.487879999999997,40.309559999999998,40.195450000000001,40.511690000000002,40.437860000000001,40.402239999999999,40.717640000000003,41.062809999999999,40.498559999999998,40.399679999999996,40.886560000000003,40.624490000000002,40.527349999999998,40.821820000000002,40.362580000000001,40.451920000000001,40.044339999999998,40.436680000000003,40.134540000000001,1147.922,7344.8509999999997,6196.9290000000001,52.362400000000001,40.307830000000003,49,49,732900.72239999997,559216.78347013833,3442.7787870800007,52,39,44269.510259534989,44,10.054143299850145,10.661283299850144,459806.18658457336,8806.2222586771422,684.84776562341517,-463.07423437658485,0.12843851530318698,-1147.9219999999996,-2609.2932586771421,0.88286306397010661,0.88286306397010661,0.96027873278010412,0.96027873278010412,8304.7244903729843,-2107.7954903729842,0.92202397604423403,0.92202397604423403,44,0.98792981972665617]
["2013-02-19T18:00:00","2013-02-19T18:00:00",53.033059999999999,52.421219999999998,51.957540000000002,52.112560000000002,52.047080000000001,51.445799999999998,48.517099999999999,43.57555,42.306959999999997,41.468000000000004,41.031959999999998,40.643450000000001,40.524859999999997,40.782850000000003,41.124130000000001,40.552990000000001,40.371540000000003,40.896149999999999,40.686279999999996,40.604379999999999,40.863750000000003,40.430419999999998,40.496589999999998,40.085349999999998,40.483040000000003,40.186390000000003,2018.3989999999999,8223.5779999999995,6205.1790000000001,52.365079999999999,40.267099999999999,37,37,553414.83120000002,420567.74264463672,12964.852940664996,58,43,49744.341086219996,44,10.484223031040102,11.091363031040103,362052.56998473953,9489.371017565054,2473.2119685513403,454.81296855134042,9.6984185024855479E-2,-2018.3989999999994,-3284.1920175650539,0.61587957287938344,0.61587957287938344,0.76452603165298694,0.76452603165298694,8969.9238852801609,-2764.7448852801608,0.69438121550717469,0.69438121550717469,44,0.79217711859953899]
["2013-02-19T21:00:00","2013-02-19T21:00:00",52.978940000000001,52.743020000000001,52.380749999999999,52.552410000000002,52.424140000000001,51.791319999999999,51.610880000000002,51.759340000000002,47.600230000000003,43.124740000000003,42.329070000000002,41.548839999999998,40.805959999999999,40.853099999999998,41.219859999999997,40.590319999999998,40.42154,40.913890000000002,40.700839999999999,40.639949999999999,40.870249999999999,40.392620000000001,40.480519999999999,40.079569999999997,40.513460000000002,40.207169999999998,1333.2750000000001,7533.1859999999997,6199.91,52.185169999999999,40.259619999999998,33,33,493586.20079999999,368919.75202258182,8514.1408233750008,56,42,44918.693151150001,44,10.258821436454216,10.865961436454215,315969.4323243142,8757.0864605428542,1659.8672422780305,326.59224227803043,8.6499408265411637E-2,-1333.2759999999998,-2557.1764605428543,0.53026798288903121,0.53026798288903121,0.71754009359250004,0.71754009359250004,8267.7807046971975,-2067.8707046971977,0.62443355135617185,0.62443355135617185,44,0.74519118053905209]
["2013-02-20T04:00:00","2013-02-20T04:00:00",52.425269999999998,52.257300000000001,51.908819999999999,52.252369999999999,52.400370000000002,51.89179,51.95252,52.131309999999999,51.950809999999997,51.725969999999997,52.046100000000003,47.570790000000002,43.484920000000002,42.690460000000002,42.123370000000001,40.974640000000001,40.801780000000001,41.084139999999998,40.78951,40.590890000000002,40.911769999999997,40.44838,40.616010000000003,40.20337,40.589460000000003,40.250239999999998,466.67619999999999,6667.5110000000004,6200.8339999999998,50.852310000000003,40.217880000000001,27,27,403843.25520000001,267170.24634507584,2840.8983676430003,46,43,35452.589501865004,44,9.9968743020135982,10.604014302013596,251919.42422090494,7092.7348750847141,568.35732486318818,101.68112486318819,7.0772243126245887E-2,-466.67700000000059,-891.90087508471424,0.42563872629037247,0.42563872629037247,0.64693324756647996,0.64693324756647996,6686.6355499224319,-485.80154992243206,0.55172444608348747,0.55172444608348747,44,0.67458433451303201]
["2013-02-20T13:00:00","2013-02-20T13:00:00",52.297240000000002,52.172719999999998,51.822139999999997,52.165100000000002,52.327829999999999,51.825420000000001,51.906019999999998,52.088900000000002,51.890230000000003,51.728540000000002,52.158569999999997,51.980589999999999,51.960479999999997,49.832239999999999,44.821899999999999,43.024180000000001,41.595350000000003,41.558039999999998,41.211320000000001,40.764899999999997,41.102069999999998,40.600160000000002,40.696930000000002,40.308430000000001,40.669609999999999,40.293430000000001,382.96050000000002,6583.5069999999996,6200.5460000000003,51.797199999999997,40.277329999999999,23,23,344014.62479999999,246945.82350893485,2298.4925397525003,46,42,37920.572392044989,44,10.020185518568734,10.627325518568735,215098.43856364134,7568.8363896602777,458.77245196570226,75.811951965702235,6.0287466366802052E-2,-382.96099999999933,-1368.2903896602775,0.30793311002134643,0.30793311002134643,0.60482438272700012,0.60482438272700012,7136.4281306313178,-935.88213063131752,0.47438276691984632,0.47438276691984632,44,0.63247546967355217]
["2013-02-20T16:00:00","2013-02-20T16:00:00",52.28895,52.156059999999997,51.81729,52.154060000000001,52.297280000000001,51.800139999999999,51.85078,52.018509999999999,51.807380000000002,51.613779999999998,51.985950000000003,51.799050000000001,51.682769999999998,51.535589999999999,48.764589999999998,44.155650000000001,42.516800000000003,41.906039999999997,41.170630000000003,40.91236,41.191049999999997,40.680230000000002,40.70626,40.333530000000003,40.723550000000003,40.325299999999999,337.00020000000001,6536.2070000000003,6200.6109999999999,51.44567,40.267449999999997,21,21,314100.30960000004,217957.68757567287,2015.8762213650004,45,40,36531.579905770013,44,9.8511268747867593,10.458266874786759,193080.70087983465,7416.7311760586344,409.26814708365771,{"$f":"AU1214-AC1214","v":72.267947083657702},5.5045077987080138E-2,{"$f":"AE1214-AD1214","v":-335.59600000000046},-1216.1201760586346,0.26704323110036837,0.26704323110036837,0.59350596921901411,0.59350596921901411,{"$f":"AO1214*1000/(500*AR1214)","v":6986.1632607295423},{"$f":"AE1214-BD1214","v":-785.55226072954247},0.44714082925364274,0.44714082925364274,44,0.62115705616556616]
["2013-02-20T23:00:00","2013-02-20T23:00:00",52.115879999999997,52.069270000000003,51.741030000000002,52.090069999999997,52.255659999999999,51.748690000000003,51.820720000000001,52.011090000000003,51.801589999999997,51.608080000000001,51.9878,51.786209999999997,51.60633,51.624360000000003,50.676169999999999,44.91545,42.874890000000001,42.060780000000001,41.334789999999998,40.957039999999999,41.243119999999998,40.743380000000002,40.784759999999999,40.351599999999998,40.718220000000002,40.396090000000001,1278.5029999999999,5222.5529999999999,6501.0559999999996,50.999110000000002,40.201450000000001,19,19,284185.99440000003,188025.53841820871,7491.8933371849971,43,39,28195.675812990001,44,9.5060255452229594,10.113165545222959,168572.30971532571,5932.1691655160994,1576.2409435034351,297.73794350343519,4.9802689607358223E-2,1278.5029999999997,568.8868344839002,0.24259248139424386,0.24259248139424386,0.62471535156015012,0.62471535156015012,5576.033673513527,925.02232648647259,0.45202971708152034,0.45202971708152034,44,0.65236643850670217]
["2013-02-21T08:00:00","2013-02-21T08:00:00",52.061079999999997,51.937420000000003,51.637869999999999,52.026859999999999,52.236130000000003,51.724969999999999,51.776240000000001,51.953139999999998,51.737349999999999,51.520319999999998,51.83372,51.496879999999997,51.015090000000001,49.066200000000002,44.797220000000003,42.701689999999999,41.43768,41.490220000000001,41.123989999999999,40.848269999999999,41.220179999999999,40.765529999999998,40.731140000000003,40.293669999999999,40.794530000000002,40.198250000000002,390.83609999999999,6107.7139999999999,6498.55,51.406820000000003,40.220410000000001,21,21,314100.30960000004,219686.39516761224,2318.2111060814987,47,46,34161.696483370004,44,10.135395850082919,10.742535850082918,198652.33280440702,6741.0680329945917,457.44855758397102,66.612457583971036,5.5045077987080138E-2,390.83600000000024,-242.51803299459152,0.27718805690012244,0.27718805690012244,0.71099059798286701,0.71099059798286701,6360.0805173214894,138.46948267851076,0.52072905185729612,0.52072905185729612,44,0.73864168492941906]
["2013-02-21T11:00:00","2013-02-21T11:00:00",52.189839999999997,52.009540000000001,51.733420000000002,52.063780000000001,52.206150000000001,51.738669999999999,51.755859999999998,51.92783,51.724679999999999,51.509689999999999,51.7667,51.480179999999997,50.940089999999998,48.794130000000003,44.666370000000001,42.637410000000003,41.37491,41.463970000000003,41.133560000000003,40.948830000000001,41.38111,40.891970000000001,40.766539999999999,40.292409999999997,41.289679999999997,40.273139999999998,221.48650000000001,7169.4030000000002,7001.915,52.333190000000002,41.10087,21,21,314100.30960000004,236375.28338058843,1319.6940872749999,50,47,40264.514352480001,44,10.404348939419569,11.01148893941957,203923.77551882659,7739.9392478903646,253.68124328760206,32.194743287602051,5.5045077987080138E-2,-167.48800000000028,-738.02424789036468,0.26251835054135603,0.26251835054135603,0.71664395850320306,0.71664395850320306,7313.1825448852333,-311.26754488523329,0.51895302521397579,0.51895302521397579,44,0.74429504544975511]
["2013-02-21T18:00:00","2013-02-21T18:00:00",52.383470000000003,52.10098,51.793610000000001,52.127119999999998,52.212479999999999,51.88449,51.81662,52.058909999999997,51.920769999999997,51.84507,52.013129999999997,52.033270000000002,51.965089999999996,51.796939999999999,51.413510000000002,47.730739999999997,43.669460000000001,42.874600000000001,41.53443,41.22298,41.619700000000002,41.086109999999998,40.957470000000001,40.56503,40.895310000000002,40.561729999999997,299.0265,7692.6040000000003,7401.75,52.719549999999998,38.897390000000001,19,19,284185.99440000003,215597.12718561941,1767.5067680550007,65,48,53164.201652319993,44,10.905075276344114,11.512215276344111,193381.94687227771,9750.3594069903738,324.16223148668644,25.135731486686439,4.9802689607358223E-2,-290.85400000000027,-2348.6094069903738,7.1836900569085108E-2,7.1836900569085108E-2,0.66350758285421518,0.66350758285421518,9236.1375071858693,-1834.3875071858693,0.36590299862016801,0.36590299862016801,44,0.69115866980076723]
["2013-02-22","2013-02-22",52.314909999999998,52.252650000000003,51.944330000000001,52.240780000000001,52.408639999999998,51.915469999999999,51.964509999999997,52.174410000000002,51.97316,51.811100000000003,52.19247,52.017960000000002,52.020209999999999,52.202300000000001,51.681480000000001,48.385680000000001,44.181010000000001,43.212000000000003,41.740960000000001,41.165930000000003,41.544879999999999,41.045639999999999,41.033720000000002,40.567070000000001,40.927280000000003,40.522820000000003,154.9145,6500.768,6606.4359999999997,50.420699999999997,40.985689999999998,19,19,284185.99440000003,175521.14550371672,913.38286315249957,45,41,30667.405543839996,44,9.7120055290449443,10.319145529044945,172224.99521073198,6315.3599845315894,188.09356325445162,33.17906325445162,4.9802689607358223E-2,105.66799999999967,291.07601546841033,2.664163563766947E-2,2.664163563766947E-2,0.67310650968967478,0.67310650968967478,5943.7877792345307,662.64822076546898,0.34762628785127897,0.34762628785127897,44,0.70075759663622683]
["2013-02-22T03:00:00","2013-02-22T03:00:00",52.055900000000001,52.084600000000002,51.773119999999999,52.18103,52.381480000000003,51.843330000000002,51.957720000000002,52.123190000000001,51.91957,51.713889999999999,52.229430000000001,51.945689999999999,51.958840000000002,52.105510000000002,51.835900000000002,48.260390000000001,44.215020000000003,43.221629999999998,41.623939999999997,41.022559999999999,41.471820000000001,41.00911,41.073979999999999,40.601370000000003,40.949129999999997,40.561329999999998,655.81989999999996,5942.4520000000002,6598.2719999999999,49.820010000000003,40.590380000000003,19,19,284185.99440000003,164186.08019619898,3769.1838739715004,36,33,27423.316626380001,44,9.1146060969595588,9.7217460969595582,161631.18798707431,6017.4441626232965,827.06456732756033,171.24466732756036,4.9802689607358223E-2,655.81999999999971,580.82783737670343,4.1901616273754896E-2,4.1901616273754896E-2,0.6869081845471211,0.6869081845471211,5641.6442793042179,956.62772069578205,0.37463917443895994,0.37463917443895994,44,0.71455927149367315]
["2013-02-22T12:00:00","2013-02-22T12:00:00",52.351329999999997,52.120820000000002,51.835380000000001,52.164319999999996,52.322110000000002,51.795319999999997,51.897350000000003,52.086559999999999,51.788640000000001,50.327500000000001,47.629719999999999,44.131360000000001,42.301400000000001,42.382040000000003,43.135869999999997,42.701270000000001,42.613100000000003,42.946680000000001,42.5732,42.15569,41.570349999999998,40.621859999999998,40.809820000000002,40.433990000000001,40.839709999999997,40.461689999999997,6443.8010000000004,6039.65,12473.49,50.971229999999998,40.478290000000001,29,29,433757.57040000003,284456.17427270889,38307.23706082,38,31,31686.842535499989,44,9.1382983304605503,9.7454383304605496,247341.49948004296,6934.9547124936216,8383.8884824171419,1940.0874824171415,7.6014631505967808E-2,6433.84,5538.5352875063782,0.25050843769025127,0.25050843769025127,0.94108893345267663,0.94108893345267663,6502.9076088776683,5970.5823911223315,0.62223076454640458,0.62223076454640458,44,0.96874002039922869]
["2013-02-22T15:00:00","2013-02-22T15:00:00",52.316929999999999,52.050710000000002,51.736109999999996,52.040550000000003,52.149479999999997,51.645850000000003,51.544620000000002,51.733960000000003,51.410159999999998,50.066780000000001,46.224730000000001,43.446689999999997,41.837159999999997,42.434359999999998,43.211060000000003,42.64837,42.433120000000002,42.92324,42.566609999999997,42.037080000000003,41.424019999999999,40.801679999999998,40.883629999999997,40.267229999999998,40.661879999999996,40.280169999999998,643.29250000000002,6642.8239999999996,5999.5309999999999,51.68627,40.275709999999997,29,29,433757.57040000003,308722.89076134108,3871.5787161500002,48,38,37899.170910720015,44,9.776067728055553,10.383207728055554,264603.66727312282,7753.4591545343364,792.0523514867366,148.75985148673658,7.6014631505967808E-2,-643.29299999999967,-1753.9281545343365,0.20276313137073967,0.20276313137073967,0.92511983055576019,0.92511983055576019,7300.0891253125928,-1300.5581253125929,0.58862882293379859,0.58862882293379859,44,0.95277091750231224]
["2013-02-22T22:00:00","2013-02-22T22:00:00",52.076970000000003,51.916939999999997,51.634929999999997,51.855629999999998,51.996499999999997,51.426490000000001,51.36795,51.224910000000001,50.233620000000002,47.423580000000001,43.915860000000002,41.986319999999999,42.10342,42.729790000000001,43.226570000000002,42.546349999999997,42.413130000000002,42.772060000000003,42.11,41.192880000000002,41.334809999999997,40.77955,40.746980000000001,40.313389999999998,40.593609999999998,40.057429999999997,1491.45,5907.9470000000001,7399.3969999999999,51.944180000000003,40.144759999999998,31,31,463671.88560000004,343920.83145612211,8963.271466500004,39,34,34855.173995370016,44,9.4288794332421197,10.036019433242117,272806.95348856138,7393.2802391100386,1901.2378999988939,409.78789999889386,8.125701988568973E-2,1491.4499999999998,6.1167608899613697,0.18681147587795149,0.18681147587795149,1.0055927952220194,1,6946.0156443938085,453.38135560619139,0.60515103171576357,0.60515103171576357,44,1]
["2013-02-23T07:00:00","2013-02-23T07:00:00",51.71331,51.733800000000002,51.294640000000001,51.484110000000001,51.171100000000003,49.643529999999998,46.125880000000002,43.534140000000001,41.94106,41.875529999999998,42.643859999999997,42.389380000000003,42.433320000000002,42.634230000000002,42.795369999999998,41.723469999999999,41.09169,41.390560000000001,41.066360000000003,40.533459999999998,40.955359999999999,40.462710000000001,40.46698,40.034460000000003,40.376640000000002,40.037280000000003,1917.8879999999999,5479.5870000000004,7397.4750000000004,49.987389999999998,40.02713,37,37,553414.83120000002,343607.9990348572,11196.658912319997,30,28,27289.055606309994,44,8.8057927961751723,9.4129327961751716,304091.19523395348,6197.9781350665198,2543.0212069453432,625.13320694534332,9.6984185024855479E-2,1917.8879999999999,1199.4968649334805,0.29551861013999325,0.29551861013999325,1.0201662254962296,1,5798.2047035114419,1599.2702964885584,0.75120620986084574,0.75120620986084574,44,1]
["2013-02-23T08:00:00","2013-02-23T08:00:00",51.727029999999999,51.728490000000001,51.249020000000002,51.389270000000003,50.96546,48.666170000000001,44.821770000000001,42.970669999999998,41.813659999999999,42.03013,42.663849999999996,42.389229999999998,42.415680000000002,42.575249999999997,42.647419999999997,41.47204,41.029159999999997,41.3583,40.997439999999997,40.488909999999997,41.102890000000002,40.411180000000002,40.447360000000003,40.010590000000001,40.364809999999999,39.918430000000001,1721.1769999999999,5679.85,7401.027,50.065849999999998,40.067929999999997,39,39,583329.14639999997,369363.43683796661,10162.345361099999,34,31,28393.342956,44,9.0259899947996018,9.6331299947996012,328543.67763867887,6291.4634233716315,2251.796283167856,{"$f":"AU1278-AC1278","v":530.61928316785611},0.10222657340457739,{"$f":"AE1278-AD1278","v":1721.1769999999997},1109.5635766283685,0.30718545892818666,0.30718545892818666,1.0180978469550483,1,{"$f":"AO1278*1000/(500*AR1278)","v":5894.9361155362812},{"$f":"AE1278-BD1278","v":1506.0908844637188},0.76704246744935511,0.76704246744935511,44,1]
["2013-02-23T17:00:00","2013-02-23T17:00:00",51.834899999999998,51.391010000000001,50.660550000000001,49.98319,46.528460000000003,43.463619999999999,42.152790000000003,42.578009999999999,42.403640000000003,42.326569999999997,42.537010000000002,42.410089999999997,42.14573,41.924869999999999,41.750819999999997,41.011200000000002,40.86618,41.149410000000003,40.814529999999998,40.551960000000001,41.091909999999999,40.832790000000003,40.758319999999998,39.943150000000003,40.370699999999999,39.99588,502.21640000000002,6893.1109999999999,7395.3270000000002,52.95185,40.158340000000003,41,41,613243.46160000004,495778.22680999094,2972.8750019639997,55,43,44093.54225480499,44,10.291530790888851,10.89867079088885,393819.75156374229,8568.898670320501,577.7323242516851,75.515924251685078,0.10746896178429931,502.21600000000035,-1173.5716703205007,0.2861000518047172,0.2861000518047172,1.005280705183939,1,8091.5449417311747,-696.21794173117451,0.78811531416481717,0.78811531416481717,44,1]
["2013-02-23T20:00:00","2013-02-23T20:00:00",51.704439999999998,51.280279999999998,50.435870000000001,49.178150000000002,45.427379999999999,43.019880000000001,42.0578,42.805840000000003,42.541960000000003,42.291820000000001,42.590179999999997,42.353349999999999,42.08643,41.799309999999998,41.734000000000002,40.99803,40.81561,41.131079999999997,40.767499999999998,40.518410000000003,41.051220000000001,40.634509999999999,40.797750000000001,39.918500000000002,40.351599999999998,40.080280000000002,1088.327,6324.3119999999999,7412.6379999999999,51.952640000000002,40.118299999999998,41,41,613243.46160000004,454312.38177070988,6325.4435901599982,44,37,37422.029237040013,44,9.6989501969830663,10.306090196983066,371143.83026347519,7716.7174749861942,1304.3563399526633,216.02933995266335,0.10746896178429931,1088.326,-304.07947498619433,0.26703681717147404,0.26703681717147404,1.0114435397319392,1,7262.1194889201888,150.51851107981111,0.78364722935271913,0.78364722935271913,44,1]
["2013-02-24T03:00:00","2013-02-24T03:00:00",51.0182,49.692390000000003,45.8292,43.776670000000003,42.7956,42.381259999999997,42.454279999999997,42.676729999999999,42.428069999999998,42.137560000000001,42.365699999999997,41.707630000000002,41.176870000000001,41.236829999999998,41.494370000000004,40.792430000000003,40.60266,41.00468,40.576329999999999,40.599040000000002,41.379779999999997,40.196370000000002,41.604030000000002,40.0411,40.41384,40.02364,1512.9159999999999,5885.1840000000002,7398.1009999999997,50.471980000000002,40.185479999999998,45,45,673072.09200000006,438827.13025178242,8316.92286848,39,34,30268.972608000011,44,9.2724899659328024,9.8796299659328,389441.78329177061,6528.7690187227909,1793.8920180094963,280.97601800949633,0.11795373854374315,1512.9169999999995,869.3319812772088,0.30300717059753457,0.30300717059753457,1.0159080328877803,1,6127.5518845086872,1270.5491154913125,0.85021685539705216,0.85021685539705216,44,1]
["2013-02-24T12:00:00","2013-02-24T12:00:00",50.451230000000002,46.379010000000001,43.516480000000001,42.811720000000001,42.832560000000001,42.362229999999997,42.390529999999998,42.619900000000001,42.341160000000002,42.007170000000002,41.787820000000004,41.300089999999997,40.996580000000002,41.041240000000002,41.327660000000002,40.702680000000001,40.585700000000003,40.895760000000003,40.724449999999997,41.068080000000002,41.65014,40.763710000000003,40.573390000000003,40.096440000000001,40.521250000000002,40.129860000000001,885.29179999999997,8286.8649999999998,7401.5739999999996,55.29965,40.219720000000002,47,47,702986.40720000002,665443.34501289763,4568.7121128830004,64,53,62482.672059724988,44,11.527070117236622,12.134210117236622,505650.51309294015,10841.032703755935,792.6926905825494,-92.599109417450563,0.12319612692346506,-885.29100000000017,-3439.4587037559349,0.21317585664735886,0.21317585664735886,0.98369245695431207,0.98369245695431207,10298.597346846413,-2897.023346846413,0.80439684573767001,0.80439684573767001,44,0.98369245695431207]
["2013-02-24T15:00:00","2013-02-24T15:00:00",53.515569999999997,53.002070000000003,49.506,45.304580000000001,43.460149999999999,42.527059999999999,42.351649999999999,42.589860000000002,42.464239999999997,42.281700000000001,42.304049999999997,42.028530000000003,41.469360000000002,41.387689999999999,41.517499999999998,40.786009999999997,40.457410000000003,41.199620000000003,40.703609999999998,40.666809999999998,41.198329999999999,41.08323,41.313249999999996,40.206440000000001,40.432119999999998,40.24268,1278.213,8681.0959999999995,7402.8829999999998,53.383110000000002,40.228169999999999,45,45,673072.09200000006,551894.0986964847,8482.7902727849978,69,53,57099.648507120015,44,11.343509014092794,11.950649014092793,476423.95898674481,10067.369530218795,1495.6201405131808,217.40714051318082,0.11795373854374315,-1278.2129999999997,-2664.4865302187955,0.12393180739721774,0.12393180739721774,0.9446618128869767,0.9446618128869767,9555.9075393788735,-2153.0245393788737,0.73145833725494636,0.73145833725494636,44,0.9446618128869767]
["2013-02-24T22:00:00","2013-02-24T22:00:00",53.34563,52.86806,52.530299999999997,52.809249999999999,52.461539999999999,45.683869999999999,43.873249999999999,43.049259999999997,42.637410000000003,42.466839999999998,42.653199999999998,42.587179999999996,42.347549999999998,42.301270000000002,42.239220000000003,41.317540000000001,40.867350000000002,41.248069999999998,40.819049999999997,41.010489999999997,41.091369999999998,41.279130000000002,41.593629999999997,41.339379999999998,41.23207,40.435569999999998,165.56559999999999,7306.7089999999998,7338.9369999999999,52.163820000000001,40.1342,41,41,613243.46160000004,448797.81201903662,1068.730914968,58,48,43948.466360290004,44,10.59081870288589,11.197958702885892,405272.42012623174,8299.352031833856,201.82215274382551,36.256552743825523,0.10746896178429931,32.228000000000065,-960.41503183385612,-1.0098580366491684E-2,0,0.91275776970672584,0.91275776970672584,7849.3710374130578,-510.43403741305792,0.63010776951806913,0.63010776951806913,43,0.91275776970672584]
["2013-02-25T07:00:00","2013-02-25T07:00:00",52.081490000000002,51.880279999999999,51.483310000000003,51.793439999999997,51.88006,51.430680000000002,51.368029999999997,51.395980000000002,50.703609999999998,48.391219999999997,45.320659999999997,43.997639999999997,43.200600000000001,43.120750000000001,43.314749999999997,42.579000000000001,42.310549999999999,42.386749999999999,41.764000000000003,41.311689999999999,41.385770000000001,40.744459999999997,40.77731,40.910080000000001,40.933329999999998,40.402419999999999,499.34890000000001,6898.7629999999999,6407.0439999999999,51.793909999999997,40.192709999999998,31,31,463671.88560000004,329591.41164103703,2915.9653787615011,53,48,40016.964657799996,44,10.456754494830982,11.063894494830979,302546.5918097723,7653.8020812444847,557.71900931650077,58.370109316500759,8.125701988568973E-2,-491.71900000000005,-1246.7580812444849,-1.3109422763802022E-2,0,0.82845231497848537,0.82845231497848537,7233.7936115525699,-826.74961155257006,0.54466743244877169,0.54466743244877169,43,0.82845231497848537]
["2013-02-25T08:00:00","2013-02-25T08:00:00",52.076500000000003,51.78651,51.540790000000001,51.889499999999998,51.989910000000002,51.529029999999999,51.516489999999997,51.678310000000003,51.38749,49.172829999999998,45.937040000000003,44.328980000000001,43.498809999999999,43.31073,43.446910000000003,42.600299999999997,42.330509999999997,42.506259999999997,41.859630000000003,41.38391,41.44511,40.880510000000001,40.818249999999999,41.26379,40.934930000000001,40.360979999999998,421.24639999999999,6826.6890000000003,6406.2709999999997,52.236400000000003,40.291910000000001,31,31,463671.88560000004,343593.01914237795,2467.5603120640012,52,48,40770.659246805008,44,10.482455480316052,11.089595480316053,303290.20165243471,7778.837567851182,470.79814776176909,49.551747761769093,8.125701988568973E-2,-420.41800000000057,-1372.5665678511823,-1.443227493778196E-2,0,0.82403170011949789,0.82403170011949789,7352.9569801121443,-946.68598011214453,0.53471321043525444,0.53471321043525444,43,0.82403170011949789]
["2013-02-25T18:00:00","2013-02-25T18:00:00",51.90493,51.784390000000002,51.461399999999998,51.82817,51.877110000000002,51.373480000000001,51.432589999999998,51.582099999999997,51.308410000000002,51.010869999999997,51.186779999999999,50.316029999999998,49.131120000000003,46.584699999999998,44.96078,43.920160000000003,43.787390000000002,44.055050000000001,43.205649999999999,42.603439999999999,42.45384,41.685920000000003,41.550359999999998,40.975020000000001,41.40598,41.162779999999998,3493.4720000000002,6160.82,9573.2810000000009,51.7879,40.513939999999998,25,25,373928.94,247917.68719990278,18763.700122400005,46,41,34728.419123600004,44,9.8504860921147603,10.457626092114761,229843.02574953501,7051.1076913046636,3809.7003430968148,316.22834309681457,6.5529854746523966E-2,3412.4610000000011,2522.1733086953373,2.6520169938871036E-2,2.6520169938871036E-2,0.79016228146443934,0.79016228146443934,6641.740451934088,2931.5405480659128,0.42438656481632087,0.42438656481632087,44,0.79016228146443934]
["2013-02-25T19:00:00","2013-02-25T19:00:00",52.012360000000001,52.019849999999998,51.625,51.815600000000003,51.872390000000003,51.328740000000003,51.35812,51.390169999999998,50.96987,50.36618,49.885190000000001,47.37229,45.10277,44.342089999999999,44.530819999999999,43.75038,43.386629999999997,43.19417,42.435290000000002,42.174239999999998,42.390560000000001,41.980600000000003,41.955159999999999,40.833399999999997,41.130510000000001,40.715440000000001,6735.0550000000003,5976,12711.05,51.35951,40.170650000000002,27,27,403843.25520000001,268228.63874830381,38042.688765300001,42,38,33432.313679999999,44,9.6237478964880019,10.230887896488001,242516.70629109253,6947.8781114373269,7906.0027703308679,1170.9477703308676,7.0772243126245887E-2,6735.0499999999993,5763.1718885626724,8.7118820057275156E-2,8.7118820057275156E-2,0.86098004403888617,0.86098004403888617,6535.5644628803821,6175.4855371196172,0.48932061408836303,0.48932061408836303,44,0.86098004403888617]
["2013-02-26T02:00:00","2013-02-26T02:00:00",44.406300000000002,44.238010000000003,43.911450000000002,44.2211,44.079149999999998,42.779829999999997,42.04224,42.129379999999998,41.837409999999998,41.34196,41.244419999999998,40.59995,40.400570000000002,40.65916,41.01878,40.485979999999998,40.387250000000002,40.844329999999999,40.596719999999998,40.390569999999997,40.787129999999998,40.319699999999997,40.523449999999997,40.16245,40.561520000000002,40.192349999999998,7221.57,5475.902,12697.47,49.42071,40.079219999999999,51,51,762815.03760000004,439266.78309610748,15215.667450750014,41,36,25576.541886989999,44,9.2341720783463597,9.841312078346359,439543.43603967567,5539.5419686764617,3295.5130837186675,-3926.0569162813322,0.13368090368290891,7221.5679999999993,7157.9280313235377,0.57054331080320686,0.57054331080320686,1.075933406290855,1,5197.7910431812343,7499.6789568187651,{"$f":"IF(BF1343>1,1+BE1344*60/$BK$7,IF(BF1343<0,BE1344*60/$BK$7,BF1343+BE1344*60/$BK$7))","v":1.0001195641391705},1,44,1]
["2013-02-26T11:00:00","2013-02-26T11:00:00",42.479979999999998,41.916310000000003,40.363149999999997,40.52196,40.697189999999999,40.232939999999999,40.222140000000003,40.4739,40.296500000000002,40.127609999999997,40.479930000000003,40.38382,40.329650000000001,40.632989999999999,40.990540000000003,40.44773,40.346490000000003,40.790260000000004,40.560250000000003,40.456049999999998,40.80733,40.32029,40.486190000000001,40.059609999999999,40.501139999999999,40.396880000000003,193.57499999999999,6233.116,6410.9160000000002,51.695129999999999,40.816879999999998,51,51,762815.03760000004,537792.83991040592,201.61804124999949,48,41,33902.697063500003,44,9.8223289698653513,10.429468969865351,467539.50312996621,6903.1890842818621,41.053001150451863,-152.52199884954814,0.13368090368290891,177.80000000000018,-492.27308428186188,0.79355588603384164,0.79355588603384164,1.0018695329931828,1,6501.3275673876806,-90.411567387680407,0.99904933966143616,0.99904933966143616,44,1]
["2013-02-26T18:00:00","2013-02-26T18:00:00",44.048720000000003,43.347619999999999,43.105269999999997,42.77176,41.032649999999997,40.395629999999997,40.335540000000002,40.600540000000002,40.429639999999999,40.246589999999998,40.493180000000002,40.442279999999997,40.373730000000002,40.698979999999999,41.085380000000001,40.539340000000003,40.4298,40.906779999999998,40.684750000000001,40.625799999999998,40.864660000000001,40.332369999999997,40.476230000000001,40.079610000000002,40.495170000000002,40.201430000000002,788.30960000000005,6988.768,6200.4579999999996,52.973820000000003,40.893479999999997,51,51,762815.03760000004,607961.40026493242,1516.4278204920006,56,44,42213.346810560026,44,10.288263126240098,10.895403126240097,489717.80978524766,8206.1172605306656,294.78791548874148,-493.52168451125857,0.13368090368290891,-788.3100000000004,-2005.659260530666,0.66592724143811077,{"$f":"IF(AZ1360>1,1,IF(AZ1360<0,0,AZ1360))","v":0.66592724143811077},0.95566581258415217,{"$f":"IF(BB1360>1,1,BB1360)","v":0.95566581258415217},7748.8361507055979,-1548.3781507055983,0.90436572523425296,0.90436572523425296,44,1]
["2013-02-26T21:00:00","2013-02-26T21:00:00",47.160260000000001,44.686599999999999,43.555619999999998,43.73227,42.143120000000003,40.504080000000002,40.452599999999997,40.615139999999997,40.432169999999999,40.296729999999997,40.573259999999998,40.438429999999997,40.385129999999997,40.695129999999999,41.07246,40.546419999999998,40.452170000000002,40.918370000000003,40.684710000000003,40.554650000000002,40.845370000000003,40.34431,40.482559999999999,40.09713,40.512140000000002,40.228760000000001,290.03890000000001,6488.9380000000001,6201.2969999999996,52.291649999999997,40.906489999999998,49,49,732900.72239999997,551672.20962246018,1005.202317675,49,41,36938.798680039996,44,9.9258600349893662,10.533000034989364,453939.40738130367,7442.9416795780089,202.54211003008103,-87.496789969918979,0.12843851530318698,-287.64100000000053,-1241.6446795780093,0.62054187035921937,0.62054187035921937,0.94328413110201736,0.94328413110201736,7013.9178880345071,-812.62088803450752,0.87278941345901762,0.87278941345901762,44,0.99697550990049422]
["2013-02-27T06:00:00","2013-02-27T06:00:00",49.533619999999999,45.236980000000003,44.822670000000002,43.882779999999997,43.092500000000001,40.85181,40.513500000000001,40.704120000000003,40.51831,40.257429999999999,40.673110000000001,40.409610000000001,40.382899999999999,40.69923,41.067070000000001,40.56035,40.468490000000003,40.945630000000001,40.650500000000001,40.391829999999999,40.791699999999999,40.315350000000002,40.510649999999998,40.17389,40.641129999999997,40.207850000000001,298.26,5903.7830000000004,6200.5510000000004,50.927619999999997,40.871049999999997,41,41,613243.46160000004,410206.92101100378,1390.7520800999996,38,35,29685.903502155001,44,9.3134543094234861,9.9205943094234854,356392.29351425206,6374.8427846193172,298.65440552874497,0.3944055287449828,0.10746896178429931,296.76800000000003,-174.29178461931679,0.57958866392541863,0.57958866392541863,0.95407343943443013,0.95407343943443013,5984.7026450737176,215.84835492628281,0.86961317183384357,0.86961317183384357,44,1]
["2013-02-27T07:00:00","2013-02-27T07:00:00",49.613849999999999,45.294159999999998,44.903959999999998,43.937840000000001,43.254660000000001,40.939790000000002,40.591160000000002,40.709609999999998,40.508029999999998,40.253360000000001,40.681179999999998,40.40269,40.37079,40.689909999999998,41.056489999999997,40.555230000000002,40.472740000000002,40.953940000000003,40.659210000000002,40.382420000000003,40.783459999999998,40.320430000000002,40.513770000000001,40.150919999999999,40.565240000000003,40.21678,208.68600000000001,5998.2349999999997,6199.6930000000002,50.899529999999999,40.850050000000003,41,41,613243.46160000004,408790.29917902173,980.51847500999997,37,35,30139.571333899985,44,9.3289243824859902,9.9360643824859896,356984.27739438991,6461.5319190460277,210.21040257348716,1.5244025734871514,0.10746896178429931,201.45800000000054,-261.83891904602751,0.57683547777212341,0.57683547777212341,0.95619173177267902,0.95619173177267902,6066.7021012919622,132.990898708038,0.87101154569732908,0.87101154569732908,44,1]
["2013-02-27T16:00:00","2013-02-27T16:00:00",50.562849999999997,47.98771,45.846040000000002,46.071750000000002,45.47692,43.57929,42.19641,41.18186,40.746670000000002,40.538989999999998,40.729129999999998,40.661270000000002,40.543849999999999,40.809399999999997,41.171669999999999,40.63494,40.487679999999997,40.977690000000003,40.733510000000003,40.677619999999997,40.957999999999998,40.451430000000002,40.557600000000001,40.134340000000002,40.516739999999999,40.299149999999997,936.37729999999999,7138.7160000000003,6202.3389999999999,53.013849999999998,40.834099999999999,47,47,702986.40720000002,557747.50334945251,4805.3478470050004,57,43,43473.888100499993,44,10.270400584227051,10.877540584227049,450525.00524993869,8465.8602639639557,935.76639150470885,-0.61090849529114166,0.12319612692346506,-936.37700000000041,-2263.5212639639558,0.44318449229265366,0.44318449229265366,0.91065509185944971,0.91065509185944971,7993.3304341864196,-1790.9914341864196,0.7790287120415641,0.7790287120415641,44,0.95332853883917645]
["2013-02-27T19:00:00","2013-02-27T19:00:00",50.761519999999997,48.79,46.67595,47.607520000000001,47.943379999999998,46.301909999999999,44.2014,41.752670000000002,40.718710000000002,40.479309999999998,40.769950000000001,40.637619999999998,40.583469999999998,40.834110000000003,41.177610000000001,40.62359,40.509709999999998,40.989249999999998,40.722799999999999,40.602730000000001,40.934939999999997,40.456940000000003,40.599930000000001,40.175640000000001,40.539670000000001,40.294080000000001,289.71550000000002,6491.2979999999998,6202.0789999999997,52.362250000000003,40.957050000000002,37,37,553414.83120000002,416751.14603883732,1516.2898066599996,50,38,37017.275974800003,44,9.7459951107406813,10.353135110740681,336559.2821190026,7596.407663698642,311.16161857888801,21.44611857888799,9.6984185024855479E-2,-289.21900000000005,-1394.3286636986422,0.38623277480274182,0.38623277480274182,0.89274656403568509,0.89274656403568509,7150.9307236601353,-948.85172366013558,0.73657518908148034,0.73657518908148034,44,0.93542001101541183]
["2013-02-28T02:00:00","2013-02-28T02:00:00",50.252369999999999,49.618409999999997,47.596919999999997,47.969270000000002,48.15005,47.601660000000003,44.838700000000003,41.475810000000003,41.171509999999998,40.971420000000002,41.42933,41.213909999999998,41.194270000000003,41.513570000000001,41.822609999999997,41.281440000000003,41.107230000000001,41.473770000000002,41.088030000000003,40.755659999999999,41.085410000000003,40.583599999999997,40.744840000000003,40.236350000000002,40.619160000000001,40.311540000000001,384.04390000000001,5815.259,6199.3029999999999,50.244779999999999,40.838810000000002,37,37,553414.83120000002,343025.42588303098,1908.8575612184998,39,34,27349.07584811499,44,9.1729214864207229,9.7800614864207205,316769.28167154675,5963.0022754695156,416.19402587154087,32.150125871540865,9.6984185024855479E-2,384.04399999999987,236.30072453048433,0.35650999849631387,0.35650999849631387,0.90532615524784055,0.90532615524784055,5592.8228848230137,606.48011517698615,0.73632653328980668,0.73632653328980668,44,0.9479996022275673]
["2013-02-28T11:00:00","2013-02-28T11:00:00",49.16046,48.16328,47.843989999999998,48.175109999999997,48.3322,47.853909999999999,41.362380000000002,41.4621,41.274299999999997,41.100050000000003,41.435250000000003,41.314929999999997,41.263249999999999,41.55359,41.908329999999999,41.361829999999998,41.280349999999999,41.735950000000003,41.506929999999997,41.389899999999997,41.723880000000001,41.257550000000002,41.412930000000003,41.021529999999998,41.430399999999999,41.012140000000002,338.12529999999998,6538.1729999999998,6200.0479999999998,51.99174,40.869970000000002,39,39,583329.14639999997,399654.57141875854,1377.5765722479998,48,39,36358.028163104995,44,9.7843617603618807,10.39150176036188,356148.21176941949,7431.8650625526898,281.58741591685572,-56.537884083144263,0.10222657340457739,-338.125,-1231.81706255269,0.31899127865030252,0.31899127865030252,0.90249364452622871,0.90249364452622871,6997.6465387884109,-797.59853878841113,0.73547537193638868,0.73547537193638868,44,0.94516709150595546]
["2013-02-28T18:00:00","2013-02-28T18:00:00",51.184930000000001,50.277610000000003,48.404640000000001,48.737569999999998,48.875410000000002,48.426200000000001,48.364989999999999,42.252690000000001,41.952640000000002,41.784140000000001,42.026040000000002,41.981560000000002,41.921309999999998,42.180599999999998,42.52317,41.96463,41.825719999999997,42.306759999999997,42.076720000000002,42.070419999999999,42.36985,41.899839999999998,42.007060000000003,41.603879999999997,42.019849999999998,41.685720000000003,836.74189999999999,7030.76,6194.0190000000002,53.270180000000003,41.077190000000002,37,37,553414.83120000002,400047.14726765268,3974.1935119494992,57,42,42862.993186200008,44,10.188722067649422,10.79586206764942,351848.00996042381,8413.8114479137366,780.11618838207471,-56.625711617925276,9.6984185024855479E-2,-836.74099999999999,-2219.7924479137364,0.15627510825525864,0.15627510825525864,0.83228423724079525,0.83228423724079525,7940.6337201439546,-1746.6147201439544,{"$f":"IF(BF1407>1,1+BE1408*60/$BK$7,IF(BF1407<0,BE1408*60/$BK$7,BF1407+BE1408*60/$BK$7))","v":0.60739648805046809},0.60739648805046809,44,0.874957684220522]
["2013-02-28T21:00:00","2013-02-28T21:00:00",51.595419999999997,49.59375,48.40654,48.715449999999997,48.847749999999998,48.371409999999997,48.382210000000001,42.479129999999998,42.026919999999997,41.846020000000003,42.18824,42.082889999999999,42.022919999999999,42.309840000000001,42.660380000000004,42.107570000000003,42.004660000000001,42.498730000000002,42.24635,42.15334,42.4754,42.025840000000002,42.161340000000003,41.775010000000002,42.173870000000001,41.62227,833.14919999999995,6397.5479999999998,7230.6970000000001,52.262300000000003,40.288290000000003,37,37,553414.83120000002,367433.0653601673,4154.5609719899985,47,37,38302.15186374,44,9.7289623785535344,10.336102378553534,335971.08932264935,7873.8410887831214,854.06044557193218,20.911245571932227,9.6984185024855479E-2,833.14900000000034,-643.14408878312133,0.11942841517371176,0.11942841517371176,0.84011199711879314,0.84011199711879314,7411.3336847772434,-180.63668477724332,0.58521686055062028,0.58521686055062028,44,0.88278544409851989]
["2013-03-01T06:00:00","2013-03-01T06:00:00",49.857570000000003,48.673659999999998,48.327719999999999,48.686019999999999,48.878599999999999,48.352649999999997,42.381619999999998,42.56494,42.378219999999999,42.164929999999998,42.643909999999998,42.408639999999998,42.417450000000002,42.711910000000003,43.054789999999997,42.530889999999999,42.426690000000001,42.910490000000003,42.627049999999997,42.375790000000002,42.76932,42.359670000000001,42.558190000000003,42.185670000000002,42.486190000000001,41.017809999999997,528.59590000000003,5878.5159999999996,6407.1109999999999,50.386429999999997,40.285229999999999,39,39,583329.14639999997,341015.32031086838,2336.3304464920016,34,31,29690.032909599999,44,9.0702071222173615,9.6773471222173608,330153.16952431342,6546.7155291028857,515.16584241371697,-13.430057586283056,0.10222657340457739,528.59500000000025,-139.60452910288586,9.1022694419757813E-2,9.1022694419757813E-2,0.88381942833034066,0.88381942833034066,6135.985933880017,271.12506611998288,0.59603958661757905,0.59603958661757905,44,0.92649287531006741]
["2013-03-01T07:00:00","2013-03-01T07:00:00",49.258670000000002,48.662590000000002,48.330329999999996,48.663780000000003,48.84684,48.306159999999998,42.446069999999999,42.608780000000003,42.41131,42.210369999999998,42.703380000000003,42.472830000000002,42.486089999999997,42.767229999999998,43.108139999999999,42.571559999999998,42.46161,42.929740000000002,42.639620000000001,42.383569999999999,42.78154,42.381509999999999,42.582470000000001,42.222479999999997,42.578710000000001,40.931820000000002,513.32740000000001,5882.7430000000004,6396.07,50.402500000000003,40.283969999999997,39,39,583329.14639999997,344730.27764619928,2137.2001303450002,34,31,29762.355763895019,44,9.0726733315488222,9.6798133315488215,330242.93889964529,6560.8789551368545,471.12908229886693,-42.198317701133078,0.10222657340457739,513.32699999999932,-164.80895513685482,8.928975977858597E-2,8.928975977858597E-2,0.88921696355414048,0.88921696355414048,6149.365642598169,246.70435740183075,0.59863363574988904,0.59863363574988904,44,0.93189041053386723]
["2013-03-01T13:00:00","2013-03-01T13:00:00",50.226770000000002,48.539960000000001,48.255310000000001,48.617179999999998,48.749470000000002,48.29609,42.584090000000003,42.783279999999998,42.598399999999998,42.45561,42.761409999999998,42.692639999999997,42.642690000000002,42.931739999999998,43.28125,42.73856,42.638500000000001,43.095529999999997,42.869199999999999,42.765210000000003,43.060850000000002,42.62,42.737960000000001,42.344799999999999,42.726439999999997,41.252220000000001,527.86289999999997,6929.4080000000004,6401.5439999999999,52.696869999999997,40.538170000000001,39,39,583329.14639999997,416582.26991763763,2368.6659945975002,51,41,42126.296524799989,44,10.10275371149568,10.709893711495681,367737.59560613125,8339.5671571930907,468.91492403744383,-58.947975962556143,0.10222657340457739,-527.86400000000049,-1938.0231571930908,1.5439040015076611E-2,1.5439040015076611E-2,0.88385625119053268,0.88385625119053268,7866.8001120464669,-1465.256112046467,0.55283361261505626,0.55283361261505626,44,0.92652969817025943]
["2013-03-01T18:00:00","2013-03-01T18:00:00",43.210270000000001,42.956699999999998,42.633229999999998,42.913589999999999,43.097279999999998,42.635210000000001,42.655929999999998,42.909550000000003,42.718620000000001,42.572879999999998,42.884700000000002,42.801650000000002,42.756619999999998,43.031649999999999,43.376199999999997,42.576599999999999,41.39273,40.947189999999999,40.332659999999997,40.241729999999997,40.567419999999998,40.087919999999997,40.210479999999997,39.816699999999997,40.209800000000001,39.865380000000002,7921.7749999999996,6870.1220000000003,14791.9,53.093670000000003,40.459339999999997,51,51,762815.03760000004,629662.08450498316,13248.732989874998,52,41,43399.69424413002,44,10.146176573724834,10.753316573724835,482954.53842992603,8554.8864498417188,2611.5715399995574,-5310.2034600004426,0.13368090368290891,7921.7779999999993,6237.0135501582809,0.2677156564971892,0.2677156564971892,1.0832959805155828,1,8071.8713982949039,6720.0286017050958,0.83048437597430069,0.83048437597430069,44,1]
["2013-03-02T01:00:00","2013-03-02T01:00:00",43.016719999999999,42.901479999999999,42.574770000000001,42.827480000000001,41.855629999999998,40.270879999999998,40.251249999999999,40.447279999999999,40.249760000000002,40.027259999999998,40.521389999999997,40.286369999999998,40.288580000000003,40.586210000000001,40.921230000000001,40.37379,40.277799999999999,40.756709999999998,40.445160000000001,40.163159999999998,40.57358,40.145319999999998,40.367289999999997,40.002400000000002,40.60445,40.921309999999998,1671.6759999999999,5733.0469999999996,7404.7240000000002,50.072620000000001,39.50215,51,51,762815.03760000004,435599.22942052968,1751.4233035800009,37,33,30300.500661045,44,9.2127180725416356,9.8198580725416349,438522.23269321251,6577.9719779671059,380.2185825701302,-1291.4574174298698,0.13368090368290891,1671.6770000000006,826.75202203289427,0.56659705820290851,0.56659705820290851,1.017577363922638,1,6171.2705901058798,1233.4534098941203,1.0129695266892633,1,44,1]
["2013-03-02T10:00:00","2013-03-02T10:00:00",42.694690000000001,40.773879999999998,40.183010000000003,40.457500000000003,40.658320000000003,40.115319999999997,40.217149999999997,40.41581,40.208210000000001,40.001759999999997,40.462649999999996,40.222110000000001,40.251449999999998,40.567279999999997,40.907510000000002,40.348790000000001,40.247770000000003,40.739519999999999,40.453049999999998,40.313160000000003,41.012689999999999,40.684600000000003,40.930810000000001,40.572229999999998,41.028820000000003,40.786729999999999,1206.049,5796.9690000000001,7003.018,50.371920000000003,39.511189999999999,51,51,762815.03760000004,456251.76918379642,1150.5466250200018,38,32,31479.65756368501,44,9.1920803229216599,9.7992203229216592,437539.8828622665,6849.2999316349205,250.33432794336287,-955.71467205663714,0.13368090368290891,1206.049,153.71806836507949,0.65238588372533501,0.65238588372533501,1.0126813745607157,1,6424.9310713118612,578.08692868813887,1.0060784734876842,1,44,1]
["2013-03-02T17:00:00","2013-03-02T17:00:00",41.146610000000003,40.720269999999999,40.491199999999999,40.860909999999997,41.0685,40.653640000000003,40.624090000000002,40.903239999999997,40.710740000000001,40.584090000000003,40.836089999999999,40.762569999999997,40.662439999999997,40.965580000000003,41.23272,40.585790000000003,40.46866,40.950130000000001,40.665210000000002,40.529119999999999,40.793089999999999,40.293790000000001,40.464350000000003,40.153179999999999,40.667960000000001,40.582000000000001,229.19710000000001,6791.1260000000002,6995.7849999999999,52.556629999999998,39.901420000000002,51,51,762815.03760000004,569988.29682263581,64.703487315500212,55,41,42971.562833229989,44,10.131577292613144,10.738717292613142,482259.61763690889,8482.6995031780934,12.772638543196038,-216.42446145680395,0.13368090368290891,204.65899999999965,-1486.9145031780936,0.58576890447830654,0.58576890447830654,1.0021519502410114,1,8003.1090608538325,-1007.3240608538326,0.96431487529210225,0.96431487529210225,44,1]
["2013-03-02T20:00:00","2013-03-02T20:00:00",41.031799999999997,40.834000000000003,40.49335,40.790779999999998,40.984099999999998,40.501530000000002,40.572150000000001,40.878540000000001,40.673540000000003,40.53716,40.8765,40.775100000000002,40.67839,40.9574,41.297150000000002,40.763730000000002,40.627459999999999,41.13344,40.879759999999997,40.744599999999998,40.975549999999998,40.439819999999997,40.554299999999998,40.139499999999998,40.51773,40.713659999999997,664.89089999999999,6336.8119999999999,7001.7030000000004,51.788899999999998,39.496729999999999,51,51,762815.03760000004,527177.64010261116,105.76419546299988,47,38,38946.585181019997,44,9.8117845546727835,10.418924554672783,467037.59256933909,7938.7363152958751,21.558605343129049,-643.33229465687089,0.13368090368290891,664.89100000000053,-937.03331529587467,0.54854616890732322,0.54854616890732322,1.0069912016949965,1,7476.1238507198605,-474.42085071986003,0.94196093862890051,0.94196093862890051,44,1]
["2013-03-03T05:00:00","2013-03-03T05:00:00",41.24747,41.12988,40.782530000000001,41.10389,41.316079999999999,40.781730000000003,40.860680000000002,41.073230000000002,40.873820000000002,40.69379,41.121479999999998,40.930100000000003,40.912889999999997,41.218859999999999,41.565300000000001,41.03436,40.932830000000003,41.4163,41.122709999999998,40.907389999999999,41.284399999999998,40.806870000000004,40.985419999999998,40.575229999999998,40.978470000000002,40.557340000000003,570.90380000000005,5823.5119999999997,6394.4160000000002,50.059699999999999,39.669640000000001,51,51,762815.03760000004,452309.08948297694,196.99891974699898,36,32,30253.319545359995,44,9.1502621964967759,9.7574021964967752,435549.35433176206,6612.557956414108,43.058639308154689,-527.84516069184531,0.13368090368290891,570.90400000000045,-218.14195641410788,0.51453291387051958,0.51453291387051958,1.0060029463663673,1,6201.1012636584601,193.31473634154008,0.94777481404122033,0.94777481404122033,44,1]
["2013-03-03T06:00:00","2013-03-03T06:00:00",41.25544,41.128570000000003,40.787199999999999,41.109839999999998,41.323889999999999,40.790430000000001,40.872860000000003,41.088419999999999,40.887799999999999,40.713540000000002,41.146979999999999,40.954279999999997,40.938220000000001,41.251249999999999,41.590310000000002,41.06429,40.95044,41.441899999999997,41.147799999999997,40.929729999999999,41.309449999999998,40.8598,41.03454,40.601819999999996,40.973210000000002,40.529670000000003,678.51099999999997,5721.77,6400.2809999999999,50.473140000000001,39.559899999999999,51,51,762815.03760000004,473305.77477608691,246.22146423499902,37,32,31221.524617400006,44,9.183277989453341,9.7904179894533403,437120.89479652484,6799.6470657333439,53.623872546987116,-624.88712745301291,0.13368090368290891,678.51099999999951,-399.36606573334393,0.51033365607385961,0.51033365607385961,1.0071344133899749,1,6377.9758231023789,22.305176897621095,0.94800934871011167,0.94800934871011167,44,1]
["2013-03-03T15:00:00","2013-03-03T15:00:00",51.391649999999998,42.753999999999998,40.991050000000001,41.232219999999998,41.34478,40.978630000000003,40.856879999999997,41.103490000000001,40.956479999999999,40.904240000000001,40.978749999999998,41.080210000000001,40.992780000000003,41.24409,41.595930000000003,40.998919999999998,40.868729999999999,41.375320000000002,41.149630000000002,41.20523,41.482959999999999,41.005040000000001,41.059620000000002,40.621720000000003,41.049239999999998,40.733580000000003,1796.6189999999999,8397.8700000000008,6601.2510000000002,53.69661,40.383890000000001,49,49,732900.72239999997,592838.31681315496,9574.2455326649961,71,51,55899.245953199999,44,11.180881287004121,11.788021287004121,511335.3006723912,9999.076909648149,1712.6101756922205,-84.008824307779378,0.12843851530318698,-1796.6190000000006,-3397.8259096481488,0.33460075792626337,0.33460075792626337,0.93070734734379401,0.93070734734379401,9484.0761807627459,-2882.8251807627457,0.8161102379634223,0.8161102379634223,44,0.96331071993823836]
["2013-03-03T22:00:00","2013-03-03T22:00:00",54.066600000000001,53.796169999999996,53.429549999999999,53.128480000000003,48.900129999999997,41.469650000000001,41.148670000000003,41.319220000000001,41.115259999999999,41.001289999999997,41.117170000000002,41.113140000000001,41.064,41.317909999999998,41.689979999999998,41.075659999999999,40.947519999999997,41.462499999999999,41.202680000000001,41.229219999999998,41.524970000000003,41.054499999999997,41.118119999999998,40.698439999999998,41.112949999999998,40.797379999999997,861.08590000000004,7348.7020000000002,6487.616,52.696170000000002,40.433889999999998,41,41,613243.46160000004,455323.76251137158,5712.9691229990021,64,50,45055.920780280016,44,10.750276898607549,11.35741689860755,411374.30995194177,8382.280978477118,1062.8505994555333,201.76469945553322,0.10746896178429931,-861.08600000000024,-1894.664978477118,0.12761109640830881,0.12761109640830881,0.82833156291496601,0.82833156291496601,7934.1845390572917,-1446.5685390572917,0.64521643778405513,0.64521643778405513,44,0.86093493550941036]
["2013-03-04T01:00:00","2013-03-04T01:00:00",55.702300000000001,53.893120000000003,53.451349999999998,53.70879,53.764029999999998,52.20879,45.60604,41.628140000000002,41.290869999999998,41.151049999999998,41.267000000000003,41.191369999999999,41.11589,41.384779999999999,41.763539999999999,41.158439999999999,41.012500000000003,41.522460000000002,41.26117,41.257770000000001,41.554830000000003,41.082920000000001,41.158119999999997,40.734470000000002,41.144129999999997,40.809289999999997,1430.904,7632.1559999999999,6201.2520000000004,54.291519999999998,40.394649999999999,37,37,553414.83120000002,465583.00087413361,10655.233790520004,60,50,53031.539875859999,44,11.022245509766826,11.629385509766827,380632.14622571215,9622.6381146870081,1933.4052722883712,502.50127228837118,9.6984185024855479E-2,-1430.9039999999995,-3421.3861146870076,-8.8908400241114877E-3,0,0.78054258788172681,0.78054258788172681,9120.2651819087041,-2919.0131819087037,0.52583924286160733,0.52583924286160733,43,0.81314596047617116]
["2013-03-04T10:00:00","2013-03-04T10:00:00",53.786569999999998,53.494120000000002,53.169829999999997,53.475110000000001,53.570680000000003,53.199550000000002,53.140320000000003,53.326009999999997,53.182690000000001,53.081139999999998,53.209130000000002,50.824579999999997,42.849170000000001,41.864179999999998,42.06635,41.342910000000003,41.209539999999997,41.70035,41.459809999999997,41.487139999999997,41.706679999999999,41.206389999999999,41.265949999999997,40.842280000000002,41.229480000000002,40.892069999999997,2403.8000000000002,8603.0660000000007,6199.2669999999998,52.242980000000003,40.568959999999997,27,27,403843.25520000001,286040.87889825145,15497.89955,65,52,50216.182272660022,44,11.047935815497707,11.655075815497707,278405.98424940667,9090.5999294851608,2805.5737847897381,401.77378478973787,7.0772243126245887E-2,-2403.7990000000009,-2891.332929485161,-3.0401812744368636E-2,0,0.63164238137743334,0.63164238137743334,8617.0494413923534,-2417.7824413923536,0.37186483278748139,0.37186483278748139,43,0.66424575397187768]
["2013-03-04T17:00:00","2013-03-04T17:00:00",54.418489999999998,54.031599999999997,53.424599999999998,53.565219999999997,53.556109999999997,53.276510000000002,53.084499999999998,53.333570000000002,53.216450000000002,53.176789999999997,53.139879999999998,53.340710000000001,53.260390000000001,53.444429999999997,53.757210000000001,53.181890000000003,53.064889999999998,53.491570000000003,53.238419999999998,49.410469999999997,42.79522,41.816690000000001,41.544530000000002,40.986930000000001,41.313009999999998,41.014119999999998,3259.3879999999999,9809.6,7637.4359999999997,54.334699999999998,40.672759999999997,11,11,164528.73360000001,136756.97307277124,21845.02136278,86,57,67009.083312000002,44,11.924808740939202,12.5319487409392,122427.1576675017,11238.600931510175,3663.7940007848674,404.4060007848675,2.8833136088470546E-2,-2172.1640000000007,-3601.1649315101749,-3.7865560480042713E-2,0,0.39455386414907473,0.39455386414907473,10694.1202357612,-3056.6842357612004,5.6270132775091769E-2,5.6270132775091769E-2,42,0.42715723674351902]
["2013-03-04T20:00:00","2013-03-04T20:00:00",53.953670000000002,53.585529999999999,53.145249999999997,53.462490000000003,53.541119999999999,53.226669999999999,53.120559999999998,53.344819999999999,53.188139999999997,53.148040000000002,53.222520000000003,53.324579999999997,53.25844,53.474550000000001,53.714579999999998,52.940190000000001,50.670749999999998,44.76623,42.179380000000002,42.032870000000003,41.989060000000002,40.682130000000001,39.684280000000001,39.157829999999997,39.547919999999998,39.252459999999999,5349.6319999999996,8657.6710000000003,14007.3,53.25562,38.414180000000002,15,15,224357.364,196042.83287286299,39323.031727360009,73,58,64246.152343119997,44,11.891439794900393,12.498579794900392,166478.96220062967,10805.445505542863,6613.670405870208,1264.0384058702084,3.9317912847914381E-2,5349.628999999999,3201.8544944571368,7.6732556475011648E-2,7.6732556475011648E-2,0.54446190455586307,0.54446190455586307,10280.552414336449,3726.7475856635501,0.15043235445071396,0.15043235445071396,44,0.57706527715030731]
["2013-03-05T05:00:00","2013-03-05T05:00:00",53.511249999999997,52.250900000000001,47.176879999999997,42.969729999999998,41.570270000000001,40.278680000000001,40.225560000000002,40.460949999999997,40.253210000000003,40.122599999999998,40.490189999999998,40.360379999999999,40.322099999999999,40.646850000000001,41.008299999999998,40.449150000000003,40.340739999999997,40.870289999999997,40.576129999999999,40.456029999999998,40.793840000000003,40.331609999999998,40.497459999999997,40.113109999999999,40.498869999999997,40.124360000000003,6987.2160000000003,6620.5619999999999,13607.78,51.450110000000002,40.595869999999998,45,45,673072.09200000006,475678.08574846567,46768.545999119982,48,41,35930.584441440013,44,9.8914799294531051,10.498619929453106,415439.17515940411,7264.9562447075796,9456.3293526706457,2469.1133526706453,0.11795373854374315,6987.2180000000008,6342.8237552924211,0.60456007742956963,0.60456007742956963,1.073469260863676,1,6844.8204969568242,6762.9595030431765,0.71969264758274454,0.71969264758274454,44,1]
["2013-03-05T07:00:00","2013-03-05T07:00:00",42.368299999999998,40.678780000000003,40.25,40.533830000000002,40.770859999999999,40.256970000000003,40.309660000000001,40.528869999999998,40.330820000000003,40.186250000000001,40.569000000000003,40.414140000000003,40.384909999999998,40.714950000000002,41.069629999999997,40.511270000000003,40.405949999999997,40.927349999999997,40.625889999999998,40.45599,40.816110000000002,40.364669999999997,40.539029999999997,40.157400000000003,40.543030000000002,40.164059999999999,2249.819,6464.5389999999998,8698.5689999999995,51.619219999999999,40.710259999999998,51,51,762815.03760000004,545261.70230151445,2479.5705162799986,45,38,35260.698684720002,44,9.6860958251489535,10.293235825148953,461054.85198603175,7280.6834293687698,511.98554320349552,-1737.8334567965044,0.13368090368290891,2234.0299999999997,1417.8855706312297,0.68535720087071794,0.68535720087071794,1.0234903981595076,1,6851.2369256263,1847.3320743736995,0.80951784259453508,0.80951784259453508,44,1]
["2013-03-05T14:00:00","2013-03-05T14:00:00",43.845910000000003,41.465049999999998,40.487929999999999,40.674349999999997,40.824579999999997,40.378189999999996,40.347610000000003,40.611109999999996,40.423740000000002,40.321080000000002,40.547910000000002,40.527290000000001,40.44229,40.754370000000002,41.110100000000003,40.5289,40.32573,40.861409999999999,40.615650000000002,40.63391,40.922429999999999,40.426099999999998,40.537289999999999,40.139470000000003,40.526130000000002,40.168289999999999,650.49019999999996,7454.0940000000001,6803.6040000000003,53.022579999999998,40.77131,49,49,732900.72239999997,587865.30984099943,1196.1278846620014,56,40,45661.059099689992,44,10.162442115299429,10.76958211529943,464759.01686143083,8986.2374774952641,235.40166253173456,-415.08853746826537,0.12843851530318698,-650.48999999999978,-2182.6334774952638,0.58859367000665697,0.58859367000665697,0.97866374967652958,0.97866374967652958,8479.6343276538464,-1676.0303276538461,0.74724773520856846,0.74724773520856846,44,0.99316022206560428]
["2013-03-05T21:00:00","2013-03-05T21:00:00",53.017690000000002,50.090890000000002,42.182009999999998,41.117719999999998,41.079859999999996,40.521979999999999,40.519550000000002,40.727130000000002,40.463009999999997,40.308390000000003,40.656480000000002,40.542140000000003,40.491970000000002,40.821779999999997,41.175449999999998,40.599829999999997,40.474939999999997,40.969729999999998,40.691659999999999,40.578960000000002,40.913429999999998,40.43168,40.586379999999998,40.212179999999996,40.589239999999997,40.215299999999999,111.66549999999999,6816.2160000000003,6801.7749999999996,52.003010000000003,40.857480000000002,47,47,702986.40720000002,517083.83388576814,714.79264027250008,47,37,37985.169957240003,44,9.7181532955418852,10.325293295541885,426299.93139875418,7817.3638143093194,147.10462338568064,35.439123385680645,0.12319612692346506,-14.441000000000713,-1015.5888143093198,0.45294004644382929,0.45294004644382929,0.94173507896428543,0.94173507896428543,7357.6931657022715,-555.91816570227184,0.64775052552720302,0.64775052552720302,44,0.95623155135336013]
["2013-03-06","2013-03-06",52.78107,51.182960000000001,42.698,41.249969999999998,41.143160000000002,40.519469999999998,40.562159999999999,40.753680000000003,40.524749999999997,40.326360000000001,40.69641,40.527659999999997,40.50911,40.831890000000001,41.185809999999996,40.61824,40.492719999999998,41.006950000000003,40.706299999999999,40.526420000000002,40.894889999999997,40.414650000000002,40.603380000000001,40.236339999999998,40.613289999999999,40.225819999999999,190.1703,6453.1949999999997,6606.36,51.206029999999998,40.810380000000002,47,47,702986.40720000002,481661.75479977432,1193.8178295374998,39,32,33542.578300874986,44,9.2624259200598384,9.8695659200598378,406308.83401673887,7242.7199073692109,257.77649178322116,{"$f":"AU1534-AC1534","v":67.606191783221163},0.12319612692346506,{"$f":"AE1534-AD1534","v":153.16499999999996},-636.35990736921121,0.42888489521158463,0.42888489521158463,0.94446154783979919,0.94446154783979919,{"$f":"AO1534*1000/(500*AR1534)","v":6797.173973517899},{"$f":"AE1534-BD1534","v":-190.81397351789929},0.63780137549012117,0.63780137549012117,44,0.95895802022887389]
["2013-03-06T09:00:00","2013-03-06T09:00:00",52.487920000000003,51.214149999999997,42.819589999999998,41.245359999999998,41.16386,40.566470000000002,40.605739999999997,40.815779999999997,40.59619,40.411709999999999,40.791559999999997,40.587220000000002,40.581189999999999,40.894710000000003,41.249389999999998,40.678109999999997,40.588569999999997,41.080860000000001,40.784520000000001,40.557899999999997,40.941969999999998,40.463000000000001,40.659790000000001,40.272269999999999,40.656730000000003,40.266689999999997,112.3382,6542.4430000000002,6601.5240000000003,51.499839999999999,41.013330000000003,47,47,702986.40720000002,492757.30982641375,686.45548999300024,43,35,34303.696971964986,44,9.4709210667440082,10.078061066744006,415454.75547171407,7244.0044067980389,144.96066119765385,32.622461197653848,0.12319612692346506,59.081000000000131,-642.48040679803853,0.40258899875675208,0.40258899875675208,0.97237789186632306,0.97237789186632306,6807.5985538848772,-206.07455388487688,0.65192542618487404,0.65192542618487404,44,0.98687436425539776]
["2013-03-06T16:00:00","2013-03-06T16:00:00",53.598849999999999,52.659559999999999,52.023769999999999,51.673720000000003,45.113619999999997,41.294910000000002,40.824469999999998,41.005809999999997,40.763109999999998,40.564340000000001,40.731859999999998,40.722720000000002,40.651530000000001,40.953449999999997,41.316929999999999,40.756740000000001,40.59066,41.073270000000001,40.816450000000003,40.775590000000001,41.074910000000003,40.567599999999999,40.709350000000001,40.312759999999997,40.694929999999999,40.31026,1344.384,7946.777,6602.393,53.771389999999997,40.86027,41,41,613243.46160000004,515108.87739465066,8932.483889279998,60,42,51300.895730119992,44,10.476454544397093,11.083594544397092,400896.11640631012,9793.560505172276,1705.2493954755287,360.86539547552866,0.10746896178429931,-1344.384,-3191.1675051722759,0.21205516174881783,0.21205516174881783,0.90046706234977092,0.90046706234977092,9257.0863224247569,-2654.6933224247568,0.49943042098325835,0.49943042098325835,44,0.91496353473884562]
["2013-03-06T19:00:00","2013-03-06T19:00:00",54.149720000000002,53.53866,52.404580000000003,52.357959999999999,52.018700000000003,45.281289999999998,41.41328,41.161810000000003,40.857489999999999,40.716230000000003,40.889589999999998,40.766590000000001,40.691220000000001,40.988680000000002,41.354860000000002,40.78651,40.633980000000001,41.120660000000001,40.856999999999999,40.80612,41.109789999999997,40.593110000000003,40.736899999999999,40.334029999999998,40.717660000000002,40.337009999999999,664.57889999999998,7262.0450000000001,6597.4660000000003,53.197780000000002,40.898350000000001,39,39,583329.14639999997,468128.66793555586,4589.8178089095009,54,40,44659.507067175,44,10.128289190990669,10.735429190990669,368667.08038823103,8818.7661756144553,906.33624738761273,241.75734738761275,0.10222657340457739,-664.57899999999972,-2221.3001756144549,0.1297942219529265,0.1297942219529265,0.87197718808076563,0.87197718808076563,8320.022660044915,-1722.5566600449147,0.43340134689992038,0.43340134689992038,44,0.88647366046984033]
["2013-03-07T04:00:00","2013-03-07T04:00:00",53.82479,53.560420000000001,53.057220000000001,52.598300000000002,52.523099999999999,50.84581,43.76681,41.466540000000002,40.997280000000003,40.805770000000003,41.078009999999999,40.87923,40.749499999999998,41.043750000000003,41.395580000000002,40.83193,40.714410000000001,41.221769999999999,40.918770000000002,40.787700000000001,41.125079999999997,40.622729999999997,40.777119999999996,40.392899999999997,40.785879999999999,40.388629999999999,260.35919999999999,6359.9530000000004,6602.2389999999996,51.240279999999998,40.920290000000001,37,37,553414.83120000002,374740.95690666838,1749.1139343360001,44,35,32817.325680234993,44,9.4202358056960147,10.027375805696014,325309.80819626368,6967.4106587420574,371.35247363518982,110.99327363518984,9.6984185024855479E-2,242.28599999999915,-365.17165874205784,3.3099068010413846E-2,3.3099068010413846E-2,0.87293404619051052,0.87293404619051052,6545.5461760181033,56.692823981896254,0.37944452561225506,0.37944452561225506,44,0.88743051857958521]
["2013-03-07T05:00:00","2013-03-07T05:00:00",53.787680000000002,53.572679999999998,53.047800000000002,52.62894,52.510860000000001,50.974910000000001,43.883809999999997,41.4831,40.998100000000001,40.824779999999997,41.084980000000002,40.890389999999996,40.765529999999998,41.04607,41.395650000000003,40.833640000000003,40.713909999999998,41.212319999999998,40.915469999999999,40.786360000000002,41.1325,40.627189999999999,40.783250000000002,40.401020000000003,40.785299999999999,40.39161,192.9605,6431.4660000000003,6600.6570000000002,51.332149999999999,41.006830000000001,37,37,553414.83120000002,377810.6028738193,1292.4561826175002,41,34,33203.472259559996,44,9.3725564040509965,9.9796964040509977,323663.29134424659,7085.2541885389619,275.79587188376399,82.835371883763997,9.6984185024855479E-2,169.1909999999998,-484.59718853896175,2.8003621259135587E-2,2.8003621259135587E-2,0.87471305719528902,0.87471305719528902,6654.2048806378343,-53.547880637834169,0.37888147988915355,0.37888147988915355,44,0.88920952958436372]
["2013-03-07T14:00:00","2013-03-07T14:00:00",54.332599999999999,54.085540000000002,53.709049999999998,54.033720000000002,54.15446,53.815489999999997,53.74606,53.948799999999999,53.787320000000001,53.633339999999997,53.022390000000001,52.225859999999997,50.734650000000002,46.081359999999997,42.44182,41.226779999999998,40.900300000000001,41.347940000000001,41.104019999999998,41.153320000000001,41.43618,40.801690000000001,40.851860000000002,40.437469999999998,40.825830000000003,40.442700000000002,5116.47,9102.5020000000004,3986.0309999999999,53.95337,41.006599999999999,23,23,344014.62479999999,290026.96762082883,35533.628326499995,71,49,58923.999909270002,44,11.162331396906108,11.769471396906107,239616.32743775466,10557.651052288615,6366.7037042725569,1250.2337042725567,6.0287466366802052E-2,-5116.4710000000005,-6571.6200522886147,-6.9099327932598709E-2,0,0.61156628671872326,0.61156628671872326,10013.024021581738,-6026.9930215817376,4.7894399544824565E-2,4.7894399544824565E-2,42,0.62606275910779796]
["2013-03-07T21:00:00","2013-03-07T21:00:00",54.330219999999997,54.180669999999999,53.849130000000002,54.160429999999998,54.299460000000003,53.945399999999999,53.917349999999999,54.088760000000001,53.930929999999996,53.876820000000002,54.037260000000003,54.034999999999997,53.993789999999997,54.142650000000003,54.203020000000002,52.38355,51.757649999999998,49.373699999999999,42.797890000000002,41.540059999999997,41.774940000000001,41.203749999999999,41.136749999999999,40.715179999999997,41.067300000000003,40.598619999999997,1006.199,7805.7030000000004,6799.5039999999999,53.329689999999999,40.770890000000001,15,15,224357.364,178233.70070060756,6908.3610942000005,58,46,49015.131418199991,44,10.641897981360621,11.249037981360619,148985.50237303137,9211.7273636808823,1298.3325166807754,292.13351668077541,3.9317912847914381E-2,-1006.1990000000005,-2412.2233636808824,-2.5364067296558487E-2,0,0.48615634168142374,0.48615634168142374,8714.5463459927632,-1915.0423459927633,-2.013630398861585E-2,0,41,0.50065281407049844]
["2013-03-08","2013-03-08",54.374920000000003,54.19464,53.855469999999997,54.134160000000001,54.273389999999999,53.879429999999999,53.854939999999999,54.014150000000001,53.852330000000002,53.784030000000001,53.997520000000002,53.958280000000002,53.944859999999998,54.182000000000002,54.476990000000001,53.653680000000001,52.220970000000001,52.291499999999999,49.193750000000001,42.876869999999997,41.9208,41.359630000000003,41.279690000000002,40.818539999999999,41.148859999999999,40.660850000000003,557.88430000000005,7355.576,6799.3609999999999,52.344230000000003,40.613210000000002,13,13,194443.04880000002,141757.32651531009,3825.4321710505001,58,48,43144.204583760002,44,10.563393376306216,11.170533376306217,128168.25301879288,8168.6259418366126,724.28092654979184,166.39662654979179,3.4075524468192467E-2,-556.21500000000015,-1369.2649418366127,-1.4397558971722405E-2,0,0.46402462504749054,0.46402462504749054,7724.6453916467472,-925.28439164674728,-9.7291884041663876E-3,0,41,0.47852109743656523]
["2013-03-08T09:00:00","2013-03-08T09:00:00",54.255040000000001,54.091320000000003,53.736710000000002,54.013919999999999,54.183819999999997,53.751420000000003,53.733409999999999,53.710590000000003,52.486319999999999,51.463239999999999,48.140799999999999,42.640909999999998,40.437100000000001,40.593000000000004,40.976660000000003,40.381340000000002,40.226799999999997,40.755189999999999,40.5154,40.497860000000003,40.81615,40.296019999999999,40.422249999999998,40.03519,40.409820000000003,40.042140000000003,5272.65,7528.8580000000002,12801.51,52.856749999999998,39.720610000000001,27,27,403843.25520000001,322925.85415075254,37469.823592499997,56,52,49450.066364059989,44,11.021811263014447,11.628951263014446,277747.65025212057,8973.1288595002625,6799.2134320492905,1526.5634320492909,7.0772243126245887E-2,5272.652,3828.3811404997377,0.29469396707955875,0.29469396707955875,0.83601925292283552,0.83601925292283552,8504.6476239580679,4296.8623760419323,0.32764883530237482,0.32764883530237482,44,0.85051572531191033]
["2013-03-08T16:00:00","2013-03-08T16:00:00",52.316200000000002,49.855899999999998,43.944719999999997,41.447110000000002,41.000340000000001,40.46564,40.29813,40.320099999999996,40.064120000000003,39.954720000000002,40.181310000000003,40.144150000000003,40.100619999999999,40.39602,40.782629999999997,40.182099999999998,40.04374,40.54365,40.305390000000003,40.30498,40.595649999999999,40.079610000000002,40.199039999999997,39.811399999999999,40.197699999999998,39.82667,4589.6499999999996,8216.4,12806.05,53.604570000000002,39.717359999999999,45,45,673072.09200000006,578667.64652528847,28661.285682250003,60,57,57051.436122000014,44,11.585252971760202,12.192392971760199,486577.13233283587,9848.9754623514145,4947.8912117178161,{"$f":"AU1598-AC1598","v":358.24121171781644},0.11795373854374315,{"$f":"AE1598-AD1598","v":4589.6499999999996},2957.0745376485847,0.53684251920146719,0.53684251920146719,1.0482592919131721,1,{"$f":"AO1598*1000/(500*AR1598)","v":9358.5297413135431},{"$f":"AE1598-BD1598","v":3447.5202586864561},0.60521136200260206,0.60521136200260206,44,1]
["2013-03-08T19:00:00","2013-03-08T19:00:00",41.040930000000003,40.7136,40.303759999999997,40.531619999999997,40.740169999999999,40.294690000000003,40.222969999999997,40.445160000000001,40.23977,40.099850000000004,40.248469999999998,40.229849999999999,40.164450000000002,40.457039999999999,40.846679999999999,40.229419999999998,40.09384,40.58905,40.306690000000003,40.136029999999998,40.380629999999996,39.844470000000001,39.964979999999997,39.565770000000001,39.948950000000004,39.581760000000003,4300.1890000000003,8226.2710000000006,11965.77,53.494709999999998,39.82076,51,51,762815.03760000004,662251.66658831958,3137.3533915650005,62,57,56242.809170224995,44,11.557678792704674,12.164818792704672,550141.56180832617,9732.5440824200832,542.90371757784624,-3757.2852824221541,0.13368090368290891,3739.4989999999998,2233.2259175799172,0.64423313829525697,0.64423313829525697,1.0393201167518253,1,9246.7976923674687,2718.9723076325317,0.72797203944691891,0.72797203944691891,44,1]
["2013-03-09T02:00:00","2013-03-09T02:00:00",52.054650000000002,43.212969999999999,40.51914,40.65164,40.832160000000002,40.369259999999997,40.29374,40.510710000000003,40.31129,40.214329999999997,40.38993,40.386040000000001,40.317749999999997,40.589930000000003,40.954099999999997,40.3367,40.165109999999999,40.636670000000002,40.388260000000002,40.509459999999997,40.854909999999997,40.294229999999999,40.270870000000002,39.679940000000002,40.013849999999998,39.643000000000001,873.09829999999999,7671.8010000000004,6798.7020000000002,52.234690000000001,39.644419999999997,47,47,702986.40720000002,552351.50341339293,5418.2952575975014,61,57,48295.022988135017,44,11.286659283895405,11.893799283895405,495104.56689883216,8557.8950818592948,960.12382784137083,87.025527841370831,0.12319612692346506,-873.09900000000016,-1759.1930818592946,{"$f":"IF(AZ1607>1,1+AY1608*60/$BK$7,IF(AZ1607<0,AY1608*60/$BK$7,AZ1607+AY1608*60/$BK$7))","v":0.49417315605165663},0.49417315605165663,{"$f":"IF(BB1607>1,1+AX1608*60/$BK$7,BB1607+AX1608*60/$BK$7)","v":0.94292660657539062},0.94292660657539062,8121.0422061734407,-1322.3402061734405,0.61158369148798342,0.61158369148798342,44,0.9728556322012234]
["2013-03-09T07:00:00","2013-03-09T07:00:00",53.190719999999999,52.683450000000001,52.172229999999999,48.515970000000003,41.399079999999998,40.55979,40.430010000000003,40.667560000000002,40.458710000000004,40.337299999999999,40.483640000000001,40.465629999999997,40.390079999999998,40.675159999999998,41.065649999999998,40.454880000000003,40.310470000000002,40.804690000000001,40.550600000000003,40.565109999999997,40.838839999999998,40.28407,40.423439999999999,40.031700000000001,40.303989999999999,39.84366,1900.8340000000001,8710.1630000000005,6809.33,52.834899999999998,39.778039999999997,43,43,643157.77679999999,521378.02306357445,12685.272724019998,62,59,56863.689434090003,44,11.700544809702471,12.30768480970247,469578.49455859809,9719.8361886425646,2168.3217201135726,267.48772011357255,0.11271135016402123,-1900.8330000000005,-2910.5061886425647,0.3703254772864279,0.3703254772864279,0.86636057681696055,0.86636057681696055,9240.3551623718649,-2431.025162371865,0.51181860325456863,0.51181860325456863,44,0.89628960244279332]
["2013-03-09T13:00:00","2013-03-09T13:00:00",54.51784,54.230249999999998,53.585520000000002,53.41328,53.337040000000002,52.563740000000003,52.376019999999997,52.228610000000003,47.97289,41.171729999999997,40.786650000000002,40.779910000000001,40.607959999999999,40.757449999999999,41.108890000000002,40.460810000000002,40.280639999999998,40.82958,40.581850000000003,40.629640000000002,40.887180000000001,40.323799999999999,40.411209999999997,39.975470000000001,40.326999999999998,39.978999999999999,3081.4160000000002,10077.870000000001,6996.4539999999997,53.950859999999999,39.848840000000003,33,33,493586.20079999999,430330.19923979207,22400.10709872,68,64,71059.162148699979,44,12.488845429270672,13.095985429270669,384653.67831147858,11379.620726533361,3587.2182461670723,505.8022461670721,8.6499408265411637E-2,-3081.4160000000011,-4383.1667265333617,0.1232831751541992,0.1232831751541992,0.70005932921771563,0.70005932921771563,10852.052719893312,-3855.5987198933126,0.29729946037570965,0.29729946037570965,44,0.7299883548435484]
["2013-03-09T20:00:00","2013-03-09T20:00:00",55.150120000000001,54.932609999999997,54.597180000000002,54.901879999999998,55.007449999999999,54.548209999999997,54.299259999999997,54.355969999999999,53.996690000000001,53.792450000000002,53.606389999999998,53.384279999999997,52.926310000000001,52.929389999999998,53.085509999999999,51.756509999999999,45.612189999999998,41.668619999999997,41.002859999999998,41.018180000000001,41.27552,40.55659,40.620449999999998,40.201050000000002,40.575780000000002,40.206600000000002,2249.712,9240.384,6990.6719999999996,53.90157,39.932740000000003,17,17,254271.67920000001,217291.96435400212,16809.308133120001,68,64,64538.676615359982,44,12.266496872583776,12.873636872583777,194627.02008006972,10522.755972751618,2740.6860015086513,490.97400150865133,4.4560301227636302E-2,-2249.7120000000004,-3532.0839727516186,-3.7139187411427244E-2,0,0.44679336867215413,0.44679336867215413,10026.487037676849,-3035.815037676849,-1.5877042845183986E-2,0,41,0.47672239429798685]
["2013-03-09T23:00:00","2013-03-09T23:00:00",54.99165,54.768149999999999,54.430619999999998,54.71808,54.842129999999997,54.405239999999999,54.381880000000002,54.575589999999998,54.365409999999997,54.220649999999999,54.24447,53.938079999999999,53.666229999999999,53.531269999999999,53.605899999999998,52.656730000000003,52.367550000000001,52.137700000000002,45.823149999999998,41.352440000000001,41.481090000000002,40.86674,40.755490000000002,40.339750000000002,40.719920000000002,40.31073,1648.9490000000001,8649.4830000000002,7000.5349999999999,52.964129999999997,39.838050000000003,13,13,194443.04880000002,153526.81803800139,12104.044176540001,63,61,56766.902908319978,44,11.818938389173713,12.426078389173712,143402.08983174659,9606.0916876119991,2048.2455831443285,399.29658314432845,3.4075524468192467E-2,-1648.9480000000003,-2605.5566876119992,-2.7396930219904633E-2,0,0.38884679398571748,0.38884679398571748,9136.7366485919574,-2136.2016485919576,-2.2461751755536656E-2,0,41,0.41877581961155019]
["2013-03-11T08:00:00","2013-03-11T08:00:00",51.334060000000001,47.684179999999998,42.303879999999999,41.613959999999999,41.410890000000002,39.943240000000003,38.794029999999999,38.475259999999999,38.185830000000003,37.896529999999998,38.324919999999999,37.980899999999998,37.964970000000001,38.244500000000002,38.615650000000002,38.061259999999997,37.967140000000001,38.466839999999998,38.110959999999999,37.843400000000003,38.281669999999998,37.733609999999999,38.009239999999998,37.606960000000001,38.004469999999998,37.637740000000001,305.12830000000002,6100.2820000000002,6401.6229999999996,49.962739999999997,39.472749999999998,47,47,702986.40720000002,540652.78604937578,2089.5674189280003,37,32,31995.948588589996,44,9.2096858468709204,9.8168258468709197,403995.31941178662,6948.325734576697,453.77604701640308,148.64774701640306,0.12319612692346506,301.34099999999944,-546.70273457669737,-5.748474689282689E-3,0,0.41270064702397852,0.41270064702397852,6518.5935021529594,-116.97050215295985,1.5740165903301247E-2,1.5740165903301247E-2,42,1]
["2013-03-11T15:00:00","2013-03-11T15:00:00",51.585729999999998,50.679549999999999,44.094299999999997,42.036769999999997,41.606699999999996,40.64461,39.325369999999999,38.766829999999999,38.287239999999997,38.128149999999998,38.316360000000003,38.186810000000001,38.051439999999999,38.310369999999999,38.680509999999998,38.107320000000001,37.914360000000002,38.408270000000002,38.124229999999997,38.13288,38.448099999999997,37.857120000000002,38.035670000000003,37.61938,38.017069999999997,37.672840000000001,880.52340000000004,7282.0919999999996,6401.5680000000002,51.90099,39.625839999999997,45,45,673072.09200000006,597578.01079328358,6125.3126033129993,58,42,44694.385806900013,44,10.251172556015291,10.85831255601529,430546.15704236447,8719.8582528344559,1195.0462388263522,314.5228388263522,0.11795373854374315,-880.52399999999943,-2318.2902528344557,-2.4376378602071966E-2,0,0.3899205031649407,0.3899205031649407,8232.2894236711218,-1830.7214236711216,-1.9249685617997607E-2,0,41,0.9745457510129516]
["2013-03-11T18:00:00","2013-03-11T18:00:00",51.920189999999998,51.167340000000003,49.775889999999997,43.806829999999998,42.090389999999999,41.090429999999998,40.485689999999998,39.392609999999998,38.508420000000001,38.23545,38.351219999999998,38.306480000000001,38.121259999999999,38.345039999999997,38.70194,38.13984,37.994459999999997,38.481430000000003,38.172750000000001,38.155329999999999,38.469799999999999,37.865119999999997,38.05097,37.641489999999997,38.036580000000001,37.691859999999998,990.14840000000004,7759.5519999999997,6769.4040000000005,52.794060000000002,39.69115,45,45,673072.09200000006,634287.84730287001,7044.0790920859999,59,44,50836.355748160007,44,10.582307731012257,11.189447731012256,444453.7345684921,9607.8014437588499,1331.2935649079247,341.14516490792471,0.11795373854374315,-990.14799999999923,-2838.3974437588495,-2.9845206236632397E-2,0,0.35809741349714486,0.35809741349714486,9086.4816513265177,-2317.0776513265173,-2.4363628329143541E-2,0,41,0.9427226613451557]
["2013-03-12T01:00:00","2013-03-12T01:00:00",52.130830000000003,51.47627,50.739060000000002,47.62453,42.934359999999998,41.398130000000002,40.943660000000001,40.298769999999998,38.854039999999998,38.382170000000002,38.587589999999999,38.374830000000003,38.235990000000001,38.441989999999997,38.783160000000002,38.204169999999998,38.08323,38.580120000000001,38.26435,38.132730000000002,38.470100000000002,37.894170000000003,38.102679999999999,37.691220000000001,38.094340000000003,37.730519999999999,187.15790000000001,6541.5010000000002,6402.5749999999998,49.984740000000002,39.5319,43,43,643157.77679999999,491799.16603696934,1347.5658894745006,44,37,34188.63165642001,44,9.5886913394839226,10.195831339483924,384823.383629811,7131.0318469923941,281.07399472241821,93.916094722418194,0.11271135016402123,-138.92600000000039,-728.45684699239428,-7.6595844182355769E-3,0,0.34057742888577669,0.34057742888577669,6706.3941169804621,-303.81911698046224,-3.194599905256897E-3,0,40,0.92520267673378753]
["2013-03-12T04:00:00","2013-03-12T04:00:00",52.00347,51.536639999999998,50.749310000000001,48.190309999999997,43.124180000000003,41.457410000000003,40.985970000000002,40.409950000000002,38.95599,38.397799999999997,38.635570000000001,38.375830000000001,38.268349999999998,38.433700000000002,38.778739999999999,38.214129999999997,38.103560000000002,38.599670000000003,38.277259999999998,38.133510000000001,38.474429999999998,37.9026,38.123370000000001,37.71593,38.115009999999998,37.75273,174.52869999999999,6416,6400.2349999999997,50.070610000000002,39.497970000000002,43,43,643157.77679999999,494354.03569900518,1243.5815631189998,42,35,33917.029119999999,44,9.4577356929920011,10.064875692992,379567.7347404848,7172.3360053573624,262.97659471293321,88.44789471293322,0.11271135016402123,-15.765000000000327,-772.10100535736274,-8.118494395867799E-3,0,0.33890334515737042,0.33890334515737042,6739.6816720977176,-339.44667209771796,-3.5692168330305339E-3,0,40,0.92352859300538126]
["2013-03-12T13:00:00","2013-03-12T13:00:00",52.560980000000001,51.66431,51.12,51.356749999999998,50.666069999999998,45.152290000000001,42.061199999999999,41.528120000000001,40.801650000000002,39.540300000000002,38.906799999999997,38.721690000000002,38.549289999999999,38.600569999999998,38.921140000000001,38.323369999999997,38.183160000000001,38.65701,38.388840000000002,38.330469999999998,38.626550000000002,38.035200000000003,38.172029999999999,37.741250000000001,38.13644,37.807850000000002,1904.6489999999999,8304.7929999999997,6400.1440000000002,52.251890000000003,39.45787,39,39,583329.14639999997,525759.28228308924,14049.767150685,65,47,53125.843868930009,44,10.842920275930515,11.450060275930515,394679.46517220826,9799.1763320183345,2591.509813435252,686.86081343525211,0.10222657340457739,-1904.6489999999994,-3399.0323320183343,-3.5740174857164048E-2,0,0.26902983343699455,0.26902983343699455,9279.5745330017708,-2879.4305330017705,-3.0276661321850959E-2,0,40,0.85365508128500522]
["2013-03-12T20:00:00","2013-03-12T20:00:00",53.667740000000002,53.272590000000001,52.500160000000001,52.538710000000002,52.175330000000002,51.306980000000003,51.186129999999999,51.19529,49.883659999999999,44.248869999999997,42.093220000000002,41.394350000000003,40.724649999999997,39.809179999999998,39.587730000000001,38.766069999999999,38.394269999999999,38.85172,38.528739999999999,38.560560000000002,38.820250000000001,38.166980000000002,38.282089999999997,37.82396,38.215310000000002,37.900379999999998,1388.9359999999999,7992.9030000000002,6603.9669999999996,52.441290000000002,39.650019999999998,31,31,463671.88560000004,420713.97626168962,10949.926964480004,55,43,51119.690178405013,44,10.531122435083612,11.138262435083611,304698.2887702841,9708.308016266863,2079.5365417082567,690.60054170825674,8.125701988568973E-2,-1388.9360000000006,-3104.3410162668633,-3.2641552036006223E-2,0,0.12827416645347525,0.12827416645347525,9179.1139733584987,-2575.1469733584991,-2.7077177890825987E-2,0,39,0.71289941430148596]
["2013-03-12T23:00:00","2013-03-12T23:00:00",53.468049999999998,53.06232,52.68779,52.960889999999999,52.608879999999999,51.77337,51.290109999999999,51.417439999999999,50.998240000000003,49.235300000000002,44.056350000000002,42.002690000000001,41.347700000000003,40.92765,40.122500000000002,39.041499999999999,38.639519999999997,38.964280000000002,38.631320000000002,38.58379,38.867829999999998,38.178049999999999,38.347859999999997,37.915210000000002,38.283830000000002,37.933979999999998,857.31100000000004,7455.7079999999996,6598.3969999999999,51.21978,39.598370000000003,29,29,433757.57040000003,359599.73891838803,6658.7645428850001,51,42,43322.919754139992,44,10.204405563616174,10.811545563616175,276197.26147418458,8491.0227223049496,1305.0764204486024,447.76542044860241,7.6014631505967808E-2,-857.31099999999969,-1892.6257223049497,-1.9900597478041421E-2,0,9.7125054996011456E-2,9.7125054996011456E-2,8014.1954726498188,-1415.7984726498189,-1.488685014801365E-2,0,39,0.68175030284402205]
["2013-03-13T06:00:00","2013-03-13T06:00:00",53.018439999999998,52.663620000000002,52.297289999999997,52.603400000000001,52.734560000000002,52.242870000000003,52.049689999999998,51.589500000000001,51.273479999999999,50.919530000000002,50.228850000000001,44.898119999999999,42.229300000000002,41.733150000000002,41.507800000000003,39.762659999999997,39.034489999999998,39.230739999999997,38.777940000000001,38.630629999999996,38.924399999999999,38.296669999999999,38.45908,37.999360000000003,38.370060000000002,38.00855,686.14059999999995,7279.9520000000002,6593.8119999999999,51.023400000000002,39.622140000000002,27,27,403843.25520000001,327971.86593223864,5149.4474652669996,42,38,41500.312769760007,44,9.8988666654488178,10.506006665448817,249449.64950665471,8384.8614538093425,1040.4115217029287,354.27092170292872,7.0772243126245887E-2,-686.14000000000033,-1791.0494538093426,-1.8832542442738021E-2,0,5.1128823307759419E-2,5.1128823307759419E-2,7900.3020065164046,-1306.4900065164047,-1.3737492533443144E-2,0,38,0.6357540711557701]
["2013-03-13T15:00:00","2013-03-13T15:00:00",53.815710000000003,52.801679999999998,52.234369999999998,52.518520000000002,52.565510000000003,52.236179999999997,52.160719999999998,52.366019999999999,52.212200000000003,52.130800000000001,52.053280000000001,51.50902,51.326860000000003,51.258800000000001,50.035400000000003,44.64855,41.938830000000003,41.744079999999997,40.766170000000002,39.83417,39.5443,38.880319999999998,38.716410000000003,38.26925,38.608440000000002,38.164099999999998,2748.1379999999999,9096.9770000000008,6348.8379999999997,53.216180000000001,38.925719999999998,19,19,284185.99440000003,266921.63612951327,21506.392101090005,68,50,64999.992969710016,44,11.430369760267112,12.037509760267113,202697.10219290684,11373.209149480926,3763.0264903324405,1014.8884903324406,4.9802689607358223E-2,-2748.139000000001,-5024.3711494809268,-5.2830301653267728E-2,0,-9.794369988209245E-2,-9.794369988209245E-2,10799.574706765206,-4450.7367067652067,-4.6798645203981235E-2,0,37,0.48668154796591834]
["2013-03-13T18:00:00","2013-03-13T18:00:00",55.128270000000001,53.740540000000003,53.228189999999998,53.33849,52.934600000000003,52.327289999999998,52.201070000000001,52.394469999999998,52.239150000000002,52.172150000000002,52.279910000000001,52.351559999999999,52.303220000000003,52.129730000000002,52.039290000000001,51.267620000000001,50.681609999999999,48.91236,44.251350000000002,42.312910000000002,41.82414,40.385719999999999,39.884149999999998,38.637210000000003,38.911299999999997,38.360849999999999,4089.6959999999999,10511.62,6451.5789999999997,56.673459999999999,39.024929999999998,15,15,224357.364,256374.69983174646,34286.825252160008,66,51,92757.320459300012,44,12.437741627662131,13.04488162766213,174127.13296338954,14915.460255743423,5513.3522272089122,1423.6562272089122,3.9317912847914381E-2,-4060.0410000000011,-8463.881255743423,-8.8996092564650395E-2,0,-0.20702504071180666,-0.20702504071180666,14221.259051152269,-7769.6800511522688,-8.1696699674377662E-2,0,37,0.37760020713620412]
["2013-03-14T01:00:00","2013-03-14T01:00:00",52.851320000000001,52.501710000000003,52.162930000000003,52.436360000000001,52.311059999999998,51.443309999999997,51.169849999999997,50.942990000000002,48.790500000000002,44.796399999999998,42.478050000000003,41.417740000000002,40.378160000000001,39.232259999999997,39.59581,39.010199999999998,38.88693,39.402709999999999,39.138060000000003,39.131149999999998,39.447670000000002,38.874130000000001,39.05124,38.638030000000001,39.038319999999999,38.67492,6323.4790000000003,8223.0769999999993,14546.55,49.913789999999999,38.019370000000002,31,31,{"$f":"3.1416*(138/2)^2*AI1703","v":463671.88560000004},{"$f":"62.4*AJ1703*(AF1703-AB1703)/1000","v":325175.63800258818},44822.083847800001,52,43,48904.365765169976,44,10.455579872592297,11.062719872592297,302512.60631693579,{"$f":"AO1703*1000/(500*AQ1703)","v":9354.6922047557182},8573.8111886638126,2250.3321886638123,{"$f":"AJ1703/$BK$7","v":8.125701988568973E-2},6323.473,{"$f":"AE1703-AT1703","v":5191.8577952442811},0.26513765296524805,0.26513765296524805,0.19618662428543387,0.19618662428543387,8841.2915319911008,5705.2584680088985,0.30619402064899787,0.30619402064899787,44,0.78081187213344472]
["2013-03-14T07:00:00","2013-03-14T07:00:00",42.179079999999999,40.823790000000002,39.33549,39.295749999999998,39.409599999999998,38.883090000000003,38.81615,39.046289999999999,38.831420000000001,38.69162,38.990250000000003,38.902720000000002,38.882579999999997,39.176180000000002,39.541289999999996,38.971989999999998,38.859110000000001,39.343319999999999,39.078299999999999,39.020060000000001,39.360349999999997,38.800060000000002,38.990499999999997,38.576079999999997,38.976700000000001,38.610779999999998,4214.3130000000001,7203.95,11412.11,50.255049999999997,38.644010000000002,51,51,762815.03760000004,554263.2736913719,7518.9665389500014,48,42,41822.675803999984,44,10.1532472449164,10.7603872449164,483291.09996292321,8238.2857021314157,1481.0959208571724,-2733.217079142828,0.13368090368290891,4208.1600000000008,3173.8242978685848,0.58783920516789079,0.58783920516789079,0.58794206869140009,0.58794206869140009,7773.4518009579151,3638.6581990420855,0.66022769150647986,0.66022769150647986,44,1]
["2013-03-14T12:00:00","2013-03-14T12:00:00",52.824979999999996,49.309690000000003,42.491630000000001,41.265830000000001,40.123550000000002,39.16563,38.979190000000003,39.15963,38.92989,38.828629999999997,38.947209999999998,39.002540000000003,38.94164,39.215490000000003,39.573360000000001,38.956150000000001,38.803730000000002,39.327950000000001,39.080109999999998,39.138469999999998,39.449129999999997,38.867519999999999,38.971530000000001,38.527209999999997,38.908119999999997,38.622459999999997,3415.1309999999999,9913.4639999999999,6498.3329999999996,52.541469999999997,39.811959999999999,47,47,702986.40720000002,610576.18949688633,24251.733165059999,72,55,63096.76956131999,44,11.669704842041012,12.276844842041012,511907.37811142934,10813.772998612443,4156.3575931571568,741.22659315715691,0.12319612692346506,-3415.1310000000003,-4315.4399986124436,0.43826052349834888,0.43826052349834888,0.47857922540221748,0.47857922540221748,10278.987862622564,-3780.654862622564,0.53636213206050609,0.53636213206050609,44,0.93310139054113306]
["2013-03-14T19:00:00","2013-03-14T19:00:00",55.128250000000001,54.6509,54.11036,53.959629999999997,53.69764,52.861350000000002,52.481670000000001,52.076030000000003,49.415649999999999,42.631680000000003,41.129269999999998,40.025379999999998,39.466720000000002,39.486170000000001,39.762129999999999,39.106619999999999,38.937869999999997,39.457850000000001,39.243859999999998,39.293109999999999,39.482419999999998,38.932459999999999,39.019959999999998,38.567729999999997,39.00271,38.698039999999999,2590.8139999999999,9800.1640000000007,7209.35,53.967500000000001,39.818579999999997,33,33,493586.20079999999,470295.99237925629,21283.809045470003,70,55,69330.868211440014,44,11.882287606010104,12.489427606010105,365971.83144683955,11669.616240625619,3582.443002760609,991.62900276060918,8.6499408265411637E-2,-2590.8140000000003,-4460.2662406256186,8.9859512605509784E-2,8.9859512605509784E-2,0.25147008181898867,0.25147008181898867,11102.329169685394,-3892.9791696853936,0.22870136821263651,0.22870136821263651,44,0.70599224695790419]
["2013-03-14T22:00:00","2013-03-14T22:00:00",54.797910000000002,54.387160000000002,54.006149999999998,54.324109999999997,54.382759999999998,53.836210000000001,53.188459999999999,53.092500000000001,52.381340000000002,51.953659999999999,48.876469999999998,42.169580000000003,41.05227,40.122320000000002,40.10078,39.240459999999999,39.054160000000003,39.578159999999997,39.314889999999998,39.369549999999997,39.518659999999997,38.96895,39.078830000000004,38.64752,39.06279,38.736249999999998,1081.4870000000001,8484.6209999999992,7403.134,52.608849999999997,39.085520000000002,29,29,433757.57040000003,375482.34491857683,8685.2382442100006,63,53,57370.164853964976,44,11.352733621520207,11.959873621520206,307278.45115150546,10106.845939768069,1530.0699432859572,448.58294328595707,7.6014631505967808E-2,-1081.4869999999992,-2703.711939768069,-1.5800248597959924E-2,0,0.20424252396856735,0.20424252396856735,9593.7744276385965,-2190.6404276385965,0.13995291473548277,0.13995291473548277,43,0.65876468910748276]
["2013-03-15T05:00:00","2013-03-15T05:00:00",53.679049999999997,53.301819999999999,52.935890000000001,53.222470000000001,53.334719999999997,52.934010000000001,52.887680000000003,53.066540000000003,52.888890000000004,52.797960000000003,53.03519,52.960970000000003,52.876060000000003,52.60398,48.091659999999997,42.113,40.720390000000002,40.340000000000003,39.692079999999997,39.54486,39.825670000000002,39.148269999999997,39.258569999999999,38.831020000000002,39.213639999999998,38.820459999999997,1699.67,9099.5580000000009,7399.8879999999999,50.511319999999998,39.1614,21,21,314100.30960000004,229139.21131859199,12627.349832649999,56,52,51639.62766767999,44,11.096475303467889,11.703615303467888,217489.3548851723,9307.3928892612385,2275.9208644755295,576.2508644755294,5.5045077987080138E-2,-1699.670000000001,-1907.5048892612385,-2.005704907273129E-2,0,8.2395164367816076E-2,8.2395164367816076E-2,8824.559989147745,-1424.6719891477451,3.5223122065435646E-2,3.5223122065435646E-2,42,0.53691732950673154]
["2013-03-15T14:00:00","2013-03-15T14:00:00",53.48668,53.009419999999999,52.584589999999999,52.902169999999998,52.994999999999997,52.682510000000001,52.558860000000003,52.779069999999997,52.659019999999998,52.616950000000003,52.644860000000001,52.794820000000001,52.73198,52.939540000000001,53.255830000000003,52.649970000000003,52.529389999999999,52.892110000000002,52.070929999999997,46.505110000000002,42.370010000000001,40.63946,40.056690000000003,38.877929999999999,38.915489999999998,38.543889999999998,3584.6889999999999,10601.05,14185.74,52.930039999999998,36.97186,11,11,164528.73360000001,147696.74655088954,26782.627471155003,81,59,84586.732044499993,44,12.645900562717451,13.253040562717452,129830.31390048281,13377.731641173577,4235.7801784580442,651.0911784580444,2.8833136088470546E-2,3584.6900000000005,808.00835882642241,8.4960533497951789E-3,8.4960533497951789E-3,-2.7481947701814183E-2,-2.7481947701814183E-2,12764.879371523786,1420.8606284762136,1.4940077748317801E-2,1.4940077748317801E-2,43,0.42704021743710124]
["2013-03-15T17:00:00","2013-03-15T17:00:00",53.345939999999999,52.923380000000002,52.551250000000003,52.887549999999997,52.96996,52.680810000000001,52.535519999999998,52.767679999999999,52.644179999999999,52.622540000000001,52.611829999999998,52.785559999999997,52.710650000000001,52.862639999999999,52.945340000000002,50.179749999999999,44.063110000000002,41.761920000000003,40.471969999999999,40.191760000000002,39.361849999999997,37.499940000000002,37.51831,37.004600000000003,37.332590000000003,37.16778,4479.2979999999998,9720.616,14199.91,53.790529999999997,36.934460000000001,17,17,254271.67920000001,263745.74025832029,36233.399865839994,80,60,81925.691869559974,44,12.616006092751995,13.223146092751996,200172.52656969239,12987.579629757312,5744.0365198708005,1264.7385198708007,4.4560301227636302E-2,4479.2939999999999,1212.3303702426874,4.8789884221880367E-2,4.8789884221880367E-2,0.11288807815651965,0.11288807815651965,12391.255650493933,1808.6543495060669,7.4061122795134313E-2,7.4061122795134313E-2,44,0.56741024329543499]
["2013-03-16","2013-03-16",53.248089999999998,52.903329999999997,52.538559999999997,52.837960000000002,52.82752,51.67268,47.354819999999997,42.923360000000002,40.871560000000002,40.02487,39.49653,38.080370000000002,36.973649999999999,37.20046,37.571330000000003,36.958350000000003,36.80986,37.377800000000001,37.120759999999997,37.171570000000003,37.449539999999999,36.882399999999997,37.0139,36.527279999999998,36.848309999999998,36.626269999999998,6289.183,7916.3429999999998,14205.53,51.037669999999999,36.859520000000003,35,35,523500.516,470769.02098402171,52268.833886529996,67,56,56119.549252724981,44,11.492628629517924,12.099768629517921,375423.17390753794,9766.1816215980889,9096.0624538552584,2806.8794538552584,9.1741796645133558E-2,6289.1870000000008,4439.3483784019118,0.25019741526154587,0.25019741526154587,0.50264124010901656,0.50264124010901656,9276.1359280571469,4929.3940719428538,0.31639405894550121,0.31639405894550121,44,0.95716340524793164]
["2013-03-16T03:00:00","2013-03-16T03:00:00",52.429859999999998,48.11927,42.891599999999997,41.134540000000001,40.54121,39.356340000000003,38.283439999999999,37.496589999999998,36.843119999999999,36.739269999999998,36.916339999999998,36.907409999999999,36.868780000000001,37.142910000000001,37.521990000000002,36.899099999999997,36.737139999999997,37.344090000000001,37.052930000000003,37.065159999999999,37.372109999999999,36.806100000000001,36.955489999999998,36.497700000000002,36.819139999999997,36.566499999999998,6121.7709999999997,8072.7740000000003,14194.55,50.273099999999999,36.858649999999997,47,47,702986.40720000002,601258.53770907735,48555.928605279994,62,54,54145.911592150012,44,11.303633585292317,11.910773585292317,495849.16757562582,9580.2665901346572,8591.207108563458,2469.4361085634582,0.12319612692346506,6121.7759999999989,4614.283409865342,0.39373022245160211,0.39373022245160211,0.69589187940865438,0.69589187940865438,9091.9218981730228,5102.6281018269765,0.47535959333051025,0.47535959333051025,44,1]
["2013-03-16T12:00:00","2013-03-16T12:00:00",51.541809999999998,49.86627,42.676650000000002,40.561959999999999,40.026560000000003,38.67013,37.447029999999998,37.353490000000001,37.087600000000002,36.917740000000002,36.952179999999998,37.038150000000002,36.96705,37.229329999999997,37.600990000000003,36.975760000000001,36.797870000000003,37.339449999999999,37.076569999999997,37.162619999999997,37.430619999999998,36.865119999999997,36.951479999999997,36.475639999999999,36.795169999999999,36.568019999999997,2077.252,9243.4709999999995,7166.2190000000001,52.784329999999997,37.235689999999998,45,45,673072.09200000006,681080.13144416059,15552.167612540001,76,63,71861.701464719998,44,12.455365019946953,13.062505019946952,523121.5760533975,11539.075948337973,2497.2640444713738,420.01204447137388,0.11795373854374315,-2077.2519999999995,-4372.8569483379733,0.22583394378916161,0.22583394378916161,0.69986555180752807,0.69986555180752807,11002.744321243803,-3836.5253212438029,0.35525031661126605,0.35525031661126605,44,0.92921121623842839]
["2013-03-16T19:00:00","2013-03-16T19:00:00",54.267409999999998,53.820010000000003,53.419319999999999,53.750050000000002,53.818809999999999,53.467449999999999,52.87621,51.893149999999999,50.272359999999999,46.505859999999998,41.22992,40.191319999999997,39.252049999999997,38.319510000000001,38.200659999999999,37.321129999999997,37.111330000000002,37.575490000000002,37.35022,37.460209999999996,37.611499999999999,37.005270000000003,37.055190000000003,36.55444,36.856169999999999,36.643549999999998,3706.4870000000001,10708.03,7001.5450000000001,52.030569999999997,36.948900000000002,31,31,463671.88560000004,445194.5832150905,32661.303989910004,77,62,80747.487405049978,44,12.697523320512206,13.304663320512203,367379.03782144451,12718.620059489318,5144.5156926228783,1438.0286926228782,8.125701988568973E-2,-3706.4850000000006,-5717.0750594893179,-6.0113950777381908E-2,0,0.44161569809901513,0.44161569809901513,12138.223337160156,-5136.6783371601559,-3.6990415258878806E-2,0,41,0.67096136252991556]
["2013-03-16T22:00:00","2013-03-16T22:00:00",53.761609999999997,53.341929999999998,52.950330000000001,53.265210000000003,53.354120000000002,53.002429999999997,52.891480000000001,53.096969999999999,52.926079999999999,52.830359999999999,52.130650000000003,50.151620000000001,44.686149999999998,40.987549999999999,40.550150000000002,39.025730000000003,37.82685,37.987079999999999,37.526589999999999,37.57396,37.816850000000002,37.137419999999999,37.166969999999999,36.662460000000003,36.958829999999999,36.732599999999998,2127.6439999999998,9522.2279999999992,7394.5839999999998,50.76211,36.861370000000001,25,25,373928.94,327352.88370841055,18115.83547622,72,60,66183.00782436,44,12.079180566810678,12.686320566810675,281845.52356996562,10958.194963358281,2999.5139779590545,871.86997795905472,6.5529854746523966E-2,-2127.6439999999993,-3563.610963358281,-3.7470687687664157E-2,0,0.35815081821071298,0.35815081821071298,10433.759335627181,-3039.1753356271811,-3.1956347367957251E-2,0,40,0.58749648264161336]
["2013-03-17T05:00:00","2013-03-17T05:00:00",53.072290000000002,52.72616,52.3596,52.663020000000003,52.774729999999998,52.413249999999998,52.3401,52.543849999999999,52.355179999999997,52.318860000000001,52.461239999999997,52.496389999999998,52.453879999999998,52.685600000000001,52.99539,52.268900000000002,48.490749999999998,42.524340000000002,40.494129999999998,39.927900000000001,38.928890000000003,37.84151,37.58117,36.975079999999998,37.250100000000003,36.948720000000002,2228.6869999999999,9625.9770000000008,7397.29,51.227640000000001,36.954160000000002,15,15,224357.364,199903.44516273329,17967.195426295002,66,62,68698.095094980003,44,12.286639042738818,12.893779042738817,172011.71195821796,11182.569107143965,2924.6721359350568,695.98513593505686,3.9317912847914381E-2,-2228.6870000000008,-3785.2791071439651,-3.9801485822337682E-2,0,0.21199732158874929,0.21199732158874929,10656.006259649315,-3258.7162596493154,-3.4264778193678541E-2,0,39,0.44134298601964961]
["2013-03-17T14:00:00","2013-03-17T14:00:00",53.024479999999997,52.612319999999997,52.262230000000002,52.586399999999998,52.696190000000001,52.34892,52.149279999999997,50.530529999999999,45.167999999999999,41.010069999999999,39.992310000000003,38.886310000000002,37.735709999999997,37.445010000000003,37.716180000000001,37.092570000000002,36.941130000000001,37.507869999999997,37.245339999999999,37.280769999999997,37.607129999999998,37.029240000000001,37.160269999999997,36.718089999999997,37.07038,36.769109999999998,6062.2910000000002,8734.1139999999996,14796.41,52.3003,36.438189999999999,33,33,493586.20079999999,478357.21851858427,49272.391626334997,66,55,69270.738510270006,44,11.880237183200208,12.487377183200207,365908.6788775819,11661.507668925238,8294.8498193303531,2232.5588193303529,8.6499408265411637E-2,6062.2960000000003,3134.9023310747616,0.24423662328126633,0.24423662328126633,0.62112744646416684,0.62112744646416684,11094.52169082597,3701.8883091740299,0.28490329523325181,0.28490329523325181,44,0.85047311089506716]
["2013-03-17T17:00:00","2013-03-17T17:00:00",52.99286,52.579830000000001,51.658749999999998,48.224020000000003,42.883220000000001,40.315689999999996,39.213679999999997,38.477069999999998,37.55171,36.954439999999998,36.98603,37.044719999999998,36.999929999999999,37.252699999999997,37.627070000000003,37.00873,36.862749999999998,37.42418,37.165300000000002,37.234870000000001,37.515250000000002,36.958269999999999,37.068899999999999,36.617759999999997,36.988340000000001,36.687820000000002,5567.9219999999996,9229.7999999999993,14797.72,52.870190000000001,36.533940000000001,41,41,613243.46160000004,619240.91397118021,{"$f":"500*AC1791*(C1791-AB1791)/1000","v":45392.595463439997},72,59,75390.160124999995,44,{"$f":"19.5286-0.30357*AP1791+0.0000341*AO1791+0.060847*AN1791","v":12.332297460262502},{"$f":"19.5286-0.30357*42+0.0000341*AO1791+0.060847*AN1791","v":12.9394374602625},{"$f":"62.4*AJ1791*AQ1791/1000","v":471912.5289223654},12226.4582682869,{"$f":"AL1791*1000/(500*AQ1791)","v":7361.5797234384545},1793.6577234384549,0.10746896178429931,5567.92,2571.2617317130989,0.33397677619499222,0.33397677619499222,0.80291838477083899,0.80291838477083899,11652.772441850895,3144.9475581491042,0.39250353559446305,{"$f":"IF(BF1791>1,1,IF(BF1791<0,0,BF1791))","v":0.39250353559446305},44,1]
["2013-03-18T01:00:00","2013-03-18T01:00:00",42.058720000000001,39.76379,38.103850000000001,37.755049999999997,37.723260000000003,37.160879999999999,36.978479999999998,37.191769999999998,37.014130000000002,36.923000000000002,37.140999999999998,37.091920000000002,37.064169999999997,37.345860000000002,37.740209999999998,37.115600000000001,36.963839999999998,37.504170000000002,37.193680000000001,37.174880000000002,37.493679999999998,36.912970000000001,37.075800000000001,36.642690000000002,37.010530000000003,36.667870000000001,1002.5309999999999,8199.2060000000001,7196.674,49.826439999999998,36.779949999999999,49,49,732900.72239999997,601780.94862606027,2702.2471206750006,58,53,53485.429543469996,44,11.220264147432328,11.827404147432327,513136.39722833107,9533.7202120521779,481.67263892684542,-520.85836107315458,0.12843851530318698,-1002.5320000000002,-2337.0462120521779,0.31610232860193144,0.31610232860193144,0.97336060589074891,0.97336060589074891,9044.3226386377301,-1847.6486386377301,0.41924691465267855,0.41924691465267855,44,0.98945856776871954]
["2013-03-18T02:00:00","2013-03-18T02:00:00",46.938110000000002,40.199869999999997,38.690159999999999,37.909039999999997,37.77957,37.237780000000001,37.10577,37.253749999999997,37.024140000000003,36.924120000000002,37.131810000000002,37.097720000000002,37.06776,37.349930000000001,37.741709999999998,37.120759999999997,36.962119999999999,37.509770000000003,37.210369999999998,37.195120000000003,37.509869999999999,36.923079999999999,37.084710000000001,36.64725,37.018830000000001,36.679040000000001,1048.9690000000001,8244.4130000000005,7195.4430000000002,49.732619999999997,36.704410000000003,49,49,732900.72239999997,596979.44042294624,5380.7231994150006,59,53,53704.971945364974,44,11.227750543336946,11.834890543336945,513478.77261025109,9566.4704587217475,958.46860484590388,-90.500395154096168,0.12843851530318698,-1048.9700000000003,-2371.0274587217473,{"$f":"IF(AZ1799>1,1+AY1800*60/$BK$7,IF(AZ1799<0,AY1800*60/$BK$7,AZ1799+AY1800*60/$BK$7))","v":0.29117142836670662},0.29117142836670662,{"$f":"IF(BB1799>1,1+AX1800*60/$BK$7,BB1799+AX1800*60/$BK$7)","v":0.96233088697140645},0.96233088697140645,9075.7023478516112,-1880.259347851611,0.39947634723676634,0.39947634723676634,44,0.97842884884937709]
["2013-03-18T09:00:00","2013-03-18T09:00:00",51.641280000000002,50.744759999999999,49.825060000000001,49.957230000000003,45.240519999999997,39.748139999999999,38.56823,37.8688,37.473080000000003,37.264270000000003,37.379399999999997,37.219360000000002,37.164239999999999,37.452309999999997,37.857089999999999,37.240839999999999,37.079239999999999,37.577869999999997,37.27055,37.253909999999998,37.580889999999997,36.998390000000001,37.174160000000001,36.712499999999999,37.08728,36.723730000000003,767.30139999999994,7969.6350000000002,7202.3329999999996,50.783459999999998,36.764670000000002,41,41,613243.46160000004,538015.13964814914,5723.1284997849989,56,51,55862.319720824977,44,11.179622102480133,11.786762102480132,427803.80182829866,9993.5971374975652,1023.8500813932443,256.54868139324435,0.10746896178429931,-767.30200000000059,-2791.2641374975656,6.6496824226652984E-2,6.6496824226652984E-2,0.85392123212371995,0.85392123212371995,9478.823655746919,-2276.4906557469194,0.21230661681037244,0.21230661681037244,44,0.87001919400169059]
["2013-03-18T18:00:00","2013-03-18T18:00:00",52.765369999999997,52.13353,51.399859999999997,51.469760000000001,51.350999999999999,50.47045,49.909080000000003,49.858780000000003,46.335410000000003,40.102179999999997,38.781480000000002,38.05247,37.7151,37.803600000000003,38.011020000000002,37.373730000000002,37.19482,37.747619999999998,37.474530000000001,37.442160000000001,37.70373,37.142910000000001,37.24295,36.787660000000002,37.17604,36.828769999999999,1581.5940000000001,8786.6170000000002,7205.0230000000001,52.145490000000002,36.729109999999999,33,33,493586.20079999999,471751.58993148437,12602.615470199999,67,54,67728.913293230013,44,11.766813943299145,12.373953943299144,362415.26816311385,11511.852506480676,2142.0608043822804,560.46680438228032,8.6499408265411637E-2,-1581.5940000000001,-4306.8295064806762,-4.5285488517319186E-2,0,0.73497624363381953,0.73497624363381953,10947.01234602658,-3741.9893460265803,-3.9346302263980212E-2,0,40,0.75107420551179016]
["2013-03-18T21:00:00","2013-03-18T21:00:00",52.460389999999997,52.058320000000002,51.685929999999999,51.933160000000001,51.830039999999997,51.164250000000003,50.782420000000002,50.31644,49.874279999999999,49.1708,42.943579999999997,39.658520000000003,38.4161,38.177869999999999,38.360529999999997,37.5214,37.290370000000003,37.837569999999999,37.53284,37.494129999999998,37.780560000000001,37.191920000000003,37.311390000000003,36.860869999999998,37.237749999999998,36.88308,1320.8409999999999,8515.9470000000001,7195.1049999999996,49.806429999999999,36.712519999999998,29,29,433757.57040000003,349789.49599955959,10287.574858854998,58,48,55753.521791384999,44,10.993371093086228,11.600511093086229,297551.77519658289,10143.116487070758,1871.5960321442967,550.75503214429682,7.6014631505967808E-2,-1320.8420000000006,-2948.0114870707584,-3.0997776936788724E-2,0,0.69167635589405374,0.69167635589405374,9612.2526574908334,-2417.1476574908338,-2.541584530412784E-2,0,40,0.70777431777202438]
["2013-03-19T04:00:00","2013-03-19T04:00:00",51.897460000000002,51.527230000000003,51.150660000000002,51.409439999999996,51.557369999999999,51.083570000000002,51.07179,51.239930000000001,51.017989999999998,50.405430000000003,50.117759999999997,49.479660000000003,43.431739999999998,40.076230000000002,39.247700000000002,38.093800000000002,37.727460000000001,38.030110000000001,37.720959999999998,37.64537,37.902569999999997,37.28772,37.457569999999997,37.007840000000002,37.342599999999997,36.966320000000003,472.90859999999998,7667.9740000000002,7195.0649999999996,48.220149999999997,36.68036,25,25,373928.94,262587.48190522834,3530.5322569019995,50,42,44243.404842729986,44,10.235794105137094,10.842934105137093,238833.4815230309,8644.8407203746519,689.84042090688627,216.93182090688629,6.5529854746523966E-2,-472.90900000000056,-1449.7757203746523,-1.5244114409201082E-2,0,0.6514387484763895,0.6514387484763895,8160.7809129391717,-965.71591293917209,-1.0154318117444036E-2,0,39,0.66753671035436013]
["2013-03-19T13:00:00","2013-03-19T13:00:00",51.975059999999999,51.386229999999998,50.952219999999997,51.29177,51.399540000000002,51.041649999999997,50.973399999999998,51.17792,51.007240000000003,50.929499999999997,51.048160000000003,50.286709999999999,49.818899999999999,47.327260000000003,41.562550000000002,39.166440000000001,38.197569999999999,38.282139999999998,37.911499999999997,37.920540000000003,38.170160000000003,37.423639999999999,37.54327,37.061419999999998,37.422800000000002,37.059420000000003,2114.4630000000002,9315.15,7200.6880000000001,50.870069999999998,36.786529999999999,21,21,314100.30960000004,270686.79710449971,15769.284450659996,66,51,65595.143815499992,44,11.511511404108552,12.118651404108549,225624.00407005224,11396.443353578847,2739.7417935983299,625.27879359832968,5.5045077987080138E-2,-2114.4619999999995,-4195.7553535788466,-4.4117565044091873E-2,0,0.62526268941407093,0.62526268941407093,10825.485712587042,-3624.797712587042,-3.8114054652955379E-2,0,39,0.64136065129204156]
["2013-03-19T16:00:00","2013-03-19T16:00:00",51.729300000000002,51.317279999999997,50.963349999999998,51.282919999999997,51.384230000000002,51.025350000000003,50.945889999999999,51.15437,50.986640000000001,50.946370000000002,51.064480000000003,51.115659999999998,51.054630000000003,50.978090000000002,50.575560000000003,48.880319999999998,43.075409999999998,40.146009999999997,38.748010000000001,38.214329999999997,38.413690000000003,37.750419999999998,37.641019999999997,37.193849999999998,37.550820000000002,37.12867,2487.1729999999998,9686.0540000000001,7198.88,50.06465,36.895409999999998,17,17,254271.67920000001,205249.40945793124,18157.146359495004,67,53,63778.984889480009,44,11.571274384731268,12.178414384731269,183596.23578126894,11023.675140508081,3138.3140276154959,651.14102761549611,4.4560301227636302E-2,-2487.174,-3824.7951405080812,-4.0216989355149453E-2,0,0.54740575658717594,0.54740575658717594,10474.103257554307,-3275.2232575543067,-3.4438346119447842E-2,0,38,0.56350371846514657]
["2013-03-19T23:00:00","2013-03-19T23:00:00",51.472070000000002,51.131360000000001,50.79757,51.084670000000003,51.2316,50.837440000000001,50.806539999999998,50.999409999999997,50.829090000000001,50.750109999999999,50.968690000000002,50.937910000000002,50.928130000000003,51.172719999999998,51.533990000000003,50.902270000000001,50.756459999999997,51.11833,50.240369999999999,48.685420000000001,42.755470000000003,39.431399999999996,38.79598,37.740929999999999,37.984850000000002,37.407739999999997,174.3929,7066.81,7197.97,50.046239999999997,36.609200000000001,9,9,134614.4184,106162.63800158017,1226.3596476285004,58,45,47478.50432119998,44,10.52865199735292,11.13579199735292,88440.041985962889,9018.9141654861196,232.95663071337677,58.563730713376771,2.3590747708748628E-2,131.15999999999985,-1820.9441654861193,-1.9146879618224099E-2,0,0.45555417061811093,0.45555417061811093,8527.1895043452805,-1329.2195043452803,-1.3976488855769142E-2,0,38,0.47165213249608151]
["2013-03-20T02:00:00","2013-03-20T02:00:00",51.466569999999997,51.140990000000002,50.795929999999998,51.092739999999999,51.261429999999997,50.810690000000001,50.819049999999997,51.002090000000003,50.831800000000001,50.727359999999997,51.003700000000002,50.935670000000002,50.91771,51.187820000000002,51.538139999999999,50.936660000000003,50.795900000000003,51.189100000000003,50.619050000000001,49.500439999999998,44.913980000000002,39.966459999999998,39.08878,38.004730000000002,38.067810000000001,37.474269999999997,226.49719999999999,6987.0029999999997,7200.7979999999998,49.129620000000003,36.690219999999997,9,9,134614.4184,97904.237277502703,1584.6083857799999,53,44,43457.062559100028,44,10.330673833265312,10.937813833265311,86777.037344094773,8413.2096822505428,306.77735283394156,80.280152833941571,2.3590747708748628E-2,213.79500000000007,-1212.411682250543,-1.2748276947625427E-2,0,0.45717350373743115,0.45717350373743115,7946.2062934246542,-745.4082934246544,-7.8378256352619174E-3,0,38,0.47327146561540173]
["2013-03-20T09:00:00","2013-03-20T09:00:00",51.409300000000002,51.090589999999999,50.748559999999998,50.979990000000001,50.947800000000001,49.6858,47.011220000000002,43.03857,39.379260000000002,37.641590000000001,37.048830000000002,36.212269999999997,36.162599999999998,36.457120000000003,36.842010000000002,36.262900000000002,36.143599999999999,36.649740000000001,36.344589999999997,36.248429999999999,36.600079999999998,36.023110000000003,36.2378,35.803249999999998,36.170789999999997,35.807400000000001,8062.6869999999999,6678.7790000000005,14741.47,50.565519999999999,36.62914,35,35,523500.516,482095.12635585095,{"$f":"500*AC1855*(C1855-AB1855)/1000","v":62896.61815265},54,45,46539.00104001,44,{"$f":"19.5286-0.30357*AP1855+0.0000341*AO1855+0.060847*AN1855","v":10.496614935464342},{"$f":"19.5286-0.30357*42+0.0000341*AO1855+0.060847*AN1855","v":11.103754935464341},{"$f":"62.4*AJ1855*AQ1855/1000","v":342886.96010205871},8867.4303718184819,{"$f":"AL1855*1000/(500*AQ1855)","v":11984.171761916237},3921.4847619162374,9.1741796645133558E-2,8062.6909999999989,5874.0396281815174,0.44312480035930152,0.44312480035930152,1.0199663600117839,1,8382.5699163026075,6358.9000836973919,0.47837954109499436,{"$f":"IF(BF1855>1,1,IF(BF1855<0,0,BF1855))","v":0.47837954109499436},44,1]
["2013-03-20T18:00:00","2013-03-20T18:00:00",51.190170000000002,50.703539999999997,47.032249999999998,41.198099999999997,39.079479999999997,37.209539999999997,36.437089999999998,36.525820000000003,36.289479999999998,36.152270000000001,36.066760000000002,36.110529999999997,36.055419999999998,36.347189999999998,36.731879999999997,36.093220000000002,35.92051,36.505629999999996,36.191389999999998,36.215980000000002,36.556919999999998,35.895479999999999,36.020069999999997,35.573219999999999,35.94238,35.578139999999998,1762,8824.7039999999997,7062.7049999999999,50.04477,35.935250000000003,43,43,643157.77679999999,580589.91672790272,13754.198430000004,63,47,62256.168791039978,44,11.154264355774464,11.761404355774465,447654.59636972181,11162.756557551107,2466.1775965314246,704.17759653142457,0.11271135016402123,-1761.9989999999998,-4100.0515575511072,{"$f":"IF(AZ1863>1,1+AY1864*60/$BK$7,IF(AZ1863<0,AY1864*60/$BK$7,AZ1863+AY1864*60/$BK$7))","v":0.32720524861268818},0.32720524861268818,{"$f":"IF(BB1863>1,1+AX1864*60/$BK$7,BB1863+AX1864*60/$BK$7)","v":0.88790213929580153},0.88790213929580153,10586.519586918928,-3523.8145869189284,0.41549805773835741,0.41549805773835741,44,0.88790213929580153]
["2013-03-20T21:00:00","2013-03-20T21:00:00",51.068620000000003,50.694609999999997,50.130940000000002,45.584359999999997,40.348460000000003,38.272579999999998,36.978029999999997,36.672229999999999,36.374859999999998,36.220950000000002,36.382129999999997,36.227919999999997,36.143210000000003,36.41046,36.792200000000001,36.164009999999998,36.003219999999999,36.53293,36.206530000000001,36.187289999999997,36.535960000000003,35.917349999999999,36.082039999999999,35.641350000000003,35.999560000000002,35.649149999999999,142.3065,7061.6989999999996,7060.6440000000002,50.622549999999997,36.003169999999997,41,41,613243.46160000004,572977.99403029773,1097.1454037775004,55,43,51618.830563309995,44,10.548143122208872,11.155283122208871,403639.37962705345,9787.2829303250055,208.02626416160129,65.71976416160129,0.10746896178429931,-1.0549999999993815,-2726.6389303250053,0.22553999605245106,0.22553999605245106,0.87258855060507756,0.87258855060507756,9254.5980228046228,-2193.9540228046226,0.33130955843029569,0.33130955843029569,44,0.87258855060507756]
["2013-03-21T04:00:00","2013-03-21T04:00:00",50.870190000000001,50.418469999999999,50.003790000000002,47.425660000000001,41.377699999999997,38.646599999999999,37.290309999999998,36.80021,36.494570000000003,36.323250000000002,36.506920000000001,36.341340000000002,36.213549999999998,36.472929999999998,36.849510000000002,36.245420000000003,36.112580000000001,36.612290000000002,36.271979999999999,36.225549999999998,36.56344,35.955120000000001,36.142870000000002,35.703650000000003,36.076630000000002,35.70317,157.2379,6969.1809999999996,7049.2669999999998,48.468800000000002,35.941940000000002,41,41,613243.46160000004,488494.60175598005,1192.415187029,54,42,43650.977350829999,44,10.215592327663304,10.822732327663303,390913.86056178424,8545.9513165233457,233.45003378805561,76.21213378805561,0.10746896178429931,80.08600000000024,-1496.6843165233458,9.2213552658333836E-2,9.2213552658333836E-2,0.86869904925013197,0.86869904925013197,8066.5355160372001,-1017.2685160372002,0.23412698072615956,0.23412698072615956,44,0.86869904925013197]
["2013-03-21T13:00:00","2013-03-21T13:00:00",50.809089999999998,50.263599999999997,49.886330000000001,50.135509999999996,47.603900000000003,41.155729999999998,38.618609999999997,37.519329999999997,36.696280000000002,36.495060000000002,36.561109999999999,36.507480000000001,36.335659999999997,36.5503,36.898260000000001,36.254040000000003,36.090119999999999,36.619300000000003,36.313429999999997,36.346739999999997,36.66883,36.058889999999998,36.180610000000001,35.719749999999998,36.091290000000001,35.740490000000001,1536.665,8594.3359999999993,7057.6710000000003,50.463039999999999,35.942770000000003,39,39,583329.14639999997,535896.97351827426,11577.695109499997,69,57,62396.03959535998,44,11.767503950201775,12.374643950201776,428334.06935466127,10604.804529390463,1967.7401696222037,431.0751696222037,0.10222657340457739,-1536.6649999999991,-3547.1335293904631,-3.7297430621039698E-2,0,0.82681058531655816,0.82681058531655816,10084.498567628296,-3026.8275676282956,5.2990780608090031E-2,5.2990780608090031E-2,42,0.82681058531655816]
["2013-03-21T16:00:00","2013-03-21T16:00:00",51.087530000000001,50.61307,50.064030000000002,50.232309999999998,50.325000000000003,49.694949999999999,44.945740000000001,40.205219999999997,38.210140000000003,36.999360000000003,36.75714,36.705889999999997,36.531350000000003,36.686660000000003,36.999139999999997,36.33455,36.13626,36.687460000000002,36.386279999999999,36.370150000000002,36.674700000000001,36.076810000000002,36.194760000000002,35.731090000000002,36.088720000000002,35.764980000000001,1853.172,8908.143,7054.9709999999995,50.239370000000001,36.010660000000001,37,37,553414.83120000002,499845.34695095319,14197.660314299999,68,59,63375.691692764995,44,11.922604086723288,12.529744086723287,411724.3059145881,10631.18279056814,2381.6374696380562,528.46546963805622,9.6984185024855479E-2,-1853.1720000000005,-3576.2117905681407,-3.7603182975685705E-2,0,0.76763758436882301,0.76763758436882301,10116.039282864343,-3061.0682828643439,-3.2186547520813763E-2,0,41,0.76763758436882301]
["2013-03-21T20:00:00","2013-03-21T20:00:00",51.401699999999998,50.834290000000003,50.312150000000003,50.536209999999997,50.480649999999997,50.012149999999998,49.892069999999997,49.68882,43.760330000000003,39.519309999999997,38.032989999999998,37.178350000000002,36.821080000000002,36.934800000000003,37.178649999999998,36.451270000000001,36.256050000000002,36.792999999999999,36.516249999999999,36.445239999999998,36.74709,36.131500000000003,36.259230000000002,35.800660000000001,36.185859999999998,35.825969999999998,1108.3920000000001,8167.9160000000002,7059.5240000000003,51.883009999999999,36.05406,33,33,493586.20079999999,494553.28226888261,8632.0072630800005,67,59,64644.766984100002,44,11.965879554157812,12.573019554157812,368546.44497011031,10804.850022351717,1442.7702074070462,334.37820740704615,8.6499408265411637E-2,-1108.3919999999998,-3745.3260223517163,-3.93813867773515E-2,0,0.70492754896976717,0.70492754896976717,10283.093366020004,-3223.5693660200041,-3.3895215329517191E-2,0,40,0.70492754896976717]
["2013-03-22T01:00:00","2013-03-22T01:00:00",51.913670000000003,51.444569999999999,50.53331,50.687109999999997,50.747680000000003,50.20496,49.997340000000001,50.133679999999998,49.845840000000003,46.720489999999998,41.019559999999998,38.791449999999998,37.488410000000002,37.265709999999999,37.423470000000002,36.605159999999998,36.340890000000002,36.877360000000003,36.612699999999997,36.634740000000001,36.885849999999998,36.21602,36.339649999999999,35.86148,36.237090000000002,35.900770000000001,1311.569,8372.4629999999997,7060.8950000000004,50.385620000000003,36.002319999999997,29,29,{"$f":"3.1416*(138/2)^2*AI1895","v":433757.57040000003},{"$f":"62.4*AJ1895*(AF1895-AB1895)/1000","v":392053.79264116671},10501.011620050002,66,61,60211.823533950024,44,11.936410182507698,12.543550182507696,323076.5166758913,{"$f":"AO1895*1000/(500*AQ1895)","v":10088.76582042864},1759.4924201647809,447.92342016478096,{"$f":"AJ1895/$BK$7","v":7.6014631505967808E-2},-1311.5679999999993,{"$f":"AE1895-AT1895","v":-3027.8708204286395},-3.183748255279633E-2,0,0.65167035816840779,0.65167035816840779,9600.4436794803059,-2539.5486794803055,-2.6702868639384449E-2,0,38,0.65167035816840779]
["2013-03-22T08:00:00","2013-03-22T08:00:00",51.753390000000003,51.432459999999999,51.052720000000001,51.297409999999999,51.292020000000001,50.478920000000002,50.40446,50.472790000000003,50.094169999999998,49.904760000000003,50.005940000000002,47.409509999999997,42.507150000000003,39.618830000000003,38.568809999999999,37.000999999999998,36.626750000000001,36.966209999999997,36.623289999999997,36.530729999999998,36.859450000000002,36.19491,36.42089,35.992310000000003,36.334449999999997,35.950890000000001,5040.2269999999999,7167.5029999999997,12124.37,49.467840000000002,37.177419999999998,25,25,373928.94,315393.23621725925,39824.09358375,48,45,44045.811110630013,44,10.411597158872485,11.018737158872485,242935.52333383006,8460.9134292321996,7649.9489897787626,2609.7219897787627,6.5529854746523966E-2,4956.8670000000011,3663.4565707678012,3.8520545152661276E-2,3.8520545152661276E-2,0.61681802570755773,0.61681802570755773,7994.7112769022779,4129.6587230977229,4.342257161651774E-2,4.342257161651774E-2,44,0.61681802570755773]
["2013-03-22T17:00:00","2013-03-22T17:00:00",51.488930000000003,50.986840000000001,50.440919999999998,50.652709999999999,50.710569999999997,50.007860000000001,50.002110000000002,49.971130000000002,46.078710000000001,40.783209999999997,38.9846,37.341709999999999,37.048499999999997,37.26549,37.624470000000002,37.027450000000002,36.91263,37.418149999999997,37.092790000000001,36.981859999999998,37.340699999999998,36.715980000000002,36.894480000000001,36.416359999999997,36.53022,36.076509999999999,210.92750000000001,6198.3950000000004,6399.625,49.642530000000001,36.108539999999998,33,33,493586.20079999999,417830.41695887333,1625.4516097750004,48,45,41944.507973025007,44,10.339942721880155,10.947082721880154,318467.94998194405,8113.1025773028787,314.4024398385522,103.47493983855219,8.6499408265411637E-2,201.22999999999956,-1713.4775773028787,-1.8016888998013916E-2,0,0.69147560716567469,0.69147560716567469,7663.1389455365461,-1263.5139455365461,-1.2291914572211717E-2,0,40,0.69147560716567469]
["2013-03-22T20:00:00","2013-03-22T20:00:00",51.447479999999999,50.941589999999998,50.422249999999998,50.625259999999997,50.662269999999999,49.986820000000002,49.986159999999998,49.703969999999998,44.787089999999999,40.229939999999999,38.242280000000001,37.380549999999999,37.260309999999997,37.476460000000003,37.815959999999997,37.20373,37.085830000000001,37.593780000000002,37.273820000000001,37.15249,37.528089999999999,36.908140000000003,37.055689999999998,36.516469999999998,36.752850000000002,36.2575,198.7901,6123.9639999999999,6287.4880000000003,49.520159999999997,36.144849999999998,33,33,493586.20079999999,408486.99602269271,1509.8088215989999,47,46,40954.95846442,44,10.367046083636723,10.974186083636722,319302.72753230401,7900.9889864506413,291.27078425590724,92.480684255907249,8.6499408265411637E-2,163.52400000000034,-1613.500986450641,-1.6965654267169099E-2,0,0.69581876994351599,0.69581876994351599,7463.8716989657587,-1176.3836989657584,-1.2369449594257892E-2,0,39,0.69581876994351599]
["2013-03-23T03:00:00","2013-03-23T03:00:00",51.234110000000001,50.765410000000003,50.334589999999999,50.470649999999999,50.516080000000002,49.930929999999996,49.66028,46.056420000000003,40.753880000000002,37.663339999999998,37.848689999999998,37.692959999999999,37.664740000000002,37.907620000000001,38.267629999999997,37.679929999999999,37.557189999999999,38.068550000000002,37.750030000000002,37.637839999999997,37.99888,37.40269,37.61074,37.09151,37.196210000000001,36.752960000000002,373.96749999999997,5933.7640000000001,6307.7309999999998,48.355539999999998,36.028390000000002,33,33,493586.20079999999,357356.89901671105,2707.7397313124998,47,45,36573.199446299986,44,10.156781101118831,10.76392110111883,312826.61255404941,7201.7303675612784,533.18855734997101,159.22105734997103,8.6499408265411637E-2,373.96699999999964,-893.99936756127863,-9.4002323596202343E-3,0,0.72273855194250969,0.72273855194250969,6795.5160768501855,-487.78507685018576,-5.128966787141114E-3,0,39,0.72273855194250969]
["2013-03-23T12:00:00","2013-03-23T12:00:00",51.095959999999998,50.689279999999997,50.21949,50.324219999999997,50.451709999999999,49.753010000000003,46.767040000000001,41.233789999999999,38.119239999999998,37.876840000000001,38.140749999999997,38.019329999999997,37.974910000000001,38.287610000000001,38.652119999999996,38.055779999999999,37.948410000000003,38.451169999999998,38.131250000000001,38.0503,38.385800000000003,37.745820000000002,37.922780000000003,37.4803,37.799370000000003,37.30048,161.64089999999999,6428.3209999999999,6309.9369999999999,50.03181,36.687840000000001,35,35,523500.516,415887.12824045587,1114.9569015659997,51,49,42889.661287185001,44,10.61556044989301,11.22270044989301,346772.48568444658,8080.5269754019,210.06086429986595,48.419964299865967,9.1741796645133558E-2,-118.38400000000001,-1770.5899754019001,-1.8617414940454401E-2,0,0.74168097987962445,0.74168097987962445,7643.3762940886272,-1333.4392940886273,-1.4020859137824722E-2,0,38,0.74168097987962445]
["2013-03-23T13:00:00","2013-03-23T13:00:00",51.07396,50.681759999999997,50.224179999999997,50.335680000000004,50.452559999999998,49.755809999999997,47.217449999999999,41.636690000000002,38.197180000000003,37.899239999999999,38.151209999999999,38.008690000000001,37.965420000000002,38.282780000000002,38.661819999999999,38.067830000000001,37.952579999999998,38.449910000000003,38.127310000000001,38.035879999999999,38.358849999999997,37.73912,37.941830000000003,37.487229999999997,37.847630000000002,37.252130000000001,212.7148,6502.3620000000001,6302.7079999999996,50.084609999999998,36.787669999999999,35,35,523500.516,419191.33785732387,1470.0539020419999,52,49,43230.758686139998,44,10.627191871197375,11.234331871197375,347152.44271985668,8135.8761957252873,276.65895560354977,63.944155603549774,9.1741796645133558E-2,-199.65400000000045,-1833.1681957252877,-1.927541295816668E-2,0,0.73958165625633454,0.73958165625633454,7696.1868639425174,-1393.4788639425178,-1.4652163731403796E-2,0,38,0.73958165625633454]
["2013-03-23T22:00:00","2013-03-23T22:00:00",50.958289999999998,50.62603,50.254179999999998,50.37865,50.463729999999998,49.867199999999997,48.271259999999998,43.257339999999999,38.40475,38.036929999999998,38.272269999999999,38.09337,38.018140000000002,38.320030000000003,38.689729999999997,38.091230000000003,37.975729999999999,38.478879999999997,38.161990000000003,38.08493,38.433399999999999,37.818370000000002,37.987490000000001,37.54316,37.845779999999998,37.380899999999997,126.2581,6266.0720000000001,6290.741,49.730580000000003,36.430500000000002,35,35,523500.516,403419.98439193674,857.12773217950019,52,49,41669.629442880003,44,10.57395736400221,11.181097364002209,345413.46129995055,7881.5580597552516,162.12051981550263,35.862419815502633,9.1741796645133558E-2,24.668999999999869,-1590.8170597552516,-1.6727137116595573E-2,0,0.7236150348542798,0.7236150348542798,7453.5849364904561,-1162.8439364904561,-1.222708158150515E-2,0,38,0.7236150348542798]
["2013-03-24T01:00:00","2013-03-24T01:00:00",50.882719999999999,50.601590000000002,50.210320000000003,50.33426,50.462560000000003,49.671529999999997,47.047350000000002,40.90607,38.308990000000001,38.092550000000003,38.449399999999997,38.24288,38.21913,38.526730000000001,38.875010000000003,38.27749,38.138710000000003,38.645359999999997,38.296999999999997,38.150709999999997,38.52243,37.894579999999998,38.092559999999999,37.649659999999997,37.945959999999999,37.474119999999999,487.79539999999997,5817.1080000000002,6304.9040000000005,48.493580000000001,36.068150000000003,35,35,523500.516,359966.44295298093,3270.3267002199996,45,42,36140.034128220002,44,9.9594691637723027,10.566609163772302,325340.32417042344,7257.4217629348841,656.72710993791816,168.93170993791819,9.1741796645133558E-2,487.79600000000028,-952.51776293488365,-1.0015542094485687E-2,0,0.73424422367926723,0.73424422367926723,6840.422233487423,-535.51823348742255,-5.6308717995262802E-3,0,38,0.73424422367926723]
["2013-03-24T08:00:00","2013-03-24T08:00:00",50.804510000000001,50.431489999999997,49.939889999999998,50.177289999999999,49.19415,43.500140000000002,38.57376,38.607939999999999,38.301349999999999,38.089979999999997,38.54316,38.317039999999999,38.350850000000001,38.65513,39.01972,38.448239999999998,38.342320000000001,38.861170000000001,38.505940000000002,38.284640000000003,38.713509999999999,38.140210000000003,38.41621,38.027920000000002,38.331989999999998,37.76229,767.55970000000002,5539.5020000000004,6307.0630000000001,47.115319999999997,35.962499999999999,39,39,583329.14639999997,340447.84838398395,5005.3412352670002,39,34,30890.534347819994,44,9.2936852212606631,9.9008252212606624,338287.7139425645,6647.6394696806356,1077.1488631477534,309.58916314775342,0.10222657340457739,767.56099999999969,-340.57646968063546,-3.5810964385248117E-3,0,0.78733737294954331,0.78733737294954331,6239.9918506766116,67.071149323388454,3.6597107470463935E-3,3.6597107470463935E-3,41,0.78733737294954331]
["2013-03-24T17:00:00","2013-03-24T17:00:00",50.727679999999999,50.260150000000003,49.782159999999998,48.273809999999997,40.479930000000003,38.646889999999999,38.606610000000003,38.857590000000002,38.627119999999998,38.498579999999997,38.766359999999999,38.70129,38.65005,38.928570000000001,39.297049999999999,38.699849999999998,38.585090000000001,39.078049999999998,38.78725,38.728729999999999,39.051879999999997,38.437269999999998,38.529339999999998,38.101599999999998,38.473050000000001,38.081069999999997,246.91800000000001,6444.2370000000001,6207.2809999999999,49.12189,36.742809999999999,43,43,{"$f":"3.1416*(138/2)^2*AI1959","v":643157.77679999999},{"$f":"62.4*AJ1959*(AF1959-AB1959)/1000","v":443101.72890353628},1561.3378239900005,53,41,39886.862680980004,44,10.026389017421419,10.63352901742142,402389.52435406588,{"$f":"AO1959*1000/(500*AQ1959)","v":7956.3764405459069},311.44569022348674,64.527690223486729,{"$f":"AJ1959/$BK$7","v":0.11271135016402123},-236.95600000000013,{"$f":"AE1959-AT1959","v":-1749.095440545907},-1.8391404017583764E-2,0,0.81706721655349834,0.81706721655349834,7502.0931650501816,-1294.8121650501816,-1.3614702263981593E-2,0,39,0.81706721655349834]
["2013-03-24T20:00:00","2013-03-24T20:00:00",50.598179999999999,50.228819999999999,49.802819999999997,48.281930000000003,40.510480000000001,38.683810000000001,38.669789999999999,38.891170000000002,38.643419999999999,38.46913,38.805410000000002,38.677759999999999,38.666840000000001,38.967109999999998,39.320320000000002,38.712769999999999,38.596699999999998,39.102580000000003,38.78839,38.66807,38.996490000000001,38.387250000000002,38.598010000000002,38.162370000000003,38.492609999999999,38.070239999999998,108.7914,6191.43,6191.5029999999997,49.142110000000002,36.370080000000002,43,43,643157.77679999999,444347.85995924182,681.46606585799998,46,36,39538.564851450006,44,9.7102770614344465,10.317417061434444,389702.98891331907,8143.6532863685743,140.35975730590135,31.568357305901358,0.11271135016402123,7.2999999999410647E-2,-1952.1502863685746,-2.0526486884238145E-2,0,0.81538339611220301,0.81538339611220301,7664.430858231276,-1472.9278582312763,-1.5487554710582848E-2,0,38,0.81538339611220301]
["2013-03-25T03:00:00","2013-03-25T03:00:00",50.443750000000001,49.965739999999997,47.194119999999998,39.562159999999999,39.348950000000002,38.689250000000001,38.80151,38.993839999999999,38.743609999999997,38.545670000000001,39.034799999999997,38.776260000000001,38.83305,39.116280000000003,39.487380000000002,38.918430000000001,38.82985,39.32629,38.972470000000001,38.715359999999997,39.158389999999997,38.600299999999997,38.88297,38.437739999999998,38.77834,38.346890000000002,852.33439999999996,5330.924,6183.2579999999998,46.797280000000001,35.983379999999997,45,45,673072.09200000006,354913.83255219093,5155.2849549919993,34,29,28824.039521800012,44,8.9189827476933807,9.5261227476933819,374594.5866937181,6463.5262422173555,1156.0253228038264,303.69092280382642,0.11795373854374315,852.33399999999983,-280.26824221735569,-2.9469669615676576E-3,0,0.85762777580666683,0.85762777580666683,6051.5784407206702,131.67955927932962,2.7629808565199478E-3,2.7629808565199478E-3,40,0.85762777580666683]
["2013-03-25T12:00:00","2013-03-25T12:00:00",48.425579999999997,40.004510000000003,38.931150000000002,39.185879999999997,39.389389999999999,38.869399999999999,38.894269999999999,39.140009999999997,38.902639999999998,38.761740000000003,39.112169999999999,38.964739999999999,38.976790000000001,39.251049999999999,39.620510000000003,39.033830000000002,38.946959999999997,39.412779999999998,39.122489999999999,39.004309999999997,39.360889999999998,38.763330000000003,38.982729999999997,38.553789999999999,38.944789999999998,38.543300000000002,2191.0129999999999,5756.4179999999997,4371.5460000000003,48.406210000000002,40.055419999999998,49,49,732900.72239999997,451060.51311148982,10826.101974819994,50,38,24035.318935110012,44,9.3033103756872517,9.9104503756872511,425468.34065128228,5167.0465596681715,2327.3655371344635,136.35253713446355,0.12843851530318698,-1384.8719999999994,-795.50055966817126,-8.3645362339433461E-3,0,0.90751867162095357,0.90751867162095357,4850.4998307795377,-478.95383077953738,3.3039962292498873E-3,3.3039962292498873E-3,41,0.90751867162095357]
["2013-03-25T13:00:00","2013-03-25T13:00:00",48.776000000000003,40.698929999999997,39.016770000000001,39.17942,39.389420000000001,38.878729999999997,38.891739999999999,39.138809999999999,38.905740000000002,38.758459999999999,39.084339999999997,38.972729999999999,38.971229999999998,39.257750000000001,39.634999999999998,39.053040000000003,38.95834,39.419040000000003,39.13767,39.045810000000003,39.387360000000001,38.779519999999998,38.96951,38.563369999999999,38.952219999999997,38.553620000000002,430.61880000000002,6288.3680000000004,6718.9870000000001,49.37782,37.303669999999997,49,49,732900.72239999997,495023.19356268964,2200.9745043720009,51,38,37963.349243600009,44,9.7782562092067611,10.38539620920676,447189.04086729104,7764.8505891787627,450.17730304502822,19.558503045028203,0.12843851530318698,430.61899999999969,-1045.8635891787626,-1.0997055603703077E-2,0,0.91204654804385255,0.91204654804385255,7310.9101432153575,-591.92314321535741,-2.9199624078122682E-3,0,41,0.91204654804385255]
["2013-03-25T20:00:00","2013-03-25T20:00:00",40.098669999999998,39.316560000000003,38.960909999999998,39.216529999999999,39.423549999999999,38.883859999999999,38.913449999999997,39.144080000000002,38.910330000000002,38.762790000000003,39.112780000000001,38.998809999999999,38.990430000000003,39.279159999999997,39.644179999999999,39.089889999999997,38.969589999999997,39.454970000000003,39.122489999999999,39.03304,39.369579999999999,38.775530000000003,38.99288,38.561439999999997,38.229889999999997,37.005299999999998,1397.212,5325.7290000000003,6722.94,50.542160000000003,37.470210000000002,51,51,762815.03760000004,644349.91108088254,2161.0468422200001,45,35,34808.831600775004,44,9.4881461575864279,10.095286157586429,451632.51544030377,7337.3303957681846,455.52562246147392,-941.68637753852613,0.13368090368290891,1397.2109999999993,-614.39039576818504,-6.4601975004687055E-3,0,0.98081097876841883,0.98081097876841883,6896.056448011982,-173.11644801198236,-1.8202863398258564E-3,0,40,1]
["2013-03-26","2013-03-26",39.556060000000002,39.236840000000001,38.902799999999999,39.204900000000002,39.426250000000003,38.837699999999998,38.918370000000003,39.135359999999999,38.901330000000002,38.726709999999997,39.157150000000001,38.972059999999999,38.99156,39.275460000000002,39.631970000000003,39.06662,38.960039999999999,39.465200000000003,39.113419999999998,38.936700000000002,39.304290000000002,38.721150000000002,38.817450000000001,36.786470000000001,37.170439999999999,36.757959999999997,1812.451,4908.8239999999996,6721.2740000000003,48.949219999999997,37.378570000000003,5,5,74785.788,56892.138314723707,2535.7095715500045,39,31,28399.142207799981,44,9.026187749285981,9.6333277492859803,42121.907160297029,6292.6105675225972,561.85615499757205,-1250.594845002428,1.3105970949304794E-2,1812.4500000000007,428.66343247740315,6.6834620947450844E-3,6.6834620947450844E-3,1.0190575650927693,1,5896.0191009601895,825.25489903981088,1.7882238521863852E-2,1.7882238521863852E-2,43,1]
["2013-03-26T07:00:00","2013-03-26T07:00:00",43.735999999999997,39.568390000000001,38.97269,39.253219999999999,39.389389999999999,38.754559999999998,38.904139999999998,39.088830000000002,38.876249999999999,38.654609999999998,39.18918,38.90672,38.964379999999998,39.251089999999998,39.597720000000002,39.043610000000001,38.945959999999999,39.427059999999997,39.063299999999998,38.600070000000002,38.187539999999998,36.963619999999999,37.092559999999999,36.632069999999999,37.033659999999998,36.631929999999997,4744.7370000000001,4744.7370000000001,0,48.3675,36.91713,49,49,732900.72239999997,536702.88240040804,16853.471889795001,34,29,27164.497101344998,44,8.8623923511558651,9.4695323511558644,405303.83439651248,6130.2853732947415,3803.3684860718017,-941.36851392819835,0.12843851530318698,-4744.7370000000001,-6130.2853732947415,-9.2353322100011612E-3,0,0.95010999794445572,0.95010999794445572,5737.2415223924472,-5737.2415223924472,3.0746364973835094E-2,3.0746364973835094E-2,43,0.95010999794445572]
["2013-03-26T16:00:00","2013-03-26T16:00:00",51.187779999999997,50.718020000000003,50.230510000000002,50.43309,50.138460000000002,49.271920000000001,48.862900000000003,48.824280000000002,48.381740000000001,47.083289999999998,45.114510000000003,40.177070000000001,39.434930000000001,39.425930000000001,39.779229999999998,39.212600000000002,39.098770000000002,39.585619999999999,39.270699999999998,39.184310000000004,39.452800000000003,38.868020000000001,39.084859999999999,38.671469999999999,39.067520000000002,38.62238,238.86590000000001,7022.75,6795.5290000000005,51.728189999999998,37.172669999999997,29,29,433757.57040000003,354728.04455237905,1500.7227899299996,58,42,51109.889040000009,44,10.469941216264001,11.077081216264,283384.37488592364,9763.1663796938865,286.67262956525065,47.806729565250635,7.6014631505967808E-2,-227.22099999999955,-2967.637379693886,-3.120413944398559E-2,0,0.62080433585505068,0.62080433585505068,9228.0426661416132,-2432.5136661416127,-2.5577415946119772E-2,0,37,0.62080433585505068]
["2013-03-26T23:00:00","2013-03-26T23:00:00",51.161279999999998,50.74203,50.3018,50.449449999999999,50.182969999999997,49.198270000000001,48.929560000000002,48.879820000000002,48.316580000000002,47.279089999999997,43.534039999999997,40.035040000000002,39.806370000000001,40.038780000000003,40.314430000000002,39.706209999999999,39.583269999999999,40.062390000000001,39.731949999999998,39.628160000000001,39.916899999999998,39.278480000000002,39.369340000000001,38.792999999999999,39.104010000000002,38.640030000000003,715.49879999999996,6087.74,6803.2389999999996,48.892159999999997,36.564480000000003,29,29,433757.57040000003,277488.99361403688,4479.4696747499975,43,35,37523.855321599985,44,9.5807284664665602,10.18786846646656,259316.52254206315,7833.1946162417526,935.10001675312219,219.60121675312223,7.6014631505967808E-2,715.4989999999998,-1029.955616241753,-1.0829786310899925E-2,0,0.63625360763769834,0.63625360763769834,7366.380012680771,-563.14101268077138,-5.9213200394890048E-3,0,37,0.63625360763769834]
["2013-03-27T02:00:00","2013-03-27T02:00:00",51.051839999999999,50.64602,50.136690000000002,50.09055,49.786630000000002,48.884880000000003,48.689300000000003,48.617150000000002,47.51972,40.878239999999998,40.354590000000002,40.032159999999998,39.967460000000003,40.195419999999999,40.535449999999997,39.951709999999999,39.810389999999998,40.297820000000002,39.956940000000003,39.839480000000002,40.211570000000002,39.667200000000001,39.927100000000003,39.422730000000001,39.669960000000003,39.031790000000001,1547.2650000000001,5853.7460000000001,7401.0110000000004,47.850270000000002,36.639589999999998,33,33,493586.20079999999,271607.23449792096,9299.1013316249973,42,34,32812.236603640005,44,9.3592152681841263,9.9663552681841239,288261.76121760305,7011.7495245958216,1987.1540647721863,439.8890647721862,8.6499408265411637E-2,1547.2650000000003,389.26147540417878,4.9673269318885951E-3,4.9673269318885951E-3,0.67670290969963576,0.67670290969963576,6584.6010343194221,816.40996568057835,1.3978135225913034E-2,1.3978135225913034E-2,42,0.67670290969963576]
["2013-03-27T11:00:00","2013-03-27T11:00:00",50.8292,50.126339999999999,49.382460000000002,49.270310000000002,49.131570000000004,48.374180000000003,42.252760000000002,40.518279999999997,40.157080000000001,39.948320000000002,40.144860000000001,40.096409999999999,40.033810000000003,40.308770000000003,40.675440000000002,40.113900000000001,40.006180000000001,40.465739999999997,40.191310000000001,40.207999999999998,40.487229999999997,39.925139999999999,40.028599999999997,39.611800000000002,40.021729999999998,39.607979999999998,1742.7439999999999,8535.4009999999998,6792.6570000000002,57.276969999999999,40.691409999999998,39,39,583329.14639999997,643146.61971768842,9777.8569138400017,62,47,70782.202704779993,44,11.445002112232999,12.052142112232998,416595.08671092446,12369.102602283383,1708.6684332524383,-34.075566747561652,0.10222657340457739,-1742.7439999999997,-5576.4456022833829,-3.6091694531020596E-2,0,0.74587750208335879,0.74587750208335879,11745.995366738272,-4953.3383667382723,1.4096065362222049E-2,1.4096065362222049E-2,42,0.74587750208335879]
["2013-03-27T12:00:00","2013-03-27T12:00:00",51.293089999999999,50.342529999999996,49.64526,49.535319999999999,49.318750000000001,48.623759999999997,47.727379999999997,40.956240000000001,40.296869999999998,40.080280000000002,40.177349999999997,40.132339999999999,40.061570000000003,40.3262,40.702309999999997,40.135509999999996,40.031289999999998,40.514069999999997,40.238489999999999,40.237200000000001,40.492089999999997,39.888219999999997,40.027079999999998,39.620910000000002,40.016959999999997,39.622190000000003,2092.277,8892.8009999999995,6800.5240000000003,54.439770000000003,40.692529999999998,37,37,553414.83120000002,511696.75655233173,12209.377819649997,67,49,61125.734809620022,44,11.237410557008044,11.844550557008043,388062.45919157838,10878.971538776763,2172.9877639890624,80.710763989062343,9.6984185024855479E-2,-2092.2769999999991,-4078.4475387767625,-4.2884095808261233E-2,0,0.72387760960654335,0.72387760960654335,10321.326168590478,-3520.8021685904778,-2.2924496036258735E-2,0,40,0.72387760960654335]
["2013-03-27T21:00:00","2013-03-27T21:00:00",53.87724,53.465249999999997,53.111089999999997,53.430239999999998,53.525649999999999,53.153269999999999,53.08605,53.243819999999999,51.839359999999999,49.944420000000001,49.71069,49.303089999999997,48.95288,48.905889999999999,47.09449,40.894669999999998,40.294429999999998,40.758009999999999,40.420729999999999,40.441490000000002,40.719529999999999,40.05057,40.176740000000002,39.767850000000003,40.163209999999999,39.766269999999999,2148.8890000000001,8946.8829999999998,6797.9939999999997,51.724330000000002,40.71405,21,21,314100.30960000004,234376.29372863955,15161.454106165002,62,51,49253.843478620009,44,10.954273062620944,11.561413062620943,214702.21096971995,8992.6265662826972,2768.1351413267471,619.24614132674697,5.5045077987080138E-2,-2148.8890000000001,-2194.6325662826976,-2.307614167929815E-2,0,0.46617564052200555,0.46617564052200555,8520.3846989710946,-1722.3906989710949,-1.8110608767592004E-2,0,37,0.46617564052200555]
["2013-03-28","2013-03-28",53.674529999999997,53.260269999999998,52.94858,53.241239999999998,53.353000000000002,52.947139999999997,52.929099999999998,53.114750000000001,52.919159999999998,52.799799999999998,51.03537,50.007620000000003,49.572929999999999,49.429310000000001,49.472189999999998,48.537480000000002,42.717140000000001,41.069629999999997,40.572049999999997,40.555019999999999,40.832430000000002,40.115519999999997,40.251629999999999,39.838290000000001,40.225140000000003,39.803899999999999,1087.0640000000001,7891.9560000000001,6804.8919999999998,51.670639999999999,40.783259999999999,19,19,284185.99440000003,210435.34556842237,7539.1312651599992,58,50,42961.361957640001,44,10.678852442755524,11.285992442755525,189370.29075090971,8046.0634113892556,1411.9740497537271,324.91004975372698,4.9802689607358223E-2,-1087.0640000000003,-1241.1714113892558,-1.3050679998805562E-2,0,0.42154443078899539,0.42154443078899539,7613.2182748743344,-808.32627487433456,-8.4993961762329408E-3,0,37,0.42154443078899539]
["2013-03-28T07:00:00","2013-03-28T07:00:00",53.495480000000001,53.145359999999997,52.818109999999997,53.119799999999998,53.275089999999999,52.821480000000001,52.854399999999998,53.041429999999998,52.85754,52.734259999999999,53.03998,52.946249999999999,50.245289999999997,50.119079999999997,50.01708,49.064320000000002,48.621110000000002,47.747250000000001,41.331789999999998,40.704799999999999,40.9587,40.29806,40.454419999999999,39.950809999999997,40.330739999999999,39.851939999999999,502.1542,7307.4290000000001,6809.268,52.25394,40.816049999999997,15,15,224357.364,173626.75376766719,3425.5804569340003,53,49,41790.78454240501,44,10.578088752896011,11.185228752896011,148092.17958648648,7901.3866339443884,647.67474294374085,145.52054294374085,3.9317912847914381E-2,-498.16100000000006,-1092.1186339443884,-1.1483418552468492E-2,0,0.38740952372817278,0.38740952372817278,7472.4952820629251,-663.22728206292504,-6.9737080190982849E-3,0,38,0.38740952372817278]
["2013-03-28T16:00:00","2013-03-28T16:00:00",53.514629999999997,53.107909999999997,52.780720000000002,53.101869999999998,53.195270000000001,52.843029999999999,52.787280000000003,52.956919999999997,51.678840000000001,50.032409999999999,49.590809999999998,49.194159999999997,48.798999999999999,48.16066,44.32544,39.631689999999999,39.264000000000003,39.810510000000001,39.548900000000003,39.609290000000001,39.918030000000002,39.341090000000001,39.452689999999997,39.034480000000002,39.448030000000003,39.072319999999998,6043.277,8745.6730000000007,14788.95,53.877540000000003,38.903179999999999,21,21,314100.30960000004,290180.22918743751,43639.439924934995,70,61,65480.427972140023,44,12.116069593849977,12.723209593849976,237473.25953915765,10808.85636467083,7203.5637608232355,1160.2867608232355,5.5045077987080138E-2,6043.277,3980.0936353291709,0.15920567769310212,0.15920567769310212,0.57955857909062958,0.57955857909062958,10293.067561158676,4495.882438841325,0.18119819010959712,0.18119819010959712,44,0.57955857909062958]
["2013-03-28T23:00:00","2013-03-28T23:00:00",49.453719999999997,47.952210000000001,43.034149999999997,39.94473,39.739040000000003,39.28642,39.205800000000004,39.41263,39.212589999999999,39.140839999999997,39.282530000000001,39.319710000000001,39.266849999999998,39.518169999999998,39.89087,39.264530000000001,39.104419999999998,39.645809999999997,39.35087,39.3842,39.686860000000003,39.106119999999997,39.229950000000002,38.81438,39.221499999999999,38.853020000000001,6659.2560000000003,8111.7190000000001,14770.98,52.806229999999999,38.910589999999999,45,45,673072.09200000006,586030.61367647606,35296.387539599986,67,60,56358.763502580005,44,11.744173835437978,12.351313835437978,493251.76069914602,9597.7400015176463,6010.876207076114,-648.37979292388627,0.11795373854374315,6659.2609999999995,5173.2399984823533,0.47725112587236296,0.47725112587236296,1.0412402144087369,1,9125.9544131859584,5645.0255868140412,0.53633395811790563,0.53633395811790563,44,1]
["2013-03-29T02:00:00","2013-03-29T02:00:00",40.454059999999998,39.857990000000001,39.396299999999997,39.569940000000003,39.703749999999999,39.278379999999999,39.233849999999997,39.443930000000002,39.242730000000002,39.159210000000002,39.315530000000003,39.317320000000002,39.280180000000001,39.542169999999999,39.91366,39.276710000000001,39.129159999999999,39.665909999999997,39.38317,39.424860000000002,39.733919999999998,39.030990000000003,39.084099999999999,38.668900000000001,39.065510000000003,38.688229999999997,456.57819999999998,7861.5309999999999,7404.9530000000004,52.150309999999998,39.110579999999999,51,51,762815.03760000004,640790.4086297506,403.11974145300024,64,59,51256.120813314999,44,11.509326719734043,12.116466719734042,547840.01965459157,8906.8843141676698,70.050968448363847,-386.52723155163613,0.13368090368290891,-456.57799999999952,-1501.9313141676694,0.51250674766669735,{"$f":"IF(AZ2064>1,1,IF(AZ2064<0,0,AZ2064))","v":0.51250674766669735},0.99519916965713462,{"$f":"IF(BB2064>1,1,BB2064)","v":0.99519916965713462},8460.57221117677,-1055.6192111767696,0.58577489612858746,0.58577489612858746,44,1]
["2013-03-29T12:00:00","2013-03-29T12:00:00",53.122799999999998,51.619439999999997,48.049259999999997,40.502110000000002,40.109569999999998,39.590470000000003,39.457210000000003,39.654539999999997,39.441479999999999,39.34686,39.44941,39.503270000000001,39.429600000000001,39.662080000000003,39.995399999999997,39.358879999999999,39.207340000000002,39.759929999999997,39.509480000000003,39.671790000000001,40.207270000000001,39.687899999999999,39.591209999999997,38.985469999999999,39.295560000000002,38.908160000000002,1786.394,9183.7710000000006,7397.3779999999997,53.687420000000003,39.151339999999998,45,45,673072.09200000006,620724.46465610398,12696.473804079997,71,62,66748.01497884003,44,12.220141310778446,12.827281310778444,513242.25117867137,10924.262376567895,2077.9585900338834,291.56459003388341,0.11795373854374315,-1786.3930000000009,-3526.8843765678948,0.29324997836052691,0.29324997836052691,0.92765038751491291,0.92765038751491291,10407.195938355751,-3009.8179383557517,0.4119655452414962,0.4119655452414962,44,0.92765038751491291]
["2013-03-29T15:00:00","2013-03-29T15:00:00",54.330100000000002,53.463050000000003,52.442210000000003,51.476970000000001,47.323279999999997,40.097169999999998,39.648960000000002,39.815730000000002,39.608350000000002,39.513199999999998,39.524979999999999,39.64734,39.614379999999997,39.861579999999996,40.229770000000002,39.631,39.49633,40.028880000000001,39.785060000000001,39.90025,40.132460000000002,39.624600000000001,39.657730000000001,39.142780000000002,39.341299999999997,38.931780000000003,2292.79,9696.6350000000002,7403.8450000000003,54.864469999999997,39.19314,41,41,613243.46160000004,609686.56121566123,17652.557056399997,74,62,75979.583487274984,44,12.534937796916077,13.142077796916077,479666.8434805412,12122.849705080778,2816.536841649583,523.74684164958308,0.10746896178429931,-2292.79,-4719.004705080778,0.15752281624355988,0.15752281624355988,0.86283631785825365,0.86283631785825365,11562.796182062531,-4158.9511820625312,0.29340567492446318,0.29340567492446318,44,0.86283631785825365]
["2013-03-29T21:00:00","2013-03-29T21:00:00",55.644649999999999,55.20035,54.84693,55.124969999999998,54.491320000000002,53.236809999999998,52.81635,52.062980000000003,49.355899999999998,40.925060000000002,40.103949999999998,39.987749999999998,39.854979999999998,39.959350000000001,40.24485,39.605449999999998,39.459859999999999,40.007869999999997,39.733960000000003,39.768689999999999,39.97777,39.427770000000002,39.550440000000002,39.068280000000001,39.465000000000003,39.144390000000001,1956.635,9350.3670000000002,7393.732,54.282820000000001,39.285600000000002,33,33,493586.20079999999,466260.29734606878,16142.493112549997,70,62,70114.755489870004,44,12.334947162204568,12.942087162204567,379913.6457081447,11368.472773796417,2617.3591017904168,660.72410179041685,8.6499408265411637E-2,-1956.6350000000002,-3974.7407737964168,-4.1793639009909019E-2,0,0.72195790099755541,0.72195790099755541,10835.154270113351,-3441.4222701133513,4.3156179723554532E-2,4.3156179723554532E-2,42,0.72195790099755541]
["2013-03-30","2013-03-30",55.333660000000002,54.860100000000003,54.49577,54.784370000000003,54.85913,54.462229999999998,54.256929999999997,53.379060000000003,52.646349999999998,51.50356,48.460509999999999,40.713230000000003,40.151580000000003,40.234630000000003,40.361379999999997,39.726059999999997,39.529859999999999,40.084449999999997,39.806510000000003,39.822389999999999,40.04515,39.502670000000002,39.590679999999999,39.111829999999998,39.46922,39.130310000000001,1789.356,9195.1589999999997,7405.8029999999999,52.471020000000003,39.197830000000003,29,29,433757.57040000003,361085.95891748549,14496.7807713,68,61,61024.546243604993,44,11.964124026906932,12.571264026906931,323826.63268022588,10201.256039533317,2423.3752071939753,634.01920719397526,7.6014631505967808E-2,-1789.3559999999998,-2795.4530395333168,-2.9393654039938259E-2,0,0.66502520622863659,0.66502520622863659,9708.5776120827595,-2302.7746120827596,-2.4213234607158192E-2,0,41,0.66502520622863659]
["2013-03-30T07:00:00","2013-03-30T07:00:00",54.529000000000003,54.161990000000003,53.8247,54.083730000000003,54.227359999999997,53.77966,53.794280000000001,53.975819999999999,53.795009999999998,53.682810000000003,53.930840000000003,53.21266,51.659329999999997,48.671500000000002,41.636969999999998,40.382379999999998,39.890799999999999,40.334820000000001,40.02599,40.005400000000002,40.185409999999997,39.620429999999999,39.778359999999999,39.338740000000001,39.686619999999998,39.287619999999997,1187.3340000000001,8580.5079999999998,7393.174,51.73959,39.268729999999998,23,23,344014.62479999999,267300.3707444215,9048.3043404600048,56,55,53503.156998440005,44,11.342562653646805,11.949702653646805,243485.26397924341,9434.0509516582551,1595.460323518837,408.1263235188369,6.0287466366802052E-2,-1187.3339999999998,-2040.8769516582552,-2.1459430799503364E-2,0,0.57818802739747366,0.57818802739747366,8954.7260796672526,-1561.5520796672527,-1.6419421448320232E-2,0,40,0.57818802739747366]
["2013-03-30T16:00:00","2013-03-30T16:00:00",56.078699999999998,55.638280000000002,55.139780000000002,54.873390000000001,54.388550000000002,53.769010000000002,53.609540000000003,53.845050000000001,53.687719999999999,53.644019999999998,53.708179999999999,53.82658,53.768470000000001,53.994230000000002,54.292729999999999,53.692909999999998,53.587420000000002,54.021700000000003,53.603499999999997,52.374830000000003,50.01435,42.341070000000002,40.692970000000003,39.687060000000002,40.003779999999999,39.688740000000003,3846.5619999999999,10839.92,9213.6579999999994,55.079410000000003,40.850859999999997,9,9,134614.4184,129280.70006818687,31522.498658759989,76,66,77118.171858000031,44,12.817151660357801,13.424291660357802,107663.30117734836,12033.589661971309,4918.7993548139093,1072.2373548139094,2.3590747708748628E-2,-1626.2620000000006,-2819.9316619713099,-2.9651042072983795E-2,0,0.34191411343147665,0.34191411343147665,11489.346895781697,-2275.6888957816973,-2.3928433480786826E-2,0,37,0.34191411343147665]
["2013-03-30T23:00:00","2013-03-30T23:00:00",54.350920000000002,53.923690000000001,53.605600000000003,53.936750000000004,54.022550000000003,53.660089999999997,53.579459999999997,53.807130000000001,53.637430000000002,53.512700000000002,53.389670000000002,52.41948,50.138660000000002,45.111229999999999,41.845410000000001,40.480460000000001,39.40701,39.199539999999999,38.633760000000002,38.68618,38.955019999999998,38.388100000000001,38.533099999999997,38.115299999999998,38.521700000000003,38.209769999999999,5433.951,8967.0820000000003,14401.03,52.916220000000003,37.530110000000001,23,23,344014.62479999999,315696.19404273352,43855.109091825012,65,61,68984.255015510003,44,12.235550096028893,12.842690096028893,262654.59015163576,11276.036545001631,7168.4736276889416,1734.5226276889416,6.0287466366802052E-2,5433.9480000000003,3124.99345499837,0.15676888592339189,0.15676888592339189,0.67320967047817959,0.67320967047817959,10742.96031434111,3658.0696856588911,0.19821508591594345,0.19821508591594345,44,0.67320967047817959]
["2013-03-31T02:00:00","2013-03-31T02:00:00",54.316499999999998,53.891750000000002,53.576030000000003,53.907910000000001,53.94314,53.367379999999997,52.505629999999996,50.755000000000003,45.758850000000002,41.49897,40.563839999999999,39.821429999999999,38.920299999999997,38.926490000000001,39.063409999999998,38.396709999999999,38.267710000000001,38.840690000000002,38.556420000000003,38.624569999999999,38.886899999999997,38.319070000000004,38.449019999999997,38.016370000000002,38.42801,38.119230000000002,5860.1239999999998,8523.3240000000005,14383.45,51.949179999999998,37.586300000000001,33,33,493586.20079999999,425959.40261184698,47459.005330739987,65,61,61209.739906559989,44,11.970439130813697,12.577579130813696,368686.87892312557,10226.816115541991,7929.367471335856,2069.2434713358562,8.6499408265411637E-2,5860.1260000000002,4156.6338844580096,0.27826729051125298,0.27826729051125298,0.85458788151236342,0.85458788151236342,9733.1512320368238,4650.2987679631769,{"$f":"IF(BF2110>1,1+BE2111*60/$BK$7,IF(BF2110<0,BE2111*60/$BK$7,BF2110+BE2111*60/$BK$7))","v":0.3356240246961823},0.3356240246961823,44,0.85458788151236342]
["2013-03-31T11:00:00","2013-03-31T11:00:00",44.81906,41.215110000000003,40.216160000000002,39.733919999999998,39.068109999999997,38.524009999999997,38.430480000000003,38.675190000000001,38.445740000000001,38.311259999999997,38.462739999999997,38.456969999999998,38.447789999999998,38.700470000000003,39.077759999999998,38.477409999999999,38.359259999999999,38.896389999999997,38.620570000000001,38.673360000000002,38.949599999999997,38.293170000000003,38.389510000000001,37.939810000000001,38.339750000000002,38.030650000000001,1398.057,8592.6579999999994,7194.6019999999999,53.133989999999997,37.545760000000001,49,49,732900.72239999997,690721.12491113541,4745.292059684999,68,61,66972.164607669984,44,12.166937813121548,12.774077813121547,556430.62878827786,11008.877605249734,780.03062604090815,-618.02637395909187,0.12843851530318698,-1398.0559999999996,-3814.2756052497343,{"$f":"IF(AZ2119>1,1+AY2120*60/$BK$7,IF(AZ2119<0,AY2120*60/$BK$7,AZ2119+AY2120*60/$BK$7))","v":0.35113027706045258},0.35113027706045258,{"$f":"IF(BB2119>1,1+AX2120*60/$BK$7,BB2119+AX2120*60/$BK$7)","v":0.95665553998600428},0.95665553998600428,10485.635924164499,-3291.0339241644988,0.45681733038418226,0.45681733038418226,44,0.9852997085583951]
["2013-03-31T12:00:00","2013-03-31T12:00:00",49.607619999999997,41.599600000000002,40.496029999999998,39.953119999999998,39.427500000000002,38.695929999999997,38.413110000000003,38.626330000000003,38.434089999999998,38.364849999999997,38.514600000000002,38.506740000000001,38.461880000000001,38.711799999999997,39.086770000000001,38.470579999999998,38.333849999999998,38.87529,38.550980000000003,38.598109999999998,38.882480000000001,38.289200000000001,38.42333,37.990879999999997,38.35772,38.045299999999997,2577.5,8805.6010000000006,6228.1,53.293559999999999,38.802410000000002,49,49,732900.72239999997,697348.75200700469,14900.939900000001,67,61,63801.642465574987,44,12.058823008076109,12.665963008076108,551486.2138601538,10581.736281035945,2471.3755048930479,-106.12449510695205,0.12843851530318698,-2577.5010000000002,-4353.6362810359442,0.30535262426115617,0.30535262426115617,0.92955360995528447,0.92955360995528447,10074.503205937614,-3846.4032059376132,0.41637313635389578,0.41637313635389578,44,0.95819777852767529]
["2013-03-31T21:00:00","2013-03-31T21:00:00",54.580680000000001,54.191789999999997,53.857439999999997,54.179699999999997,53.898829999999997,52.524790000000003,49.568959999999997,42.191380000000002,40.62717,39.8489,39.323090000000001,39.10172,38.845309999999998,38.970979999999997,39.303370000000001,38.63505,38.478400000000001,39.028210000000001,38.743720000000003,38.786169999999998,38.97052,38.388109999999998,38.5379,38.081330000000001,38.470390000000002,38.141159999999999,1680.0540000000001,8479.598,6799.5439999999999,52.779380000000003,37.38205,37,37,553414.83120000002,505502.90234299231,13809.640667040001,63,56,65281.584336670021,44,11.805054025880448,12.412194025880449,407664.93961686536,11059.938259249291,2339.6149880830462,659.56098808304614,9.6984185024855479E-2,-1680.0540000000001,-4260.3942592492913,-4.4797230774092638E-2,0,0.70947479367035704,0.70947479367035704,10518.943580893518,-3719.3995808935179,-1.2634956002890226E-2,0,41,0.73811896224274787]
["2013-04-01T04:00:00","2013-04-01T04:00:00",53.97475,53.579700000000003,53.232529999999997,53.550669999999997,53.625720000000001,53.210090000000001,53.155679999999997,53.283540000000002,50.048470000000002,42.104120000000002,40.880180000000003,40.179819999999999,39.438380000000002,39.390689999999999,39.574689999999997,38.853659999999998,38.628700000000002,39.157060000000001,38.842199999999998,38.85566,39.072890000000001,38.472160000000002,38.631480000000003,38.168340000000001,38.548119999999997,38.211640000000003,744.29390000000001,7540.5429999999997,6796.2489999999998,50.569850000000002,37.152290000000001,33,33,493586.20079999999,380630.13596952666,5866.1933090144994,53,50,50587.844067540005,44,10.938915482703116,11.546055482703114,336916.17860033514,9249.1516453401164,1072.536545014955,328.24264501495497,8.6499408265411637E-2,-744.29399999999987,-2452.9026453401166,-2.579180216270539E-2,0,0.63665192015889083,0.63665192015889083,8762.7924780587655,-1966.5434780587657,-2.0677828541954782E-2,0,39,0.66529608873128165]
["2013-04-01T07:00:00","2013-04-01T07:00:00",53.756740000000001,53.300069999999998,52.947940000000003,53.243229999999997,53.319809999999997,52.877670000000002,52.861550000000001,53.060220000000001,52.82206,51.03537,42.909840000000003,40.953380000000003,40.237580000000001,39.78105,39.780180000000001,39.063600000000001,38.791780000000003,39.219970000000004,38.904829999999997,38.89564,39.12368,38.504570000000001,38.685650000000003,38.232990000000001,38.597560000000001,38.238210000000002,1414.97,8211.3619999999992,6796.393,50.251660000000001,37.26623,31,31,463671.88560000004,347586.65847742633,10979.12719705,52,50,53314.033227829997,44,11.031878533069005,11.639018533069002,319186.72787902789,9665.4496454101809,1990.4365632995546,575.46656329955454,8.125701988568973E-2,-1414.9689999999991,-2869.0566454101809,-3.0167581877981173E-2,0,0.59266178779967915,0.59266178779967915,9161.2592722235386,-2364.8662722235385,-2.4866116537612001E-2,0,39,0.62130595637206998]
["2013-04-01T16:00:00","2013-04-01T16:00:00",54.513890000000004,53.466459999999998,52.698039999999999,53.047780000000003,53.060839999999999,52.77993,52.636150000000001,52.895499999999998,52.75121,52.695599999999999,52.740549999999999,52.878450000000001,52.831339999999997,53.010330000000003,53.169980000000002,47.597999999999999,41.594929999999998,41.028950000000002,40.05057,39.602580000000003,39.735379999999999,39.097380000000001,38.934199999999997,38.426990000000004,38.794310000000003,38.459530000000001,2736.3229999999999,10079.31,7342.9889999999996,54.179340000000003,38.387639999999998,19,19,284185.99440000003,278762.62980565365,21964.957259140003,79,60,79584.719863500024,44,12.536178947345352,13.143318947345351,222306.6443599675,12696.80661033525,3504.2507531836532,767.92775318365329,4.9802689607358223E-2,-2736.3209999999999,-5353.8176103352507,-5.6294368177758757E-2,0,0.37946314734430958,0.37946314734430958,12110.292717133569,-4767.3037171335691,-5.0127286769993229E-2,0,37,0.40810731591670041]
["2013-04-01T23:00:00","2013-04-01T23:00:00",53.411029999999997,53.009900000000002,52.664450000000002,53.010800000000003,53.064579999999999,52.741109999999999,52.654330000000002,52.878900000000002,52.696109999999997,52.514679999999998,49.965290000000003,43.70476,41.142499999999998,40.647649999999999,40.442070000000001,39.310299999999998,38.855159999999998,38.938609999999997,38.609769999999997,38.680050000000001,38.955779999999997,38.396650000000001,38.529580000000003,38.08305,38.504899999999999,38.194890000000001,5344.1880000000001,8999.1620000000003,14343.35,50.968629999999997,36.333390000000001,27,27,403843.25520000001,321895.93754313508,40658.956397159985,66,58,65852.447834439983,44,11.946214471154404,12.553354471154403,301042.44389533653,11024.822632047797,6807.0025856870407,1462.8145856870406,7.0772243126245887E-2,5344.1880000000001,3318.5273679522033,0.12309422424210484,0.12309422424210484,0.60262396973252619,0.60262396973252619,10491.609710497438,3851.7402895025625,0.15309362011029015,0.15309362011029015,44,0.63126813830491701]
["2013-04-02T02:00:00","2013-04-02T02:00:00",53.373159999999999,52.96405,52.614170000000001,52.95664,52.79325,49.201970000000003,43.602539999999998,41.224620000000002,40.193150000000003,39.65213,39.493470000000002,38.784689999999998,38.469850000000001,38.684939999999997,39.033659999999998,38.423690000000001,38.298580000000001,38.85136,38.585290000000001,38.640270000000001,38.926949999999998,38.377429999999997,38.514209999999999,38.060569999999998,38.486150000000002,38.16348,6269.5240000000003,8054.6670000000004,14324.19,50.355800000000002,36.16142,37,37,553414.83120000002,421038.42859955045,47678.726896159998,67,60,57165.502085730011,44,11.771683621123394,12.378823621123393,406512.55657732562,9712.3748693263988,8100.5790557612572,1831.0550557612569,9.6984185024855479E-2,6269.5230000000001,4611.8151306736017,0.25971372815789562,0.25971372815789562,0.79670220859812269,0.79670220859812269,9236.0152847128411,5088.1747152871594,0.30518203267866401,0.30518203267866401,44,0.82534637717051351]
["2013-04-02T11:00:00","2013-04-02T11:00:00",49.386560000000003,40.639679999999998,39.222990000000003,39.030729999999998,38.918460000000003,38.485230000000001,38.362290000000002,38.601730000000003,38.374589999999998,38.279580000000003,38.431640000000002,38.470649999999999,38.441299999999998,38.686439999999997,39.04871,38.434370000000001,38.288690000000003,38.816569999999999,38.508969999999998,38.560760000000002,38.853520000000003,38.305320000000002,38.412939999999999,37.959910000000001,38.386369999999999,38.090620000000001,2586.433,9992.9060000000009,7406.473,53.858550000000001,38.814320000000002,49,49,732900.72239999997,721114.82275576412,14608.095991010003,68,64,75167.78811619,44,12.628949574762078,13.236089574762079,577559.81502936909,11904.044381712738,2313.4300924287618,-273.00290757123821,0.12843851530318698,-2586.4330000000009,-4497.571381712738,0.35079876625196987,0.35079876625196987,0.91508079588586477,0.91508079588586477,11358.005352202545,-3951.5323522025446,0.44485287815581742,0.44485287815581742,44,0.93885210767555161]
["2013-04-02T15:00:00","2013-04-02T15:00:00",54.419409999999999,53.667990000000003,51.671199999999999,46.01464,40.083399999999997,39.114919999999998,38.711979999999997,38.823500000000003,38.590029999999999,38.425539999999998,38.62238,38.566040000000001,38.531199999999998,38.781860000000002,39.159590000000001,38.529609999999998,38.392569999999999,38.941789999999997,38.605510000000002,38.60866,38.913820000000001,38.346209999999999,38.476170000000003,38.02449,38.420859999999998,38.116160000000001,1757.3589999999999,9148.6610000000001,7391.3010000000004,53.56635,38.754350000000002,43,43,643157.77679999999,620063.17473594565,14325.331558374999,63,60,67754.983365999986,44,12.1327849327806,12.7399249327806,486925.6069866058,11168.908662171736,2361.4251200761887,604.06612007618878,0.11271135016402123,-1757.3599999999997,-3777.6076621717357,0.18358744863163229,0.18358744863163229,0.83330297499994854,0.83330297499994854,10636.637770394125,-3245.3367703941249,0.30021159631667371,0.30021159631667371,44,0.85707428678963538]
["2013-04-02T20:00:00","2013-04-02T20:00:00",54.455329999999996,54.077910000000003,53.761519999999997,53.940910000000002,53.464919999999999,50.658459999999998,42.647129999999997,39.688769999999998,39.056370000000001,38.763770000000001,38.877809999999997,38.76294,38.679000000000002,38.880769999999998,39.249079999999999,38.596359999999997,38.461039999999997,39.018160000000002,38.666899999999998,38.674619999999997,38.980699999999999,38.394939999999998,38.531790000000001,38.083930000000002,38.485239999999997,38.173789999999997,943.96609999999998,8346.4159999999993,7402.45,52.946599999999997,38.784880000000001,37,37,553414.83120000002,510150.71031597955,7684.6109078969994,60,54,59099.803197759968,44,11.472561289043616,12.079701289043616,396182.93951856217,10302.808886137873,1339.6504432250645,395.68434322506448,9.6984185024855479E-2,-943.96599999999944,-2900.358886137873,-9.0620389387000289E-3,0,0.7460839403747449,0.7460839403747449,9784.9775890342517,-2382.5275890342518,0.13552243882934764,0.13552243882934764,43,0.76985525216443174]
["2013-04-03T03:00:00","2013-04-03T03:00:00",54.351149999999997,54.011670000000002,53.660240000000002,53.911540000000002,52.894120000000001,48.666409999999999,40.19679,39.324730000000002,38.9696,38.803649999999998,39.155659999999997,39.011539999999997,38.973509999999997,39.240369999999999,39.611339999999998,39.021799999999999,38.912399999999998,39.408059999999999,39.0886,39.007510000000003,39.328899999999997,38.755360000000003,38.911839999999998,38.374980000000001,38.629179999999998,38.244799999999998,789.93939999999998,6606.3620000000001,7396.3010000000004,50.21114,38.524270000000001,39,39,583329.14639999997,435571.64961848786,6361.5202275949996,50,49,38603.846933469998,44,10.469414180431329,11.076554180431327,381083.94087997347,7374.5954201765198,1215.2581067019953,425.31870670199532,0.10222657340457739,789.93900000000031,21.705579823480548,{"$f":"IF(AZ2183>1,1+AY2184*60/$BK$7,IF(AZ2183<0,AY2184*60/$BK$7,AZ2183+AY2184*60/$BK$7))","v":2.2823002033837151E-4},2.2823002033837151E-4,{"$f":"IF(BB2183>1,1+AX2184*60/$BK$7,BB2183+AX2184*60/$BK$7)","v":0.77908501457999457},0.77908501457999457,6970.3711650091418,425.92983499085858,0.11096791100623274,0.11096791100623274,43,0.80285632636968141]
["2013-04-03T06:00:00","2013-04-03T06:00:00",54.326770000000003,53.98845,53.627870000000001,53.575530000000001,51.515990000000002,43.729509999999998,39.166809999999998,39.324100000000001,39.099699999999999,38.932960000000001,39.28895,39.145710000000001,39.103949999999998,39.382530000000003,39.743679999999998,39.165979999999998,39.073099999999997,39.583829999999999,39.239370000000001,39.140860000000004,39.479179999999999,38.908180000000002,39.083359999999999,38.57347,38.806669999999997,38.398249999999997,703.04679999999996,6697.625,7400.6719999999996,50.636090000000003,38.483699999999999,39,39,583329.14639999997,445454.17868513818,5599.2475073680016,50,48,40696.075536875018,44,10.479912175807439,11.08705217580744,381466.06516890891,7766.49171370361,1068.5676393918063,365.52083939180636,0.10222657340457739,703.04699999999957,-365.81971370361043,-3.8465243212915121E-3,0,0.80207252098210646,0.80207252098210646,7341.1895049391223,59.482495060877227,0.11685270454540812,0.11685270454540812,43,0.8258438327717933]
["2013-04-03T15:00:00","2013-04-03T15:00:00",54.272440000000003,53.753880000000002,51.81212,46.56494,40.027500000000003,39.479660000000003,39.486490000000003,39.736989999999999,39.517110000000002,39.34937,39.727290000000004,39.592210000000001,39.570279999999997,39.82103,40.180549999999997,39.585900000000002,39.502940000000002,40.016579999999998,39.681930000000001,39.591920000000002,39.904089999999997,39.338230000000003,39.450589999999998,38.998109999999997,39.383850000000002,38.976939999999999,699.95749999999998,6695.9769999999999,7395.9340000000002,50.429279999999999,38.474760000000003,43,43,643157.77679999999,459617.27969400125,5353.0999706250013,49,46,40023.595483019984,44,10.335286605970982,10.942426605970981,414786.52525983594,7745.0383349596223,1035.8880551086734,335.93055510867339,0.11271135016402123,699.95700000000033,-349.10433495962207,-3.6707653108559958E-3,0,0.87708711174122178,0.87708711174122178,7315.3052653202558,80.628734679744412,0.12757663499161415,0.12757663499161415,43,0.90085842353090861]
["2013-04-03T22:00:00","2013-04-03T22:00:00",53.308489999999999,50.085290000000001,39.933199999999999,40.04289,40.233620000000002,39.669899999999998,39.732660000000003,39.977200000000003,39.753520000000002,39.576909999999998,40.013260000000002,39.80762,39.815779999999997,40.09722,40.46349,39.892229999999998,39.802239999999998,40.298389999999998,39.956960000000002,39.783439999999999,40.157780000000002,39.587150000000001,39.757719999999999,39.335140000000003,39.71913,39.308439999999997,1141.7460000000001,6252.7780000000002,7394.5240000000003,49.754350000000002,38.498469999999998,47,47,702986.40720000002,458223.96302807628,7992.2505436500014,44,42,35190.259417320012,44,9.9270818461306138,10.534221846130613,435464.8647018823,7089.7490244903147,1610.191326621373,468.44532662137294,0.12319612692346506,1141.7460000000001,304.77497550968565,4.5091939506623196E-3,4.5091939506623196E-3,0.94498390250816444,0.94498390250816444,6681.1312560777242,713.39274392227617,0.15195773310143529,0.15195773310143529,43,0.96875521429785127]
["2013-04-04T01:00:00","2013-04-04T01:00:00",50.908070000000002,40.549059999999997,39.821980000000003,40.101880000000001,40.272919999999999,39.717019999999998,39.791849999999997,40.023060000000001,39.804160000000003,39.611420000000003,40.072000000000003,39.869349999999997,39.888660000000002,40.174430000000001,40.53801,39.972149999999999,39.890050000000002,40.392769999999999,40.046390000000002,39.876350000000002,40.247489999999999,39.729190000000003,39.927289999999999,39.462879999999998,39.8337,39.401679999999999,1150.327,6249.7449999999999,7400.0720000000001,48.697589999999998,38.49933,49,49,732900.72239999997,425129.89923239988,6618.0555447650022,43,42,31868.262221849993,44,9.8138017417650865,10.420941741765084,448814.64488827257,6494.5804002187324,1348.7241170972943,198.39711709729431,0.12843851530318698,1150.3270000000002,905.49159978126772,2.7836056457882598E-2,2.7836056457882598E-2,0.98004214646848309,0.98004214646848309,6116.1962155739284,1283.8757844260717,0.18745875619451591,0.18745875619451591,44,1]
["2013-04-04T08:00:00","2013-04-04T08:00:00",50.509250000000002,50.294339999999998,49.975720000000003,49.784239999999997,45.079279999999997,40.313609999999997,40.026730000000001,40.227319999999999,39.965269999999997,39.750520000000002,40.21078,40.001730000000002,40.022640000000003,40.316809999999997,40.676169999999999,40.107460000000003,40.025260000000003,40.52843,40.185040000000001,40.017539999999997,40.353149999999999,39.8352,40.05782,39.643720000000002,40.059649999999998,39.639240000000001,6278.8010000000004,6278.8010000000004,0,49.866570000000003,39.893000000000001,41,41,613243.46160000004,391363.01893263304,34125.314829005001,44,42,31311.030644785005,44,9.7948001449871693,10.401940144987169,374811.66194734786,6393.3985750203419,6968.0471931772536,689.24619317725319,0.10746896178429931,-6278.8010000000004,-6393.3985750203419,-6.7225363186553519E-2,0,0.80848315066721166,0.80848315066721166,6020.22895889748,-6020.22895889748,6.125739967524696E-2,6.125739967524696E-2,42,0.80848315066721166]
["2013-04-04T11:00:00","2013-04-04T11:00:00",51.155749999999998,50.941569999999999,50.621879999999997,50.762540000000001,50.705889999999997,50.147329999999997,50.189109999999999,50.358220000000003,50.018120000000003,48.080010000000001,44.084919999999997,40.33746,40.132530000000003,40.394419999999997,40.745899999999999,40.162219999999998,40.093299999999999,40.584989999999998,40.251829999999998,40.102499999999999,40.411799999999999,39.873629999999999,40.092289999999998,39.687089999999998,40.108789999999999,39.68486,6540.0420000000004,6540.0420000000004,0,50.658250000000002,39.943339999999999,29,29,433757.57040000003,297010.95749218337,37510.051188689991,45,42,35037.98071311001,44,9.9218891423170525,10.529029142317052,268550.5385565341,7062.7639979713813,7561.0704071886648,1021.0284071886645,7.6014631505967808E-2,-6540.0420000000004,-7062.7639979713813,-7.4263612583082256E-2,0,0.60489844167936735,0.60489844167936735,6655.5007569101363,-6655.5007569101363,-6.9981317498298196E-2,0,40,0.60489844167936735]
["2013-04-04T20:00:00","2013-04-04T20:00:00",51.780619999999999,51.483159999999998,51.129910000000002,51.42315,51.488169999999997,50.932250000000003,50.831600000000002,51.009160000000001,50.66046,50.315219999999997,50.563800000000001,50.358220000000003,50.29139,50.471159999999998,50.705770000000001,49.721530000000001,42.037770000000002,40.926349999999999,40.596760000000003,40.494320000000002,40.742730000000002,40.188850000000002,40.349820000000001,39.919130000000003,40.287559999999999,39.850110000000001,839.13580000000002,6395.7669999999998,7234.902,49.235399999999998,36.960290000000001,19,19,284185.99440000003,166431.28141426024,5005.6590266289995,50,45,39254.371729684994,44,10.24820907598226,10.855349075982259,181733.60319361251,7660.7281211078489,976.88464189519323,137.74884189519321,4.9802689607358223E-2,839.13500000000022,-425.82612110784885,-4.4774802180552907E-3,0,0.42760770481900223,0.42760770481900223,7232.2633671055873,2.6386328944126944,2.7744720208111838E-5,2.7744720208111838E-5,39,0.42760770481900223]
["2013-04-05T03:00:00","2013-04-05T03:00:00",51.649059999999999,51.325069999999997,50.94773,51.218200000000003,51.262799999999999,50.616570000000003,50.542110000000001,50.590820000000001,50.24362,50.005989999999997,50.406889999999997,50.169989999999999,49.945990000000002,46.704839999999997,41.384650000000001,40.530830000000002,40.429679999999998,40.876420000000003,40.52664,40.368360000000003,40.708300000000001,40.132260000000002,40.155059999999999,39.497259999999997,39.451929999999997,39.044550000000001,1301.7819999999999,5942.1049999999996,7243.8869999999997,47.923400000000001,37.02816,23,23,344014.62479999999,190597.94528770194,8204.1621184099986,44,41,32370.330040100005,44,9.7700752543674128,10.37721525436741,209729.44342889573,6626.4238907739909,1679.4470676656413,377.66506766564135,6.0287466366802052E-2,1301.7820000000002,617.46310922600878,2.0150358769011029E-2,2.0150358769011029E-2,0.51251642566882816,0.51251642566882816,6238.7315376302813,1005.1554623697184,4.5437410477524254E-2,4.5437410477524254E-2,44,0.51251642566882816]
["2013-04-05T06:00:00","2013-04-05T06:00:00",51.559989999999999,51.216099999999997,50.828719999999997,51.098689999999998,51.09019,50.405859999999997,50.327060000000003,50.436779999999999,50.168210000000002,49.928049999999999,50.317230000000002,49.73198,43.956949999999999,40.945799999999998,41.070779999999999,40.47325,40.397210000000001,40.861519999999999,40.517470000000003,40.314979999999998,40.584690000000002,39.916589999999999,39.817140000000002,38.871490000000001,39.28884,38.899270000000001,1253.3019999999999,5983.2139999999999,7236.5159999999996,48.288580000000003,37.033459999999998,25,25,373928.94,219082.3275033994,7933.8528487199983,39,37,33670.895777840022,44,9.5710365460243452,10.178176546024345,223322.58314222342,7035.9977450564365,1657.8879018105085,404.58590181050863,6.5529854746523966E-2,1253.3019999999997,200.51825494356308,3.2464698626678314E-2,3.2464698626678314E-2,0.55259440777507796,0.55259440777507796,6616.2923438367889,620.22365616321076,7.0509887395618517E-2,7.0509887395618517E-2,44,0.55259440777507796]
["2013-04-05T15:00:00","2013-04-05T15:00:00",51.789099999999998,51.150309999999998,50.744390000000003,51.001989999999999,50.886330000000001,50.383609999999997,50.183660000000003,50.340850000000003,50.144109999999998,49.98124,50.019300000000001,48.668950000000002,41.78848,40.928060000000002,41.07002,40.429679999999998,40.32291,40.75882,40.445369999999997,40.491320000000002,40.69661,39.910049999999998,39.676699999999997,39.179510000000001,39.500439999999998,39.019069999999999,1562.7439999999999,8885.3559999999998,7322.6130000000003,52.156979999999997,37.364989999999999,27,27,403843.25520000001,331072.955673697,9978.1438811599983,66,54,65716.048549219995,44,11.698175255528403,12.305315255528402,294791.90052578336,11235.264836396338,1705.9316796343021,143.18767963430219,7.0772243126245887E-2,-1562.7429999999995,-3912.6518363963378,-4.1140785708552903E-2,0,0.5334415469707382,0.5334415469707382,10680.920754093771,-3358.3077540937711,-3.5311963709450778E-2,0,40,0.5334415469707382]
["2013-04-05T22:00:00","2013-04-05T22:00:00",52.654789999999998,51.644039999999997,51.006999999999998,51.149979999999999,51.135370000000002,50.657299999999999,50.429160000000003,50.518880000000003,50.255029999999998,50.055070000000001,50.266089999999998,50.163400000000003,49.811889999999998,45.592550000000003,41.600490000000001,40.632040000000003,40.393300000000004,40.83343,40.528590000000001,40.549219999999998,40.851010000000002,40.229430000000001,40.268149999999999,39.611930000000001,39.717289999999998,39.20702,165.77950000000001,7193.4409999999998,7317.9,51.170670000000001,36.979460000000003,23,23,344014.62479999999,256817.84331768367,1114.6822933574999,58,53,51041.815926804993,44,11.13693692310405,11.74407692310405,239071.19664622936,9166.2216063945853,200.17753553852745,34.398035538527438,6.0287466366802052E-2,124.45899999999983,-1848.3216063945856,-1.943474817304577E-2,0,0.4806241801039785,0.4806241801039785,8692.3504096589731,-1374.4504096589735,-1.4452083174078941E-2,0,38,0.4806241801039785]
["2013-04-06T01:00:00","2013-04-06T01:00:00",52.624000000000002,51.627200000000002,50.99051,51.158830000000002,51.144919999999999,50.655320000000003,50.441600000000001,50.5336,50.252560000000003,50.050310000000003,50.299030000000002,50.169989999999999,49.726059999999997,44.885150000000003,41.564770000000003,40.651919999999997,40.41724,40.845239999999997,40.548110000000001,40.544029999999999,40.851170000000003,40.239199999999997,40.28745,39.53857,39.738729999999997,39.220210000000002,147.57830000000001,7269.3419999999996,7310.2030000000004,49.623820000000002,36.892049999999998,23,23,344014.62479999999,223329.22502064897,989.05427087850023,57,52,46275.795197670013,44,10.913568616240548,11.520708616240549,234276.25807529094,8480.4149448983571,181.2522201778587,33.67392017785869,6.0287466366802052E-2,40.861000000000786,-1170.2119448983567,-1.2304554780676236E-2,0,0.48293777449968167,0.48293777449968167,8033.4980666789552,-723.29506667895475,-7.6053092855047711E-3,0,38,0.48293777449968167]
["2013-04-06T09:00:00","2013-04-06T09:00:00",52.408200000000001,51.726660000000003,51.032780000000002,51.181170000000002,51.17163,50.669339999999998,50.497109999999999,50.56758,50.27563,50.072159999999997,50.306260000000002,50.195320000000002,49.896160000000002,46.33287,41.742849999999997,40.739989999999999,40.442529999999998,40.8566,40.591920000000002,40.602879999999999,40.892310000000002,40.296469999999999,40.364040000000003,39.65455,39.7331,39.240609999999997,430.88810000000001,7743.2910000000002,7312.402,50.412379999999999,37.117150000000002,23,23,344014.62479999999,239818.94132987835,2836.8789183395011,62,52,51474.417400964987,44,11.090841633372907,11.697981633372907,238081.6915289904,9282.328447658263,511.57144103531112,80.683341035311116,6.0287466366802052E-2,-430.88900000000012,-1969.926447658263,-2.0713399820251718E-2,0,0.47756315104411662,0.47756315104411662,8800.5638945636219,-1488.1618945636219,-1.5647737688888063E-2,0,38,0.47756315104411662]
["2013-04-06T10:00:00","2013-04-06T10:00:00",52.315869999999997,51.77017,51.098109999999998,51.20814,51.177770000000002,50.699620000000003,50.503689999999999,50.589280000000002,50.29609,50.09075,50.29468,50.220419999999997,49.982509999999998,47.433190000000003,41.948549999999997,40.774009999999997,40.442889999999998,40.85633,40.604529999999997,40.650080000000003,40.897210000000001,40.31176,40.391939999999998,39.699939999999998,39.768859999999997,39.27158,717.59990000000005,8029.0690000000004,7311.4690000000001,50.874650000000003,37.189019999999999,23,23,{"$f":"3.1416*(138/2)^2*AI2263","v":344014.62479999999},{"$f":"62.4*AJ2263*(AF2263-AB2263)/1000","v":249077.44820887575},4680.2905997854996,66,55,54941.433789235009,44,11.391607892212914,11.998747892212913,244538.09421028069,{"$f":"AO2263*1000/(500*AQ2263)","v":9645.9488966069348},821.70851456094385,104.10861456094381,{"$f":"AJ2263/$BK$7","v":6.0287466366802052E-2},-717.60000000000036,{"$f":"AE2263-AT2263","v":-2334.4798966069347},-2.4546609609836467E-2,0,0.47001772429547733,0.47001772429547733,9157.8611839809619,-1846.3921839809618,-1.9414460665396413E-2,0,38,0.47001772429547733]
["2013-04-06T19:00:00","2013-04-06T19:00:00",54.301969999999997,53.311790000000002,52.191870000000002,52.26782,51.989849999999997,51.560679999999998,51.162460000000003,51.11224,50.852960000000003,50.682079999999999,50.65849,50.597520000000003,50.44332,50.539439999999999,50.77711,50.117730000000002,49.808579999999999,48.374490000000002,42.37153,41.044220000000003,41.217750000000002,40.576279999999997,40.515360000000001,40.040370000000003,40.38458,40.124180000000003,2700.9850000000001,10022.23,7321.2439999999997,53.195500000000003,38.126300000000001,15,15,224357.364,182997.16651010994,19146.999061574992,71,62,75513.494158000001,44,12.519044150787801,13.1261841507878,175265.36011735105,12063.779510394663,3058.859579206789,357.87457920678889,3.9317912847914381E-2,-2700.9859999999999,-4742.5355103946631,-4.9866853813410779E-2,0,0.2956536056949074,0.2956536056949074,11505.780094280923,-4184.536094280923,-4.3999596678419531E-2,0,37,0.2956536056949074]
["2013-04-07T02:00:00","2013-04-07T02:00:00",53.201349999999998,52.253039999999999,51.674390000000002,51.83,51.655670000000001,51.01088,50.816409999999998,50.9133,50.611960000000003,50.414200000000001,50.48377,50.377659999999999,50.27657,50.385779999999997,50.392130000000002,48.06897,43.316940000000002,41.984859999999998,41.142490000000002,40.737200000000001,39.837699999999998,38.959299999999999,39.056480000000001,38.608739999999997,39.009140000000002,38.763399999999997,5123.1390000000001,8223.1080000000002,13346.25,50.522030000000001,37.266080000000002,19,19,284185.99440000003,208518.20866229641,36983.812362525001,62,58,54502.554246299995,44,11.559183099798831,12.166323099798831,204981.37568488353,9430.1740487610277,6399.0356486642459,1275.8966486642457,4.9802689607358223E-2,5123.1419999999998,3916.0759512389723,0.11597314778196983,0.11597314778196983,0.40862083078536204,0.40862083078536204,8959.5769895674057,4386.6730104325943,0.13130221658788957,0.13130221658788957,44,0.40862083078536204]
["2013-04-07T05:00:00","2013-04-07T05:00:00",51.922629999999998,51.219180000000001,50.788609999999998,51.022759999999998,50.969029999999997,50.460639999999998,50.266159999999999,50.387419999999999,50.144449999999999,49.90945,49.771929999999998,47.366109999999999,43.026040000000002,41.713619999999999,41.538499999999999,40.511150000000001,39.4602,39.439860000000003,38.809739999999998,38.831919999999997,39.121470000000002,38.595230000000001,38.7029,38.26491,38.653210000000001,38.411299999999997,4699.7190000000001,8641.9959999999992,13341.71,50.805340000000001,37.371429999999997,27,27,403843.25520000001,312327.56622157019,31749.727158135,63,60,58047.898242180017,44,11.801773330058339,12.408913330058338,297402.55326558213,9837.1484723123522,5380.5010942331082,680.78209423310818,7.0772243126245887E-2,4699.7139999999999,3504.561527687647,0.23631470488142711,0.23631470488142711,0.56416480867441166,0.56416480867441166,9355.8390969770953,3985.8709030229038,0.26650104082677528,0.26650104082677528,44,0.56416480867441166]
["2013-04-07T14:00:00","2013-04-07T14:00:00",47.028329999999997,42.674709999999997,41.143819999999998,41.059780000000003,40.535150000000002,39.373669999999997,38.878210000000003,39.056719999999999,38.586829999999999,38.474699999999999,38.586480000000002,38.620820000000002,38.565060000000003,38.775959999999998,39.108789999999999,38.478360000000002,38.290039999999998,38.562640000000002,38.227409999999999,38.29871,38.558610000000002,38.035269999999997,38.113970000000002,37.643120000000003,38.019950000000001,37.839500000000001,4245.9440000000004,9953.8330000000005,14199.78,52.644910000000003,37.265230000000003,49,49,732900.72239999997,677095.89070831868,19507.628802759991,70,64,76543.383156719996,44,12.675857365644152,13.282997365644153,579705.04926796549,12077.034467771526,3077.9186354103736,-1168.0253645896269,0.12843851530318698,4245.9470000000001,2122.745532228475,0.48495366364213688,0.48495366364213688,0.98661994058286651,0.98661994058286651,11525.016688582029,2674.7633114179716,0.56468541465500766,0.56468541465500766,44,0.98661994058286651]
["2013-04-07T21:00:00","2013-04-07T21:00:00",52.728380000000001,49.092190000000002,41.257429999999999,40.588470000000001,39.873579999999997,39.046930000000003,38.737589999999997,38.90775,38.683489999999999,38.539169999999999,38.611989999999999,38.621569999999998,38.533209999999997,38.753529999999998,39.077689999999997,38.437040000000003,38.188749999999999,38.654850000000003,38.377459999999999,38.4146,38.624310000000001,38.0349,38.069330000000001,37.563389999999998,37.958480000000002,37.736490000000003,2380.5889999999999,9785.3109999999997,7404.7219999999998,53.116840000000003,38.14134,47,47,702986.40720000002,674679.84404985968,17844.764211604997,70,63,73269.962440250019,44,12.503386719212527,13.110526719212526,548477.960632456,11720.018597467586,2854.3889127551315,473.79991275513157,0.12319612692346506,-2380.5889999999999,-4315.2965974675863,0.34997045204302069,0.34997045204302069,0.88680840992074594,0.88680840992074594,11177.272127881515,-3772.5501278815154,0.47024649786462641,0.47024649786462641,44,0.91762898617926714]
["2013-04-08","2013-04-08",53.61515,53.13223,52.166960000000003,49.620759999999997,41.746879999999997,40.346359999999997,39.496209999999998,39.24436,38.880580000000002,38.718290000000003,38.792470000000002,38.753430000000002,38.669690000000003,38.882899999999999,39.172359999999998,38.51878,38.330860000000001,38.78951,38.531460000000003,38.591239999999999,38.835129999999999,38.170299999999997,38.171599999999998,37.653770000000002,38.00611,37.797649999999997,1882.9010000000001,9279.4130000000005,7396.5119999999997,52.275149999999996,38.224899999999998,43,43,643157.77679999999,581026.1629300128,14891.393283750003,68,62,65189.036251624995,44,12.166980136180413,12.774120136180413,488297.96463274671,10715.729872489102,2447.8371982326366,{"$f":"AU2301-AC2301","v":564.93619823263657},0.11271135016402123,{"$f":"AE2301-AD2301","v":-1882.9010000000007},-3319.2178724891028,0.23909258987982451,0.23909258987982451,0.82430033245307399,0.82430033245307399,{"$f":"AO2301*1000/(500*AR2301)","v":10206.422917064745},{"$f":"AE2301-BD2301","v":-2809.9109170647453},0.37560284257346399,0.37560284257346399,44,0.85512090871159518]
["2013-04-08T08:00:00","2013-04-08T08:00:00",53.624000000000002,52.951799999999999,52.573430000000002,52.901150000000001,52.924300000000002,52.586500000000001,52.472000000000001,52.073399999999999,46.937869999999997,40.824890000000003,40.230510000000002,39.556930000000001,39.232460000000003,39.298229999999997,39.547199999999997,38.83719,38.603340000000003,39.125970000000002,38.85324,38.883330000000001,39.108919999999998,38.485080000000004,38.506549999999997,38.028869999999998,38.338459999999998,38.071869999999997,2253.6179999999999,9654.8330000000005,7401.2150000000001,52.968559999999997,38.296169999999996,33,33,493586.20079999999,458814.75878754992,17524.280053170005,68,63,70829.737580434987,44,12.420175051492834,13.027315051492835,382538.64585688704,11405.594089742184,2821.9054853117691,568.28748531176916,8.6499408265411637E-2,-2253.6180000000004,-4004.3790897421841,-3.6604858215217168E-3,0,0.68879980915345751,0.68879980915345751,10874.034641899356,-3472.8196418993557,0.17023192598334971,0.17023192598334971,43,0.7196203854119787]
["2013-04-08T11:00:00","2013-04-08T11:00:00",54.381450000000001,53.57002,53.064050000000002,53.116900000000001,53.015210000000003,52.662480000000002,52.545520000000003,52.754939999999998,52.578220000000002,52.43253,50.752099999999999,44.45879,40.793370000000003,40.227620000000002,40.077860000000001,39.186819999999997,38.907089999999997,39.293509999999998,39.031190000000002,39.080770000000001,39.309040000000003,38.657380000000003,38.650770000000001,38.146439999999998,38.44829,38.231259999999999,3412.8739999999998,10815.78,7402.9030000000002,53.547499999999999,38.326340000000002,27,27,403843.25520000001,385966.47766712558,27559.281773030001,73,66,82314.358952399984,44,12.99434164027684,13.601481640276841,327455.05897667515,12669.261934327025,4241.7357548316486,828.8617548316488,7.0772243126245887E-2,-3412.8770000000004,-5266.3589343270251,-5.5374756927266774E-2,0,0.59205104564908306,0.59205104564908306,12103.734156233377,-4700.8311562333765,3.16704732602743E-2,3.16704732602743E-2,42,0.62287162190760426]
["2013-04-08T20:00:00","2013-04-08T20:00:00",54.290199999999999,53.803629999999998,53.486939999999997,53.85398,53.8904,53.583359999999999,53.481319999999997,53.706299999999999,53.560250000000003,53.460169999999998,53.29524,53.000599999999999,52.818680000000001,52.97139,53.250390000000003,52.631100000000004,52.412520000000001,52.519779999999997,48.836550000000003,42.46828,41.154910000000001,39.830199999999998,39.319429999999997,38.061549999999997,38.379910000000002,38.207569999999997,3160.36,11369.56,14529.92,52.598849999999999,37.53237,13,13,194443.04880000002,174612.94402247056,25413.450273400002,73,67,85649.624174399985,44,13.16892118434704,13.776061184347039,159781.76351225996,13007.842172554818,3859.6100496990084,699.25004969900829,3.4075524468192467E-2,3160.3600000000006,1522.0778274451823,2.9209027119821471E-2,{"$f":"IF(AZ2320>1,1,IF(AZ2320<0,0,AZ2320))","v":2.9209027119821471E-2},0.36852887134386014,{"$f":"IF(BB2320>1,1,BB2320)","v":0.36852887134386014},12434.559200668884,2095.3607993311161,4.1355127250172402E-2,4.1355127250172402E-2,44,0.39934944760238134]
["2013-04-09T03:00:00","2013-04-09T03:00:00",54.248950000000001,53.733409999999999,53.04148,53.104700000000001,53.041080000000001,52.648539999999997,52.541350000000001,52.72222,52.40363,51.559719999999999,47.618639999999999,42.068530000000003,40.511249999999997,40.126019999999997,39.519579999999998,38.114409999999999,37.809379999999997,38.355379999999997,38.114359999999998,38.165570000000002,38.423769999999998,37.912680000000002,37.989319999999999,37.519739999999999,37.861240000000002,37.686520000000002,4709.9459999999999,10021.17,14731.11,51.318370000000002,37.443379999999998,29,29,433757.57040000003,368966.0916899718,39004.075464389993,69,65,69521.816769150013,44,12.497268951828017,13.104408951828015,338256.9850720492,11125.921517273713,6242.0158539813992,1532.0698539813993,7.6014631505967808E-2,4709.9400000000005,3605.1884827262875,0.24658242566364469,0.24658242566364469,0.67841046311572828,0.67841046311572828,10610.446762568714,4120.6632374312867,0.29811783542334652,0.29811783542334652,44,0.70923103937424947]
["2013-04-09T06:00:00","2013-04-09T06:00:00",53.419429999999998,52.887009999999997,52.534599999999998,52.859290000000001,52.769210000000001,51.90813,48.728490000000001,42.921500000000002,40.602519999999998,39.8553,39.256489999999999,38.393039999999999,38.10895,38.196100000000001,38.513030000000001,37.895319999999998,37.77657,38.305599999999998,38.072220000000002,38.135829999999999,38.396120000000003,37.879860000000001,37.946559999999998,37.472439999999999,37.809350000000002,37.656849999999999,4174.8999999999996,10553.39,14728.29,52.544559999999997,37.614359999999998,35,35,523500.516,486328.36930444156,32903.597620999994,70,66,78782.111688999998,44,12.8738920085949,13.481032008594902,420544.12042828888,12239.051195458727,5111.6783640926624,936.77836409266274,9.1741796645133558E-2,4174.9000000000015,2489.2388045412736,0.33573234594535667,0.33573234594535667,0.81597738817248355,0.81597738817248355,11687.845802720749,3040.444197279252,0.40435655573724827,0.40435655573724827,44,0.84679796443100475]
["2013-04-09T13:00:00","2013-04-09T13:00:00",43.203890000000001,40.904559999999996,39.776539999999997,39.288130000000002,38.662399999999998,38.233350000000002,37.95673,38.143639999999998,37.964449999999999,37.878489999999999,37.916589999999999,38.022359999999999,37.938049999999997,38.158580000000001,38.493319999999997,37.865430000000003,37.705379999999998,38.2057,37.993600000000001,38.093249999999998,38.346110000000003,37.81438,37.853729999999999,37.362299999999998,37.683010000000003,37.569099999999999,3024.1219999999998,11728.28,14752.41,54.156999999999996,38.401649999999997,49,49,732900.72239999997,758614.51492937491,8520.1462021900043,77,69,92391.578149000008,44,13.520515814880902,14.127655814880899,618333.81841588253,13666.871798975644,1260.3285730878094,-1763.7934269121904,0.12843851530318698,3024.1299999999992,1085.5382010243557,0.45147552606159508,0.45147552606159508,1.0317981485414751,1,13079.534122240208,1672.8758777597923,0.562670018859878,0.562670018859878,44,1]
["2013-04-09T22:00:00","2013-04-09T22:00:00",55.212820000000001,54.088549999999998,53.456589999999998,53.588729999999998,53.568600000000004,53.118049999999997,52.880510000000001,52.969650000000001,52.49371,48.426929999999999,41.810189999999999,40.217280000000002,39.368319999999997,39.002299999999998,39.061549999999997,38.289560000000002,38.100650000000002,38.591720000000002,38.340339999999998,38.424340000000001,38.592019999999998,37.976939999999999,38.02843,37.520580000000002,37.856780000000001,37.688749999999999,4476.4579999999996,11751.95,7275.4930000000004,53.806559999999998,38.643940000000001,31,31,463671.88560000004,466338.6221172142,39222.881672030002,74,69,89095.176054499985,44,13.40810850345845,14.015248503458452,387938.48821278557,13289.745683594225,5850.6211613536634,1374.1631613536638,8.125701988568973E-2,-4476.4570000000003,-6014.2526835942244,-6.3238716655333732E-2,0,0.5947538456901329,0.5947538456901329,12714.034436494587,-5438.5414364945864,0.10433528353372365,0.10433528353372365,43,0.61772123726313355]
["2013-04-10T01:00:00","2013-04-10T01:00:00",54.396479999999997,53.872030000000002,53.530450000000002,53.897550000000003,53.929409999999997,53.620780000000003,53.50177,53.704439999999998,53.430190000000003,53.090479999999999,53.06973,52.960120000000003,52.588099999999997,49.01905,42.288469999999997,40.215800000000002,39.2684,39.20805,38.619480000000003,38.660240000000002,38.866639999999997,38.267220000000002,38.150759999999998,37.635219999999997,37.962110000000003,37.770400000000002,4471.018,11738.97,7267.9489999999996,52.552990000000001,37.703119999999998,21,21,314100.30960000004,289736.68437104748,37167.751474719989,73,68,87161.089216950015,44,13.281309142297998,13.888449142297995,260311.79076172056,13125.376163312312,5597.0011806063631,1125.983180606363,5.5045077987080138E-2,-4471.0209999999997,-5857.4271633123126,-6.1589726304714439E-2,0,0.44597612619280003,0.44597612619280003,12551.594252737172,-5283.6452527371721,-5.5556519259091497E-2,0,41,0.46894351776580057]
["2013-04-10T05:00:00","2013-04-10T05:00:00",54.144530000000003,53.759459999999997,53.405059999999999,53.735320000000002,53.865099999999998,53.345829999999999,53.414059999999999,53.587490000000003,53.384610000000002,53.174169999999997,53.598520000000001,53.371420000000001,53.212949999999999,53.163209999999999,52.636009999999999,44.319850000000002,40.672469999999997,40.345559999999999,39.254829999999998,38.69867,38.92465,38.356340000000003,38.381279999999997,37.935760000000002,38.302790000000002,37.865549999999999,186.96629999999999,7116.0649999999996,7241.7939999999999,49.014600000000002,36.977379999999997,19,19,284185.99440000003,197708.40091799601,1521.8103291870004,45,43,42828.819969650016,44,10.248403760965067,10.855543760965066,181737.0555825276,8358.1445400853208,296.98485045708139,110.0185504570814,4.9802689607358223E-2,125.72900000000027,-1116.350540085321,-1.1738212410838488E-2,0,0.40987101735996012,0.40987101735996012,7890.6816485151367,-648.88764851513679,-6.8229295150052426E-3,0,40,0.43283840893296066]
["2013-04-10T10:00:00","2013-04-10T10:00:00",54.061599999999999,53.710250000000002,53.363630000000001,53.712319999999998,53.851230000000001,53.313560000000003,53.407209999999999,53.561109999999999,53.375190000000003,53.12518,53.575809999999997,53.201309999999999,52.880459999999999,52.464460000000003,46.354430000000001,40.875549999999997,39.851280000000003,39.600209999999997,39.247059999999998,39.002200000000002,39.3872,38.858069999999998,38.982140000000001,38.513370000000002,38.894359999999999,37.997570000000003,745.40279999999996,6486.25,7231.6530000000002,49.2286,36.987949999999998,21,21,314100.30960000004,220126.60800791776,5987.0864706419979,41,40,39697.958031250004,44,9.9591003688656254,10.566240368865627,195196.96617396563,7972.1976003685431,1202.3347991067483,456.93199910674832,5.5045077987080138E-2,745.40300000000025,-740.54460036854289,-7.7866848330284235E-3,0,0.43845878449829345,0.43845878449829345,7514.1122377309521,-282.45923773095183,-1.8968317267209576E-3,0,40,0.46142617607129399]
["2013-04-10T19:00:00","2013-04-10T19:00:00",54.02216,53.661230000000003,53.339239999999997,53.673830000000002,53.809699999999999,53.296990000000001,53.336329999999997,53.521419999999999,53.25788,52.801580000000001,52.841430000000003,50.24973,42.1723,40.497549999999997,40.061970000000002,39.428100000000001,39.332210000000003,39.789490000000001,39.506,39.36909,39.704439999999998,39.165280000000003,39.285919999999997,38.858269999999997,39.184570000000001,38.772750000000002,582.16200000000003,6641.5209999999997,7223.683,49.349829999999997,36.972000000000001,27,27,403843.25520000001,266540.50286515482,4438.8135122099993,46,42,41103.808939714982,44,10.128733884844282,10.735873884844281,255242.26185806753,8116.2777908932912,876.47944208541946,294.31744208541943,7.0772243126245887E-2,582.16200000000026,-892.59479089329125,-9.3854635046019142E-3,0,0.51567163271609162,0.51567163271609162,7657.2823750734988,-433.59937507349878,-4.5592144967570476E-3,0,41,0.53863902428909216]
["2013-04-11T02:00:00","2013-04-11T02:00:00",53.884650000000001,53.601819999999996,53.280949999999997,53.665680000000002,53.788609999999998,53.195340000000002,53.136859999999999,53.031410000000001,52.167270000000002,46.619219999999999,41.249929999999999,39.777520000000003,39.46913,39.73254,40.078919999999997,39.52758,39.452530000000003,39.912489999999998,39.587310000000002,39.378689999999999,39.769649999999999,39.268459999999997,39.27861,38.882840000000002,39.29204,38.923290000000001,1341.481,5878.2659999999996,7219.7470000000003,48.079720000000002,37.02561,31,31,463671.88560000004,264924.13980017905,10035.19008708,41,37,32489.499486630004,44,9.5307509324940831,10.137890932494084,275754.41437773773,6817.8257341424178,2105.8550702161538,764.37407021615377,8.125701988568973E-2,1341.4810000000007,401.92126585758251,1.2876856281637639E-2,1.2876856281637639E-2,0.59781905964387161,0.59781905964387161,6409.518449738749,810.22855026125126,3.1464779449961865E-2,3.1464779449961865E-2,44,0.62078645121687215]
["2013-04-11T05:00:00","2013-04-11T05:00:00",53.860750000000003,53.579569999999997,53.261760000000002,53.636830000000003,53.690660000000001,52.924849999999999,52.710140000000003,51.387349999999998,43.844090000000001,40.211849999999998,39.891739999999999,39.51576,39.455309999999997,39.736969999999999,40.066659999999999,39.505629999999996,39.429090000000002,39.910130000000002,39.597000000000001,39.38449,39.763280000000002,39.169550000000001,39.267890000000001,38.74559,39.143949999999997,38.780079999999998,1287.348,5941.509,7228.8559999999998,48.171520000000001,36.973739999999999,33,33,493586.20079999999,289254.275833608,9707.0351815800041,41,36,33265.855325010009,44,9.4963776665828412,10.103517666582842,292486.33276578103,7006.009342292793,2044.3658671534206,757.01786715342064,8.6499408265411637E-2,1287.3469999999998,222.84665770720676,2.813193993803953E-2,2.813193993803953E-2,0.64236993623814209,0.64236993623814209,6585.0046335913439,643.85136640865585,5.950057817577957E-2,5.950057817577957E-2,44,0.66533732781114263]
["2013-04-11T12:00:00","2013-04-11T12:00:00",53.967399999999998,53.521160000000002,53.069519999999997,53.142969999999998,52.640770000000003,47.194499999999998,40.983229999999999,40.172089999999997,39.754519999999999,39.375790000000002,39.622079999999997,39.459560000000003,39.423380000000002,39.701860000000003,40.038939999999997,39.470759999999999,39.380560000000003,39.846980000000002,39.570970000000003,39.464039999999997,39.723950000000002,39.180259999999997,39.323369999999997,38.896799999999999,39.244140000000002,38.843589999999999,830.53639999999996,6405.3720000000003,7235.9089999999997,49.602249999999998,36.99729,39,39,583329.14639999997,391612.4131425682,6280.4373558419993,51,41,40369.728922559989,44,10.042854756259297,10.649994756259296,365557.28928500594,8039.4927343540849,1250.7275089142679,420.19110891426794,0.10222657340457739,830.53699999999935,-803.58373435408521,3.4770239114512679E-3,{"$f":"IF(AZ2384>1,1,IF(AZ2384<0,0,AZ2384))","v":3.4770239114512679E-3},0.72585627685107357,{"$f":"IF(BB2384>1,1,BB2384)","v":0.72585627685107357},7581.1734834580238,-345.26448345802419,6.7477177071696204E-2,6.7477177071696204E-2,43,0.74882366842407411]
["2013-04-11T21:00:00","2013-04-11T21:00:00",53.408209999999997,52.925699999999999,52.619,52.946210000000001,53.013399999999997,52.568570000000001,48.899810000000002,42.050420000000003,40.103789999999996,39.687049999999999,39.855260000000001,39.66292,39.517919999999997,39.783149999999999,40.138289999999998,39.573990000000002,39.477020000000003,39.922379999999997,39.662579999999998,39.623130000000003,39.912610000000001,39.384079999999997,39.503540000000001,39.03922,39.448090000000001,39.051009999999998,591.10389999999995,7647.7,7263.0690000000004,50.57685,37.464359999999999,37,37,553414.83120000002,398022.81779758428,4243.2984565399984,54,45,50140.194886500001,44,10.619415645629651,11.22655564562965,366721.18809885136,9443.1175047065535,799.1585597812624,208.05465978126244,9.6984185024855479E-2,-384.6309999999994,-2180.0485047065531,-2.2922793061237335E-2,0,0.6675300124211957,0.6675300124211957,8932.4270896958351,-1669.3580896958347,-1.7552981024314851E-2,0,40,0.69049740399419623]
["2013-04-12","2013-04-12",53.270040000000002,52.83775,52.512270000000001,52.850029999999997,52.94406,52.500329999999998,50.60895,43.498370000000001,40.26972,39.746780000000001,39.912700000000001,39.752249999999997,39.585990000000002,39.813189999999999,40.14725,39.586329999999997,39.501849999999997,39.951799999999999,39.673909999999999,39.617959999999997,39.924059999999997,39.392989999999998,39.51202,39.071350000000002,39.45872,39.064709999999998,305.05610000000001,7561.2070000000003,7268.643,48.9589,37.395800000000001,35,35,523500.516,323207.88679308735,2166.7112845065008,49,44,43715.496330850001,44,10.339486424881986,10.946626424881986,337754.13226468459,8456.0285752005257,419.11390865455508,114.05780865455506,9.1741796645133558E-2,-292.56400000000031,-1187.3855752005256,-1.2485132218598795E-2,0,0.65715172796225629,0.65715172796225629,7987.026255227539,-718.38325522753894,-7.5536625275479915E-3,0,40,0.68011911953525683]
["2013-04-12T07:00:00","2013-04-12T07:00:00",53.147030000000001,52.766930000000002,52.45673,52.794829999999997,51.277569999999997,43.639209999999999,40.313949999999998,40.166679999999999,39.866570000000003,39.540950000000002,39.781309999999998,39.622819999999997,39.572110000000002,39.858330000000002,40.208309999999997,39.634630000000001,39.539709999999999,40.014600000000002,39.735570000000003,39.640059999999998,39.969949999999997,39.455199999999998,39.59778,39.186869999999999,39.588090000000001,39.211039999999997,826.75559999999996,6433.107,7259.8620000000001,49.358060000000002,36.99371,39,39,583329.14639999997,369348.87694247277,5760.8288870220013,49,45,39770.593267725009,44,10.265812230429423,10.872952230429423,373672.88309389428,7748.163004548036,1122.3327989471757,295.5771989471757,0.10222657340457739,826.75500000000011,-488.30100454803596,-5.1343916682053872E-3,0,0.72717861919765781,0.72717861919765781,7315.509610429749,-55.647610429748966,9.2255591776504598E-3,9.2255591776504598E-3,41,0.75014601077065834]
["2013-04-12T10:00:00","2013-04-12T10:00:00",53.204149999999998,52.73818,52.368659999999998,52.551569999999998,49.921880000000002,42.231529999999999,40.073790000000002,40.140349999999998,39.890709999999999,39.574669999999998,39.695259999999998,39.672980000000003,39.605080000000001,39.888010000000001,40.246510000000001,39.684399999999997,39.590409999999999,40.041690000000003,39.77852,39.729790000000001,40.025309999999998,39.496690000000001,39.612050000000004,39.188920000000003,39.596980000000002,39.243020000000001,302.63639999999998,7541.8649999999998,7273.3519999999999,51.099789999999999,37.478549999999998,39,39,583329.14639999997,431583.33024525427,2112.5730615659995,64,52,51364.776606300002,44,11.087102882274831,11.694242882274832,403567.6482468606,9265.6805211788705,381.08658032630177,78.450180326301791,0.10222657340457739,-268.51299999999992,-1992.3285211788707,-2.0948953338600907E-2,0,0.7266547293672172,0.7266547293672172,8784.6262683930563,-1511.2742683930564,-1.5890759879129378E-2,0,40,0.74962212094021774]
["2013-04-12T19:00:00","2013-04-12T19:00:00",54.301609999999997,53.120820000000002,52.479970000000002,52.713790000000003,52.661299999999997,52.319290000000002,52.138449999999999,50.809690000000003,43.444330000000001,40.320430000000002,40.082320000000003,40.07291,39.866340000000001,40.011710000000001,40.281950000000002,39.67839,39.555320000000002,40.064210000000003,39.787059999999997,39.82179,40.113669999999999,39.611269999999998,39.68544,39.248539999999998,39.674990000000001,39.322009999999999,1806.95,9011.8009999999995,7204.8509999999997,54.525230000000001,38.45478,33,33,493586.20079999999,468255.81502293836,13533.694109999997,67,55,72411.848690225001,44,11.987349040336673,12.594489040336672,369207.70039815817,12081.378200728737,2257.9961698720831,451.04616987208306,8.6499408265411637E-2,-1806.9499999999998,-4876.5272007287376,-5.1275750809428221E-2,0,0.58972717828524523,0.58972717828524523,11498.973631770188,-4294.1226317701885,-4.5151878160111653E-2,0,39,0.61269456985824577]
["2013-04-13T02:00:00","2013-04-13T02:00:00",53.68694,53.18412,52.820970000000003,53.09834,53.101010000000002,52.509419999999999,52.310560000000002,52.476849999999999,52.259059999999998,51.13579,44.571770000000001,40.825139999999998,40.271329999999999,40.32864,40.515520000000002,39.816409999999998,39.691960000000002,40.203499999999998,39.948070000000001,39.923099999999998,40.207799999999999,39.70514,39.767539999999997,39.320720000000001,39.715420000000002,39.363190000000003,945.89449999999999,8200.2109999999993,7254.317,50.154310000000002,37.540300000000002,29,29,433757.57040000003,292077.55156911851,6774.3781721874984,57,50,51718.771778054994,44,10.977480117631675,11.584620117631676,297121.66254814505,9422.7037942862644,1234.2319183628874,288.33741836288743,7.6014631505967808E-2,-945.89399999999932,-2168.3867942862644,-2.2800172406638491E-2,0,0.50635386135141236,0.50635386135141236,8928.8679737265702,-1674.5509737265702,-1.7607583206683989E-2,0,38,0.5293212529244129]
["2013-04-13T05:00:00","2013-04-13T05:00:00",53.406779999999998,52.950049999999997,52.638640000000002,52.931019999999997,52.981529999999999,52.604559999999999,52.51455,52.538240000000002,52.323659999999997,52.114170000000001,49.771180000000001,42.645159999999997,40.576279999999997,40.475879999999997,40.667490000000001,39.881500000000003,39.749940000000002,40.241570000000003,39.975529999999999,39.946269999999998,40.238900000000001,39.746920000000003,39.815640000000002,39.331809999999997,39.72974,39.393659999999997,1122.5340000000001,8380.7620000000006,7258.2269999999999,50.264620000000001,37.684370000000001,27,27,403843.25520000001,273946.22570945724,7865.1018230400005,56,50,52716.040575250008,44,11.011486983616027,11.618626983616025,277487.48027868982,9574.7360286010626,1428.5267438888993,305.99274388889921,7.0772243126245887E-2,-1122.5350000000008,-2316.5090286010627,-2.4357649369942693E-2,0,0.47613115711759518,0.47613115711759518,9074.401071587441,-1816.1740715874412,-1.9096722993228829E-2,0,38,0.49909854869059578]
["2013-04-13T12:00:00","2013-04-13T12:00:00",53.110280000000003,52.649439999999998,52.324089999999998,52.675139999999999,52.70731,52.418259999999997,52.301499999999997,52.535359999999997,52.392960000000002,52.314039999999999,52.415120000000002,52.47242,52.319879999999998,50.863050000000001,44.644440000000003,40.758279999999999,40.18139,40.45176,40.178179999999998,40.202500000000001,40.466830000000002,39.828940000000003,39.86665,39.424660000000003,39.840139999999998,39.481459999999998,2502.4789999999998,9771.2279999999992,7268.7489999999998,52.074179999999998,37.987409999999997,21,21,314100.30960000004,246815.54044406139,17052.917922390006,74,58,68822.520726780014,44,12.0474939567832,12.654633956783199,236129.18669993529,11425.2011204422,2830.9485746267692,328.46957462676937,5.5045077987080138E-2,-2502.4789999999994,-4156.4521204421999,-4.3704299064970836E-2,0,0.34388572418786417,0.34388572418786417,10877.046457734865,-3608.297457734865,-3.7940557629096705E-2,0,38,0.36685311576086471]
["2013-04-13T21:00:00","2013-04-13T21:00:00",54.72681,54.251950000000001,53.8247,53.153289999999998,52.856050000000003,52.52037,52.37867,52.587260000000001,52.442039999999999,52.369639999999997,52.491010000000003,52.564410000000002,52.51914,52.72842,53.019260000000003,52.426000000000002,52.29242,52.690440000000002,52.055999999999997,47.7074,42.326000000000001,40.667149999999999,40.37912,39.802509999999998,40.185220000000001,39.731540000000003,3285.9070000000002,9128.5570000000007,10068.26,52.491300000000003,37.912430000000001,11,11,164528.73360000001,130999.26239961202,24636.531329944999,69,56,66542.022895295013,44,11.848034980729562,12.455174980729561,121638.95272014316,11232.583800355656,4158.7539824140467,872.84698241404658,2.8833136088470546E-2,939.70299999999952,-1164.3238003556562,-1.2242642067002398E-2,0,0.15819420191783928,0.15819420191783928,10685.040233998754,-616.78023399875383,-6.4853261923720701E-3,0,37,0.18116159349083982]
["2013-04-14","2013-04-14",53.146769999999997,52.708770000000001,52.361499999999999,52.686430000000001,52.747190000000003,52.437849999999997,52.34008,52.551780000000001,52.390929999999997,52.3172,52.46396,52.488059999999997,52.371200000000002,52.280450000000002,49.805500000000002,44.524529999999999,41.177190000000003,41.003860000000003,40.333390000000001,38.809229999999999,38.131459999999997,37.649239999999999,37.725960000000001,37.27017,37.692729999999997,37.385530000000003,5729.3209999999999,8773.7810000000009,14503.1,50.266539999999999,37.221510000000002,19,19,284185.99440000003,228421.60446932382,45150.601659019987,64,56,57227.118179214987,44,11.530396729911232,12.137536729911231,204470.9010562191,9926.3051427815972,7831.5781697075363,2102.2571697075364,4.9802689607358223E-2,5729.3189999999995,4576.7948572184032,0.13230521580360355,0.13230521580360355,0.33706753315580257,0.33706753315580257,9429.7746655937026,5073.3253344062978,0.14842661376491348,0.14842661376491348,44,0.36003492472880311]
["2013-04-14T05:00:00","2013-04-14T05:00:00",52.995530000000002,52.602130000000002,52.302549999999997,52.552430000000001,52.269030000000001,49.821339999999999,44.968609999999998,41.753340000000001,40.782550000000001,39.930329999999998,39.354430000000001,37.854179999999999,37.06221,37.169879999999999,37.514960000000002,36.915640000000003,36.79316,37.335160000000002,37.066929999999999,37.053989999999999,37.37518,36.859780000000001,36.957610000000003,36.496650000000002,36.91771,36.636679999999998,5951.2839999999997,8531.5630000000001,14482.85,50.348269999999999,37.32414,37,37,553414.83120000002,473503.50935681717,48678.081131700012,56,52,55558.092807595,44,11.230094964738992,11.83723496473899,387809.82921851036,9894.5009783158621,8669.2198569188822,2717.9358569188826,9.6984185024855479E-2,5951.2870000000003,4588.3490216841383,0.38881804141635018,0.38881804141635018,0.65054114131386964,0.65054114131386964,9387.0051533305959,5095.8448466694044,0.4307759116818024,0.4307759116818024,44,0.67350853288687018]
["2013-04-14T09:00:00","2013-04-14T09:00:00",42.364730000000002,41.063009999999998,40.077849999999998,39.485390000000002,38.268059999999998,37.409439999999996,36.695030000000003,36.902970000000003,36.734769999999997,36.624659999999999,36.822580000000002,36.818199999999997,36.776020000000003,37.04251,37.408209999999997,36.798299999999998,36.671729999999997,37.198050000000002,36.951729999999998,36.96743,37.273269999999997,36.752299999999998,36.828580000000002,36.366779999999999,36.776510000000002,36.501649999999998,5089.9650000000001,9416.0360000000001,14506,51.461019999999998,37.224299999999999,51,51,762815.03760000004,712060.90107499226,14921.435996100008,65,60,67026.734020959993,44,12.107951630114737,12.715091630114735,576334.36086626118,11071.523254891767,2464.733334247489,-2625.2316657525112,0.13368090368290891,5089.9639999999999,3434.4767451082334,0.56342364187305782,0.56342364187305782,0.88798915985289706,0.88798915985289706,10542.862917670564,3963.1370823294365,0.62679160729912409,0.62679160729912409,44,1]
["2013-04-14T16:00:00","2013-04-14T16:00:00",52.786259999999999,52.304380000000002,51.487209999999997,51.573270000000001,50.169510000000002,45.542720000000003,40.919989999999999,39.82508,38.179409999999997,37.396059999999999,37.132739999999998,37.163409999999999,36.92557,37.137920000000001,37.485219999999998,36.881929999999997,36.756250000000001,37.24747,37.01679,37.115879999999997,37.345739999999999,36.826740000000001,36.803730000000002,36.284460000000003,36.622709999999998,36.50197,5323.8360000000002,12679.53,7355.6980000000003,52.28145,36.994500000000002,39,39,583329.14639999997,574368.9493798383,43347.44466822,81,69,96915.670566749992,44,13.674787366326175,14.281927366326176,497758.68739587435,14174.358689540202,6339.7614174187465,1015.9254174187463,0.10222657340457739,-5323.8320000000003,-6818.6606895402019,0.23798637813497353,0.23798637813497353,0.66604306074385622,0.66604306074385622,13571.791548983376,-6216.0935489833755,0.34323877383755586,0.34323877383755586,44,0.76226014294451705]
["2013-04-15T01:00:00","2013-04-15T01:00:00",53.074649999999998,52.618250000000003,52.247680000000003,52.597450000000002,52.644849999999998,52.345750000000002,52.223770000000002,52.438630000000003,52.285240000000002,52.222920000000002,52.317520000000002,52.40202,52.347909999999999,52.542819999999999,52.820030000000003,52.150820000000003,51.57911,50.971200000000003,47.333820000000003,41.872230000000002,40.406219999999998,38.724800000000002,38.014710000000001,36.976570000000002,37.110340000000001,36.812800000000003,4292.5810000000001,11642.43,7349.8490000000002,50.350830000000002,37.065890000000003,13,13,194443.04880000002,164260.25166382189,34902.654167424989,71,67,77334.492002099985,44,12.885375177271611,13.49251517727161,156341.42998659323,12003.452121209408,5417.4059640870137,1124.8249640870135,3.4075524468192467E-2,-4292.5810000000001,-4653.6031212094076,-4.8931746750731253E-2,0,0.1913291611827187,0.1913291611827187,11463.317400208876,-4113.4684002088761,-4.3252333467974524E-2,0,39,0.28754624338337953]
["2013-04-15T04:00:00","2013-04-15T04:00:00",52.807490000000001,52.382719999999999,52.038559999999997,52.36542,52.42436,52.1158,52.014040000000001,52.241370000000003,52.084060000000001,52.019640000000003,52.148389999999999,52.220440000000004,52.181280000000001,52.40014,52.71264,52.114820000000002,51.979610000000001,52.434060000000002,51.992939999999997,50.568449999999999,45.944760000000002,40.9345,39.512680000000003,37.79233,38.033650000000002,37.699680000000001,3250.058,11512.37,14762.43,51.323720000000002,37.214190000000002,9,9,134614.4184,114441.11458156018,24550.62937649,69,66,81217.064943049991,44,12.956923914558004,13.564063914558005,108837.37968550369,12536.473236799204,3789.5768375865296,539.51883758652957,2.3590747708748628E-2,3250.0599999999995,2225.9567632007966,2.3405509618687044E-2,2.3405509618687044E-2,0.16715819202780186,0.16715819202780186,11975.329142452882,2787.1008575471187,2.9305832443828776E-2,2.9305832443828776E-2,44,0.26337527422846269]
["2013-04-15T11:00:00","2013-04-15T11:00:00",52.783410000000003,52.318480000000001,51.990169999999999,52.344169999999998,52.39132,52.109819999999999,51.980789999999999,52.226550000000003,52.079459999999997,52.021529999999998,52.080419999999997,52.190899999999999,52.061709999999998,51.832929999999998,50.156979999999997,44.290570000000002,40.403170000000003,39.579450000000001,38.430950000000003,38.375889999999998,38.475999999999999,37.886000000000003,37.897970000000001,37.405439999999999,37.741370000000003,37.616480000000003,1586.2919999999999,13173.7,14759.99,53.388399999999997,37.832970000000003,19,19,284185.99440000003,279686.70717294817,12029.589861780001,79,70,102461.28409549996,44,13.924739787656549,14.53187978765655,246930.2798549447,14716.437887956195,1727.8010282739381,141.50902827393816,4.9802689607358223E-2,1586.2899999999991,43.5521120438043,8.9395442370958964E-2,8.9395442370958964E-2,0.34854221775121641,0.34854221775121641,14101.587075132715,658.40292486728504,0.13925331331319493,0.13925331331319493,44,0.44475929995187724]
["2013-04-15T20:00:00","2013-04-15T20:00:00",52.786450000000002,52.335369999999998,51.997549999999997,52.341009999999997,52.378570000000003,52.124420000000001,51.960439999999998,52.221550000000001,52.078879999999998,52.027880000000003,52.031350000000003,52.115070000000003,51.54269,49.558689999999999,44.433450000000001,40.479050000000001,39.090260000000001,38.551450000000003,38.295870000000001,38.447609999999997,38.63485,38.004440000000002,37.981769999999997,37.448050000000002,37.766089999999998,37.59122,913.13710000000003,13485.77,14398.91,53.725189999999998,37.337179999999996,21,21,314100.30960000004,316223.54225761176,6937.6641280165004,78,69,110502.46680885,44,14.138097118181786,14.745237118181787,277104.71455528785,15631.872646672136,981.41412808581856,68.277028085818529,5.5045077987080138E-2,913.13999999999942,-1232.9626466721365,-1.2964366407849821E-2,0,0.3941719662957992,0.3941719662957992,14988.225136453539,-589.3151364535388,7.4739731206153404E-2,7.4739731206153404E-2,43,0.49038904849646003]
["2013-04-15T23:00:00","2013-04-15T23:00:00",52.769089999999998,52.339019999999998,51.998609999999999,52.331099999999999,52.393239999999999,52.10501,51.97193,52.224159999999998,52.062890000000003,51.989519999999999,51.925870000000003,51.319600000000001,48.560090000000002,43.016030000000001,40.93282,38.961069999999999,38.080660000000002,38.518630000000002,38.285339999999998,38.405459999999998,38.585120000000003,37.965420000000002,37.953539999999997,37.165860000000002,37.216349999999998,36.961280000000002,2128.9450000000002,12276.46,14405.4,52.425789999999999,36.653060000000004,23,23,344014.62479999999,331969.09857482888,16826.979030224997,75,69,96816.644467899983,44,13.671410576355392,14.278550576355389,293477.50722648704,14163.373110210541,2461.6302664960026,332.68526649600244,6.0287466366802052E-2,2128.9400000000005,242.02688978945844,2.5448664549990985E-3,2.5448664549990985E-3,0.44863930643453448,0.44863930643453448,13561.130585372412,844.26941462758805,8.6030490148257352E-2,8.6030490148257352E-2,43,0.54485638863519537]
["2013-04-16T06:00:00","2013-04-16T06:00:00",52.728940000000001,52.306040000000003,51.972209999999997,52.29956,52.33625,51.850490000000001,50.707970000000003,47.645859999999999,41.969259999999998,40.008229999999998,38.880420000000001,38.393990000000002,38.130929999999999,38.365279999999998,38.698099999999997,38.025910000000003,37.792810000000003,38.292389999999997,37.74371,37.227119999999999,37.380040000000001,36.864429999999999,36.912379999999999,36.421140000000001,36.74973,36.603610000000003,2726.3850000000002,11794.84,14521.23,51.987760000000002,36.451630000000002,35,35,523500.516,502545.29290501529,21981.928916024997,71,65,91623.083784600007,44,13.250922157054861,13.85806215705486,432860.35020970885,13828.936989991958,3317.7960983374583,591.41109833745804,9.1741796645133558E-2,2726.3899999999994,692.29301000804116,6.7048397473252849E-2,6.7048397473252849E-2,0.64906049852177139,0.64906049852177139,13223.073002015153,1298.1569979848464,0.19401002476515553,0.19401002476515553,44,0.74527758072243233]
["2013-04-16T09:00:00","2013-04-16T09:00:00",52.705399999999997,52.281010000000002,51.89367,51.869450000000001,50.194740000000003,45.292569999999998,40.937049999999999,39.726419999999997,38.640790000000003,38.130609999999997,38.098840000000003,38.162280000000003,38.052010000000003,38.271790000000003,38.544640000000001,37.735939999999999,37.207210000000003,37.485210000000002,37.039189999999998,37.096890000000002,37.347149999999999,36.828650000000003,36.875689999999999,36.387430000000002,36.711709999999997,36.574710000000003,2656.8380000000002,11864.74,14521.58,52.313580000000002,36.670090000000002,39,39,583329.14639999997,572890.75598979532,21428.315079109994,73,67,92802.97077130001,44,13.412850303301331,14.019990303301331,488224.24673666258,13837.919409039885,3195.1918637063741,538.35386370637389,0.10222657340457739,2656.84,683.66059096011486,9.0997143533537855E-2,9.0997143533537855E-2,0.7370750204870552,0.7370750204870552,13238.66404521655,1282.9159547834497,0.23685743075272886,0.23685743075272886,44,0.83329210268771614]
["2013-04-16T16:00:00","2013-04-16T16:00:00",52.350169999999999,50.293950000000002,45.325920000000004,41.230249999999998,39.872810000000001,38.662109999999998,38.15372,38.353290000000001,38.114899999999999,38.007919999999999,37.910170000000001,38.009180000000001,37.801909999999999,37.58005,37.653939999999999,36.991210000000002,36.86683,37.353789999999996,37.151240000000001,37.29298,37.49841,36.954799999999999,36.928699999999999,36.398530000000001,36.738210000000002,36.596159999999998,287.52809999999999,14336.37,14613.91,55.329079999999998,38.808579999999999,45,45,673072.09200000006,786776.99278892321,2264.8602813405,86,72,118422.00029249999,44,14.59069420997425,15.19783420997425,612804.75831991457,16232.53816278958,310.45271030246573,22.924610302465737,0.11795373854374315,277.53999999999905,-1618.6281627895805,5.1823386778229938E-2,5.1823386778229938E-2,0.8376902789448617,0.8376902789448617,15584.06265739895,-970.1526573989504,0.24359236296136863,0.24359236296136863,44,0.93390736114552264]
["2013-04-17T01:00:00","2013-04-17T01:00:00",46.733199999999997,41.599420000000002,39.70543,38.950369999999999,38.764879999999998,38.277059999999999,38.06277,38.291609999999999,38.042439999999999,37.866259999999997,37.758859999999999,37.650480000000002,37.193869999999997,37.355150000000002,37.711509999999997,37.093780000000002,36.95458,37.48563,37.246850000000002,37.302379999999999,37.460039999999999,36.907139999999998,36.957529999999998,36.455820000000003,36.792859999999997,36.637169999999998,2332.511,12268.76,14601.27,52.868040000000001,37.057189999999999,49,49,732900.72239999997,742286.46012646263,11774.550515664998,73,69,96989.762023000018,44,13.677313884984301,14.284453884984302,625504.66535210435,14182.574566703575,1721.7635881840424,-610.74741181595755,0.12843851530318698,2332.5100000000002,418.69543329642511,4.4025023995651665E-3,4.4025023995651665E-3,0.92862539418453516,0.92862539418453516,13579.764799402636,1021.5052005973648,0.20534379527783345,0.20534379527783345,43,1]
["2013-04-17T04:00:00","2013-04-17T04:00:00",40.4206,39.121670000000002,38.340620000000001,38.438510000000001,38.50094,38.133769999999998,37.932830000000003,38.118270000000003,37.801929999999999,37.45993,37.286729999999999,37.247019999999999,37.118160000000003,37.362450000000003,37.698839999999997,37.090679999999999,36.933250000000001,37.477580000000003,37.196959999999997,37.16854,37.373989999999999,36.857880000000002,36.905670000000001,36.414470000000001,36.76202,36.581139999999998,2142.8690000000001,12346.55,14489.42,52.812339999999999,36.554679999999998,51,51,762815.03760000004,772599.5745494907,4113.7299053700026,73,70,100363.00603650001,44,13.853188505844653,14.46032850584465,659407.03988426446,14489.51712367978,593.90369280464517,-1548.9653071953549,0.13368090368290891,2142.8700000000008,-9.7123679779542726E-2,1.6571784509661208E-2,1.6571784509661208E-2,1.0018298080457799,1,13881.151592916407,608.26840708359305,0.2364377594433246,0.2364377594433246,44,1]
["2013-04-17T11:00:00","2013-04-17T11:00:00",54.972659999999998,54.52854,54.193379999999998,54.549349999999997,54.548360000000002,54.236989999999999,54.073250000000002,54.052610000000001,53.005000000000003,49.412730000000003,43.209159999999997,39.442509999999999,38.76784,38.735729999999997,38.91666,38.220440000000004,38.042949999999998,38.492150000000002,38.084960000000002,37.985500000000002,38.11242,37.538730000000001,37.329990000000002,36.685310000000001,36.990589999999997,36.788110000000003,6400.38,13802.56,7402.183,54.135280000000002,37.887360000000001,29,29,433757.57040000003,469526.69790098385,58194.015064499981,80,71,112131.4453376,44,14.315339286012161,14.922479286012159,387465.73558070394,15665.915155383869,8130.3018953050805,1729.9218953050804,7.6014631505967808E-2,-6400.3769999999995,-8263.7321553838701,-8.689156305577489E-2,0,0.57762843979137579,0.57762843979137579,15028.527523936096,-7626.3445239360963,-8.0189554020688669E-2,0,40,0.61489310070195602]
["2013-04-17T20:00:00","2013-04-17T20:00:00",56.433630000000001,55.933509999999998,55.522170000000003,55.814779999999999,55.675269999999998,55.282130000000002,55.020940000000003,55.129179999999998,54.90164,54.773879999999998,54.687280000000001,54.70852,54.493040000000001,54.650919999999999,54.905560000000001,54.27299,54.118969999999997,54.501130000000003,54.190249999999999,54.226790000000001,53.045999999999999,47.330620000000003,40.379379999999998,38.758839999999999,38.697650000000003,38.17718,572.27750000000003,13631.25,14195.79,55.529859999999999,38.562370000000001,7,7,104700.1032,113370.02893610633,5223.8777824375002,78,70,115644.04903124999,44,14.374272071965626,14.981412071965625,93911.236808043963,16090.421616102902,726.83719304655619,154.55969304655616,1.834835932902671E-2,564.54000000000087,-1894.6316161029008,-1.9921689067670726E-2,0,0.20669388338832395,0.20669388338832395,15438.337651449032,-1242.547651449031,-1.3065150899808317E-2,0,38,0.24395854429890418]
["2013-04-17T23:00:00","2013-04-17T23:00:00",56.396009999999997,55.912520000000001,55.4938,55.74821,55.636989999999997,55.232669999999999,54.95937,55.110039999999998,54.868699999999997,54.693489999999997,54.648809999999997,54.656329999999997,54.500300000000003,54.64208,54.871850000000002,54.225439999999999,54.068019999999997,54.401420000000002,54.096200000000003,53.776789999999998,51.818489999999997,42.708150000000003,40.041319999999999,38.555120000000002,38.670020000000001,38.302320000000002,1024.1600000000001,13173.37,14197.53,55.294510000000002,38.711889999999997,7,7,104700.1032,111014.84450746611,9265.4167751999976,77,72,109224.49441470004,44,14.277059259541273,14.884199259541271,93276.117658868781,15300.699174685566,1297.9447107089613,273.78471070896126,1.834835932902671E-2,1024.1599999999999,-1103.1691746855649,-1.1599612874786497E-2,0,0.23605133452610039,0.23605133452610039,14676.569765039052,-479.03976503905142,-5.0370115061141845E-3,0,38,0.27331599543668061]
["2013-04-18T05:00:00","2013-04-18T05:00:00",56.029949999999999,55.578029999999998,55.144089999999998,55.3735,55.381549999999997,54.833440000000003,54.708570000000002,54.838760000000001,54.530679999999997,54.288730000000001,54.548349999999999,54.388460000000002,54.302900000000001,54.454180000000001,54.615020000000001,53.724249999999998,52.872120000000002,49.419449999999998,42.092100000000002,39.931060000000002,39.172910000000002,37.951140000000002,38.057400000000001,37.625929999999997,38.011670000000002,37.642749999999999,5353.6260000000002,8707.7420000000002,12081.7,51.984209999999997,38.409320000000001,13,13,194443.04880000002,174008.46569453867,49219.0959936,50,49,59103.319899189984,44,11.168446208562379,11.775586208562379,135509.50802386418,10583.982551463238,8813.9558671761843,3460.3298671761841,3.4075524468192467E-2,3373.9580000000005,1497.7174485367632,1.963680955444045E-2,1.963680955444045E-2,0.37912274092630494,0.37912274092630494,10038.280702529137,2043.419297470864,3.6112730514997665E-2,3.6112730514997665E-2,44,0.41638740183688516]
["2013-04-18T08:00:00","2013-04-18T08:00:00",55.371600000000001,54.983260000000001,54.546709999999997,54.796039999999998,54.847700000000003,54.268520000000002,54.256439999999998,54.407499999999999,54.057859999999998,53.688360000000003,53.730789999999999,52.361139999999999,47.808109999999999,41.308929999999997,39.36242,38.580770000000001,38.49841,39.003509999999999,38.6813,38.525550000000003,38.90428,38.408659999999998,38.605130000000003,38.199089999999998,38.600540000000002,38.203560000000003,7152.5129999999999,7387.8850000000002,14540.4,50.175379999999997,36.929340000000003,25,25,373928.94,279340.46165817772,61397.314642259989,47,46,48930.110112699978,44,10.638998754843071,11.24613875484307,248241.52248853084,9198.2546929852924,11541.934735975185,4389.4217359751847,6.5529854746523966E-2,7152.5149999999994,5342.1453070147072,0.1685976264626142,0.1685976264626142,0.59658432668367223,0.59658432668367223,8701.6728460030026,5838.727153996997,0.20159508711409946,0.20159508711409946,44,0.63384898759425246]
["2013-04-18T15:00:00","2013-04-18T15:00:00",54.440750000000001,53.805149999999998,53.378320000000002,53.481369999999998,51.289650000000002,39.790390000000002,38.84601,39.040239999999997,38.805660000000003,38.658430000000003,38.931220000000003,38.88476,38.832189999999997,39.134799999999998,39.482239999999997,38.911059999999999,38.797049999999999,39.256169999999997,38.967680000000001,38.920920000000002,39.224550000000001,38.703850000000003,38.819020000000002,38.404060000000001,38.804850000000002,38.450150000000001,764.98009999999999,7766.8029999999999,7001.8220000000001,50.863,39.00018,41,41,613243.46160000004,474994.98398486531,6116.24539353,56,47,46068.092982230002,44,10.602250970694044,11.209390970694043,405709.89176767145,8690.2475916799194,1153.7635565194735,388.78345651947348,0.10746896178429931,-764.98099999999977,-1688.4255916799193,0.33665990713811961,0.33665990713811961,0.844177505857163,0.844177505857163,8219.5532482845738,-1217.7312482845737,0.40402032940672228,0.40402032940672228,44,0.88144216676774323]
["2013-04-19","2013-04-19",53.634590000000003,53.29569,52.947580000000002,53.299529999999997,53.42586,52.934229999999999,50.011960000000002,39.81382,39.126710000000003,38.8401,39.146909999999998,38.897599999999997,38.864820000000002,39.187919999999998,39.536099999999998,38.976010000000002,38.87565,39.349539999999998,39.035339999999998,38.902790000000003,39.247309999999999,38.74691,38.8964,38.494340000000001,38.887039999999999,38.49897,183.66380000000001,7136.357,6995.9340000000002,49.762210000000003,38.897150000000003,37,37,553414.83120000002,388954.42955398158,1389.9327422780004,44,40,38768.473493209996,44,9.927404946118461,10.534544946118462,342823.92346863612,7810.3942981329019,280.01935043889864,96.355550438898632,9.6984185024855479E-2,-140.42299999999977,-814.4602981329017,0.15840396060229986,0.15840396060229986,0.7893187940224814,0.7893187940224814,7360.2559372997985,-364.32193729979826,0.27221456918942638,0.27221456918942638,44,0.82658345493306162]
["2013-04-19T03:00:00","2013-04-19T03:00:00",53.52863,53.163089999999997,52.839759999999998,53.197859999999999,53.332210000000003,52.794829999999997,50.694220000000001,40.277949999999997,39.129669999999997,38.873939999999997,39.242060000000002,38.95881,38.889159999999997,39.209670000000003,39.555340000000001,38.99465,38.8932,39.402839999999998,39.058459999999997,38.889879999999998,39.240560000000002,38.741370000000003,38.917810000000003,38.523000000000003,38.904859999999999,38.519640000000003,405.63029999999998,6967.4620000000004,7372.9579999999996,49.027560000000001,38.593510000000002,37,37,553414.83120000002,362870.89943913766,3044.0505581984994,42,38,36349.423440550003,44,9.7232213393227571,10.330361339322756,335772.83352422423,7476.8273130932985,626.1403401129453,220.51004011294532,9.6984185024855479E-2,405.49599999999919,-103.86931309329884,0.14629931535575544,0.14629931535575544,0.79226318230903969,0.79226318230903969,7037.3963207240558,335.56167927594379,0.27402218481262341,0.27402218481262341,44,0.82952784321961992]
["2013-04-19T10:00:00","2013-04-19T10:00:00",53.509030000000003,53.164700000000003,52.84966,53.193530000000003,53.313189999999999,52.56964,45.834020000000002,39.626869999999997,39.33643,39.104610000000001,39.414110000000001,39.2804,39.234999999999999,39.560960000000001,39.898220000000002,39.323149999999998,39.234259999999999,39.727600000000002,39.413379999999997,39.30639,39.612119999999997,39.097819999999999,39.192169999999997,38.778109999999998,39.135599999999997,38.665509999999998,137.79390000000001,7433.5450000000001,7405.4350000000004,49.78143,39.064909999999998,37,37,553414.83120000002,383867.01540300081,1022.6732552640003,50,40,39830.866831700012,44,9.9636325589609722,10.570772558960972,344074.97471918754,7995.2500447996563,205.28120626934216,67.487306269342156,9.6984185024855479E-2,-28.109999999999673,-589.81504479965588,0.12617396952560356,0.12617396952560356,0.81590731748706991,0.81590731748706991,7536.0370511301762,-130.60205113017582,0.28703383482814981,0.28703383482814981,44,0.85317197839765013]
["2013-04-19T19:00:00","2013-04-19T19:00:00",52.831829999999997,52.431049999999999,52.118160000000003,52.482390000000002,52.532910000000001,52.198709999999998,52.134,52.361539999999998,52.24192,52.005099999999999,42.611620000000002,39.711419999999997,39.506410000000002,39.674840000000003,39.9711,39.392530000000001,39.294269999999997,39.782600000000002,39.519219999999997,39.45908,39.738660000000003,39.217829999999999,39.329239999999999,38.893349999999998,39.287100000000002,38.893770000000004,1824.2550000000001,9225.5409999999993,7401.2860000000001,51.013339999999999,38.174019999999999,29,29,433757.57040000003,328034.00681954611,12713.287822649992,56,45,59224.836536060007,44,10.929201925879648,11.536341925879647,295814.94220390677,10837.906909894198,2326.4805443013629,502.22554430136279,7.6014631505967808E-2,-1824.2549999999992,-3436.6209098941981,-3.6135411564170536E-2,0,0.68264011853326934,0.68264011853326934,10267.524474669053,-2866.2384746690532,9.2143935635183138E-2,9.2143935635183138E-2,42,0.71990477944384956]
["2013-04-19T20:00:00","2013-04-19T20:00:00",52.790930000000003,52.412619999999997,52.132530000000003,52.467289999999998,52.51867,52.167929999999998,52.108040000000003,52.332790000000003,52.213970000000003,52.105829999999997,50.309379999999997,40.03546,39.605449999999998,39.758890000000001,40.025390000000002,39.422269999999997,39.323790000000002,39.802990000000001,39.525469999999999,39.471290000000003,39.761049999999997,39.230339999999998,39.333289999999998,38.912570000000002,39.29674,38.910049999999998,1522.4670000000001,8917.1020000000008,7394.634,50.729660000000003,38.13035,29,29,433757.57040000003,319915.1477605541,10566.590865480004,57,44,56174.66619981001,44,10.764344117413522,11.371484117413521,291352.82288229448,10437.173986092852,1963.2577238749527,440.79072387495262,7.6014631505967808E-2,-1522.4680000000008,-3042.5399860928519,-3.1991726024065796E-2,0,0.66663165870725571,0.66663165870725571,9879.9181566437619,-2485.2841566437619,6.6011648074551482E-2,6.6011648074551482E-2,42,0.70389631961783594]
["2013-04-20T05:00:00","2013-04-20T05:00:00",52.609650000000002,52.265900000000002,51.950659999999999,52.293959999999998,52.377850000000002,51.906799999999997,51.91977,52.148260000000001,51.961080000000003,51.758879999999998,52.101689999999998,51.1126,39.999940000000002,40.105640000000001,40.377459999999999,39.757599999999996,39.661920000000002,40.133659999999999,39.823219999999999,39.705039999999997,40.045560000000002,39.561430000000001,39.602420000000002,39.038359999999997,39.394930000000002,38.993560000000002,355.00670000000002,7039.125,7394.1310000000003,48.99098,37.559240000000003,27,27,403843.25520000001,251933.17571145881,2416.9015889015004,44,39,40234.723413749991,44,9.916557068408876,10.523697068408875,249895.44446148732,8114.6557492066559,487.44772449321368,132.44102449321366,7.0772243126245887E-2,355.00600000000031,-720.52474920665554,-7.5761799271467593E-3,0,0.65312291590637339,0.65312291590637339,7646.4997333552592,-252.36873335525888,-2.6536089620665926E-3,0,41,0.69038757681695362]
["2013-04-20T08:00:00","2013-04-20T08:00:00",52.64611,52.283630000000002,51.951810000000002,52.284280000000003,52.37379,51.9191,51.912840000000003,52.135289999999998,51.953949999999999,51.765430000000002,52.089060000000003,48.788209999999999,39.978810000000003,40.178910000000002,40.481990000000003,39.896279999999997,39.794640000000001,40.273359999999997,39.979219999999998,39.876829999999998,40.20917,39.714379999999998,39.743009999999998,39.312530000000002,39.59263,39.108409999999999,193.06209999999999,7296.97,7402.3789999999999,49.474850000000004,37.965519999999998,27,27,403843.25520000001,261232.41296477459,1306.808395585,52,43,41991.617865050015,44,10.219855169198206,10.826995169198206,257538.50174217677,8217.6541976072731,255.73912231625587,62.677022316255886,7.0772243126245887E-2,105.40899999999965,-815.27519760727318,-8.5724627696879899E-3,0,0.66126953735927718,0.66126953735927718,7756.8369079007743,-354.45790790077444,-3.7270571063840931E-3,0,41,0.69853419826985741]
["2013-04-20T15:00:00","2013-04-20T15:00:00",52.137500000000003,51.684600000000003,51.358890000000002,51.713659999999997,51.751240000000003,51.449599999999997,51.320059999999998,51.582140000000003,51.440559999999998,51.346469999999997,51.478070000000002,51.542360000000002,51.500830000000001,51.723770000000002,52.018590000000003,51.383569999999999,48.315899999999999,40.592320000000001,40.125419999999998,40.155119999999997,40.331240000000001,39.820059999999998,39.872929999999997,39.432130000000001,39.814250000000001,39.482170000000004,3162.6,10561.6,7398.9989999999998,50.21904,38.412100000000002,17,17,254271.67920000001,170357.11456933123,20011.873328999998,70,51,62350.088751999989,44,11.400855026443201,12.007995026443199,180892.26803790312,10937.791702005661,3510.5916674818441,347.99166748184416,4.4560301227636302E-2,-3162.6010000000006,-3538.7927020056613,-3.7209728416392175E-2,0,0.47410310286791491,0.47410310286791491,10384.762587708741,-2985.7635877087414,-3.13947330543628E-2,0,40,0.51136776377849513]
["2013-04-21","2013-04-21",52.642359999999996,52.027920000000002,51.37706,51.678550000000001,51.752920000000003,51.392049999999998,51.331800000000001,51.55592,51.401649999999997,51.284390000000002,51.522849999999998,51.482810000000001,51.470460000000003,51.711559999999999,52.020969999999998,51.426650000000002,51.322620000000001,51.839779999999998,51.48292,51.502890000000001,48.553429999999999,40.355969999999999,40.142040000000001,39.664790000000004,40.015120000000003,39.639110000000002,495.98950000000002,7896.7939999999999,7400.8050000000003,50.347180000000002,38.044499999999999,9,9,134614.4184,89947.142390756839,3224.7377329374985,56,46,48575.864803960008,44,10.626918989815037,11.234058989815036,89265.478797946882,9142.0410469893832,606.89984294189594,110.91034294189592,2.3590747708748628E-2,-495.98899999999958,-1741.2360469893829,-1.8308763997559405E-2,0,0.35112234151874872,0.35112234151874872,8647.9632780991469,-1247.1582780991466,-1.3113630757185368E-2,0,39,0.38838700242932894]
["2013-04-21T03:00:00","2013-04-21T03:00:00",52.371000000000002,51.820529999999998,51.464869999999998,51.750329999999998,51.809559999999998,51.399039999999999,51.361789999999999,51.585949999999997,51.414960000000001,51.282330000000002,51.582000000000001,51.505479999999999,51.492980000000003,51.747900000000001,52.059579999999997,51.474769999999999,51.404530000000001,51.849559999999997,51.53416,51.559519999999999,51.444609999999997,42.075330000000001,40.505499999999998,39.757890000000003,40.085279999999997,39.636299999999999,569.34019999999998,7968.5339999999997,7399.1940000000004,49.321959999999997,38.061700000000002,9,9,134614.4184,81358.960033736977,3625.1883224700009,53,47,44863.882329419976,44,10.561187387433222,11.168327387433221,88713.337301018895,8495.9921046005875,686.51150471652841,117.17130471652843,2.3590747708748628E-2,-569.33999999999924,-1096.7981046005871,-1.1532622291402094E-2,0,0.33158765646479454,0.33158765646479454,8034.1273626884413,-634.93336268844087,-6.6762028684961726E-3,0,39,0.36885231737537477]
["2013-04-21T10:00:00","2013-04-21T10:00:00",52.063070000000003,51.65504,51.356670000000001,51.678570000000001,51.79081,51.401519999999998,51.352919999999997,51.583150000000003,51.401220000000002,51.202660000000002,51.381399999999999,51.188420000000001,48.755659999999999,42.272959999999998,39.310180000000003,38.462299999999999,38.382429999999999,38.865090000000002,38.61739,38.595359999999999,38.887140000000002,38.399079999999998,38.500630000000001,38.062089999999998,38.461019999999998,38.126899999999999,5631.7640000000001,8848.6839999999993,14480.45,50.174770000000002,37.251240000000003,23,23,344014.62479999999,258625.75300780463,39242.610251940016,63,55,57178.116567259996,44,11.467878774943566,12.075018774943565,246175.3640744795,9971.8732102731647,6843.9178721843655,1212.1538721843654,6.0287466366802052E-2,5631.7660000000014,4508.5767897268361,0.27787577822050857,0.27787577822050857,0.66899817413532492,0.66899817413532492,9470.4807724039729,5009.9692275960278,{"$f":"IF(BF2621>1,1+BE2622*60/$BK$7,IF(BF2621<0,BE2622*60/$BK$7,BF2621+BE2622*60/$BK$7))","v":0.3088168885141927},0.3088168885141927,44,0.70626283504590515]
["2013-04-21T19:00:00","2013-04-21T19:00:00",39.602670000000003,38.451860000000003,37.960030000000003,38.226999999999997,38.345939999999999,38.020389999999999,37.908540000000002,38.178339999999999,38.026949999999999,37.962330000000001,38.077030000000001,38.134779999999999,38.106400000000001,38.353319999999997,38.719670000000001,38.106270000000002,37.971690000000002,38.52064,38.283839999999998,38.31861,38.636650000000003,38.139229999999998,38.196559999999998,37.762149999999998,38.172080000000001,37.84816,3121.183,8974.6280000000006,10064.379999999999,52.467129999999997,37.64564,51,51,762815.03760000004,695857.97737393202,2738.0733926650055,65,56,66508.679577859992,44,11.846897973605028,12.454037973605026,563908.2960063623,11228.032810958919,462.24309498831713,-2658.9399050116826,0.13368090368290891,1089.7519999999986,-1163.6528109589199,0.55322965707330163,0.55322965707330163,1.0114585338491962,1,10680.661118717942,-616.28111871794317,0.63537287219929761,0.63537287219929761,44,1]
["2013-04-21T23:00:00","2013-04-21T23:00:00",43.425249999999998,39.047620000000002,38.353529999999999,38.474249999999998,38.508420000000001,38.108159999999998,38.020449999999997,38.274630000000002,38.124549999999999,38.033290000000001,38.229970000000002,38.20543,38.19294,38.427259999999997,38.792310000000001,38.157240000000002,38.051810000000003,38.56917,38.304389999999998,38.324539999999999,38.65625,38.153869999999998,38.244709999999998,37.80894,38.220939999999999,37.886539999999997,1227.104,8526.4480000000003,7299.3450000000003,50.383600000000001,37.51773,49,49,732900.72239999997,571528.10843707155,3398.286597920001,59,53,54850.085764880001,44,11.266798924582409,11.873938924582408,515264.57242802816,9736.5873185516102,603.2390602987449,-623.86493970125514,0.12843851530318698,-1227.1030000000001,-2437.24231855161,0.42227418018658724,0.42227418018658724,0.94696515534416281,0.94696515534416281,9238.7346967609592,-1939.3896967609589,0.52643086147230578,0.52643086147230578,44,0.98709724665616572]
["2013-04-22T04:00:00","2013-04-22T04:00:00",50.848820000000003,49.621879999999997,39.12679,38.866810000000001,38.855719999999998,38.356879999999997,38.165599999999998,38.351109999999998,38.191969999999998,38.075139999999998,38.314749999999997,38.264060000000001,38.2532,38.516930000000002,38.867989999999999,38.245869999999996,38.156649999999999,38.647539999999999,38.390790000000003,38.367489999999997,38.677030000000002,38.174210000000002,38.282089999999997,37.854550000000003,38.24586,37.90287,1148.5239999999999,8442.4940000000006,7293.97,49.32152,37.432250000000003,47,47,702986.40720000002,500894.51808703505,7434.3671389000019,55,50,50187.545319689983,44,10.925265295401431,11.532405295401428,479251.53105779656,9187.4282157366924,1360.9494942020699,212.42549420207001,0.12319612692346506,-1148.5240000000003,-1893.4582157366922,0.31806940569321657,{"$f":"IF(AZ2640>1,1,IF(AZ2640<0,0,AZ2640))","v":0.31806940569321657},0.88782100703159794,{"$f":"IF(BB2640>1,1,BB2640)","v":0.88782100703159794},8703.742893896102,-1409.7728938961018,0.44776853418521773,0.44776853418521773,44,0.92795309834360085]
["2013-04-22T07:00:00","2013-04-22T07:00:00",50.818539999999999,50.399340000000002,49.658949999999997,39.888660000000002,39.066319999999997,38.50226,38.352710000000002,38.444049999999997,38.232349999999997,38.105930000000001,38.359409999999997,38.311500000000002,38.292259999999999,38.564239999999998,38.913879999999999,38.282260000000001,38.193469999999998,38.700470000000003,38.426749999999998,38.393729999999998,38.706299999999999,38.190689999999996,38.301459999999999,37.873579999999997,38.268979999999999,37.923789999999997,1432.846,8733.3940000000002,7300.5469999999996,49.916780000000003,37.438879999999997,45,45,673072.09200000006,503701.96460282936,9238.0954792500015,57,54,54487.208496300023,44,11.315271809723832,11.922411809723831,475238.00491561345,9630.7378934505468,1632.8543643664309,200.0083643664309,0.11795373854374315,-1432.8470000000007,-2330.1908934505473,0.24365600293741491,0.24365600293741491,0.84298042642704529,0.84298042642704529,9140.2996920238329,-1839.7526920238333,0.38915719232399598,0.38915719232399598,44,0.8831125177390482]
["2013-04-22T14:00:00","2013-04-22T14:00:00",51.857770000000002,51.356299999999997,50.997590000000002,51.146000000000001,51.001449999999998,50.492570000000001,50.163640000000001,50.28942,47.929580000000001,40.040129999999998,38.833199999999998,38.749220000000001,38.54748,38.670189999999998,39.012819999999998,38.377789999999997,38.234769999999997,38.763219999999997,38.521680000000003,38.597230000000003,38.806249999999999,38.316299999999998,38.335050000000003,37.856499999999997,38.227809999999998,38.015270000000001,4269.3149999999996,11582.91,7313.59,51.439869999999999,37.619709999999998,33,33,493586.20079999999,413474.71222260396,29548.996443750002,76,63,80038.834732800009,44,12.734205264388482,13.341345264388481,392210.7069913887,12570.683928997214,4640.8858393989449,371.57083939894528,8.6499408265411637E-2,-4269.32,-5257.0939289972139,-5.527733716828985E-2,0,0.59936510454630521,0.59936510454630521,11998.615304027018,-4685.0253040270181,0.1238521578421492,0.1238521578421492,43,0.63949719585830811]
["2013-04-22T23:00:00","2013-04-22T23:00:00",52.445659999999997,51.982170000000004,51.62567,51.95872,52.011789999999998,51.697130000000001,51.578949999999999,51.81026,51.656730000000003,51.59599,51.685409999999997,51.721870000000003,51.636339999999997,51.686149999999998,51.658630000000002,50.872160000000001,50.630450000000003,50.789729999999999,50.409709999999997,50.300049999999999,44.687809999999999,39.291679999999999,39.067279999999997,38.257309999999997,38.599580000000003,38.195230000000002,3612.9229999999998,10916.95,7304.0290000000005,49.786630000000002,37.683709999999998,9,9,134614.4184,97367.061133165815,25742.85315344499,69,61,66063.486247000023,44,12.135951881022702,12.743091881022702,101941.26410172164,10887.23602312649,4242.4118694306535,629.48886943065372,2.3590747708748628E-2,-3612.9210000000003,-3583.2070231264897,-3.7676736508097518E-2,0,0.16210965382074433,0.16210965382074433,10368.517603703895,-3064.4886037038941,-3.2222511540255891E-2,0,39,0.20224174513274723]
["2013-04-23T06:00:00","2013-04-23T06:00:00",52.007449999999999,51.614570000000001,51.298630000000003,51.631230000000002,51.715580000000003,51.381320000000002,51.299849999999999,51.514710000000001,51.345799999999997,51.271050000000002,51.430929999999996,51.425530000000002,51.355759999999997,51.390689999999999,51.317450000000001,50.370719999999999,50.031979999999997,49.71837,44.148000000000003,38.292369999999998,37.033389999999997,36.510530000000003,36.612490000000001,36.133420000000001,36.471209999999999,36.255780000000001,4594.6710000000003,9984.4719999999998,14579.14,51.216540000000002,36.788870000000003,13,13,194443.04880000002,181522.58509414151,36186.870675284998,65,61,72026.333570119998,44,12.339284974741092,12.946424974741094,149715.58308724299,11674.312363732612,5865.3107938362182,1270.6397938362179,3.4075524468192467E-2,4594.6679999999997,2904.8276362673878,0.13724419968907939,0.13724419968907939,0.2664588260086363,0.2664588260086363,11126.829794425221,3452.3102055747786,0.15970703238692105,0.15970703238692105,44,0.3065909173206392]
["2013-04-23T09:00:00","2013-04-23T09:00:00",51.974719999999998,51.604930000000003,51.300719999999998,51.630249999999997,51.736699999999999,51.342739999999999,51.290059999999997,51.490299999999998,51.24353,50.875529999999998,50.742260000000002,50.393459999999997,50.066830000000003,48.461979999999997,42.709389999999999,37.632240000000003,36.303130000000003,36.538150000000002,36.248829999999998,36.205750000000002,36.538029999999999,35.998019999999997,36.129689999999997,35.660209999999999,36.028750000000002,35.733879999999999,5613.1549999999997,8916.6509999999998,14529.81,51.22925,36.170659999999998,21,21,314100.30960000004,303707.07209647284,45581.176125099992,52,50,67136.095791045009,44,11.503210866474635,12.110350866474636,225461.31470015508,11672.583693429253,7924.9483738394092,2311.7933738394095,5.5045077987080138E-2,5613.1589999999997,2857.2263065707466,0.22304177246849699,0.22304177246849699,0.41993790575819617,0.41993790575819617,11087.390700941525,3442.4192990584743,0.26328067151721474,0.26328067151721474,44,0.46006999707019908]
["2013-04-23T18:00:00","2013-04-23T18:00:00",51.832470000000001,51.394359999999999,50.697000000000003,50.698340000000002,50.610990000000001,49.751660000000001,45.068660000000001,36.833199999999998,36.40334,36.212589999999999,36.584780000000002,36.401969999999999,36.37697,36.689630000000001,37.049550000000004,36.462060000000001,36.373010000000001,36.896509999999999,36.571429999999999,36.401299999999999,36.76885,36.209960000000002,36.394089999999998,35.94988,36.328769999999999,35.978290000000001,186.00550000000001,7183.33,7338.2290000000003,49.23809,37.839869999999998,37,37,553414.83120000002,457901.80667373538,1474.482338995,46,42,40938.587836300008,44,10.123099845217832,10.730239845217831,349581.87214466708,8088.1525347474389,291.31044078194043,105.30494078194042,9.6984185024855479E-2,154.89900000000034,-749.92353474743868,0.30284147226548747,0.30284147226548747,0.64569194285082088,0.64569194285082088,7630.5075052996499,-292.27850529964962,0.38867187370568634,0.38867187370568634,44,0.68582403416282378]
["2013-04-23T19:00:00","2013-04-23T19:00:00",51.833219999999997,51.385039999999996,50.677100000000003,50.638800000000003,50.587780000000002,49.660089999999997,43.648800000000001,36.895040000000002,36.451360000000001,36.207439999999998,36.572989999999997,36.410159999999998,36.391379999999998,36.71358,37.073410000000003,36.487139999999997,36.391950000000001,36.912869999999998,36.594209999999997,36.424959999999999,36.781059999999997,36.23075,36.423960000000001,35.962769999999999,36.331470000000003,35.962470000000003,327.68970000000002,7011.3980000000001,7335.7790000000005,49.666809999999998,37.917409999999997,37,37,553414.83120000002,473253.14448718209,2600.340653137499,46,42,41189.859830600006,44,10.13166822022346,10.738808220223461,349877.76457104873,8130.913672909739,513.30947611313445,185.61977611313444,9.6984185024855479E-2,324.38100000000031,-795.13467290973858,0.29448078326082794,0.29448078326082794,0.6491027470232712,0.6491027470232712,7671.2162068470006,-335.4372068470002,0.38514481563289898,0.38514481563289898,44,0.6892348383352741]
["2013-04-24T04:00:00","2013-04-24T04:00:00",51.162219999999998,50.582599999999999,50.03989,49.819589999999998,39.3309,36.58249,36.619759999999999,36.82479,36.616869999999999,36.391979999999997,36.83616,36.582520000000002,36.61148,36.91357,37.286349999999999,36.727829999999997,36.653449999999999,37.164490000000001,36.841430000000003,36.579059999999998,36.997100000000003,36.466349999999998,36.699190000000002,36.25121,36.568219999999997,36.182450000000003,963.86739999999998,6368.4250000000002,7332.2929999999997,47.460149999999999,37.861069999999998,41,41,613243.46160000004,431556.88910170621,7219.2559812489981,40,36,30565.510524500001,44,9.4042959088854516,10.011435908885449,359868.47376951942,6500.3293857695016,1535.3102563325417,571.44285633254174,0.10746896178429931,963.86799999999948,831.96361423049802,0.33299006927493963,0.33299006927493963,0.72589708482377657,0.72589708482377657,6106.1192026155204,1226.1737973844793,0.46231178952601404,0.46231178952601404,44,0.76602917613577948]
["2013-04-24T07:00:00","2013-04-24T07:00:00",50.836530000000003,50.38156,49.582099999999997,41.081040000000002,37.226320000000001,36.509189999999997,36.579259999999998,36.78546,36.579070000000002,36.384300000000003,36.861980000000003,36.617400000000004,36.654159999999997,36.965530000000001,37.324939999999998,36.755609999999997,36.676450000000003,37.174779999999998,36.83419,36.562370000000001,36.984810000000003,36.431469999999997,36.409590000000001,35.928959999999996,36.267429999999997,36.055840000000003,962.67880000000002,6359.3630000000003,7322.0420000000004,46.900669999999998,35.990810000000003,43,43,643157.77679999999,435236.05336061394,7114.5284561859999,38,35,34689.880009589986,44,9.4840899083270198,10.091229908327019,380625.40965764155,7315.3840473680684,1500.3081001877581,537.62930018775808,0.11271135016402123,962.67900000000009,6.6579526319319484,0.32739078806992422,0.32739078806992422,0.75621469572124089,0.75621469572124089,6875.2531306347119,446.78886936528852,0.47089335963442996,0.47089335963442996,44,0.7963467870332438]
["2013-04-24T14:00:00","2013-04-24T14:00:00",50.216270000000002,49.738669999999999,49.420490000000001,49.781410000000001,49.87106,49.535159999999998,49.514229999999998,49.612189999999998,45.106650000000002,39.055520000000001,36.958190000000002,36.773739999999997,36.69426,36.986310000000003,37.37133,36.774850000000001,36.669420000000002,37.138260000000002,36.871670000000002,36.830750000000002,37.128039999999999,36.546550000000003,36.686230000000002,36.250529999999998,36.546709999999997,36.04786,7700.4639999999999,7700.4639999999999,0,49.122210000000003,36.576079999999997,31,31,463671.88560000004,378281.81149164814,54551.665571120007,57,46,48305.511202160022,44,10.617699931993657,11.224839931993657,307203.24636783538,9099.0537520473754,10275.608826868964,2575.1448268689637,8.125701988568973E-2,-7700.4639999999999,-9099.0537520473754,4.7048162825934353E-3,4.7048162825934353E-3,0.51577700161443119,0.51577700161443119,8606.8953312157264,-8606.8953312157264,0.181609683966657,0.181609683966657,43,0.55590909292643409]
["2013-04-24T23:00:00","2013-04-24T23:00:00",51.11121,50.697090000000003,50.394460000000002,50.728070000000002,50.842170000000003,50.437280000000001,50.407209999999999,50.633279999999999,50.417589999999997,50.221870000000003,50.405029999999996,50.288980000000002,50.197809999999997,50.326079999999997,50.50712,49.79101,49.620600000000003,50.035420000000002,49.78284,49.794899999999998,49.869149999999998,46.721400000000003,40.757710000000003,37.159759999999999,37.411110000000001,36.945569999999996,5084.5870000000004,7714.2020000000002,12618.98,50.367750000000001,38.751449999999998,5,5,74785.788,62636.390417817238,36013.214495340013,54,46,44805.242346300016,44,10.498340764008832,11.105480764008831,48991.905251884767,8535.6807048794944,6860.7440556326974,1776.1570556326969,1.3105970949304794E-2,4904.7779999999993,4083.2992951205051,4.2935111098247235E-2,4.2935111098247235E-2,0.12168498795567458,0.12168498795567458,8069.0324531481729,4549.9475468518267,4.7841828211986473E-2,4.7841828211986473E-2,44,0.16181707926767747]
["2013-04-25T06:00:00","2013-04-25T06:00:00",50.702390000000001,50.18141,49.701520000000002,49.885480000000001,49.936,49.461129999999997,49.413620000000002,49.604529999999997,49.122239999999998,44.364649999999997,39.134909999999998,38.310929999999999,38.128169999999997,38.412080000000003,38.761420000000001,38.185920000000003,38.098089999999999,38.601990000000001,38.330500000000001,38.253160000000001,38.580089999999998,38.041110000000003,38.206989999999998,37.78246,38.174959999999999,37.82011,6573.2560000000003,8013.3310000000001,14586.59,48.881210000000003,37.835380000000001,31,31,463671.88560000004,320032.19625375408,42339.262151840005,50,43,44256.945979865006,44,10.297102857913398,10.904242857913395,297927.37093678128,8595.9995914488172,8223.5290325961869,1650.2730325961866,8.125701988568973E-2,6573.259,5990.5904085511829,0.47822695239263624,0.47822695239263624,0.5975021433085822,0.5975021433085822,8117.3808317643961,6469.209168235604,0.5179027329750876,0.5179027329750876,44,0.63763423462058511]
["2013-04-25T09:00:00","2013-04-25T09:00:00",50.146709999999999,49.665129999999998,49.264969999999998,48.616759999999999,42.6068,38.366329999999998,38.196849999999998,38.463039999999999,38.244959999999999,38.075899999999997,38.299100000000003,38.200189999999999,38.143340000000002,38.436750000000004,38.765129999999999,38.008690000000001,37.751899999999999,38.083880000000001,37.806530000000002,37.74192,38.068440000000002,37.525669999999998,37.665579999999999,37.233170000000001,37.621589999999998,37.275120000000001,6181.5820000000003,8396.7019999999993,14578.28,49.736899999999999,36.839120000000001,41,41,613243.46160000004,476867.35854561313,39783.39452768999,59,48,54149.40756077999,44,10.938670797822599,11.545810797822597,418583.46475043683,9900.5461562219643,7273.8992265146317,1092.3172265146313,0.10746896178429931,6181.5780000000013,4677.7338437780363,0.64372738148475572,0.64372738148475572,0.80082356148568801,0.80082356148568801,9379.9229017319303,5198.3570982680703,0.69921941108193042,0.69921941108193042,44,0.84095565279769091]
["2013-04-25T18:00:00","2013-04-25T18:00:00",52.145769999999999,50.215989999999998,49.727589999999999,49.87527,43.004300000000001,38.582360000000001,38.193809999999999,38.450369999999999,38.273000000000003,38.153869999999998,38.202590000000001,38.231839999999998,38.13438,38.357509999999998,38.653910000000003,38.007919999999999,37.803249999999998,38.234110000000001,37.931649999999998,37.907919999999997,38.191180000000003,37.592410000000001,37.483580000000003,36.980620000000002,37.351410000000001,37.005159999999997,2021.8,9415.9140000000007,7394.1139999999996,53.216360000000002,38.569580000000002,41,41,613243.46160000004,620344.13405265112,15305.642649000001,71,56,68956.410428460003,44,11.930365595610487,12.537505595610487,456532.04663075699,11559.815141596497,2565.8296095521791,544.02960955217918,0.10746896178429931,-2021.8000000000011,-4165.7011415964971,0.45933107607781931,0.45933107607781931,0.76560938291182112,0.76560938291182112,11000.020682360035,-3605.9066823600351,0.56684664442955768,0.56684664442955768,44,0.80574147422382403]
["2013-04-25T23:00:00","2013-04-25T23:00:00",53.282519999999998,52.734610000000004,52.066119999999998,51.37941,50.273040000000002,49.815519999999999,48.293120000000002,39.76482,38.541020000000003,38.369259999999997,38.422910000000002,38.361759999999997,38.271949999999997,38.501089999999998,38.814990000000002,38.156820000000003,37.975589999999997,38.519240000000003,38.188569999999999,38.115369999999999,38.400570000000002,37.802460000000004,37.729669999999999,37.25759,37.585259999999998,37.199060000000003,2388.5300000000002,9797.5409999999993,7409.01,49.592129999999997,38.518729999999998,37,37,553414.83120000002,427970.94550702639,19207.913356899997,64,52,54246.045254699995,44,11.185354143185272,11.792494143185271,386264.79060393735,9699.4774703221447,3434.4756743535927,1045.9456743535925,9.6984185024855479E-2,-2388.530999999999,-2290.4674703221444,0.2916638718604066,0.2916638718604066,0.67681485140491593,0.67681485140491593,9200.0970441097197,-1791.0870441097195,0.42708069578531288,0.42708069578531288,44,0.71694694271691883]
["2013-04-26T03:00:00","2013-04-26T03:00:00",52.102620000000002,51.642139999999998,51.28575,51.594760000000001,51.625790000000002,51.226860000000002,51.074599999999997,50.320219999999999,49.744590000000002,46.079050000000002,39.099269999999997,38.697760000000002,38.505870000000002,38.71255,38.987929999999999,38.307989999999997,38.112870000000001,38.640129999999999,38.344799999999999,38.332839999999997,38.638950000000001,38.039769999999997,38.002040000000001,37.515349999999998,37.847589999999997,37.365569999999998,2079.125,9481.6929999999993,7402.5680000000002,48.931899999999999,38.122419999999998,31,31,463671.88560000004,334650.07933168334,15320.084540625005,62,52,51246.085424820005,44,11.083055512986363,11.690195512986364,320667.43786994979,9247.6457173337021,2764.5958323810582,685.47083238105824,8.125701988568973E-2,-2079.1249999999991,-1845.0777173337019,0.19702273019554731,0.19702273019554731,0.57378306908869381,0.57378306908869381,8767.3615668603543,-1364.7935668603541,0.35298283655104373,0.35298283655104373,44,0.61391516040069671]
["2013-04-26T10:00:00","2013-04-26T10:00:00",51.790689999999998,51.308230000000002,50.988480000000003,51.307989999999997,51.381390000000003,51.017670000000003,50.950989999999997,51.160519999999998,50.995959999999997,50.895060000000001,51.03989,50.341729999999998,49.586309999999997,42.129600000000003,39.577010000000001,38.718330000000002,38.394449999999999,38.885399999999997,38.590960000000003,38.573860000000003,38.862819999999999,38.184339999999999,38.294359999999998,37.808190000000003,38.193710000000003,37.755470000000003,1499.5150000000001,8902.1,7402.585,50.97466,37.339880000000001,23,23,344014.62479999999,283769.90853181842,10523.011459149995,62,56,60689.087518999993,44,11.648449884397902,12.255589884397899,250051.59606852345,10420.113941561927,1806.7659754873764,307.25097548737631,6.0287466366802052E-2,-1499.5150000000003,-3017.5289415619272,2.1263933388727882E-3,2.1263933388727882E-3,0.43591763912674458,0.43591763912674458,9903.9031317881872,-2501.3181317881872,0.19552521534624054,0.19552521534624054,43,0.47604973043874749]
["2013-04-26T13:00:00","2013-04-26T13:00:00",52.199240000000003,51.406489999999998,51.06221,51.328499999999998,51.371029999999998,51.046439999999997,50.950989999999997,51.175899999999999,51.023380000000003,50.931640000000002,51.060879999999997,51.077240000000003,50.959539999999997,50.155239999999999,48.098950000000002,39.650840000000002,38.690669999999997,38.9739,38.723199999999999,38.723500000000001,39.013530000000003,38.30939,38.364620000000002,37.905540000000002,38.25421,37.860340000000001,2619.6289999999999,10015.6,7395.9679999999998,52.0501,37.746479999999998,21,21,314100.30960000004,278117.29977094103,18781.299134050005,71,65,71629.668236000012,44,12.569146686847601,13.1762866868476,246353.50682259072,11397.697874105255,2988.4764020938383,368.84740209383835,5.5045077987080138E-2,-2619.6320000000005,-4001.7298741052555,-4.207742423760135E-2,0,0.36786335755456068,0.36786335755456068,10872.512102745888,-3476.5441027458883,9.8962514344342181E-2,9.8962514344342181E-2,42,0.40799544886656358]
["2013-04-26T22:00:00","2013-04-26T22:00:00",54.463889999999999,53.121499999999997,51.931959999999997,51.7639,51.621749999999999,51.198650000000001,51.035110000000003,51.258270000000003,51.098770000000002,51.017620000000001,51.085569999999997,51.167430000000003,51.099550000000001,51.314900000000002,51.573720000000002,50.670160000000003,49.934159999999999,48.17698,41.489640000000001,39.710659999999997,38.70476,38.053159999999998,38.08954,37.651580000000003,38.047730000000001,37.75168,3957.2530000000002,10627.99,14585.25,53.730260000000001,38.404940000000003,15,15,224357.364,223698.5143700187,33067.221579564997,72,67,81438.673853399989,44,13.025327778400941,13.63246777840094,182353.28002931588,12504.664026719463,5077.3726607323051,1120.119660732305,3.9317912847914381E-2,3957.26,2080.5859732805366,2.7262017105939427E-2,2.7262017105939427E-2,0.26745454685146819,0.26745454685146819,11947.75225985571,2637.4977401442902,4.4982938167186855E-2,4.4982938167186855E-2,44,0.30758663816347109]
["2013-04-27T05:00:00","2013-04-27T05:00:00",51.722259999999999,51.26361,50.919199999999996,51.246029999999998,51.310119999999998,50.839440000000003,50.30057,49.593539999999997,44.418059999999997,39.48798,39.074710000000003,38.897869999999998,37.957210000000003,38.038319999999999,38.306980000000003,37.639490000000002,37.341650000000001,37.444749999999999,36.594949999999997,36.610109999999999,36.894629999999999,36.356900000000003,36.447949999999999,35.974249999999998,36.354030000000002,36.07244,3617.01,11117.68,14734.69,51.564329999999998,36.461190000000002,33,33,493586.20079999999,477146.78720663826,28302.777719099999,67,65,83955.938757599986,44,12.98947251163416,13.596612511634159,400072.88177460479,12926.766453742282,4357.8024733106467,740.79247331064653,8.6499408265411637E-2,3617.01,1807.923546257718,0.21286807161610533,0.21286807161610533,0.58855546057379837,0.58855546057379837,12349.537605158894,2385.1523948411068,0.27095355766064344,0.27095355766064344,44,0.62868755188580128]
["2013-04-27T08:00:00","2013-04-27T08:00:00",51.597549999999998,51.095939999999999,50.376089999999998,49.751530000000002,45.754719999999999,40.2986,39.268450000000001,38.698549999999997,38.11459,37.82931,37.935569999999998,37.773040000000002,37.154870000000003,37.226939999999999,37.34984,36.37039,35.887230000000002,36.432769999999998,36.151310000000002,36.156309999999998,36.47945,35.922870000000003,36.04269,35.574979999999996,35.961379999999998,35.69867,5367.2280000000001,9333.5949999999993,14700.82,51.408670000000001,36.235720000000001,41,41,613243.46160000004,601165.01838032634,42666.456952319997,64,60,70809.085127625003,44,12.236929802852014,12.844069802852012,468263.15275940771,11573.014844151809,6973.3924505108935,1606.1644505108934,0.10746896178429931,5367.2250000000004,3127.8051558481911,0.28860110584055393,0.28860110584055393,0.7296212408113556,0.7296212408113556,11025.957693238623,3674.8623067613771,0.36465701182225513,0.36465701182225513,44,0.7697533321233585]
["2013-04-27T17:00:00","2013-04-27T17:00:00",52.58014,50.724229999999999,43.374389999999998,39.350009999999997,38.86354,38.099710000000002,37.775739999999999,37.903869999999998,37.589060000000003,37.195120000000003,36.973210000000002,36.842030000000001,36.308489999999999,36.321109999999997,36.646030000000003,36.01905,35.883110000000002,36.448270000000001,36.199330000000003,36.202449999999999,36.433889999999998,35.828530000000001,35.930929999999996,35.46716,35.876800000000003,35.56785,2941.4079999999999,10257.65,7316.24,52.27946,36.724089999999997,45,45,673072.09200000006,701882.58213141887,25020.042952160002,73,62,79780.770540250014,44,12.664558275422527,13.271698275422525,531907.62972014013,12599.060907647534,3951.1907810815865,1009.7827810815866,0.11795373854374315,-2941.41,-5282.8209076475341,0.12080857883049387,0.12080857883049387,0.7747630812009908,0.7747630812009908,12022.692030000971,-4706.4520300009717,0.24954610751927886,0.24954610751927886,44,0.88458099489743935]
["2013-04-27T18:00:00","2013-04-27T18:00:00",53.008380000000002,51.808,49.602020000000003,42.021360000000001,39.398440000000001,38.496699999999997,37.9557,38.069609999999997,37.75582,37.46416,37.184429999999999,36.962380000000003,36.68242,36.683500000000002,36.730690000000003,36.068399999999997,35.926909999999999,36.478630000000003,36.184440000000002,36.158290000000001,36.453270000000003,35.888190000000002,35.98809,35.501519999999999,35.88964,35.580840000000002,3018.3850000000002,10343.73,7325.3419999999996,52.519039999999997,36.640099999999997,43,43,{"$f":"3.1416*(138/2)^2*AI2774","v":643157.77679999999},{"$f":"62.4*AJ2774*(AF2774-AB2774)/1000","v":679781.54743161041},26301.512661450004,72,62,82123.734023099998,44,12.74445333018771,13.351593330187709,511473.72247139283,{"$f":"AO2774*1000/(500*AQ2774)","v":12887.76095692924},4127.523084752449,1109.1380847524488,{"$f":"AJ2774/$BK$7","v":0.11271135016402123},-3018.3879999999999,{"$f":"AE2774-AT2774","v":-5562.4189569292403},6.2320807391318636E-2,6.2320807391318636E-2,0.74302530869127525,0.74302530869127525,12301.712910536262,-4976.3709105362623,0.19722051919777556,0.19722051919777556,44,0.85284322238772381]
["2013-04-28T03:00:00","2013-04-28T03:00:00",52.59534,52.10201,51.750349999999997,52.021909999999998,52.085419999999999,51.664830000000002,51.48,47.442869999999999,39.591140000000003,38.721499999999999,38.533329999999999,38.194029999999998,37.94838,38.028289999999998,38.18862,37.25808,36.865870000000001,36.969259999999998,36.561079999999997,36.48536,36.800269999999998,36.062339999999999,36.170580000000001,35.686549999999997,36.089239999999997,35.770009999999999,1037.954,8334.9670000000006,7297.0129999999999,49.31297,36.04739,35,35,523500.516,442400.18460564327,8731.9592874099999,56,54,55284.08576793001,44,11.342445324686414,11.949585324686414,370517.2211629278,9748.1776081576045,1539.6960774243651,501.74207742436511,9.1741796645133558E-2,-1037.9540000000006,-2451.1646081576046,-2.5773527034155981E-2,0,0.57365503026272069,0.57365503026272069,9252.8877389108566,-1955.8747389108566,-2.0565648790364915E-2,0,40,0.68347294395916924]
["2013-04-28T10:00:00","2013-04-28T10:00:00",52.076900000000002,51.61383,51.310180000000003,51.617820000000002,51.713540000000002,51.336509999999997,51.281350000000003,51.489100000000001,51.305759999999999,50.719859999999997,42.41207,39.348509999999997,38.734529999999999,38.650269999999999,38.749220000000001,37.941180000000003,37.632129999999997,37.849460000000001,37.316540000000003,36.888530000000003,37.127369999999999,36.421959999999999,36.359059999999999,35.849409999999999,36.21011,35.890129999999999,2293.4870000000001,9607.8510000000006,7314.3639999999996,50.430079999999997,36.031509999999997,29,29,433757.57040000003,393545.15527001867,18562.073283495003,65,60,69169.657586534988,44,12.181025323700844,12.788165323700843,329697.38564189553,11356.951610953525,3047.7029297982717,754.21592979827165,7.6014631505967808E-2,-2293.487000000001,-4042.5876109535257,-4.2507035525928841E-2,0,0.46526570054031996,0.46526570054031996,10817.760927494417,-3503.3969274944175,-3.6837548617359363E-2,0,39,0.57508361423676857]
["2013-04-28T13:00:00","2013-04-28T13:00:00",52.719889999999999,51.607230000000001,51.242910000000002,51.600470000000001,51.638480000000001,51.366379999999999,51.23648,51.479410000000001,51.337229999999998,51.270809999999997,51.350430000000003,50.940089999999998,43.418610000000001,39.614539999999998,39.416159999999998,38.378059999999998,37.98798,38.322560000000003,37.873420000000003,37.663420000000002,37.651179999999997,36.943910000000002,36.66178,35.998089999999998,36.356400000000001,36.003830000000001,3282.8829999999998,10484.91,7202.0290000000005,52.633830000000003,36.775199999999998,25,25,373928.94,388030.54818528,27438.434600489996,75,67,83138.154136650031,44,13.083280056059767,13.690420056059766,305274.34348853951,12709.068946077177,4194.4274651189435,911.54446511894366,6.5529854746523966E-2,-3282.8809999999994,-5507.0399460771769,-5.7905471732101171E-2,0,0.37801155696874833,0.37801155696874833,12145.449708075354,-4943.4207080753531,-5.1979123244828798E-2,0,39,0.48782947066519694]
["2013-04-28T22:00:00","2013-04-28T22:00:00",55.632379999999998,55.159410000000001,54.786259999999999,55.08464,54.795740000000002,53.894080000000002,53.243310000000001,52.85033,51.981110000000001,51.520899999999997,51.50188,51.550530000000002,51.466760000000001,51.688110000000002,51.977939999999997,51.37762,51.258130000000001,51.73565,51.470709999999997,51.353569999999998,47.38111,40.431040000000003,39.271039999999999,37.695599999999999,38.068420000000003,37.738610000000001,3660.4380000000001,10840.16,14500.6,52.857619999999997,36.947429999999997,9,9,134614.4184,126998.77244706808,32749.517835629991,69,65,86234.502615199992,44,13.06717153917832,13.674311539178321,109763.45308528219,13198.648591495039,5012.4876278603324,1352.0496278603323,2.3590747708748628E-2,3660.4400000000005,1301.9514085049614,1.3689770043425215E-2,1.3689770043425215E-2,0.11127858689817614,0.11127858689817614,12612.628046118329,1887.9719538816717,1.9851663993171054E-2,1.9851663993171054E-2,44,0.22109650059462471]
["2013-04-29T05:00:00","2013-04-29T05:00:00",52.160350000000001,51.692239999999998,51.324339999999999,51.62997,51.688740000000003,51.350270000000002,51.258780000000002,51.47025,51.246969999999997,50.973799999999997,49.807079999999999,43.698860000000003,39.776150000000001,38.724490000000003,37.883620000000001,37.02149,36.877830000000003,37.446899999999999,37.183750000000003,37.20617,37.487079999999999,36.968539999999997,37.093409999999999,36.636420000000001,37.06044,36.740479999999998,5162.5810000000001,9576.9869999999992,14739.57,51.073439999999998,36.123240000000003,27,27,403843.25520000001,361187.99951840687,39803.163942235005,62,60,71588.935523699984,44,12.26352270135817,12.870662701358169,309038.55390318023,11675.101399008558,6491.3100275546203,1328.7290275546202,7.0772243126245887E-2,5162.5830000000005,3064.4686009914421,0.2249547247225383,0.2249547247225383,0.47371566371043605,0.47371566371043605,11124.358890416048,3615.2111095839518,0.27171813684279755,0.27171813684279755,44,0.58353357740688461]
["2013-04-29T08:00:00","2013-04-29T08:00:00",52.004620000000003,51.567219999999999,51.236020000000003,51.557769999999998,51.542169999999999,50.973089999999999,48.434910000000002,42.226700000000001,39.428640000000001,38.006399999999999,37.31324,36.986370000000001,36.921750000000003,37.193820000000002,37.5441,36.938839999999999,36.807949999999998,37.371209999999998,37.110039999999998,37.141240000000003,37.430399999999999,36.908499999999997,37.024720000000002,36.568109999999997,36.976819999999996,36.679110000000001,4552.0519999999997,10196.620000000001,14748.67,52.054470000000002,36.654640000000001,35,35,523500.516,502258.15496599145,34881.25922326,69,65,78513.107287300008,44,12.803871958496931,13.41101195849693,418256.81520923501,12263.963204536261,5448.5485853538275,{"$f":"AU2812-AC2812","v":896.49658535382787},9.1741796645133558E-2,{"$f":"AE2812-AD2812","v":4552.0499999999993},2484.7067954637387,0.31175942564747777,0.31175942564747777,0.63011890125454695,0.63011890125454695,{"$f":"AO2812*1000/(500*AR2812)","v":11708.752110619926},{"$f":"AE2812-BD2812","v":3039.9178893800745},0.37600476358700152,0.37600476358700152,44,0.7399368149509955]
["2013-04-29T16:00:00","2013-04-29T16:00:00",50.828389999999999,43.254390000000001,39.462960000000002,38.335720000000002,37.776269999999997,37.340820000000001,37.013629999999999,37.198360000000001,37.054699999999997,36.99091,36.958190000000002,37.150359999999999,37.063090000000003,37.283439999999999,37.651069999999997,37.051499999999997,36.950110000000002,37.43927,37.243380000000002,37.41084,37.644350000000003,37.108179999999997,37.140419999999999,36.643749999999997,37.05753,36.839019999999998,2096.5479999999998,12385.57,13669.69,54.380360000000003,38.56823,47,47,702986.40720000002,769474.59164619585,14664.69284738,84,66,97921.121482050017,44,13.526532242537908,14.133672242537905,593359.62211073702,14478.377713707003,2168.2856454905468,71.737645490547038,0.12319612692346506,1284.1200000000008,-808.68771370700233,0.34280670554467646,0.34280670554467646,0.82592756219375485,0.82592756219375485,13856.430204648197,-186.7402046481966,0.45779735309413538,0.45779735309413538,44,0.9357454758902034]
["2013-04-29T17:00:00","2013-04-29T17:00:00",49.921019999999999,41.835659999999997,39.283439999999999,38.153759999999998,37.710659999999997,37.317619999999998,37.01202,37.213650000000001,37.079270000000001,37.015309999999999,36.99371,37.175089999999997,37.091479999999997,37.320140000000002,37.67454,37.066029999999998,36.962429999999998,37.452190000000002,37.256,37.414999999999999,37.646769999999997,37.118160000000003,37.145150000000001,36.646050000000002,37.032739999999997,36.850079999999998,312.488,12603.23,12914.4,54.57987,37.566299999999998,47,47,702986.40720000002,777741.20564465446,2042.2559493599999,83,67,107212.96791555001,44,13.904231205920256,14.511371205920256,609927.8977164675,15421.631923079645,293.76035526371737,-18.727644736282627,0.12319612692346506,311.17000000000007,-2507.2319230796456,0.31644364141779868,0.31644364141779868,0.82919945522799965,0.82919945522799965,14776.407603963704,-1862.0076039637042,0.43821869927429496,0.43821869927429496,44,0.9390173689244482]
["2013-04-30T02:00:00","2013-04-30T02:00:00",53.446269999999998,52.97092,52.601149999999997,52.93074,52.967970000000001,52.639400000000002,52.521909999999998,52.70675,52.441929999999999,49.000860000000003,41.90822,39.30021,38.034590000000001,38.003619999999998,38.118310000000001,37.407260000000001,37.231160000000003,37.761920000000003,37.500129999999999,37.48677,37.70825,37.169429999999998,37.264589999999998,36.78622,37.17465,36.928370000000001,2921.2139999999999,9990.1980000000003,7068.9849999999997,50.689819999999997,36.339910000000003,29,29,433757.57040000003,372473.90651209932,24126.160365299995,66,61,71679.221091089959,44,12.327448439206169,12.934588439206168,333660.54285541159,11629.206391668473,3914.2180126374324,993.00401263743242,7.6014631505967808E-2,-2921.2130000000006,-4560.2213916684732,-4.7949855725212355E-2,0,0.47228371499759225,0.47228371499759225,11083.34005801411,-4014.35505801411,-4.2210175631654252E-2,0,41,0.58210162869404081]
["2013-04-30T09:00:00","2013-04-30T09:00:00",52.880879999999998,52.46884,52.144240000000003,52.456090000000003,52.504750000000001,52.16986,52.089779999999998,52.297750000000001,52.141869999999997,52.062980000000003,52.231180000000002,52.257219999999997,52.225119999999997,52.47222,52.742319999999999,48.249940000000002,40.88326,39.38494,38.193069999999999,37.945360000000001,38.162480000000002,37.579149999999998,37.452750000000002,36.956090000000003,37.32714,37.068640000000002,3983.97,11061.06,7077.0910000000003,52.018909999999998,36.559190000000001,19,19,284185.99440000003,265116.21842150559,31497.744896399989,68,64,85500.445251599987,44,12.981293183079561,13.588433183079559,230199.94681827977,13172.870228837503,4852.7900036116062,868.82000361160635,4.9802689607358223E-2,-3983.9689999999991,-6095.7792288375022,-6.409595268543794E-2,0,0.24692115474900145,0.24692115474900145,12584.297850920137,-5507.2068509201363,-5.7907226704601931E-2,0,38,0.35673906844545011]
["2013-04-30T12:00:00","2013-04-30T12:00:00",53.740349999999999,53.234929999999999,52.419539999999998,52.71416,52.657260000000001,52.216709999999999,52.083170000000003,52.307189999999999,52.167310000000001,52.100200000000001,52.202150000000003,52.293030000000002,52.24868,52.471739999999997,52.773330000000001,52.181820000000002,52.056089999999998,52.56118,51.680750000000003,45.852159999999998,40.821280000000002,38.55104,38.178019999999997,37.210230000000003,37.513500000000001,37.176110000000001,4846.0079999999998,11945.45,7099.4440000000004,53.145249999999997,37.366399999999999,9,9,134614.4184,134139.81319116615,40135.219776959995,75,67,94242.731866249989,44,13.461946156639126,14.069086156639125,113079.53607026489,14001.35326195338,5962.7663504160155,1116.7583504160157,2.3590747708748628E-2,-4846.0060000000003,-6901.9092619533794,-7.2572255799643659E-2,0,0.1035134742506249,0.1035134742506249,13397.136220077431,-6297.6922200774306,-6.6219029169550997E-2,0,36,0.21333138794707357]
["2013-04-30T21:00:00","2013-04-30T21:00:00",53.092080000000003,52.541429999999998,52.121609999999997,52.462339999999998,52.494840000000003,52.21266,52.085659999999997,52.313310000000001,52.177869999999999,52.11891,52.180630000000001,52.288849999999996,52.232950000000002,52.424610000000001,52.577849999999998,51.333240000000004,44.694940000000003,40.534649999999999,39.016199999999998,38.521030000000003,38.152720000000002,37.60277,37.675989999999999,37.208779999999997,37.607700000000001,37.368459999999999,2851.127,11845.74,14696.87,53.656779999999998,37.645740000000004,17,17,254271.67920000001,258439.48901140929,22415.018759870003,73,66,94831.308484799971,44,13.421169619331682,14.028309619331679,212947.69616237466,14131.601220240322,3340.248189335704,489.121189335704,4.4560301227636302E-2,2851.130000000001,565.26877975967909,7.2683845377848957E-3,7.2683845377848957E-3,0.27033038909987922,0.27033038909987922,13519.990798337942,1176.8792016620591,3.3611805257915253E-2,3.3611805257915253E-2,43,0.38014830279632789]
["2013-05-01T05:00:00","2013-05-01T05:00:00",52.804040000000001,52.400210000000001,52.055210000000002,52.387830000000001,52.452289999999998,52.059249999999999,51.711539999999999,49.669609999999999,42.626260000000002,39.494599999999998,38.679040000000001,38.082500000000003,37.88758,38.041370000000001,38.269179999999999,37.424120000000002,36.151020000000003,36.381819999999998,36.099960000000003,36.126899999999999,36.395800000000001,35.869079999999997,36.001150000000003,35.514150000000001,35.91395,35.67098,4119.1409999999996,10455.52,14574.66,51.735819999999997,36.592939999999999,33,33,493586.20079999999,494793.52054453589,35286.744950729997,66,64,79163.342348799983,44,12.765197974094079,13.37233797409408,393165.27559876023,12402.994847311495,5528.5856157251219,1409.4446157251223,8.6499408265411637E-2,4119.1399999999994,2171.6651526885053,0.16115877985441851,0.16115877985441851,0.55291061646374018,0.55291061646374018,11839.865624419797,2734.7943755802025,0.22910386284646089,0.22910386284646089,44,0.66272853016018873]
["2013-05-01T08:00:00","2013-05-01T08:00:00",52.774929999999998,52.359839999999998,51.895850000000003,51.81626,47.78725,41.126170000000002,38.97645,38.632759999999998,37.95129,37.690399999999997,37.759889999999999,37.689540000000001,36.636969999999998,36.300339999999998,36.618099999999998,36.011330000000001,35.883090000000003,36.46996,36.180140000000002,36.220709999999997,36.486550000000001,35.97484,36.095709999999997,35.606830000000002,36.0105,35.77469,3606.203,10974.13,14580.33,52.711799999999997,36.801299999999998,39,39,583329.14639999997,616506.37893205311,30653.158244359995,67,65,87301.947682499987,44,13.103571415973251,13.71071141597325,476966.57604155759,13324.908898665433,4678.5959752917133,1072.3929752917134,0.10222657340457739,3606.2000000000007,1255.4211013345666,0.21041162620503162,0.21041162620503162,0.67347930171858594,0.67347930171858594,12734.853069811023,1845.4769301889773,0.29666475164137712,0.29666475164137712,44,0.7832972154150345]
["2013-05-01T15:00:00","2013-05-01T15:00:00",52.931310000000003,45.724699999999999,39.829360000000001,39.010339999999999,38.51979,37.920760000000001,37.590330000000002,37.727550000000001,37.090159999999997,36.291319999999999,36.23122,36.368470000000002,36.280920000000002,36.537860000000002,36.892989999999998,36.280819999999999,36.17409,36.710250000000002,36.463700000000003,36.569159999999997,36.773249999999997,36.220210000000002,36.286029999999997,35.782629999999997,36.176070000000003,35.974930000000001,5069.8320000000003,12467.02,7397.1850000000004,54.110799999999998,37.733870000000003,47,47,702986.40720000002,795554.45378736674,42982.998964080005,80,70,102085.75692429997,44,13.91193431111863,14.519074311118629,610265.80483912327,14675.997548768108,6179.2987233597469,1109.4667233597465,0.12319612692346506,-5069.835,-7278.8125487681073,0.13674687137112385,0.13674687137112385,0.75853437819120206,0.75853437819120206,14062.295534381727,-6665.1105343817262,0.2670815739196743,0.2670815739196743,44,0.86835229188765062]
["2013-05-01T18:00:00","2013-05-01T18:00:00",55.628770000000003,55.13626,54.348170000000003,54.532789999999999,53.575060000000001,50.325839999999999,43.193040000000003,39.87565,38.619219999999999,38.089260000000003,37.853059999999999,37.857550000000003,37.642760000000003,37.351089999999999,37.188679999999998,36.386119999999998,36.254829999999998,36.771769999999997,36.504730000000002,36.554430000000004,36.745579999999997,36.195889999999999,36.293010000000002,35.80574,36.23142,35.994210000000002,5572.3059999999996,12970.37,7398.0640000000003,54.852209999999999,38.203830000000004,37,37,553414.83120000002,651224.92573442287,54704.888247679999,80,69,107967.82425029998,44,14.05166580693523,14.658805806935231,485247.37626292964,15367.263317209299,7786.2495449728513,2213.9435449728517,9.6984185024855479E-2,-5572.3060000000005,-7969.1993172092989,-8.3794606596027041E-2,0,0.5875363863407651,0.5875363863407651,14730.780347635044,-7332.7163476350433,3.9969372066817624E-2,3.9969372066817624E-2,42,0.69735430003721366]
["2013-05-02T03:00:00","2013-05-02T03:00:00",54.140560000000001,53.723269999999999,53.383560000000003,53.699800000000003,53.706490000000002,53.377870000000001,53.307000000000002,53.508540000000004,53.342509999999997,53.255409999999998,53.413330000000002,53.45073,53.413989999999998,53.654699999999998,53.92501,53.261499999999998,52.978610000000003,47.716149999999999,40.496729999999999,39.288290000000003,38.899619999999999,38.137709999999998,38.029130000000002,37.280549999999998,37.429639999999999,36.433979999999998,2993.2150000000001,10397.64,7404.4219999999996,50.232979999999998,36.944600000000001,15,15,224357.364,193184.61338816636,26499.800427350005,67,62,69083.89571159998,44,12.299794843765559,12.906934843765558,172195.89185061323,11233.341139281973,4308.9825097012981,1315.767509701298,3.9317912847914381E-2,-2993.2179999999998,-3828.919139281973,-4.0260352413482615E-2,0,0.20193258872630454,0.20193258872630454,10704.926699923582,-3300.5046999235828,-3.4704175650519919E-2,0,37,0.31175050242275321]
["2013-05-02T10:00:00","2013-05-02T10:00:00",53.761620000000001,53.417160000000003,53.077959999999997,53.416229999999999,53.541820000000001,53.08484,53.111789999999999,53.313960000000002,53.131839999999997,52.975879999999997,53.32338,53.215000000000003,53.193759999999997,53.463760000000001,53.742370000000001,53.157240000000002,53.02572,53.350909999999999,52.934910000000002,42.261980000000001,39.998570000000001,38.678510000000003,38.576540000000001,37.819830000000003,37.96754,37.215730000000001,150.1722,7263.95,7395.0529999999999,49.671880000000002,38.685220000000001,11,11,164528.73360000001,127882.22210597436,1242.3663511290001,50,45,39903.274453500002,44,10.270336658864352,10.877476658864351,105441.36620962509,7770.5874264714375,241.93293606528678,91.760736065286778,2.8833136088470546E-2,131.10300000000007,-375.53442647143765,-3.9486726679661376E-3,0,0.17458422312324937,0.17458422312324937,7336.8623449964825,58.19065500351735,6.1186360755905865E-4,6.1186360755905865E-4,37,0.28440213681969806]
["2013-05-02T13:00:00","2013-05-02T13:00:00",53.733170000000001,53.383009999999999,53.053579999999997,53.378909999999998,53.50808,53.051839999999999,53.059890000000003,53.273209999999999,53.088090000000001,52.938189999999999,53.266060000000003,53.171590000000002,53.148110000000003,53.424889999999998,53.728050000000003,53.14817,53.046129999999998,53.38897,52.941760000000002,44.919649999999997,40.32508,38.827469999999998,38.71123,37.90211,38.017020000000002,37.43347,219.08260000000001,7605.2920000000004,7409.55,50.748010000000001,38.90652,11,11,164528.73360000001,136694.96285119237,1785.4903276100003,50,44,45028.994582539999,44,10.384276715264615,10.991416715264615,106611.142392422,8672.5336423958252,343.88342617745849,124.80082617745848,2.8833136088470546E-2,-195.74200000000019,-1262.983642395825,{"$f":"IF(AZ2887>1,1+AY2888*60/$BK$7,IF(AZ2887<0,AY2888*60/$BK$7,AZ2887+AY2888*60/$BK$7))","v":-1.328003143593553E-2},0,{"$f":"IF(BB2887>1,1+AX2888*60/$BK$7,BB2887+AX2888*60/$BK$7)","v":0.17067994846203036},0.17067994846203036,8193.4832877375702,-783.93328773757003,-8.2429085820008383E-3,0,39,0.28049786215847905]
["2013-05-02T22:00:00","2013-05-02T22:00:00",53.606079999999999,53.295470000000002,52.97298,53.319710000000001,53.473599999999998,52.97945,53.022820000000003,53.237290000000002,53.039819999999999,52.860869999999998,53.239089999999997,53.108750000000001,53.085050000000003,53.372909999999997,53.652749999999997,53.061839999999997,52.95091,53.30932,52.216349999999998,41.674689999999998,39.977469999999997,39.408740000000002,39.411740000000002,38.895359999999997,39.192480000000003,37.784770000000002,851.68939999999998,6549.3739999999998,7401.0630000000001,49.605800000000002,37.8748,13,13,194443.04880000002,143427.46786095088,6737.4210105569982,46,41,38415.353197000004,44,9.9762105440177002,10.583350544017701,121043.81912372932,7701.3918315980254,1350.6974378356795,499.00803783567949,3.4075524468192467E-2,851.68900000000031,-300.32883159802532,-3.1579002220280448E-3,0,0.19932899590567452,0.19932899590567452,7259.5824993653832,141.48050063461687,2.7749769761894619E-3,2.7749769761894619E-3,41,0.30914690960212327]
["2013-05-03T05:00:00","2013-05-03T05:00:00",53.452550000000002,53.257240000000003,52.92492,53.298990000000003,53.461910000000003,52.934660000000001,53.031190000000002,53.22289,53.021439999999998,52.829149999999998,53.2669,53.039589999999997,53.035809999999998,53.287889999999997,53.464289999999998,52.506500000000003,47.589860000000002,40.401200000000003,39.845019999999998,39.62444,39.92239,39.438079999999999,39.654159999999997,39.240180000000002,39.629449999999999,39.156410000000001,1180.498,6216.3609999999999,7396.8590000000004,48.296489999999999,37.87809,17,17,254271.67920000001,145021.56175243371,8438.2823388600009,40,37,32382.267721199994,44,9.5270943292929218,10.134234329292919,151162.1450355812,6797.9315837430831,1771.4283174282941,590.93031742829407,4.4560301227636302E-2,1180.4980000000005,598.92741625691724,3.4909182628079301E-2,3.4909182628079301E-2,0.28268306022471262,0.28268306022471262,6390.6688298294657,1006.1901701705347,6.7441221481517932E-2,6.7441221481517932E-2,44,0.3925009739211614]
["2013-05-03T08:00:00","2013-05-03T08:00:00",53.48171,53.252479999999998,52.926479999999998,53.288870000000003,53.446309999999997,52.933219999999999,53.01343,53.218319999999999,53.02028,52.838380000000001,53.235140000000001,53.023609999999998,52.976500000000001,53.134860000000003,52.985759999999999,46.397950000000002,39.821750000000002,40.213389999999997,39.881070000000001,39.690289999999997,40.009459999999997,39.530990000000003,39.733840000000001,39.30603,39.689230000000002,39.243639999999999,824.81849999999997,6579.4110000000001,7404.2290000000003,48.709620000000001,37.98668,19,19,284185.99440000003,167862.17381047999,5871.9117701475006,48,41,35275.314694170003,44,9.8691352310711977,10.476275231071199,175011.40859342663,7148.6130989698104,1189.9546682997802,365.13616829978025,4.9802689607358223E-2,824.81800000000021,255.61590103018989,4.9303410735833858E-2,4.9303410735833858E-2,0.31493362944165276,0.31493362944165276,6734.323777509825,669.90522249017522,9.483849511247093E-2,9.483849511247093E-2,44,0.42475154313810154]
["2013-05-03T13:00:00","2013-05-03T13:00:00",53.688450000000003,53.21293,52.909660000000002,53.254640000000002,53.316719999999997,52.988439999999997,52.912909999999997,53.156579999999998,52.997799999999998,52.8735,53.083190000000002,53.079039999999999,52.963509999999999,52.99729,52.311900000000001,42.174010000000003,39.933329999999998,40.395690000000002,40.143979999999999,40.14855,40.370750000000001,39.809170000000002,39.883009999999999,39.408099999999997,39.746969999999997,39.271090000000001,903.81460000000004,8302.5529999999999,7398.7380000000003,54.927639999999997,38.70393,19,19,284185.99440000003,277640.82719089516,6515.3102307280014,65,47,67349.10606581498,44,11.327933516844292,11.935073516844291,200880.57918124463,11890.801789341174,1150.3086985883053,246.49409858830529,4.9802689607358223E-2,-903.8149999999996,-4492.063789341174,-4.7233191572866304E-2,0,0.30641044114350224,0.30641044114350224,11285.913902543352,-3887.1759025433521,9.3421348234891052E-3,9.3421348234891052E-3,41,0.41622835483995102]
["2013-05-03T17:00:00","2013-05-03T17:00:00",54.898800000000001,53.272010000000002,52.904739999999997,53.252540000000003,53.327370000000002,52.990929999999999,52.918340000000001,53.149839999999998,52.995640000000002,52.895859999999999,53.044699999999999,53.083869999999997,53.03416,53.238990000000001,53.441879999999998,52.509010000000004,50.193100000000001,41.329929999999997,40.221069999999997,40.277630000000002,40.48283,39.88749,39.958599999999997,39.498579999999997,39.854170000000003,39.486660000000001,1869.7629999999999,9269.1270000000004,7399.3639999999996,53.233870000000003,38.544069999999998,17,17,254271.67920000001,218120.83307133804,14408.52456141,66,47,68080.810902300029,44,11.352884651768433,11.960024651768432,180131.14355614976,11993.570443208038,2538.3019388232033,668.53893882320335,4.4560301227636302E-2,-1869.7630000000008,-4594.2064432080388,-4.8307202042019104E-2,0,0.23242175924309824,0.23242175924309824,11384.727520981067,-3985.3635209810673,-4.1905335164801848E-2,0,38,0.34223967293954705]
["2013-05-04T02:00:00","2013-05-04T02:00:00",53.69435,53.280799999999999,52.959470000000003,53.282139999999998,53.391150000000003,52.976759999999999,52.954979999999999,53.171950000000002,52.99192,52.857759999999999,53.166049999999998,53.086930000000002,53.056370000000001,53.325510000000001,53.631450000000001,53.025359999999999,52.923679999999997,53.185250000000003,52.498170000000002,49.082099999999997,40.890659999999997,40.247100000000003,40.195219999999999,39.712580000000003,40.061489999999999,39.592869999999998,163.41480000000001,7453.5640000000003,7396.7960000000003,49.628230000000002,38.037970000000001,11,11,164528.73360000001,103028.95649405404,1152.1952669520003,48,41,43194.372343320007,44,10.139175096907213,10.746315096907214,104094.78383883079,8520.2932054099219,227.2759383164136,63.861138316413587,2.8833136088470546E-2,-56.768000000000029,-1123.4972054099217,-1.1813358229823738E-2,0,0.12833041016540223,0.12833041016540223,8038.9178902359436,-642.12189023594328,-6.7517888607484785E-3,0,37,0.23814832386185097]
["2013-05-04T09:00:00","2013-05-04T09:00:00",53.668849999999999,53.263440000000003,52.946269999999998,53.270029999999998,53.375230000000002,52.947240000000001,52.926499999999997,53.15493,52.984299999999998,52.841569999999997,53.136609999999997,53.076250000000002,53.041260000000001,53.309640000000002,53.597439999999999,52.980319999999999,52.77975,53.010330000000003,51.659230000000001,43.30735,41.440460000000002,40.882240000000003,40.95346,40.474260000000001,40.682920000000003,39.94182,1816.0170000000001,9211.5149999999994,7395.4979999999996,49.857050000000001,38.761020000000002,13,13,194443.04880000002,120303.92716700119,12464.259919754999,62,48,51105.623392725,44,10.834877757691924,11.442017757691922,131462.23986984973,9433.5394520614627,2300.7661366380144,484.74913663801431,3.4075524468192467E-2,-1816.0169999999998,-2038.0414520614631,-2.1429616063573329E-2,0,0.11566971823346929,0.11566971823346929,8932.9739692755029,-1537.4759692755033,-1.6166265752454712E-2,0,38,0.22548763192991803]
["2013-05-04T12:00:00","2013-05-04T12:00:00",53.566960000000002,53.08379,52.750810000000001,53.091999999999999,53.157449999999997,52.837859999999999,52.747990000000001,52.980499999999999,52.826729999999998,52.744259999999997,52.878909999999998,52.934010000000001,52.88747,53.129629999999999,53.416490000000003,52.773870000000002,52.573540000000001,52.416510000000002,48.126989999999999,43.063389999999998,42.131729999999997,41.076770000000003,39.787619999999997,39.271749999999997,39.63373,39.26285,5737.7839999999997,8874.7919999999995,14612.58,51.972340000000003,37.126759999999997,13,13,194443.04880000002,154207.37181989022,41036.946746120004,70,51,65875.717309680025,44,11.521078960260089,12.128218960260089,139788.08803430677,11435.685413997522,7123.8027076577891,1386.0187076577895,3.4075524468192467E-2,5737.7880000000005,3176.8945860024778,3.3404438944858471E-2,3.3404438944858471E-2,0.16808795347543573,0.16808795347543573,10863.213720915099,3749.3662790849012,3.9799108662992404E-2,3.9799108662992404E-2,44,0.27790586717188448]
["2013-05-04T21:00:00","2013-05-04T21:00:00",53.350059999999999,52.786299999999997,51.194499999999998,46.755090000000003,42.760449999999999,41.35369,40.852209999999999,40.078069999999997,38.450960000000002,37.407679999999999,36.95964,36.847659999999998,36.814219999999999,37.088099999999997,37.442749999999997,36.841389999999997,36.725670000000001,37.279710000000001,36.994250000000001,36.984819999999999,37.298380000000002,36.773060000000001,36.894500000000001,36.431609999999999,36.816899999999997,36.535539999999997,6467.8639999999996,8138.5919999999996,14606.46,50.750430000000001,37.155340000000002,43,43,643157.77679999999,570486.82391104905,54377.014292640008,56,46,55322.445356639997,44,10.856977386661425,11.464117386661425,435723.56497943745,10191.132096232895,10016.971088002094,3549.1070880020943,0.11271135016402123,6467.8679999999995,4415.3279037671036,0.32587534486023995,0.32587534486023995,0.69774126602830044,0.69774126602830044,9651.4094353234777,4955.0505646765214,0.38730231773575713,0.38730231773575713,44,0.807559179724749]
["2013-05-05T04:00:00","2013-05-05T04:00:00",41.807560000000002,40.770380000000003,38.579479999999997,38.020940000000003,37.44688,36.804870000000001,36.78584,37.037410000000001,36.828249999999997,36.660490000000003,37.019419999999997,36.875979999999998,36.829880000000003,37.137860000000003,37.48357,36.904110000000003,36.814520000000002,37.317869999999999,37.012970000000003,36.889670000000002,37.237609999999997,36.7104,36.89396,36.444479999999999,36.844349999999999,36.487780000000001,225.0737,7086.6180000000004,7306.7020000000002,48.631590000000003,37.171399999999998,47,47,702986.40720000002,532704.64176505269,598.67128389300024,49,44,40606.994368710017,44,10.233486507973012,10.840626507973012,448905.71939426439,7936.1016085911097,117.00240840236989,-108.07129159763011,0.12319612692346506,220.08399999999983,-629.39960859110943,0.3899099049487853,0.3899099049487853,0.85338371510115874,0.85338371510115874,7491.6323957558325,-184.93039575583225,0.48646877390444049,0.48646877390444049,44,1]
["2013-05-05T07:00:00","2013-05-05T07:00:00",41.691110000000002,40.223889999999997,38.431109999999997,37.697899999999997,37.417079999999999,36.848260000000003,36.815550000000002,37.019489999999998,36.79815,36.620939999999997,36.980020000000003,36.845649999999999,36.821820000000002,37.136539999999997,37.486870000000003,36.91384,36.820279999999997,37.32535,37.028680000000001,36.89875,37.235639999999997,36.721679999999999,36.899909999999998,36.455590000000001,36.856839999999998,36.50488,291.75200000000001,7011.1390000000001,7298.14,49.576560000000001,36.944139999999997,51,51,762815.03760000004,622207.50201137853,756.54648748000022,51,45,44283.826263190007,44,10.419713475574781,11.02685347557478,495974.80150307249,8500.0084439936454,145.21445129051727,-146.53754870948273,0.13368090368290891,287.0010000000002,-1201.8684439936451,0.35831345124101754,0.35831345124101754,0.86220901488389934,0.86220901488389934,8031.9968631634856,-733.85686316348529,0.4695345967900596,0.4695345967900596,44,1]
["2013-05-05T14:00:00","2013-05-05T14:00:00",47.880130000000001,41.587820000000001,40.651670000000003,39.571249999999999,38.189869999999999,37.26641,36.936230000000002,37.032020000000003,36.848999999999997,36.753900000000002,36.900979999999997,36.944279999999999,36.880560000000003,37.16198,37.50967,36.8748,36.749079999999999,37.284480000000002,37.02055,37.057229999999997,37.310960000000001,36.796610000000001,36.886650000000003,36.460880000000003,36.860909999999997,36.538739999999997,1880.1179999999999,9192.0619999999999,7311.9430000000002,50.872770000000003,36.87829,49,49,732900.72239999997,655538.2667747644,10661.575742010004,67,54,64319.063908880009,44,11.65053807929281,12.257678079292809,532814.11713893421,11041.389414141839,1830.2288992058575,-49.88910079414245,0.12843851530318698,-1880.1189999999997,-3729.4464141418384,0.154617471913716,0.154617471913716,0.7849139724062153,0.7849139724062153,10494.493898895216,-3182.5508988952161,0.30422249285629865,0.30422249285629865,44,0.96361564939156974]
["2013-05-05T17:00:00","2013-05-05T17:00:00",51.229550000000003,49.654670000000003,43.789459999999998,41.378869999999999,40.644489999999998,38.705190000000002,37.454459999999997,37.35492,37.10765,36.942140000000002,36.92624,36.983759999999997,36.900950000000002,37.18233,37.5349,36.92286,36.74812,37.299109999999999,37.024419999999999,37.060209999999998,37.363759999999999,36.823239999999998,36.923580000000001,36.478389999999997,36.873440000000002,36.554459999999999,1766.1980000000001,9078.6119999999992,7312.415,52.088830000000002,36.98283,45,45,673072.09200000006,652438.8570212475,12959.557303910004,69,56,68570.756436000011,44,11.917214794467601,12.524354794467602,500519.42881360115,11507.849379006413,2174.9305567482593,408.73255674825919,0.11795373854374315,-1766.1969999999992,-4195.4343790064131,2.5074121306842549E-2,2.5074121306842549E-2,0.72324399879842882,0.72324399879842882,10949.986256583828,-3637.5712565838285,0.1922414473220273,0.1922414473220273,44,0.90194567578378326]
["2013-05-06T02:00:00","2013-05-06T02:00:00",51.914790000000004,51.40849,50.99183,51.198909999999998,49.587580000000003,43.318289999999998,41.119750000000003,40.45176,38.597380000000001,37.507950000000001,37.536450000000002,37.383940000000003,37.174430000000001,37.348880000000001,37.691969999999998,37.08614,36.98639,37.504930000000002,37.171239999999997,37.131230000000002,37.450119999999998,36.897419999999997,37.033729999999998,36.572380000000003,36.962949999999999,36.618690000000001,818.11469999999997,8121.7290000000003,7303.6149999999998,48.936700000000002,36.872579999999999,39,39,583329.14639999997,448372.34573955182,6256.9821313350003,55,50,48990.756631740012,44,10.884454801142336,11.491594801142334,396191.31103841576,9001.9679491155366,1149.7097917441529,331.59509174415291,0.10222657340457739,-818.11400000000049,-1698.3529491155368,-1.7857856425427528E-2,0,0.61199127636116013,0.61199127636116013,8526.3633950737694,-1222.7483950737696,-1.2856965505916087E-2,0,41,0.79069295334651457]
["2013-05-06T09:00:00","2013-05-06T09:00:00",51.574379999999998,51.154269999999997,50.752220000000001,50.992469999999997,51.096499999999999,50.666069999999998,48.911470000000001,43.075560000000003,41.10857,39.942059999999998,38.544350000000001,37.824939999999998,37.523620000000001,37.584339999999997,37.860860000000002,37.213090000000001,37.085549999999998,37.589970000000001,37.284709999999997,37.226869999999998,37.512509999999999,36.971699999999998,37.098350000000003,36.616790000000002,37.009889999999999,36.672060000000002,2507.7429999999999,9823.8619999999992,7316.1189999999997,50.670319999999997,37.779670000000003,37,37,553414.83120000002,483403.10896760743,18685.594331879995,65,55,63317.983345149973,44,11.677248232069614,12.284388232069613,403251.41121603333,10844.67540413463,3200.3420601376151,692.5990601376152,9.6984185024855479E-2,-2507.7429999999995,-3528.5564041346306,-3.7102095702118046E-2,0,0.52667544314671078,0.52667544314671078,10308.691348560948,-2992.5723485609478,-3.1466325872449935E-2,0,40,0.70537712013206522]
["2013-05-06T12:00:00","2013-05-06T12:00:00",52.366950000000003,51.309510000000003,50.866030000000002,51.077590000000001,51.097000000000001,50.748399999999997,50.631419999999999,50.824869999999997,49.545090000000002,44.201689999999999,41.29372,40.477420000000002,38.845140000000001,38.148290000000003,38.24926,37.334530000000001,37.155189999999997,37.686230000000002,37.390340000000002,37.409689999999998,37.578330000000001,37.018210000000003,37.14085,36.684359999999998,37.056939999999997,36.70926,3037.7289999999998,10363.379999999999,7325.6490000000003,51.708410000000001,37.736620000000002,31,31,463671.88560000004,433972.29176478781,23781.909493005005,72,59,72397.484525099993,44,12.230247222305911,12.83738722230591,353859.27975345444,11839.087666692327,3889.0316868870495,851.30268688704973,8.125701988568973E-2,-3037.7309999999989,-4513.4386666923265,-4.7457944319959769E-2,0,0.43878556372417837,0.43878556372417837,11279.161915331806,-3953.5129153318057,-4.1570432138288052E-2,0,39,0.61748724070953287]
["2013-05-06T19:00:00","2013-05-06T19:00:00",53.862189999999998,53.200899999999997,52.605130000000003,52.588590000000003,52.55527,51.934730000000002,51.642249999999997,51.307250000000003,51.017890000000001,50.884810000000002,50.875239999999998,50.89479,50.796259999999997,50.996009999999998,50.883189999999999,46.091560000000001,41.553139999999999,41.144770000000001,39.466900000000003,38.30574,38.232819999999997,37.655090000000001,37.445340000000002,36.906730000000003,37.277569999999997,36.882060000000003,3192.529,10527.22,7334.69,51.876910000000002,37.734349999999999,19,19,284185.99440000003,265906.76474723959,27104.778724384993,71,59,74440.920241600019,44,12.299928380238562,12.907068380238561,218117.16437390112,12104.285153594725,4407.3067560185718,1214.7777560185718,4.9802689607358223E-2,-3192.5299999999997,-4769.5951535947252,-5.0151380786111983E-2,0,0.20184271865604231,0.20184271865604231,11534.907548111112,-4200.2175481111126,-4.4164484166139523E-2,0,37,0.38054439564139675]
["2013-05-07T04:00:00","2013-05-07T04:00:00",52.820920000000001,52.412669999999999,52.052990000000001,52.368920000000003,52.453850000000003,52.111620000000002,51.996789999999997,51.96313,51.315919999999998,50.898389999999999,50.97195,50.931100000000001,50.838430000000002,51.02176,51.043810000000001,48.882390000000001,44.342489999999998,42.086309999999997,40.038539999999998,37.999769999999998,37.976080000000003,37.437429999999999,37.559289999999997,37.108310000000003,37.506599999999999,37.158239999999999,5406.2659999999996,9305.2800000000007,14711.55,49.687049999999999,36.059600000000003,13,13,194443.04880000002,152015.1368883219,42338.307176440008,60,56,63403.618967999981,44,11.741015406808801,12.3481554068088,142456.63109855895,10800.363813717715,7212.0350258440767,1805.7690258440771,3.4075524468192467E-2,5406.2699999999986,3911.1861862822843,0.12424353375062178,0.12424353375062178,0.21878233839925101,0.21878233839925101,10269.326369676086,4442.2236303239133,0.14085825236074506,0.14085825236074506,44,0.39748401538460548]
["2013-05-07T06:00:00","2013-05-07T06:00:00",52.754849999999998,52.369039999999998,52.011510000000001,52.280140000000003,52.127560000000003,51.236240000000002,50.916249999999998,51.02037,50.801110000000001,50.660960000000003,50.763069999999999,50.495460000000001,48.620199999999997,44.618070000000003,42.167450000000002,40.038670000000003,37.998179999999998,37.688789999999997,37.400559999999999,37.409320000000001,37.737180000000002,37.200360000000003,37.333199999999998,36.893219999999999,37.281210000000002,36.933030000000002,5336.7910000000002,9371.4339999999993,14708.22,50.135469999999998,36.074269999999999,19,19,284185.99440000003,234121.58889015531,42218.873289809984,57,54,65886.803880399995,44,11.703998012321641,12.31113801232164,207549.40836784436,11258.8542498104,7214.4361687968749,1877.6451687968747,4.9802689607358223E-2,5336.7860000000001,3449.3657501895996,0.19903960207310306,0.19903960207310306,0.33090296366436189,0.33090296366436189,10703.609010711598,4004.6109892884015,0.22717553272461932,0.22717553272461932,44,0.50960464064971644]
["2013-05-07T13:00:00","2013-05-07T13:00:00",51.456099999999999,50.876339999999999,50.136310000000002,48.325800000000001,43.585940000000001,41.251309999999997,39.389449999999997,38.114260000000002,37.476289999999999,37.162430000000001,37.160060000000001,37.289679999999997,37.073500000000003,37.145699999999998,37.474670000000003,36.870460000000001,36.75027,37.293329999999997,37.061779999999999,37.132469999999998,37.393639999999998,36.871679999999998,36.97343,36.536409999999997,36.949649999999998,36.614400000000003,4032.4850000000001,10701.16,14733.64,52.131149999999998,36.655079999999998,41,41,613243.46160000004,593770.03812558413,29924.466312249991,81,63,82805.950620599993,44,12.828563916162461,13.43570391616246,490902.85566218954,12909.621242370609,4665.2870122974145,632.80201229741442,0.10746896178429931,4032.4799999999996,1824.0187576293902,0.38668752519608152,0.38668752519608152,0.66594565155573104,0.66594565155573104,12326.254156432951,2407.3858435670481,0.4563876182705372,0.4563876182705372,44,0.8446473285410856]
["2013-05-07T16:00:00","2013-05-07T16:00:00",48.54374,43.136789999999998,40.95778,39.651859999999999,38.032470000000004,37.505949999999999,37.250039999999998,37.252989999999997,37.120959999999997,37.065959999999997,37.023310000000002,37.121549999999999,36.869579999999999,37.078749999999999,37.44211,36.82226,36.723370000000003,37.24371,37.029730000000001,37.119959999999999,37.363250000000001,36.830370000000002,36.931049999999999,36.496729999999999,36.905650000000001,36.572870000000002,3345.4690000000001,11392.76,14738.23,52.697589999999998,36.944580000000002,47,47,702986.40720000002,707332.64034613327,20024.087244014998,83,64,89735.131103799984,44,13.12569597063958,13.732835970639581,575776.39718972472,13673.199699966452,3051.1276946847152,-294.3413053152849,0.12319612692346506,3345.4699999999993,1065.030300033548,0.42928825106829144,0.42928825106829144,0.77969285464338101,0.77969285464338101,13068.696268658738,1669.533731341262,0.51788496289622976,0.51788496289622976,44,0.95839453162873545]
["2013-05-08T01:00:00","2013-05-08T01:00:00",52.440379999999998,52.004570000000001,51.621459999999999,51.927860000000003,51.581580000000002,42.808329999999998,40.493290000000002,38.526139999999998,37.63626,37.405009999999997,37.423160000000003,37.390450000000001,37.231160000000003,37.430610000000001,37.738950000000003,37.100589999999997,36.929349999999999,37.487560000000002,37.243229999999997,37.269649999999999,37.420810000000003,36.895009999999999,36.990859999999998,36.549149999999997,36.934919999999998,36.589759999999998,2221.201,9611.0930000000008,7389.8909999999996,50.393250000000002,37.033000000000001,39,39,583329.14639999997,502443.4296361545,17603.706497309999,66,58,64203.302626625002,44,11.889978619567914,12.497118619567912,432792.11532128841,10799.565698286877,2961.099773272716,739.89877327271597,0.10222657340457739,-2221.2020000000011,-3409.6746982868772,9.9429395086770983E-2,9.9429395086770983E-2,0.63616035285050443,0.63616035285050443,10274.896891207523,-2885.0058912075237,0.24291398637945291,0.24291398637945291,44,0.78992915763996296]
["2013-05-08T08:00:00","2013-05-08T08:00:00",52.194870000000002,51.761299999999999,51.286960000000001,51.566240000000001,51.664369999999998,51.328569999999999,51.256230000000002,51.467649999999999,51.262569999999997,50.565730000000002,42.467750000000002,40.341790000000003,38.312420000000003,38.095359999999999,38.24868,37.485840000000003,37.208739999999999,37.756839999999997,37.46463,37.492379999999997,37.689900000000002,37.079940000000001,37.165419999999997,36.700859999999999,37.077779999999997,36.743920000000003,2884.915,10277.64,7392.7259999999997,51.267699999999998,37.08981,27,27,403843.25520000001,365996.62900374003,22287.338709624997,70,61,72857.624689799995,44,12.367632001922182,12.974772001922181,311662.0894465695,11781.984567211643,3604.1400174521837,719.22501745218369,7.0772243126245887E-2,-2884.9139999999998,-4389.2585672116429,-4.6152214325157322E-2,0,0.47052676406154148,0.47052676406154148,11230.659726275931,-3837.9337262759318,2.1140235309545369E-2,2.1140235309545369E-2,42,0.62429556885100002]
["2013-05-08T11:00:00","2013-05-08T11:00:00",52.47533,52.045650000000002,51.563899999999997,51.780619999999999,51.793399999999998,51.391939999999998,51.24485,51.468690000000002,51.328229999999998,51.286250000000003,51.318309999999997,51.433199999999999,49.554130000000001,42.391669999999998,40.543340000000001,38.285609999999998,37.67342,37.931539999999998,37.665590000000002,37.75658,37.958199999999998,37.290840000000003,37.24915,36.717669999999998,37.011879999999998,36.806199999999997,3583.25,10983.78,7400.5320000000002,51.743450000000003,37.168320000000001,21,21,314100.30960000004,292767.99861333036,28073.205036250005,81,62,80045.01069570001,44,12.67356886472337,13.280708864723371,248400.16681874351,12631.802699001972,4430.1972610716184,846.94726107161841,5.5045077987080138E-2,-3583.2480000000005,-5231.2706990019715,-5.5005810843955449E-2,0,0.36699205844349742,0.36699205844349742,12054.328049960954,-4653.7960499609535,-4.8933775359653355E-2,0,40,0.5207608632329559]
["2013-05-08T19:00:00","2013-05-08T19:00:00",54.202710000000003,53.433039999999998,52.520530000000001,52.59113,52.544559999999997,52.165790000000001,51.893389999999997,51.932209999999998,51.714199999999998,51.622459999999997,51.531149999999997,51.634779999999999,51.484900000000003,51.643210000000003,51.944879999999998,51.347859999999997,51.237900000000003,51.656640000000003,51.263649999999998,46.654499999999999,41.716700000000003,39.107190000000003,38.290179999999999,37.27017,37.550440000000002,37.19894,2509.2660000000001,11689.55,14198.81,54.035159999999998,37.180970000000002,9,9,134614.4184,141423.23291331754,21333.490966410005,82,65,98508.948357249974,44,13.485730138982225,14.092870138982224,113279.32008796686,14609.360760155994,3163.8614663870258,654.59546638702568,2.3590747708748628E-2,2509.2600000000002,-410.55076015599479,-4.3168627192798729E-3,0,0.34987006985757901,0.34987006985757901,13979.969642204369,218.84035779563055,2.3010645058430092E-3,2.3010645058430092E-3,39,0.50363887464703738]
["2013-05-09T04:00:00","2013-05-09T04:00:00",52.174079999999996,51.734360000000002,51.310789999999997,51.606200000000001,51.684530000000002,51.326909999999998,51.206020000000002,51.268650000000001,49.832920000000001,44.277430000000003,40.52675,39.138770000000001,37.721339999999998,37.290179999999999,37.561340000000001,36.945140000000002,36.796010000000003,37.3673,37.113700000000001,37.169759999999997,37.42004,36.887230000000002,36.99962,36.498779999999996,36.825980000000001,36.616889999999998,4948.9620000000004,9651.0930000000008,14600.06,51.982959999999999,37.090710000000001,31,31,463671.88560000004,444588.43423248333,38495.971068389998,69,62,71863.244864624998,44,12.394570649883713,13.001710649883712,358613.67013268149,11595.923230353965,6211.7474103471532,1262.7854103471527,8.125701988568973E-2,4948.9669999999987,3004.1367696460347,0.19220138628683472,0.19220138628683472,0.75104385977378019,0.75104385977378019,11054.429190095496,3545.6308099045036,0.2480833320580996,0.2480833320580996,44,0.90481266456323861]
["2013-05-09T07:00:00","2013-05-09T07:00:00",52.001519999999999,51.600009999999997,51.208150000000003,51.46407,51.297429999999999,47.233710000000002,41.667729999999999,39.814120000000003,38.466340000000002,37.245339999999999,37.184559999999998,37.215400000000002,37.08155,37.284709999999997,37.629820000000002,36.99371,36.843130000000002,37.415120000000002,37.164380000000001,37.200220000000002,37.328429999999997,36.783700000000003,36.907910000000001,36.411230000000003,36.750120000000003,36.538620000000002,3353.4580000000001,11291.96,14645.42,52.06476,37.161670000000001,39,39,583329.14639999997,565147.43956862227,25927.092854099996,68,64,84142.548078199994,44,12.93498888946662,13.542128889466621,470830.21612136927,13010.068860085375,4008.8310976769785,655.37309767697843,0.10222657340457739,3353.4600000000009,1635.3511399146246,0.25350070311987161,0.25350070311987161,0.86972650378572824,0.86972650378572824,12426.782932726035,2218.6370672739649,0.32748937589917448,0.32748937589917448,44,1]
["2013-05-09T14:00:00","2013-05-09T14:00:00",45.467820000000003,41.131320000000002,38.917369999999998,38.229030000000002,37.812559999999998,37.17998,37.054389999999998,37.237369999999999,36.988779999999998,36.837949999999999,36.984729999999999,36.972450000000002,36.916840000000001,37.220030000000001,37.639780000000002,36.87106,36.651690000000002,37.253270000000001,36.9619,36.97739,37.250660000000003,36.714120000000001,36.851489999999998,36.383589999999998,36.721060000000001,36.481299999999997,2858.2130000000002,11184.02,14042.23,53.277720000000002,36.806429999999999,47,47,702986.40720000002,736797.66885642696,12842.69414438001,69,67,92107.618392900025,44,13.389138787197892,13.996278787197891,587332.67246249923,13758.557567715899,1918.3749378503167,-939.83806214968354,0.12319612692346506,2858.2099999999991,283.67243228410007,0.28839113316868342,0.28839113316868342,1.0300535314760706,1,13161.729598748629,880.50040125137093,0.40662989374357539,0.40662989374357539,44,1]
["2013-05-09T17:00:00","2013-05-09T17:00:00",44.079619999999998,39.829140000000002,37.934959999999997,37.650480000000002,37.585050000000003,37.117809999999999,36.966290000000001,37.157589999999999,36.940080000000002,36.835450000000002,36.965119999999999,36.961030000000001,36.967930000000003,37.234099999999998,37.576880000000003,36.925139999999999,36.767859999999999,37.32311,37.017800000000001,37.021140000000003,37.294029999999999,36.744459999999997,36.863120000000002,36.438079999999999,36.795639999999999,36.476480000000002,3895.1019999999999,10783.92,6888.8230000000003,53.465679999999999,37.690860000000001,49,49,732900.72239999997,776967.16986707994,14807.502910139992,71,65,85057.198447199989,44,13.027025467049521,13.63416546704952,595765.02183268452,13058.575599217664,2273.3513414238732,-1621.7506585761266,0.12843851530318698,-3895.0969999999998,-6169.7525992176634,0.20034907780304528,0.20034907780304528,0.95712768644265722,0.95712768644265722,12477.067064025687,-5588.2440640256864,0.33721180577629756,0.33721180577629756,44,0.95904380003853862]
["2013-05-10","2013-05-10",54.176250000000003,53.761569999999999,53.406829999999999,53.725859999999997,53.700400000000002,52.221490000000003,47.458370000000002,41.352939999999997,38.91713,38.019599999999997,37.81185,37.53989,37.341589999999997,37.516559999999998,37.825330000000001,37.084060000000001,36.870890000000003,37.46743,37.136809999999997,37.198720000000002,37.748690000000003,37.209850000000003,37.057049999999997,36.553280000000001,36.90605,36.547539999999998,3866.5160000000001,10653.56,6787.0479999999998,51.980800000000002,36.822510000000001,35,35,523500.516,504149.5413902789,34080.844637180009,67,66,80744.876006200007,44,12.94082227181142,13.547962271811421,422730.49333367241,12479.095116248367,5267.1837880684325,{"$f":"AU3066-AC3066","v":1400.6677880684324},9.1741796645133558E-2,{"$f":"AE3066-AD3066","v":-3866.5119999999997},-5692.0471162483673,-5.9850786741158804E-2,0,0.68754386782403842,0.68754386782403842,{"$f":"AO3066*1000/(500*AR3066)","v":11919.855456669215},{"$f":"AE3066-BD3066","v":-5132.8074566692148},-5.3970488683343226E-2,0,41,0.68945998141991982]
["2013-05-10T09:00:00","2013-05-10T09:00:00",53.707900000000002,53.13588,52.78246,53.124569999999999,53.232140000000001,52.8307,52.760219999999997,52.991489999999999,52.797780000000003,52.721890000000002,52.897530000000003,52.969070000000002,52.91845,52.630429999999997,51.047539999999998,43.55283,39.416989999999998,38.939169999999997,37.969349999999999,37.914230000000003,38.13364,37.369199999999999,37.430810000000001,36.945650000000001,37.245579999999997,36.776809999999998,3855.2359999999999,10761.75,6906.5190000000002,52.865090000000002,37.394190000000002,19,19,284185.99440000003,285296.78423910355,32636.67384362001,66,65,83246.979037500016,44,12.965296985178751,13.572436985178751,229916.28294487917,12841.507469156102,5034.4660644377909,1179.230064437791,4.9802689607358223E-2,-3855.2309999999998,-5934.9884691561019,-6.240526860094231E-2,0,0.34968391568372392,0.34968391568372392,12267.06436410891,-5360.5453641089098,-5.6365109221908731E-2,0,37,0.35160002927960532]
["2013-05-10T12:00:00","2013-05-10T12:00:00",54.487439999999999,53.987050000000004,53.252220000000001,53.565579999999997,53.321359999999999,52.930999999999997,52.811160000000001,53.054000000000002,52.892429999999997,52.834069999999997,52.894500000000001,52.968989999999998,52.918509999999998,53.15663,53.537370000000003,52.939779999999999,52.60248,52.490319999999997,49.10192,43.057850000000002,39.650680000000001,38.179310000000001,38.072119999999998,37.137540000000001,37.500480000000003,36.943840000000002,5328.4440000000004,11430.76,6102.32,53.666519999999998,37.53069,11,11,164528.73360000001,171684.94903859819,46740.04507919999,75,67,92222.400065399983,44,13.393052842230141,14.00019284223014,137501.02224580836,13771.677174991806,6979.7447422625246,1651.3007422625242,2.8833136088470546E-2,-5328.4400000000005,-7669.3571749918065,-8.0641823819748937E-2,0,0.19269344710134928,0.19269344710134928,13174.447110074172,-7072.1271100741724,-7.436206391601273E-2,0,36,0.19460956069723068]
["2013-05-10T19:00:00","2013-05-10T19:00:00",54.665680000000002,54.08278,53.641350000000003,53.906669999999998,53.713970000000003,53.151479999999999,52.90484,53.11835,52.954369999999997,52.945369999999997,52.955350000000003,53.051139999999997,52.957369999999997,53.152259999999998,53.452370000000002,52.905929999999998,52.799349999999997,53.182380000000002,52.458559999999999,50.79007,44.07629,39.525030000000001,38.653080000000003,37.243020000000001,36.2502,35.809730000000002,2172.1460000000002,11005.16,13177.31,52.785989999999998,36.150820000000003,9,9,134614.4184,142599.56047004825,20478.938184349998,77,63,91536.353738599966,44,13.12627066248626,13.733410662486259,110259.882157874,13947.046513402,3120.298020804496,948.15202080449581,2.3590747708748628E-2,2172.1499999999996,-769.73651340200013,-8.0936322152003852E-3,0,0.17223347990828311,0.17223347990828311,13330.461891544204,-153.15189154420477,-1.6103628470768481E-3,0,37,0.17414959350416451]
["2013-05-11T04:00:00","2013-05-11T04:00:00",53.521320000000003,53.109110000000001,52.743949999999998,53.094059999999999,53.134340000000002,52.740940000000002,52.511749999999999,52.041609999999999,49.273409999999998,43.274299999999997,40.042279999999998,38.339120000000001,36.221260000000001,36.085059999999999,36.452759999999998,35.833799999999997,35.687910000000002,36.292659999999998,35.985860000000002,36.018210000000003,36.296030000000002,35.72139,35.877180000000003,35.388530000000003,35.797190000000001,35.528770000000002,4801.0209999999997,9107.5210000000006,13908.54,49.88353,36.158569999999997,27,27,403843.25520000001,361737.35557532054,43191.305196775007,61,57,62500.180712080015,44,11.771055162281929,12.37819516228193,296628.46099378122,10619.299604057547,7338.5613441305059,2537.5403441305061,7.0772243126245887E-2,4801.0190000000002,3289.2403959424537,0.21170687337636071,0.21170687337636071,0.56585471403552234,0.56585471403552234,10098.431943055268,3810.1080569447331,0.26348001934908466,0.26348001934908466,44,0.56777082763140374]
["2013-05-11T07:00:00","2013-05-11T07:00:00",53.39132,52.895740000000004,52.302399999999999,51.696959999999997,47.807989999999997,41.696730000000002,39.441989999999997,37.970649999999999,36.05583,35.784509999999997,35.922719999999998,35.869410000000002,35.842799999999997,36.113280000000003,36.49147,35.860370000000003,35.734639999999999,36.31176,35.994909999999997,36.025790000000001,36.316310000000001,35.671950000000002,35.799799999999998,35.319980000000001,35.729179999999999,35.442799999999998,4683.098,9211.2919999999995,13894.39,50.822330000000001,36.176960000000001,39,39,583329.14639999997,559810.87387263123,42027.339057480007,63,58,67451.389759020007,44,12.000738390782583,12.607878390782583,436823.74205589056,11241.206592892226,7004.125527769188,2321.0275277691881,0.10222657340457739,4683.098,2653.1834071077737,0.29801303794846484,0.29801303794846484,0.71384538958418964,0.71384538958418964,10699.879498890572,3194.5105011094274,0.3667962178190286,0.3667962178190286,44,0.71576150318007103]
["2013-05-11T13:00:00","2013-05-11T13:00:00",39.569519999999997,36.511069999999997,35.870609999999999,36.177729999999997,36.155380000000001,35.810209999999998,35.631250000000001,35.958399999999997,35.800020000000004,35.709910000000001,35.745350000000002,35.871220000000001,35.78002,36.103920000000002,36.463270000000001,35.72063,35.62124,36.137509999999999,35.839730000000003,35.936779999999999,36.242220000000003,35.64987,35.684890000000003,35.503430000000002,35.639919999999996,35.387540000000001,2606.6080000000002,9755.8340000000007,7149.2259999999997,52.546250000000001,36.326729999999998,49,49,732900.72239999997,784719.37155781116,5450.3912619199946,78,60,79117.472339840009,44,12.520245806788544,13.127385806788544,572588.46505666373,12638.325726311556,870.65243702559962,-1735.9555629744004,0.12843851530318698,-2606.6080000000011,-5489.099726311556,0.32764756987543947,0.32764756987543947,0.90542629828623777,0.90542629828623777,12053.804695665473,-4904.5786956654729,0.43238938067822907,0.43238938067822907,44,0.90734241188211917]
["2013-05-11T16:00:00","2013-05-11T16:00:00",52.555169999999997,47.195950000000003,40.279609999999998,37.149990000000003,36.384050000000002,36.050089999999997,35.824120000000001,36.072000000000003,35.877940000000002,35.774369999999998,35.745249999999999,35.916029999999999,35.826630000000002,36.054630000000003,36.374119999999998,35.86271,35.751930000000002,36.221220000000002,35.848930000000003,36.037500000000001,36.2562,35.651499999999999,35.764560000000003,36.637569999999997,36.136040000000001,35.476669999999999,3442.5219999999999,10443.42,7000.8950000000004,52.428150000000002,35.987780000000001,45,45,673072.09200000006,711957.04982040054,29396.555988499997,81,61,85846.844432700003,44,12.810564395155071,13.417704395155072,538039.84273401892,13402.507771658697,4589.4240225071917,1146.9020225071918,0.11795373854374315,-3442.5249999999996,-6401.6127716586961,0.13607202055912782,0.13607202055912782,0.80942626276749652,0.80942626276749652,12796.055406273221,-5795.1604062732204,0.25963675977120221,0.25963675977120221,44,0.81134237636337792]
["2013-05-11T23:00:00","2013-05-11T23:00:00",53.107019999999999,52.633609999999997,52.272039999999997,52.677370000000003,52.634700000000002,51.958280000000002,50.157649999999997,42.204320000000003,39.85,36.48789,36.364989999999999,36.310870000000001,36.089210000000001,36.292450000000002,36.59319,35.934199999999997,35.713279999999997,36.263030000000001,35.997860000000003,36.035960000000003,36.283650000000002,36.100200000000001,37.072279999999999,36.061549999999997,36.351739999999999,36.405099999999997,1551.1279999999999,8857.73,7306.6030000000001,51.026960000000003,35.999119999999998,33,33,493586.20079999999,450350.05554424017,12953.407882880001,66,59,66556.274601600016,44,12.031061963914562,12.638201963914561,370554.04878073762,11064.073113616399,2153.3274322303187,602.19943223031873,8.6499408265411637E-2,-1551.1269999999995,-3757.4701136163994,-3.9509079574266845E-2,0,0.60656744360071169,0.60656744360071169,10532.554360443983,-3225.9513604439826,-3.3920261545294497E-2,0,40,0.60848355719659308]
["2013-05-12T08:00:00","2013-05-12T08:00:00",52.422280000000001,52.035910000000001,51.68009,51.968060000000001,52.00132,51.653559999999999,51.592799999999997,51.810130000000001,51.58764,48.635109999999997,41.952539999999999,38.531179999999999,37.139629999999997,36.86656,37.12959,36.313160000000003,36.137900000000002,36.721710000000002,36.459949999999999,36.513379999999998,36.829270000000001,35.886859999999999,36.254910000000002,36.684040000000003,37.160429999999998,36.52684,1640.7919999999999,8943.1990000000005,7302.4059999999999,49.839750000000002,36.01332,29,29,433757.57040000003,360333.51098496123,13040.555394240002,64,50,61826.257474785009,44,11.32214537989017,11.929285379890167,306450.53535387688,10921.297227749385,2303.5484807326334,662.75648073263346,7.6014631505967808E-2,-1640.7930000000006,-3618.8912277493846,-3.8051949094587909E-2,0,0.48835055304170544,0.48835055304170544,10365.458701995482,-3063.0527019954816,-3.220741330842887E-2,0,38,0.49026666663758683]
["2013-05-12T11:00:00","2013-05-12T11:00:00",52.386099999999999,51.919310000000003,51.514409999999998,51.870510000000003,51.944229999999997,51.650950000000002,51.532879999999999,51.765659999999997,51.601120000000002,51.457999999999998,50.755400000000002,42.645870000000002,40.060650000000003,37.682949999999998,37.78725,36.6614,36.221510000000002,36.658639999999998,36.355089999999997,36.394939999999998,36.685119999999998,35.95758,35.981459999999998,35.464840000000002,35.884599999999999,36.893439999999998,1566.5509999999999,8875.0280000000002,7308.4780000000001,51.210520000000002,36.077629999999999,25,25,373928.94,334062.80221362057,12135.021007830001,70,52,67152.411235460007,44,11.625461223129188,12.232601223129187,271258.81487176998,11552.644655828082,2087.6627214904865,521.11172149048662,6.5529854746523966E-2,-1566.5500000000002,-4244.1666558280822,-4.4626600627882068E-2,0,0.43541313860361186,0.43541313860361186,10979.252901417145,-3670.774901417145,-3.8597495999702726E-2,0,37,0.43732925219949326]
["2013-05-12T18:00:00","2013-05-12T18:00:00",52.919559999999997,52.31268,51.52073,51.841819999999998,51.907730000000001,51.582180000000001,51.441510000000001,51.68244,51.560119999999998,51.504260000000002,51.543810000000001,51.704900000000002,51.651400000000002,51.847410000000004,50.723669999999998,42.363480000000003,36.962589999999999,36.802439999999997,36.561599999999999,36.670400000000001,36.719329999999999,36.131010000000003,36.199770000000001,35.698520000000002,36.060589999999998,35.719450000000002,2702.4319999999998,10016.27,7313.8410000000003,52.43141,36.284170000000003,19,19,284185.99440000003,296356.63018871663,23241.063833759992,75,54,80867.55779739999,44,12.214841720891341,12.82198172089134,216608.30511154307,13240.868714506587,3805.381087175323,1102.9490871753233,4.9802689607358223E-2,-2702.4290000000001,-5927.0277145065866,-6.2321562788411916E-2,0,0.26971394792294778,0.26971394792294778,12613.89378923219,-5300.0527892321898,{"$f":"IF(BF3131>1,1+BE3132*60/$BK$7,IF(BF3131<0,BE3132*60/$BK$7,BF3131+BE3132*60/$BK$7))","v":-5.5729041367158366E-2},0,36,0.27163006151882918]
["2013-05-13T03:00:00","2013-05-13T03:00:00",52.414029999999997,52.007919999999999,51.633090000000003,51.939439999999998,52.01793,51.669330000000002,51.893349999999998,51.757680000000001,51.668480000000002,51.487609999999997,51.656849999999999,51.667319999999997,51.641330000000004,51.878230000000002,52.19162,51.593969999999999,51.46602,51.84675,50.882260000000002,43.414610000000003,37.739829999999998,37.072029999999998,37.139659999999999,36.674610000000001,37.113729999999997,36.814259999999997,1478.62,8782.2199999999993,7303.6,49.2089,36.407470000000004,11,11,164528.73360000001,127250.72397198124,11533.065958699999,57,49,56212.487287299984,44,11.06986881649693,11.677008816496929,113649.83744377353,10155.944613097678,2083.6861122532523,605.06611225325241,2.8833136088470546E-2,-1478.619999999999,-2852.3446130976772,-2.9991858054632659E-2,0,0.1035631041478564,0.1035631041478564,9627.8915552216858,-2324.2915552216855,-2.4439481148837958E-2,0,null,0.10547921774373779]
["2013-05-13T06:00:00","2013-05-13T06:00:00",52.206609999999998,51.830289999999998,51.495809999999999,51.864130000000003,52.019889999999997,51.647260000000003,51.589280000000002,51.713819999999998,51.536230000000003,51.45364,51.668689999999998,51.642209999999999,51.639130000000002,51.857619999999997,52.051439999999999,51.004800000000003,46.981360000000002,40.109679999999997,37.551870000000001,37.072159999999997,37.008940000000003,36.452159999999999,36.569830000000003,36.101309999999998,36.489379999999997,36.184780000000003,5476.4570000000003,8857.4989999999998,14333.96,49.912770000000002,36.198039999999999,15,15,224357.364,192190.48052370563,43871.431528154986,57,49,60739.103630135018,44,11.224226433787605,11.831366433787604,157138.04219091934,10822.857858122996,7817.2748539875302,2340.8178539875298,3.9317912847914381E-2,5476.4609999999993,3511.1021418770033,{"$f":"IF(AZ3143>1,1+AY3144*60/$BK$7,IF(AZ3143<0,AY3144*60/$BK$7,AZ3143+AY3144*60/$BK$7))","v":7.6045572257944838E-2},7.6045572257944838E-2,{"$f":"IF(BB3143>1,1+AX3144*60/$BK$7,BB3143+AX3144*60/$BK$7)","v":0.22515116856518871},0.22515116856518871,10267.470620583334,4066.4893794166655,8.7674434339965274E-2,8.7674434339965274E-2,44,0.22706728216107011]
["2013-05-13T13:00:00","2013-05-13T13:00:00",52.24691,51.775469999999999,51.43065,51.776249999999997,51.805799999999998,51.552810000000001,51.36412,51.335659999999997,49.62932,41.149290000000001,37.644010000000002,37.633339999999997,37.129980000000003,36.918869999999998,37.24371,36.656239999999997,36.513359999999999,37.019260000000003,36.822719999999997,36.949919999999999,37.213470000000001,36.768770000000004,36.790100000000002,36.180709999999998,36.51784,36.354900000000001,3815.7370000000001,10645.64,14461.38,53.031269999999999,36.948399999999999,31,31,463671.88560000004,482499.50878666813,30319.865280684997,85,63,85606.222093400007,44,12.924053173384941,13.53119317338494,373933.25452067889,13247.581226250692,4692.0056539420621,876.26865394206197,8.125701988568973E-2,3815.74,1213.7987737493077,0.21434826773788018,0.21434826773788018,0.49789616979687579,0.49789616979687579,12653.166797113267,1808.2132028867327,0.26705901279009869,0.26705901279009869,44,0.49981228339275718]
["2013-05-13T16:00:00","2013-05-13T16:00:00",52.24091,51.762999999999998,51.390929999999997,51.755789999999998,51.616100000000003,50.600320000000004,43.68835,38.423589999999997,37.848610000000001,37.307139999999997,36.748449999999998,36.792740000000002,36.708799999999997,36.898150000000001,37.188720000000004,36.58831,36.517910000000001,37.044829999999997,36.919960000000003,37.07188,37.323590000000003,37.034489999999998,36.818089999999998,36.277360000000002,36.559429999999999,36.363219999999998,2854.9459999999999,11422.22,14277.17,54.119239999999998,37.690010000000001,37,37,553414.83120000002,613170.15621163056,22664.973777370004,87,63,93829.139745299981,44,13.204454665314731,13.811594665314729,455990.56150085595,14211.740223058056,3432.9284096685983,577.98240966859839,9.6984185024855479E-2,2854.9500000000007,65.42977694194451,0.22693745908112589,0.22693745908112589,0.59057779476752614,0.59057779476752614,13587.01033718207,690.15966281793044,0.29891405191414522,0.29891405191414522,44,0.59249390836340754]
["2013-05-13T23:00:00","2013-05-13T23:00:00",43.908700000000003,38.496079999999999,37.710030000000003,37.577129999999997,37.282879999999999,37.018880000000003,36.760289999999998,36.944580000000002,36.780279999999998,36.540329999999997,36.536299999999997,36.707520000000002,36.69209,36.996879999999997,37.526229999999998,36.90916,36.968829999999997,37.650010000000002,37.082520000000002,37.074809999999999,37.329270000000001,36.792189999999998,36.914400000000001,36.388779999999997,36.751010000000001,36.521680000000003,3079.9369999999999,11194.11,14274.04,50.00076,36.449779999999997,49,49,732900.72239999997,616438.83408353303,11375.778108869999,72,59,75845.580363900022,44,12.347827290408993,12.954967290408991,564703.24817157793,12284.846326415991,1842.5554296027415,-1237.3815703972584,0.12843851530318698,3079.9300000000003,1989.19367358401,0.26041899743843189,0.26041899743843189,0.81619457154691666,0.81619457154691666,11709.111827715862,2564.9281722841388,0.37819713977591962,0.37819713977591962,44,0.81811068514279806]
["2013-05-14T08:00:00","2013-05-14T08:00:00",43.685180000000003,37.276009999999999,36.62227,36.696129999999997,36.849299999999999,36.636670000000002,36.711539999999999,37.063760000000002,36.898200000000003,36.8063,36.775219999999997,36.816119999999998,36.763559999999998,37.020319999999998,37.4056,36.778599999999997,36.65504,37.325040000000001,37.096939999999996,37.162730000000003,37.435049999999997,36.830419999999997,36.86251,36.394979999999997,36.746720000000003,36.537039999999998,3235.9679999999998,10642.95,7406.9780000000001,51.34066,37.061399999999999,49,49,732900.72239999997,677014.02862922952,11565.576149760007,71,62,75986.725108500003,44,12.535181326199851,13.14232132619985,573271.51124174008,12123.753638837235,1845.2985798596681,-1390.6694201403318,0.12843851530318698,-3235.9720000000007,-4716.7756388372354,0.32440488310730614,0.32440488310730614,0.91986239464355291,0.91986239464355291,11563.6687343836,-4156.6907343836001,0.4932816174771974,0.4932816174771974,44,0.96597437334636593]
["2013-05-14T11:00:00","2013-05-14T11:00:00",53.134799999999998,52.06203,50.55856,47.319789999999998,40.47551,36.899120000000003,36.470460000000003,36.690399999999997,36.582090000000001,36.654420000000002,36.779989999999998,37.043080000000003,36.977800000000002,37.142569999999999,37.473489999999998,36.967379999999999,36.884259999999998,37.449930000000002,37.21425,37.328850000000003,37.522579999999998,36.956470000000003,36.904800000000002,36.403030000000001,36.740099999999998,36.488120000000002,4715.0870000000004,12117,7401.9110000000001,52.680160000000001,37.021979999999999,41,41,613243.46160000004,619610.94998185744,39245.272230579998,82,67,94865.083530000018,44,13.483168348373001,14.090308348373,515952.20547260914,14071.630803519156,5821.3724276928842,1106.2854276928838,0.10746896178429931,-4715.0889999999999,-6669.7198035191559,0.12878459930873104,0.12878459930873104,0.78487466805116102,0.78487466805116102,13465.295603833118,-6063.3846038331176,0.31650795297989348,0.31650795297989348,44,0.83098664675397405]
["2013-05-14T18:00:00","2013-05-14T18:00:00",54.525649999999999,54.054229999999997,53.647680000000001,53.98574,54.010420000000003,53.721380000000003,53.548319999999997,53.774430000000002,53.628830000000001,53.557720000000003,53.473579999999998,53.564219999999999,53.234870000000001,53.354019999999998,53.595440000000004,52.81438,52.60483,52.919339999999998,52.295569999999998,51.122669999999999,45.713749999999997,38.211590000000001,37.674889999999998,36.631860000000003,36.674250000000001,36.922649999999997,2987.5790000000002,12745.76,11446.3,53.601410000000001,39.13646,9,9,134614.4184,140100.57840687071,26295.176568500003,83,64,92183.390556000013,44,13.209181617959601,13.816321617959602,110956.32918499601,13957.471889199358,3981.3483270982188,993.76932709821858,2.3590747708748628E-2,-1299.4600000000009,-2511.1718891993587,-2.6404492117051141E-2,0,0.21438849529478413,0.21438849529478413,13344.129227011101,-1897.8292270111015,-1.9955311334781203E-2,0,38,0.26050047399759713]
["2013-05-15T03:00:00","2013-05-15T03:00:00",54.302100000000003,53.900480000000002,53.472270000000002,53.7393,53.73883,53.195300000000003,52.996119999999998,53.102969999999999,52.84064,52.688310000000001,52.520380000000003,52.115850000000002,50.93383,46.932079999999999,39.889580000000002,37.755800000000001,37.191499999999998,37.330199999999998,37.279820000000001,37.296379999999999,37.477989999999998,36.588990000000003,36.230469999999997,35.731659999999998,36.063049999999997,35.908540000000002,2738.65,11896.36,14635.01,51.949240000000003,37.098779999999998,21,21,314100.30960000004,314395.46337892499,25186.761547000002,72,68,88333.209162800034,44,13.321278432451482,13.928418432451481,261095.18322581073,13261.971756046283,3781.4330921337773,1042.7830921337772,5.5045077987080138E-2,2738.6499999999996,1373.038243953717,8.2432162105178716E-2,8.2432162105178716E-2,0.45141625795826851,0.45141625795826851,12683.882178179634,1951.1278218203661,0.12774581931794937,0.12774581931794937,44,0.49752823666108154]
["2013-05-15T08:00:00","2013-05-15T08:00:00",54.089320000000001,53.625509999999998,52.986750000000001,53.24859,53.199390000000001,52.817140000000002,52.58164,52.501800000000003,51.69632,50.127000000000002,44.429409999999997,38.859360000000002,37.784529999999997,37.443359999999998,37.545859999999998,37.286110000000001,36.720170000000003,37.135289999999998,36.690869999999997,36.768050000000002,37.198070000000001,36.702660000000002,36.569890000000001,36.030589999999997,36.337580000000003,36.173450000000003,1276.08,12023.63,13299.71,53.328830000000004,36.789859999999997,29,29,433757.57040000003,464335.61916073819,11431.041694799998,70,67,99429.227930550041,44,13.638805672431758,14.245945672431755,369154.35720582044,14580.342343542183,1676.2525941557578,{"$f":"AU3194-AC3194","v":400.17259415575791},7.6014631505967808E-2,{"$f":"AE3194-AD3194","v":1276.08},-1280.6323435421837,7.7581839776469597E-2,7.7581839776469597E-2,0.54846468299679751,0.54846468299679751,{"$f":"AO3194*1000/(500*AR3194)","v":13958.95087862955},{"$f":"AE3194-BD3194","v":-659.24087862955093},0.15504111360533099,0.15504111360533099,44,0.59457666169961054]
["2013-05-15T12:00:00","2013-05-15T12:00:00",53.882629999999999,53.244959999999999,52.847450000000002,53.057310000000001,53.110939999999999,52.550159999999998,52.089239999999997,51.589840000000002,49.05903,41.415889999999997,38.379060000000003,37.682459999999999,37.145969999999998,37.160249999999998,38.050879999999999,36.763359999999999,36.523339999999997,37.048450000000003,36.706829999999997,36.998179999999998,37.299109999999999,36.719909999999999,36.55359,36.141770000000001,36.311230000000002,36.210940000000001,486.00560000000002,12816.05,13302.06,54.541319999999999,37.73142,31,31,463671.88560000004,530355.18796194647,4294.2701507319998,76,69,107718.25944749999,44,14.04315564715975,14.650295647159751,406312.3870224338,15341.033333812857,611.58193480544696,125.57633480544695,8.125701988568973E-2,486.01000000000022,-2038.9733338128572,4.364194343508012E-3,4.364194343508012E-3,0.57886509801305441,0.57886509801305441,14705.267667193228,-1403.2076671932282,0.10829022010134598,0.10829022010134598,43,0.62497707671586744]
["2013-05-15T15:00:00","2013-05-15T15:00:00",54.372630000000001,53.932070000000003,53.489669999999997,53.39629,53.119390000000003,52.507660000000001,52.044069999999998,51.353059999999999,48.16574,42.765790000000003,39.395350000000001,38.124679999999998,37.36497,37.443330000000003,37.911119999999997,37.018650000000001,36.513150000000003,37.090389999999999,36.706769999999999,36.938040000000001,37.24371,36.658940000000001,36.826689999999999,36.394399999999997,36.566180000000003,36.304479999999998,8779.3719999999994,13249.23,4622.0860000000002,55.28763,37.982590000000002,31,31,463671.88560000004,549241.8643999648,79313.505100900016,72,69,114639.22755959998,44,14.279160659782359,14.886300659782361,413140.74970937351,16056.858003213656,11108.987004297616,2329.6150042976169,8.125701988568973E-2,-8627.1440000000002,-11434.772003213657,-0.12023444054855073,0,0.49491944952493616,0.49491944952493616,15401.976646799236,-10779.890646799235,-3.8768123103625707E-2,0,41,0.54103142822774919]
["2013-05-15T22:00:00","2013-05-15T22:00:00",55.808759999999999,55.44502,55.08567,55.412619999999997,55.477930000000001,55.0867,55.015210000000003,55.180140000000002,54.90314,54.702089999999998,54.373800000000003,53.56335,53.034179999999999,53.099519999999998,53.183309999999999,52.074460000000002,51.097929999999998,49.058869999999999,41.823309999999999,38.76061,38.354480000000002,37.578159999999997,37.303620000000002,37.168849999999999,36.828449999999997,36.64705,2608.0030000000002,12166.73,14774.74,52.072209999999998,36.885429999999999,13,13,194443.04880000002,187157.26465037517,24986.898582564998,64,63,92386.725914699986,44,13.155268353691271,13.762408353691271,159616.1103559706,14045.585909887874,3798.7668378583639,1190.7638378583638,3.4075524468192467E-2,2608.0100000000002,729.15409011212614,{"$f":"IF(AZ3207>1,1+AY3208*60/$BK$7,IF(AZ3207<0,AY3208*60/$BK$7,AZ3207+AY3208*60/$BK$7))","v":9.6442428361548684E-3},9.6442428361548684E-3,{"$f":"IF(BB3207>1,1+AX3208*60/$BK$7,BB3207+AX3208*60/$BK$7)","v":0.25269863312313229},0.25269863312313229,13425.953298344119,1348.7867016558812,2.2661401905061926E-2,2.2661401905061926E-2,43,0.29881061182594532]
["2013-05-16T07:00:00","2013-05-16T07:00:00",38.044029999999999,37.311459999999997,36.811070000000001,37.007759999999998,37.12603,36.687550000000002,36.597340000000003,36.799680000000002,36.453360000000004,36.281390000000002,36.437159999999999,36.424439999999997,36.403149999999997,36.669240000000002,37.065689999999996,36.412030000000001,36.276409999999998,36.854770000000002,36.553420000000003,36.601430000000001,36.928519999999999,36.339449999999999,36.498910000000002,36.021909999999998,36.376660000000001,36.134749999999997,1708.154,11140.57,12848.72,50.967460000000003,36.41534,51,51,762815.03760000004,706031.92834885779,1630.6721345600022,65,63,81059.455754200011,44,12.769008441218222,13.37614844121822,607800.43922224198,12696.280392851955,255.41092592533812,-1452.7430740746618,0.13368090368290891,1708.1499999999996,152.43960714804416,0.61396900763445783,0.61396900763445783,0.9855398993858222,0.9855398993858222,12119.999431886927,728.72056811307266,0.67946053454908095,0.67946053454908095,44,1]
["2013-05-16T10:00:00","2013-05-16T10:00:00",37.771239999999999,37.229349999999997,36.724020000000003,36.944870000000002,37.083109999999998,36.615090000000002,36.477930000000001,36.676879999999997,36.481119999999997,36.352519999999998,36.459060000000001,36.485889999999998,36.459339999999997,36.723030000000001,37.107120000000002,36.459980000000002,36.296340000000001,36.872750000000003,36.587400000000002,36.634340000000002,36.926270000000002,36.3887,36.502830000000003,36.053510000000003,36.438510000000001,36.246960000000001,787.35910000000001,12609.9,13397.26,50.810020000000002,36.19388,51,51,762815.03760000004,693196.6804757939,600.07786447399906,70,67,92154.031893000007,44,13.3907214875513,13.997861487551301,637393.76781709644,13763.863579519761,89.625919713416806,-697.73318028658321,0.13368090368290891,787.36000000000058,-366.60357951976039,0.59832328534546075,0.59832328534546075,1.0058003585979398,1,13166.872950551086,230.38704944891469,0.68243481992477195,0.68243481992477195,44,1]
["2013-05-16T17:00:00","2013-05-16T17:00:00",53.769579999999998,53.288910000000001,52.943300000000001,53.311070000000001,53.335250000000002,53.034579999999998,52.901040000000002,53.152459999999998,52.921579999999999,52.744190000000003,52.463880000000003,51.97186,49.16301,46.250509999999998,43.086069999999999,39.220750000000002,37.197180000000003,37.373069999999998,36.990850000000002,37.051670000000001,37.258609999999997,36.735439999999997,36.746859999999998,36.126959999999997,36.348289999999999,36.228569999999998,14784.21,14784.21,0,53.015900000000002,36.612319999999997,19,19,{"$f":"3.1416*(138/2)^2*AI3227","v":284185.99440000003},{"$f":"62.4*AJ3227*(AF3227-AB3227)/1000","v":297693.18192874745},129664.98772605001,81,73,121256.98573590005,44,14.748214213594192,15.355354213594193,261533.12152746352,{"$f":"AO3227*1000/(500*AQ3227)","v":16443.616017474335},17583.822128991193,2799.6121289911935,{"$f":"AJ3227/$BK$7","v":4.9802689607358223E-2},-14784.21,{"$f":"AE3227-AT3227","v":-16443.616017474335},-0.11517909340825777,0,0.37664756556991041,0.37664756556991041,15793.446904474591,-15793.446904474591,1.547978641787584E-2,1.547978641787584E-2,42,0.37683178501895753]
["2013-05-17T02:00:00","2013-05-17T02:00:00",53.697479999999999,53.214179999999999,52.854410000000001,53.188920000000003,53.21,52.851489999999998,52.683860000000003,52.850569999999998,52.528060000000004,52.037269999999999,50.256430000000002,46.144440000000003,40.783279999999998,37.972740000000002,37.589010000000002,36.777380000000001,36.645330000000001,37.174050000000001,36.946579999999997,37.058929999999997,37.298110000000001,36.733980000000003,36.837470000000003,36.357660000000003,36.72804,36.543930000000003,8469.6039999999994,11984.13,20453.740000000002,52.134039999999999,36.230809999999998,25,25,373928.94,363766.62234328402,72641.887847099977,74,71,95293.187869949994,44,13.741154706365297,14.348294706365294,320624.64181657642,13869.749654416955,10572.894258071365,2103.2902580713653,6.5529854746523966E-2,8469.6100000000024,6583.9903455830463,0.18687024326137069,0.18687024326137069,0.59132873096814187,0.59132873096814187,13282.859018455392,7170.8809815446093,0.2147949354865783,0.2147949354865783,44,0.59151295041718899]
["2013-05-17T03:00:00","2013-05-17T03:00:00",53.623309999999996,53.130710000000001,52.768560000000001,53.099469999999997,53.08437,52.617440000000002,52.209699999999998,51.442430000000002,48.192970000000003,43.094389999999997,38.712780000000002,37.14799,36.918050000000001,37.033999999999999,37.37576,36.742370000000001,36.614019999999996,37.137309999999999,36.905799999999999,37.023510000000002,37.268270000000001,36.70628,36.80124,36.316099999999999,36.67597,36.50311,9188.0540000000001,12003.1,21191.15,52.189169999999997,36.961449999999999,31,31,463671.88560000004,453846.74511288747,78650.661045399975,73,71,91389.922965999984,44,13.608053373140599,14.2151933731406,393723.51825265941,13431.740817005355,11559.428654305493,2371.3746543054931,8.125701988568973E-2,9188.0500000000011,7759.4091829946465,0.26845894672152282,0.26845894672152282,0.68793931937092234,0.68793931937092234,12858.062576718781,8333.0874232812203,0.30241575591909747,0.30241575591909747,44,0.68812353881996946]
["2013-05-17T12:00:00","2013-05-17T12:00:00",38.397440000000003,37.23066,36.775239999999997,37.154699999999998,37.223739999999999,36.767809999999997,36.546320000000001,36.82846,36.71069,36.71264,36.715470000000003,36.889580000000002,36.822110000000002,37.06006,37.439140000000002,36.801569999999998,36.699309999999997,37.180540000000001,36.969529999999999,37.086579999999998,37.312109999999997,36.728279999999998,36.767049999999998,36.272770000000001,36.61721,36.513579999999997,2629.85,15334.98,12705.13,54.64902,37.137709999999998,51,51,762815.03760000004,863240.74795873486,2477.1346105000075,84,74,134267.79431190001,44,15.252729786035792,15.859869786035791,726024.72666282195,17605.739588309643,324.81197074216556,-2305.0380292578343,0.13368090368290891,-2629.8500000000004,-4900.6095883096441,0.39311989586868623,0.39311989586868623,0.95676216014658289,0.95676216014658289,16931.765030015489,-4226.63503001549,0.48658649955109556,0.48658649955109556,44,1]
["2013-05-17T15:00:00","2013-05-17T15:00:00",55.387349999999998,54.786450000000002,53.681170000000002,51.83672,47.190939999999998,42.670119999999997,38.870429999999999,37.79054,36.9938,36.833959999999998,36.731009999999998,36.913330000000002,36.81203,37.006259999999997,37.415439999999997,36.841030000000003,36.742109999999997,37.211100000000002,37.000970000000002,37.160510000000002,37.372700000000002,36.746720000000003,36.78051,36.287390000000002,36.638979999999997,36.544130000000003,15796.66,15796.66,0,55.507620000000003,36.934069999999998,39,39,583329.14639999997,690266.08151061193,148829.96982259996,89,76,146700.02717150003,44,15.798362926548151,16.405502926548152,575056.28297275002,18571.547932346824,18841.188864258915,3044.5288642589148,0.10222657340457739,-15796.66,-18571.547932346824,8.070609303910356E-2,8.070609303910356E-2,0.71934703192928029,0.71934703192928029,17884.246259113846,-17884.246259113846,0.19553869882794803,0.19553869882794803,44,0.76258487178269752]
["2013-05-17T22:00:00","2013-05-17T22:00:00",56.683169999999997,56.224870000000003,55.883800000000001,56.298650000000002,56.289279999999998,56.033439999999999,55.876480000000001,56.15598,56.021259999999998,55.952500000000001,55.96801,56.13805,56.059620000000002,56.145060000000001,56.186149999999998,55.480499999999999,55.219819999999999,55.444299999999998,55.088979999999999,55.015239999999999,53.636279999999999,48.293520000000001,40.04786,37.38288,37.32414,36.899230000000003,1618.625,14773.21,13180.2,54.902760000000001,39.415900000000001,5,5,74785.788,84015.870296694324,16011.389941249994,83,75,114395.3175103,44,14.635925327101232,15.243065327101231,68300.494622656814,15632.126422300757,2187.9573150871202,569.33231508712015,1.3105970949304794E-2,-1593.0099999999984,-2451.9264223007558,-2.5781537364163262E-2,0,0.18422043547048494,0.18422043547048494,15009.489896617077,-1829.289896617076,-1.9234633384824534E-2,0,38,0.22745827532390217]
["2013-05-18T07:00:00","2013-05-18T07:00:00",56.364570000000001,55.713160000000002,55.22419,55.378950000000003,55.122219999999999,54.391469999999998,52.843310000000002,48.535780000000003,42.218159999999997,39.360430000000001,38.510269999999998,38.605159999999998,38.530430000000003,38.800710000000002,39.042940000000002,38.200839999999999,38.063549999999999,38.587620000000001,38.338149999999999,38.485689999999998,38.717199999999998,38.173470000000002,38.234909999999999,37.747700000000002,38.100279999999998,37.948880000000003,7512.0110000000004,13703.52,21215.53,53.528790000000001,37.764859999999999,33,33,493586.20079999999,479857.78374804987,69169.43292629499,73,69,108010.66501680002,44,14.053126677072882,14.660266677072883,432833.19492800598,15371.762811049748,9843.991947947381,2331.9809479473806,8.6499408265411637E-2,7512.0099999999984,5843.7671889502508,0.46684913466125322,0.46684913466125322,0.75471757622385394,0.75471757622385394,14735.156923948369,6480.3730760516301,0.51958117612850452,0.51958117612850452,44,0.79795541607727116]
["2013-05-18T10:00:00","2013-05-18T10:00:00",54.38194,50.437820000000002,43.496830000000003,39.41639,39.011159999999997,38.640799999999999,38.454880000000003,38.731189999999998,38.53669,38.311450000000001,38.205750000000002,38.2988,38.200510000000001,38.413670000000003,38.771630000000002,38.142040000000001,38.037840000000003,38.530430000000003,38.273879999999998,38.246470000000002,38.410409999999999,37.863860000000003,37.901899999999998,37.411299999999997,37.752749999999999,37.633270000000003,5768.549,15297.74,21066.29,53.749510000000001,38.008659999999999,45,45,673072.09200000006,676877.22161118255,48307.761789914985,82,73,120399.71533950001,44,14.718981293076951,15.326121293076952,618192.77713690663,16359.789165046337,6564.0088574114116,795.45985741141158,0.11795373854374315,5768.5500000000011,4706.5008349536638,0.63725787947145307,0.63725787947145307,0.96366322890109823,0.96366322890109823,15711.700701975578,5354.5892980244225,0.71010707982047616,0.71010707982047616,44,1]
["2013-05-18T17:00:00","2013-05-18T17:00:00",56.71698,56.189450000000001,55.816850000000002,56.237169999999999,56.192520000000002,55.963439999999999,55.445480000000003,55.100619999999999,53.729259999999996,52.216439999999999,49.617809999999999,47.025350000000003,43.871659999999999,41.532850000000003,40.324590000000001,38.875100000000003,38.340589999999999,38.678780000000003,38.497680000000003,38.685679999999998,38.903790000000001,38.36739,38.337429999999998,37.772489999999998,38.056870000000004,37.336289999999998,16519.07,16519.07,0,56.38373,38.098199999999999,25,25,373928.94,444437.07665220863,160075.48737915,90,75,151029.97502854999,44,15.885167148473556,16.492307148473557,370651.23972561606,19015.220125406464,20154.082847599377,3635.012847599377,6.5529854746523966E-2,-16519.07,-19015.220125406464,0.1352691817298807,0.1352691817298807,0.48914064628490428,0.48914064628490428,18315.202799570536,-18315.202799570536,0.25832364923132545,0.25832364923132545,44,0.48914064628490428]
["2013-05-19T01:00:00","2013-05-19T01:00:00",57.008099999999999,56.541179999999997,56.171660000000003,56.560859999999998,56.56297,56.305250000000001,56.1676,56.427759999999999,56.225990000000003,56.083829999999999,56.080919999999999,56.125599999999999,55.86506,55.825830000000003,55.650550000000003,54.4208,53.087859999999999,51.449269999999999,48.041890000000002,43.325870000000002,40.282069999999997,39.141579999999998,39.149900000000002,38.651919999999997,39.004109999999997,38.882759999999998,7558.6930000000002,14073.46,21632.15,53.820309999999999,38.181440000000002,11,11,164528.73360000001,153357.74591820888,68501.940290310013,78,69,110046.50569509999,44,14.12254884420291,14.729688844202911,144990.46077614898,15584.51054538535,9701.0732334523309,2142.3802334523307,2.8833136088470546E-2,7558.6900000000023,6047.6394546146512,0.12640539622995794,0.12640539622995794,0.36781628275585121,0.36781628275585121,14942.135826366817,6690.0141736331843,0.13977809147985212,0.13977809147985212,44,0.36781628275585121]
["2013-05-19T02:00:00","2013-05-19T02:00:00",56.972560000000001,56.519120000000001,56.155320000000003,56.55133,56.550809999999998,56.259259999999998,56.069960000000002,56.299550000000004,56.060549999999999,55.868690000000001,55.726280000000003,55.551360000000003,54.958100000000002,54.440109999999997,53.199399999999997,50.361150000000002,46.385559999999998,42.499830000000003,39.355849999999997,39.242820000000002,39.451270000000001,38.949019999999997,38.963180000000001,38.464820000000003,38.816879999999998,38.686790000000002,8324.4249999999993,13274.14,21598.57,53.372959999999999,37.86195,15,15,224357.364,205604.90423964686,76109.260466124979,76,68,102947.65914069999,44,13.819631176697872,14.426771176697871,193473.4477887839,14898.756388562144,11014.658711653243,2690.2337116532435,3.9317912847914381E-2,8324.43,6699.8136114378558,0.19685265491814188,0.19685265491814188,0.45534607203842559,0.45534607203842559,14271.753239835274,7326.8167601647256,0.21681816835349421,0.21681816835349421,44,0.45534607203842559]
["2013-05-19T11:00:00","2013-05-19T11:00:00",57.07734,56.537260000000003,55.884509999999999,55.51032,54.36101,51.379480000000001,46.462870000000002,42.786790000000003,39.477499999999999,38.75714,38.702060000000003,38.82179,38.681719999999999,38.862050000000004,39.189050000000002,38.533349999999999,38.353900000000003,38.767899999999997,38.53351,38.678100000000001,38.874789999999997,38.330190000000002,38.220840000000003,37.514519999999997,37.737099999999998,37.586379999999998,11842.63,11842.63,0,57.126289999999997,38.20505,35,35,523500.516,638299.14517783804,115412.11381240001,82,71,112038.62223059998,44,14.312174018063459,14.91931401806346,467527.66217277205,15656.408605596262,16127.8242797688,4285.1942797688007,9.1741796645133558E-2,-11842.63,-15656.408605596262,0.25513080694116747,0.25513080694116747,0.71848991729520106,0.71848991729520106,15019.272614672494,-15019.272614672494,0.33301647496209352,0.33301647496209352,44,0.71848991729520106]
["2013-05-19T14:00:00","2013-05-19T14:00:00",57.098109999999998,56.593980000000002,56.21611,56.61168,56.560499999999998,56.313740000000003,56.137810000000002,56.400570000000002,56.257489999999997,56.18085,56.158619999999999,56.363790000000002,56.278559999999999,56.36515,56.458469999999998,53.027279999999998,49.012500000000003,41.827860000000001,39.551810000000003,39.43477,39.627650000000003,39.032879999999999,38.844749999999998,38.173859999999998,38.414009999999998,38.180030000000002,1904.896,15486.08,13581.23,56.97193,40.639380000000003,15,15,224357.364,263084.71166961978,18018.487459839995,88,74,126463.58795199997,44,14.9866063491632,15.593746349163199,209810.98293816452,16876.881263924206,2404.612096966981,499.71609696698101,3.9317912847914381E-2,-1904.8500000000004,-3295.6512639242064,-3.4653142699276183E-2,0,0.40498167335715896,0.40498167335715896,16219.782612891653,-2638.5526128916536,-1.6610141271462247E-2,0,41,0.40498167335715896]
["2013-05-19T21:00:00","2013-05-19T21:00:00",58.830060000000003,57.64911,56.40654,56.659280000000003,56.637540000000001,56.37191,56.200479999999999,56.458500000000001,56.328310000000002,56.252899999999997,56.246940000000002,56.441600000000001,56.35698,56.517499999999998,56.800840000000001,56.169139999999999,55.980440000000002,55.85181,53.264400000000002,49.2973,42.226909999999997,39.720399999999998,39.353700000000003,38.561259999999997,38.884549999999997,38.543640000000003,2568.2779999999998,17093.560000000001,14525.28,56.784219999999998,39.8322,9,9,134614.4184,153219.7722418691,26050.583092379999,84,72,144885.18549559999,44,15.49308882539996,16.100228825399959,130141.0120265271,18703.202070082978,3362.8650020610066,794.58700206100684,2.3590747708748628E-2,-2568.2800000000007,-4177.9220700829774,-4.3930051479005756E-2,0,0.29336550655594534,0.29336550655594534,17997.903889046218,-3472.6238890462173,-3.651397600386444E-2,0,40,0.29336550655594534]
["2013-05-20T06:00:00","2013-05-20T06:00:00",56.961570000000002,56.53058,56.156080000000003,56.499879999999997,56.472099999999998,56.046489999999999,55.606670000000001,54.582999999999998,51.218829999999997,45.685540000000003,41.021230000000003,38.893300000000004,38.680210000000002,38.898119999999999,39.034050000000001,37.630119999999998,37.465359999999997,37.956949999999999,37.747889999999998,37.879800000000003,38.111150000000002,37.595529999999997,37.623350000000002,37.116729999999997,37.467950000000002,37.33549,6623.3329999999996,14569.53,21192.86,52.53886,37.439070000000001,29,29,433757.57040000003,411501.59438495629,64995.031662320005,74,69,109998.42169934999,44,14.120909179947837,14.728049179947835,382203.19848255359,15579.50983149887,9205.5023984737636,2582.169398473764,7.6014631505967808E-2,6623.33,5613.3501685011306,0.38443698308811708,0.38443698308811708,0.73814254695874204,0.73814254695874204,14937.269743655159,6255.5902563448417,0.43107494355618364,0.43107494355618364,44,0.73814254695874204]
["2013-05-20T13:00:00","2013-05-20T13:00:00",42.635469999999998,39.479610000000001,38.871859999999998,38.857590000000002,38.50779,38.115340000000003,37.791640000000001,38.041350000000001,37.722020000000001,37.408410000000003,37.357219999999998,37.556620000000002,37.359789999999997,37.464910000000003,37.769680000000001,37.146920000000001,37.030679999999997,37.503590000000003,37.332369999999997,37.527830000000002,37.756740000000001,37.239780000000003,37.217610000000001,36.682789999999997,37.048699999999997,36.958469999999998,3765.7809999999999,16786.75,20552.53,55.332439999999998,38.40907,49,49,732900.72239999997,840296.86330860981,10689.169368499999,87,75,142044.19067374998,44,15.578751901974876,16.185891901974877,712463.13983818016,18235.631656184654,1372.2754474503138,-2393.5055525496864,0.12843851530318698,3765.7799999999988,2316.8983438153446,0.60686672422403876,0.60686672422403876,1.0395964564402047,1,17551.605006878719,3000.9249931212798,0.70263478952969538,0.70263478952969538,44,1]
["2013-05-20T16:00:00","2013-05-20T16:00:00",56.467579999999998,55.941139999999997,55.474919999999997,55.233600000000003,53.665059999999997,50.964689999999997,48.557679999999998,44.869619999999998,41.998800000000003,40.078029999999998,38.707230000000003,38.33822,38.067010000000003,38.075609999999998,38.26193,37.526429999999998,37.34487,37.750019999999999,37.575339999999997,37.769159999999999,37.936459999999997,37.357599999999998,37.244509999999998,36.689129999999999,37.031419999999997,36.99559,16309.84,16309.84,0,57.11,37.395960000000002,35,35,523500.516,657066.01047581888,158792.52069079998,89,75,160766.4190768,44,16.217179890518882,16.824319890518879,529757.40734289098,19826.680120973382,19583.247119757922,{"$f":"AU3322-AC3322","v":3273.4071197579215},9.1741796645133558E-2,{"$f":"AE3322-AD3322","v":-16309.84},-19826.680120973382,0.20487191221558418,0.20487191221558418,0.65421988384251961,0.65421988384251961,{"$f":"AO3322*1000/(500*AR3322)","v":19111.193810264835},{"$f":"AE3322-BD3322","v":-19111.193810264835},0.32288772596356019,0.32288772596356019,44,0.65421988384251961]
["2013-05-21T01:00:00","2013-05-21T01:00:00",56.941040000000001,56.449039999999997,56.059330000000003,56.420699999999997,56.437959999999997,56.170459999999999,56.023769999999999,56.286659999999998,56.131720000000001,56.051189999999998,56.089060000000003,56.252830000000003,56.182250000000003,56.380229999999997,56.73442,55.972340000000003,55.22871,54.706859999999999,53.047089999999997,50.39987,45.814169999999997,41.648989999999998,39.7943,37.585470000000001,37.838659999999997,37.664230000000003,4378.92,14527.98,18906.900000000001,52.219070000000002,36.953020000000002,5,5,74785.788,67922.099145508604,42205.804422599991,78,71,110892.4345395,44,14.273089017796952,14.88022901779695,66607.270665941673,15538.673429588996,5914.0392622751888,1535.1192622751887,1.3105970949304794E-2,4378.9200000000019,3368.226570411005,4.6014008143324972E-2,4.6014008143324972E-2,0.29407993523548309,0.29407993523548309,14904.667718066863,4002.2322819331384,5.9404711856778307E-2,5.9404711856778307E-2,44,0.29407993523548309]
["2013-05-21T02:00:00","2013-05-21T02:00:00",56.867710000000002,56.417909999999999,56.047870000000003,56.408499999999997,56.426560000000002,56.14423,56.018830000000001,56.276629999999997,56.111490000000003,56.040819999999997,56.101469999999999,56.243960000000001,56.180610000000001,56.434269999999998,56.432589999999998,55.008670000000002,53.973660000000002,52.861879999999999,48.856029999999997,45.090800000000002,41.63391,39.343559999999997,37.665860000000002,37.12782,37.463839999999998,37.316139999999997,4423.7709999999997,14481.46,18905.23,51.938319999999997,36.753070000000001,9,9,134614.4184,122825.43040186299,43245.834185235006,77,70,109952.29523249998,44,14.180183267428252,14.787323267428249,119112.68449705659,15507.880703496881,6099.4746498897912,1675.7036498897914,2.3590747708748628E-2,4423.7700000000004,3397.3492965031182,8.1736486203951367E-2,8.1736486203951367E-2,0.34059503067560021,0.34059503067560021,14871.155954869771,4034.0740451302281,0.10182222886641756,0.10182222886641756,44,0.34059503067560021]
["2013-05-21T11:00:00","2013-05-21T11:00:00",56.772709999999996,56.285080000000001,55.879629999999999,55.658920000000002,54.841009999999997,53.177030000000002,50.752319999999997,46.364379999999997,42.294550000000001,39.806510000000003,38.3872,37.904490000000003,37.691699999999997,37.923589999999997,38.263069999999999,37.536569999999998,37.404269999999997,37.898009999999999,37.706760000000003,37.873190000000001,38.110759999999999,37.587560000000003,37.588470000000001,37.089019999999998,37.439120000000003,37.32009,3091,15621.54,18712.54,54.809289999999997,37.967570000000002,33,33,493586.20079999999,538663.49366115674,30064.024209999992,81,72,131546.80132439997,44,15.03824992516204,15.645389925162039,463174.7731878768,17494.961445519737,3998.3408122107066,907.34081221070664,8.6499408265411637E-2,3091,1217.5785544802638,0.35848547285148685,0.35848547285148685,0.75309612962797778,0.75309612962797778,16816.046382178942,1896.4936178210592,0.44032172507631495,0.44032172507631495,44,0.75309612962797778]
["2013-05-21T14:00:00","2013-05-21T14:00:00",56.018720000000002,54.825530000000001,53.101990000000001,51.009309999999999,46.792110000000001,42.38514,39.949089999999998,38.68468,37.987169999999999,37.720880000000001,37.736330000000002,37.712690000000002,37.66554,37.934150000000002,38.298699999999997,37.6633,37.506120000000003,38.027979999999999,37.717649999999999,37.76097,38.024889999999999,37.495049999999999,37.554769999999998,37.072330000000001,37.40728,37.222659999999998,4443.3689999999997,14250.56,18693.93,53.717179999999999,36.900230000000001,39,39,583329.14639999997,600396.21856517019,41758.915163070007,62,61,119825.47749599999,44,13.9692357826136,14.576375782613601,508476.5328197772,17155.62388103396,5978.6971618080952,1535.3281618080955,0.10222657340457739,4443.3700000000008,1538.3061189660402,0.39836503740988655,{"$f":"IF(AZ3344>1,1,IF(AZ3344<0,0,AZ3344))","v":0.39836503740988655},0.86733511032018984,{"$f":"IF(BB3344>1,1,BB3344)","v":0.86733511032018984},16441.05219061728,2252.8778093827204,0.50198898413384163,0.50198898413384163,44,0.86733511032018984]
["2013-05-21T21:00:00","2013-05-21T21:00:00",54.564990000000002,54.12724,53.736539999999998,53.97777,53.975659999999998,53.536549999999998,53.347299999999997,53.35454,52.571069999999999,51.250109999999999,48.601379999999999,43.94238,40.568289999999998,39.392499999999998,38.991129999999998,38.215560000000004,37.977879999999999,38.449840000000002,37.73986,37.568040000000003,37.79909,37.240049999999997,37.335169999999998,36.870710000000003,37.24783,36.986640000000001,9194.6620000000003,9510.31,18704.97,53.328539999999997,36.302959999999999,27,27,403843.25520000001,411812.92415033962,80813.493383850015,64,60,80959.271864899987,44,12.583051170593091,13.190191170593089,317090.61353302223,12867.987385142938,12844.8167758728,3650.1547758727993,7.0772243126245887E-2,9194.6600000000017,5836.9826148570628,7.9866600630990062E-2,7.9866600630990062E-2,0.65394456409058765,0.65394456409058765,12275.678315473529,6429.2916845264717,0.12564814136014774,0.12564814136014774,44,0.65394456409058765]
["2013-05-22T06:00:00","2013-05-22T06:00:00",36.95552,36.478349999999999,36.153309999999998,36.437779999999997,36.590910000000001,36.195439999999998,36.131160000000001,36.429749999999999,36.239240000000002,36.097169999999998,36.371139999999997,36.329610000000002,36.287309999999998,36.59308,36.961170000000003,36.350369999999998,36.232579999999999,36.78622,36.472900000000003,36.482210000000002,36.803800000000003,36.254100000000001,36.398760000000003,35.953850000000003,36.370800000000003,36.071919999999999,5533.5659999999998,9069.9570000000003,14603.52,50.809719999999999,36.082149999999999,51,51,762815.03760000004,701514.24477521586,2444.7294588000036,55,54,66789.213307244994,44,11.734770173777056,12.341910173777055,558571.05104343523,11383.131040179142,416.66422479463375,-5116.901775205366,0.13368090368290891,5533.5630000000001,3220.3889598208589,0.60525898095534758,0.60525898095534758,1.0581843565711826,1,10823.156604907481,3780.3633950925196,0.70267475471321683,0.70267475471321683,44,1]
["2013-05-22T13:00:00","2013-05-22T13:00:00",36.845770000000002,36.412930000000003,36.069699999999997,36.423340000000003,36.506709999999998,36.243519999999997,36.046469999999999,36.401960000000003,36.269759999999998,36.168419999999998,36.23995,36.387,36.318669999999997,36.577300000000001,36.923810000000003,36.317360000000001,36.208730000000003,36.771700000000003,36.507689999999997,36.570979999999999,36.861789999999999,36.313639999999999,36.415869999999998,35.951799999999999,36.375590000000003,36.093679999999999,2201.1019999999999,11583.8,13784.91,52.708509999999997,36.059170000000002,51,51,762815.03760000004,790860.23148085852,827.71340159000283,81,65,96431.312345999977,44,13.414882750998601,14.0220227509986,638543.83570240147,14376.765587283518,123.402256576322,-2077.6997434236778,0.13368090368290891,2201.1100000000006,-591.85558728351862,0.65753117350193147,0.65753117350193147,1.023144250655933,1,13754.265566161981,30.644433838018813,0.79910177728546661,0.79910177728546661,44,1]
["2013-05-22T16:00:00","2013-05-22T16:00:00",51.526690000000002,51.023449999999997,48.65202,47.748170000000002,45.958030000000001,42.254899999999999,39.418210000000002,38.271090000000001,37.197090000000003,36.64528,36.462260000000001,36.58493,36.440130000000003,36.67286,37.02026,36.384650000000001,36.290570000000002,36.764400000000002,36.53595,36.657200000000003,36.905909999999999,36.38523,36.545200000000001,36.145350000000001,36.5717,36.279269999999997,12497.97,12497.97,0,53.029269999999997,36.49718,39,39,583329.14639999997,609695.62381727993,95280.898868700024,85,64,103308.78242864998,44,13.588557480816966,14.195697480816964,494619.94209215924,15205.261128635839,14023.695893137818,1525.7258931378183,0.10222657340457739,-12497.97,-15205.261128635839,0.31774126521126772,0.31774126521126772,0.73735101318674623,0.73735101318674623,14554.942801261295,-14554.942801261295,0.47971951113498246,0.47971951113498246,44,0.73735101318674623]
["2013-05-22T20:00:00","2013-05-22T20:00:00",53.714829999999999,53.195819999999998,52.657150000000001,52.689369999999997,52.277810000000002,51.683669999999999,51.145949999999999,50.783110000000001,49.445729999999998,47.034350000000003,42.510469999999998,40.161830000000002,37.98903,37.791730000000001,37.874319999999997,37.018740000000001,36.841030000000003,37.288359999999997,36.996319999999997,37.098579999999998,37.326569999999997,36.773290000000003,36.853969999999997,36.36645,36.795099999999998,36.531750000000002,7632.4210000000003,13664,21296.42,53.467770000000002,37.592619999999997,27,27,403843.25520000001,426784.6406885758,65574.250318339982,75,65,108459.02480000003,44,13.825027745680002,14.432167745680001,348388.19858205353,15690.243346367379,9486.3101217037929,1853.8891217037926,7.0772243126245887E-2,7632.4199999999983,5606.1766536326195,0.13085705629759092,0.13085705629759092,0.63385901872178607,0.63385901872178607,15030.177962345982,6266.2420376540158,0.32006831739959307,0.32006831739959307,44,0.63385901872178607]
["2013-05-23T01:00:00","2013-05-23T01:00:00",39.002589999999998,37.758629999999997,37.129570000000001,37.211829999999999,37.22992,36.87218,36.714709999999997,36.978789999999996,36.809660000000001,36.678519999999999,36.786729999999999,36.880290000000002,36.774970000000003,36.946710000000003,37.255879999999998,36.643569999999997,36.51164,37.012810000000002,36.789279999999998,36.885800000000003,37.113759999999999,36.561909999999997,36.624659999999999,36.13899,36.558709999999998,36.286230000000003,2270.9160000000002,11396.94,13667.85,52.063690000000001,36.584870000000002,51,51,762815.03760000004,751001.70557146764,3084.3126928799938,71,66,88205.591405399988,44,13.195232666924142,13.802372666924139,628088.56674473442,13369.312028351078,467.48894403526407,-1803.4270559647362,0.13368090368290891,2270.91,298.53797164892239,0.41992404269080724,0.41992404269080724,1.023878184305675,1,12781.221538348251,886.6284616517496,0.64119102722992549,0.64119102722992549,44,1]
["2013-05-23T10:00:00","2013-05-23T10:00:00",38.922739999999997,37.618630000000003,37.104210000000002,37.289909999999999,37.259039999999999,36.89864,36.708100000000002,36.962910000000001,36.802790000000002,36.69735,36.770009999999999,36.79551,36.699480000000001,37.044229999999999,37.441969999999998,36.760100000000001,36.634439999999998,37.143470000000001,36.90504,36.930059999999997,37.124839999999999,36.613250000000001,36.765219999999999,36.245469999999997,36.620179999999998,36.475110000000001,1799.3689999999999,14591.76,12792.39,53.904299999999999,37.089280000000002,51,51,762815.03760000004,829623.48925170267,2202.0947727349967,79,73,122680.36811759998,44,14.796751552810161,15.403891552810158,704320.31854795979,16582.067716653772,297.64570485293859,-1501.7232951470614,0.13368090368290891,-1799.3700000000008,-3789.6777166537722,0.27318407732588668,0.27318407732588668,0.95167372875518241,0.95167372875518241,15928.490238587689,-3136.1002385876891,{"$f":"IF(BF3387>1,1+BE3388*60/$BK$7,IF(BF3387<0,BE3388*60/$BK$7,BF3387+BE3388*60/$BK$7))","v":0.55301225457498659},0.55301225457498659,44,1]
["2013-05-23T17:00:00","2013-05-23T17:00:00",56.665930000000003,56.303359999999998,55.952939999999998,56.356679999999997,56.323770000000003,56.048839999999998,55.721609999999998,55.899189999999997,55.700789999999998,55.561450000000001,55.430999999999997,55.36242,53.277270000000001,50.14875,46.050890000000003,41.121009999999998,38.679729999999999,37.699910000000003,37.342950000000002,37.407119999999999,37.534399999999998,36.953220000000002,36.974829999999997,36.485529999999997,36.904919999999997,36.76688,15071.6,15071.6,0,56.074170000000002,36.995829999999998,19,19,284185.99440000003,342380.15184791666,149955.26099000001,84,73,143770.55457200002,44,15.5159269109052,16.123066910905202,275147.12897651084,18531.996882629352,19329.204352542496,4257.6043525424957,4.9802689607358223E-2,-15071.6,-18531.996882629352,-0.1948604027088788,0,0.36006463957828994,0.36006463957828994,17834.144752541783,-17834.144752541783,-0.18446298671080955,0,41,0.40839091082310752]
["2013-05-23T20:00:00","2013-05-23T20:00:00",56.831389999999999,56.47757,56.108110000000003,56.485410000000002,56.43788,56.146769999999997,55.94238,56.174280000000003,55.931069999999998,55.738059999999997,55.752270000000003,55.91093,55.811459999999997,55.897219999999997,56.015160000000002,55.102989999999998,54.318219999999997,51.722369999999998,41.700110000000002,38.852989999999998,38.739379999999997,37.995190000000001,37.58202,36.733460000000001,37.009320000000002,36.78584,3590.2159999999999,16013.51,19177.66,54.936320000000002,39.025329999999997,13,13,194443.04880000002,220224.2433071257,35983.927169399998,81,72,127395.39873745004,44,14.896687096947048,15.503827096947047,180745.1727837603,17103.856435778755,4831.1315039670271,1240.9155039670272,3.4075524468192467E-2,3164.1499999999996,2073.8035642212453,2.1805647832913156E-2,2.1805647832913156E-2,0.32484255386825378,0.32484255386825378,16434.058241340455,2743.6017586595444,2.8848447738856638E-2,2.8848447738856638E-2,44,0.37316882511307137]
["2013-05-24T05:00:00","2013-05-24T05:00:00",56.010300000000001,55.43629,54.424570000000003,51.946249999999999,44.466650000000001,39.530610000000003,38.520530000000001,38.540770000000002,38.072670000000002,37.69699,37.604089999999999,37.473619999999997,37.225740000000002,36.697369999999999,36.960479999999997,36.370280000000001,36.244230000000002,36.724409999999999,36.356299999999997,36.438679999999998,36.684269999999998,36.154519999999998,36.216479999999997,35.71566,36.121299999999998,35.900080000000003,5943.9040000000005,14664.08,20607.990000000002,52.11992,37.328310000000002,41,41,613243.46160000004,620674.75567956408,59766.608549439996,74,71,108452.6761844,44,14.189893257888041,14.797033257888039,542996.01789899007,15285.904441051673,8423.827785486159,2479.9237854861585,0.10746896178429931,5943.9100000000017,5322.085558948329,0.46843202980920728,0.46843202980920728,0.83511023929579942,0.83511023929579942,14658.705470785608,5949.2845292143938,0.53510405299259578,0.53510405299259578,44,0.883436510540617]
["2013-05-24T12:00:00","2013-05-24T12:00:00",38.124769999999998,37.485550000000003,37.089919999999999,36.681919999999998,36.666719999999998,36.30988,36.09104,36.307560000000002,36.23648,36.099730000000001,36.09778,36.355179999999997,36.229390000000002,36.368020000000001,36.597859999999997,35.876089999999998,35.708829999999999,36.157440000000001,35.941989999999997,36.071199999999997,36.312199999999997,35.776389999999999,35.840089999999996,35.310389999999998,35.729340000000001,35.559139999999999,4643.6660000000002,15401.14,20044.810000000001,54.294620000000002,36.329340000000002,51,51,762815.03760000004,891802.44695281272,5956.9643997899975,82,74,138342.8962096,44,15.391690760747361,15.99883076074736,732639.22158255312,17976.309212553671,774.04938708640611,-3869.6166129135941,0.13368090368290891,4643.6700000000019,2068.5007874463299,0.7031213267402473,0.7031213267402473,1.0488273018810672,1,17294.125836873034,2750.6841631269672,0.81831763979616756,0.81831763979616756,44,1]
["2013-05-24T15:00:00","2013-05-24T15:00:00",47.673369999999998,47.091209999999997,45.133989999999997,41.251510000000003,39.081490000000002,37.192869999999999,36.139189999999999,36.312139999999999,36.073549999999997,35.907530000000001,35.9649,36.054380000000002,35.9298,36.138019999999997,36.473869999999998,35.838749999999997,35.71819,36.238010000000003,36.021889999999999,36.139620000000001,36.380209999999998,35.852919999999997,35.901440000000001,35.37856,35.761249999999997,35.636020000000002,15884.91,15884.91,0,54.589120000000001,36.00685,43,43,643157.77679999999,760645.62035080814,95606.110694249975,83,74,147588.84327285,44,15.706977555604187,16.314117555604184,630368.84133037704,18792.774453311788,12173.71201503221,-3711.19798496779,0.11271135016402123,-15884.91,-18792.774453311788,0.52666458891581158,0.52666458891581158,0.83297320956838383,0.83297320956838383,18093.389700033225,-18093.389700033225,0.66362488209797177,0.66362488209797177,44,0.83297320956838383]
["2013-05-25","2013-05-25",54.814,54.345359999999999,53.590519999999998,53.378,52.598500000000001,51.165390000000002,48.79016,46.014139999999998,41.988379999999999,39.448680000000003,37.442700000000002,36.731290000000001,36.548789999999997,36.84122,37.23189,36.616950000000003,36.503599999999999,37.079700000000003,36.79804,36.857619999999997,37.126069999999999,36.61739,36.701180000000001,36.2057,36.572560000000003,36.397449999999999,8797.9869999999992,12099.39,20897.38,51.209969999999998,36.45176,31,31,463671.88560000004,428572.50252259319,81014.283742425003,68,66,89282.66924594999,44,13.231961021286896,13.839101021286893,382841.99097616971,13495.001852305435,12245.242199866432,3447.255199866433,8.125701988568973E-2,8797.9900000000016,7402.378147694566,0.26875178089013591,0.26875178089013591,0.75977362200434884,0.75977362200434884,12902.957946273827,7994.4220537261735,0.46706221008291082,0.46706221008291082,44,0.75977362200434884]
["2013-05-25T01:00:00","2013-05-25T01:00:00",53.890160000000002,53.02073,51.659480000000002,50.24635,47.77337,43.965110000000003,40.078209999999999,38.416469999999997,37.209980000000002,36.630809999999997,36.576360000000001,36.605629999999998,36.584389999999999,36.855800000000002,37.217919999999999,36.603259999999999,36.480049999999999,37.06315,36.782139999999998,36.836759999999998,37.099899999999998,36.598260000000003,36.683860000000003,36.186810000000001,36.557650000000002,36.377070000000003,9031.9,11869.09,20900.990000000002,51.106009999999998,36.394269999999999,39,39,583329.14639999997,536129.56784879311,79088.238785499983,70,66,87307.483058299986,44,13.164607172288029,13.77174717228803,479188.2616249306,13263.970875194114,12015.28275784538,2983.3827578453802,0.10222657340457739,9031.9000000000015,7637.0191248058873,0.34905357629729888,0.34905357629729888,0.85474232302307129,0.85474232302307129,12679.216655092683,8221.7733449073185,0.55351258427175309,0.55351258427175309,44,0.85474232302307129]
["2013-05-25T10:00:00","2013-05-25T10:00:00",36.971739999999997,36.705300000000001,36.385480000000001,36.723959999999998,36.827100000000002,36.490070000000003,36.362690000000001,36.661340000000003,36.502139999999997,36.402900000000002,36.538589999999999,36.623480000000001,36.570700000000002,36.821300000000001,37.181820000000002,36.561909999999997,36.435400000000001,37.00873,36.746639999999999,36.82105,37.085740000000001,36.570210000000003,36.633330000000001,36.141120000000001,36.527329999999999,36.380339999999997,536.65279999999996,13320.05,13854.75,53.056139999999999,36.434049999999999,51,51,762815.03760000004,793762.38265022915,158.68823296000002,74,71,110703.53495225,44,14.266647541871727,14.873787541871724,679087.54873931897,15519.207946694132,22.246043787688716,-514.40675621231128,0.13368090368290891,534.70000000000073,-1664.4579466941323,0.73017850977828147,0.73017850977828147,1.0056222682309051,1,14885.722233238113,-1030.9722332381134,0.97596755336968777,0.97596755336968777,44,1]
["2013-05-25T17:00:00","2013-05-25T17:00:00",54.980220000000003,54.699719999999999,54.383940000000003,54.778309999999998,54.50076,53.407919999999997,52.326949999999997,51.145769999999999,48.620849999999997,45.467529999999996,43.030760000000001,40.199480000000001,38.368160000000003,38.466259999999998,38.814149999999998,38.199260000000002,38.043430000000001,38.587049999999998,38.361400000000003,38.437240000000003,38.601730000000003,38.116,38.232889999999998,37.858730000000001,38.301580000000001,38.124519999999997,14918.52,14918.52,0,54.845260000000003,38.150359999999999,29,29,433757.57040000003,452571.44759986218,125731.04878200006,74,68,124531.59977400003,44,14.555643552293402,15.162783552293403,393969.92436991562,17111.108736154605,17275.917527149082,2357.3975271490817,7.6014631505967808E-2,-14918.52,-17111.108736154605,9.0209272934064666E-2,9.0209272934064666E-2,0.48070692849428465,0.48070692849428465,16425.954950094154,-16425.954950094154,0.38444249763444316,0.38444249763444316,44,0.52254850689570653]
["2013-05-25T20:00:00","2013-05-25T20:00:00",55.383479999999999,55.081699999999998,54.68967,55.033299999999997,54.936700000000002,54.49615,54.235230000000001,54.242460000000001,53.814129999999999,53.273150000000001,52.51473,50.440739999999998,47.833530000000003,43.671950000000002,39.363549999999996,38.202840000000002,38.046460000000003,38.566249999999997,38.30292,38.335790000000003,38.574829999999999,38.08961,38.15437,37.646059999999999,38.005839999999999,37.946820000000002,292.50189999999998,13639.59,13414.12,52.704819999999998,36.597149999999999,23,23,344014.62479999999,316802.79276662006,2550.1280898269993,71,68,109851.00732764999,44,14.055035349872865,14.662175349872866,301712.59325608442,15631.551909066333,362.87750636643773,70.375606366437751,6.0287466366802052E-2,-225.46999999999935,-2217.4319090663321,-2.3104225428771285E-2,0,0.43012860602929304,0.43012860602929304,14984.271393071629,-1570.1513930716283,0.29158547229858012,0.29158547229858012,43,0.47197018443071492]
["2013-05-26T05:00:00","2013-05-26T05:00:00",39.897799999999997,39.437559999999998,38.91827,39.034379999999999,38.962150000000001,38.514130000000002,38.135800000000003,38.063639999999999,37.613950000000003,37.325159999999997,37.396430000000002,37.4465,37.231059999999999,37.195569999999996,37.369770000000003,36.65222,36.456440000000001,36.903559999999999,36.671419999999998,36.773919999999997,37.032040000000002,36.51426,36.551450000000003,36.053519999999999,36.418010000000002,36.278680000000001,6882.3620000000001,12717.88,19600.240000000002,52.668770000000002,36.292349999999999,51,51,762815.03760000004,780162.68426412472,12454.046980719984,73,70,104136.67219480002,44,13.981870521842682,14.589010521842681,665532.25988107594,14895.957165690555,1781.456488423933,-5100.9055115760675,0.13368090368290891,6882.3600000000024,4704.2828343094461,0.43224658289897855,0.43224658289897855,1.0487944010445338,1,14276.043195511647,5324.1968044883542,0.77367822292025867,0.77367822292025867,44,1]
["2013-05-26T12:00:00","2013-05-26T12:00:00",38.944870000000002,37.947569999999999,37.29336,37.628860000000003,37.494950000000003,36.988669999999999,36.407069999999997,36.669739999999997,36.558750000000003,36.459890000000001,36.512729999999998,36.672780000000003,36.589260000000003,36.8003,37.153919999999999,36.540469999999999,36.462359999999997,36.940049999999999,36.743189999999998,36.864730000000002,37.081150000000001,36.538040000000002,36.52216,36.026260000000001,36.409410000000001,36.300260000000002,2066.1019999999999,14876.37,12810.26,54.099899999999998,37.28604,51,51,762815.03760000004,847256.78268606728,2732.0170051099999,82,73,125064.60124409999,44,14.878053902423812,15.485193902423809,708190.28261231608,16811.957002484778,367.25461851767074,-1698.8473814823292,0.13368090368290891,-2066.1100000000006,-4001.6970024847778,0.46181690754692156,0.46181690754692156,0.94705962038584302,0.94705962038584302,16152.797573238568,-3342.5375732385673,0.85059320881430511,0.85059320881430511,44,1]
["2013-05-26T15:00:00","2013-05-26T15:00:00",54.23471,53.62021,51.195650000000001,47.86571,43.61403,39.423850000000002,37.374870000000001,37.415379999999999,37.116239999999998,36.825679999999998,36.682429999999997,36.785339999999998,36.661839999999998,36.832689999999999,37.19191,36.571579999999997,36.504390000000001,36.956789999999998,36.768259999999998,36.918100000000003,37.11459,36.570360000000001,36.548870000000001,36.035179999999997,36.39434,36.318440000000002,15161.11,15161.11,0,54.821660000000001,36.652320000000003,39,39,583329.14639999997,673512.37376288767,135815.27012984996,84,74,137733.68118369998,44,15.37091652836417,15.978056528364171,559497.34575548244,17921.336171403716,17671.720470178618,2510.6104701786171,0.10222657340457739,-15161.11,-17921.336171403716,0.17874238821459093,0.17874238821459093,0.73424830342505654,0.73424830342505654,17240.354725143927,-17240.354725143927,0.58852413290550354,0.58852413290550354,44,0.78718868303921352]
["2013-05-26T19:00:00","2013-05-26T19:00:00",56.070979999999999,55.751800000000003,55.402810000000002,55.818350000000002,55.765340000000002,55.518230000000003,55.317880000000002,55.61721,55.483840000000001,55.347679999999997,55.324210000000001,55.279089999999997,54.94079,54.639180000000003,54.508850000000002,52.575020000000002,47.014629999999997,39.078670000000002,38.008510000000001,37.918379999999999,38.000720000000001,37.316940000000002,37.673110000000001,36.642919999999997,36.759360000000001,36.426079999999999,3055.3939999999998,16060.6,13005.21,54.994500000000002,37.736289999999997,17,17,254271.67920000001,294616.81600982998,30011.4547953,83,73,138588.60376300005,44,15.339222388318301,15.946362388318303,243380.58166031557,18069.834344215938,3913.0347074380311,857.64070743803131,4.4560301227636302E-2,-3055.3900000000012,-5064.6243442159393,-5.3253556296901719E-2,0,0.32804308289561029,0.32804308289561029,17381.84551287067,-4376.6355128706709,0.10548756911427228,0.10548756911427228,42,0.38098346250976728]
["2013-05-26T20:00:00","2013-05-26T20:00:00",56.019069999999999,55.69941,55.37236,55.791890000000002,55.744779999999999,55.499200000000002,55.304490000000001,55.606479999999998,55.482230000000001,55.360610000000001,55.373330000000003,55.508240000000001,55.174689999999998,55.059820000000002,54.894030000000001,53.58419,52.268070000000002,44.771210000000004,38.348619999999997,38.05303,38.077219999999997,37.477739999999997,37.672359999999998,37.104480000000002,36.99212,36.550890000000003,2026.2070000000001,15024.21,12998,55.033329999999999,37.693019999999997,15,15,224357.364,258752.3027661411,19723.281296629993,81,72,130262.22945255002,44,14.994446024331957,15.601586024331956,209920.73760274641,17374.730515708205,2630.7449124328314,604.53791243283126,3.9317912847914381E-2,-2026.2099999999991,-4376.7305157082046,-4.6020484259769401E-2,0,0.30673787228752725,0.30673787228752725,16698.588111413206,-3700.5881114132062,6.6576592913667826E-2,6.6576592913667826E-2,42,0.35967825190168423]
["2013-05-26T21:00:00","2013-05-26T21:00:00",56.015279999999997,55.691040000000001,55.36374,55.785609999999998,55.747120000000002,55.502740000000003,55.31288,55.623559999999998,55.49004,55.365340000000003,55.408610000000003,55.521650000000001,55.31897,55.137540000000001,55.017209999999999,53.987520000000004,52.869439999999997,49.162909999999997,38.937950000000001,38.217660000000002,38.200110000000002,37.787309999999998,37.673290000000001,37.321330000000003,37.094769999999997,36.645760000000003,3037.7049999999999,14684.05,15697.83,54.427210000000002,37.53886,15,15,224357.364,248938.51320610271,29419.443875799992,80,72,123994.68790875001,44,14.780722857688376,15.387862857688376,206928.63474600788,16777.892272603251,3980.7855351941876,943.08053519418763,3.9317912847914381E-2,1013.7800000000007,-1080.0622726032507,-1.1356648218919603E-2,0,0.3173975750874653,0.3173975750874653,16115.907589701119,-418.077589701119,6.2180587021335797E-2,6.2180587021335797E-2,42,0.37033795470162229]
["2013-05-26T22:00:00","2013-05-26T22:00:00",55.986199999999997,55.677520000000001,55.360149999999997,55.76728,55.734029999999997,55.478209999999997,55.292189999999998,55.603499999999997,55.467480000000002,55.342170000000003,55.343640000000001,55.329279999999997,54.973849999999999,54.673050000000003,54.36891,52.383929999999999,46.778880000000001,39.847009999999997,38.103630000000003,38.195990000000002,38.104709999999997,37.499470000000002,37.424579999999999,36.885939999999998,37.232210000000002,37.143239999999999,5668.82,14391.35,20060.169999999998,53.267040000000001,36.760339999999999,17,17,254271.67920000001,255829.12374770155,53408.674253599995,79,71,118776.8485225,44,14.54194753461725,15.149087534617252,230730.57811224271,16335.755336725089,7345.4637525627313,1676.6437525627316,4.4560301227636302E-2,5668.8199999999979,3724.4146632749089,3.9161507836258207E-2,{"$f":"IF(AZ3472>1,1,IF(AZ3472<0,0,AZ3472))","v":3.9161507836258207E-2},0.37700413314379383,{"$f":"IF(BB3472>1,1,BB3472)","v":0.37700413314379383},15681.056466415219,4379.1135335847794,0.10822612825829081,0.10822612825829081,44,0.42994451275795081]
["2013-05-26T23:00:00","2013-05-26T23:00:00",55.970979999999997,55.671469999999999,55.350760000000001,55.762340000000002,55.72692,55.474150000000002,55.29401,55.587000000000003,55.399169999999998,55.166629999999998,54.942729999999997,54.770530000000001,54.096739999999997,53.418460000000003,49.327629999999999,42.185119999999998,38.152369999999998,38.099629999999998,37.640709999999999,37.610669999999999,37.73939,37.248640000000002,37.219810000000003,36.702590000000001,37.063070000000003,36.95449,6553.5990000000002,13991.2,20544.79,52.39526,36.552750000000003,19,19,284185.99440000003,273814.35598930536,62313.224923754991,78,71,110827.86295599998,44,14.2708871267996,14.878027126799601,253068.58194382148,15532.021516430328,8732.9153920271256,2179.3163920271254,4.9802689607358223E-2,6553.59,5012.7684835696728,9.1869809676646472E-2,9.1869809676646472E-2,0.44591387852508557,0.44591387852508557,14898.193424633184,5646.596575366817,0.16759901125515228,0.16759901125515228,44,0.49885425813924256]
["2013-05-27","2013-05-27",55.95008,55.65849,55.342979999999997,55.752609999999997,55.723770000000002,55.45111,55.239539999999998,55.372399999999999,55.015900000000002,54.495559999999998,54.06944,53.20384,48.611310000000003,42.465310000000002,38.972119999999997,37.689950000000003,37.318460000000002,37.498640000000002,37.301589999999997,37.460500000000003,37.692169999999997,37.202010000000001,37.182209999999998,36.673459999999999,37.037840000000003,36.93488,7467.442,13161.52,20628.96,52.281469999999999,36.452660000000002,23,23,344014.62479999999,329437.76741050853,70997.45155920001,77,70,104165.59969559999,44,13.982856949619961,14.589996949619961,300163.17471850844,14899.043889372135,10154.927825551364,2687.4858255513636,6.0287466366802052E-2,7467.4399999999987,5729.9161106278643,0.15211878165071377,0.15211878165071377,0.5244325818693707,0.5244325818693707,14279.043382296702,6349.9166177032967,0.23436716997706919,0.23436716997706919,44,0.57737296148352768]
["2013-05-27T01:00:00","2013-05-27T01:00:00",55.933309999999999,55.651859999999999,55.326979999999999,55.713830000000002,55.629469999999998,55.229810000000001,54.776339999999998,54.619459999999997,53.875830000000001,52.601300000000002,47.605870000000003,41.5886,38.201419999999999,37.952689999999997,37.828069999999997,37.07161,36.995069999999998,37.45731,37.276539999999997,37.425800000000002,37.657640000000001,37.168990000000001,37.144579999999998,36.637709999999998,36.998339999999999,36.89546,7998.1779999999999,12894.73,20892.900000000001,51.994999999999997,36.51585,27,27,403843.25520000001,380505.67686285073,76134.056518650003,76,70,99799.729939749988,44,13.833980790945475,14.441120790945476,348613.81370335672,14428.201317883893,11006.818307638643,3008.6403076386432,7.0772243126245887E-2,7998.1700000000019,6464.6986821161081,0.22009385182620433,0.22009385182620433,0.60853180965388065,0.60853180965388065,13821.604484095724,7071.2955159042776,0.30872048983943989,0.30872048983943989,44,0.66147218926803764]
["2013-05-27T02:00:00","2013-05-27T02:00:00",55.913730000000001,55.617870000000003,55.218420000000002,55.432609999999997,55.059199999999997,54.411209999999997,53.578969999999998,52.267800000000001,46.378169999999997,40.185789999999997,37.958359999999999,37.63711,37.214709999999997,37.279359999999997,37.629710000000003,37.019039999999997,36.939590000000003,37.404539999999997,37.22419,37.357909999999997,37.594090000000001,37.111739999999998,37.096919999999997,36.584249999999997,36.940480000000001,36.846179999999997,7906.65,12865.19,20771.84,52.123350000000002,36.549410000000002,31,31,463671.88560000004,442016.27936118149,75380.222103750013,75,70,100180.84857430001,44,13.846976936383632,14.454116936383631,400636.32373144908,14469.706858696321,10887.60708565704,2980.9570856570408,8.125701988568973E-2,7906.65,6302.1331413036787,0.28635957643305904,0.28635957643305904,0.69166872214291186,0.69166872214291186,13861.912009598685,6909.9279904013147,0.38137706103501601,0.38137706103501601,44,0.74460910175706885]
["2013-05-27T03:00:00","2013-05-27T03:00:00",55.77176,55.273739999999997,54.604790000000001,54.545169999999999,53.702559999999998,50.878129999999999,44.335590000000003,39.458300000000001,37.843519999999998,37.268270000000001,37.065359999999998,37.103209999999997,37.011830000000003,37.232860000000002,37.586329999999997,36.973869999999998,36.889629999999997,37.368819999999999,37.182369999999999,37.314329999999998,37.542050000000003,37.057659999999998,37.051009999999998,36.532040000000002,36.892899999999997,36.790689999999998,8014.991,12808.4,20823.39,52.00938,36.399720000000002,37,37,553414.83120000002,525548.32246395212,76066.552610185012,74,69,99967.384571999981,44,13.778850813905201,14.385990813905199,475826.23279197741,14510.264451243773,11041.059031341125,3026.0680313411249,9.6984185024855479E-2,8014.99,6313.1255487562266,0.35274088410182064,0.35274088410182064,0.7759448090103539,0.7759448090103539,13897.879661562636,6925.5103384373633,0.45419747763984214,0.45419747763984214,44,0.82888518862451088]
["2013-05-27T04:00:00","2013-05-27T04:00:00",55.056100000000001,54.280700000000003,52.870080000000002,49.527990000000003,43.042679999999997,38.509590000000003,37.556510000000003,37.415979999999998,37.008420000000001,36.819580000000002,36.907730000000001,37.013849999999998,36.934460000000001,37.164520000000003,37.51923,36.908720000000002,36.807479999999998,37.307040000000001,37.103020000000001,37.226349999999996,37.458300000000001,36.982700000000001,36.982550000000003,36.46378,36.828870000000002,36.720689999999998,8194.7999999999993,12763.7,20958.5,52.010750000000002,36.460369999999998,41,41,613243.46160000004,585095.42972223402,75127.508933999998,72,68,99240.192603000032,44,13.693206567762303,14.300346567762302,523989.61031154875,14494.806912011336,10972.960725046169,2778.1607250461693,0.10746896178429931,8194.7999999999993,6463.693087988664,0.42070538064739554,0.42070538064739554,0.86211156363653729,0.86211156363653729,13879.410842632326,7079.0891573676745,0.52863274615155398,0.52863274615155398,44,0.91505194325069428]
["2013-05-27T05:00:00","2013-05-27T05:00:00",53.057609999999997,48.394770000000001,41.438279999999999,38.404899999999998,37.849919999999997,37.161000000000001,36.779730000000001,37.030990000000003,36.876049999999999,36.763269999999999,36.871220000000001,36.983510000000003,36.902279999999998,37.139519999999997,37.499400000000001,36.884639999999997,36.77854,37.291469999999997,37.088419999999999,37.193899999999999,37.431449999999998,36.955950000000001,36.963650000000001,36.453040000000001,36.810099999999998,36.699689999999997,7704.7380000000003,13268.35,20973.09,52.56859,36.39161,45,45,673072.09200000006,666489.01617410139,63016.74391248,72,68,107320.91629150001,44,13.968759245540152,14.575899245540151,586683.6773016993,15365.848090733567,9022.5255951203453,1317.787595120345,0.11795373854374315,7704.74,5607.2419092664331,0.47966445685735959,0.47966445685735959,0.94312543109377123,0.94312543109377123,14725.803805804631,6247.2861941953688,0.59432176559983529,0.59432176559983529,44,0.99606581070792821]
["2013-05-27T06:00:00","2013-05-27T06:00:00",41.125480000000003,38.2547,37.260829999999999,37.323259999999998,37.168500000000002,36.841749999999998,36.68289,36.994109999999999,36.859589999999997,36.744489999999999,36.863599999999998,36.967709999999997,36.899389999999997,37.13053,37.483490000000003,36.871040000000001,36.770600000000002,37.280149999999999,37.080390000000001,37.177489999999999,37.412190000000002,36.940480000000001,36.948619999999998,36.44153,36.786929999999998,36.684719999999999,7754.9269999999997,13083.29,20838.22,52.597239999999999,36.305750000000003,49,49,732900.72239999997,727727.35795995744,17218.884812260017,72,68,106573.14410104997,44,13.943260213845805,14.550400213845805,637667.19016033912,15286.689406430456,2469.8506013911265,-5285.0763986088732,0.12843851530318698,7754.93,5551.5305935695451,0.53803773923836429,0.53803773923836429,1.024667036801443,1,14648.826497519645,6189.3935024803559,0.65940205446754641,0.65940205446754641,44,1]
["2013-05-27T07:00:00","2013-05-27T07:00:00",37.955219999999997,37.293900000000001,36.812159999999999,37.088039999999999,37.13194,36.834350000000001,36.678139999999999,36.998100000000001,36.855269999999997,36.748489999999997,36.875500000000002,36.974179999999997,36.903509999999997,37.133029999999998,37.487789999999997,36.871110000000002,36.764690000000002,37.27657,37.067500000000003,37.150959999999998,37.382559999999998,36.892209999999999,36.89725,36.38503,36.733150000000002,36.617980000000003,7608.6940000000004,13239.37,20848.060000000001,52.80903,36.376849999999997,51,51,762815.03760000004,770688.44826688897,5087.324982279978,73,68,108775.85546330002,44,14.018372671298533,14.625512671298532,667269.74972407799,15519.041762387964,725.80820920760061,-6882.8857907923993,0.13368090368290891,7608.6900000000005,5329.0182376120374,0.59407134675517659,0.59407134675517659,1.0800039200781832,1,14874.80923342461,5973.250766575391,0.72220964380763575,0.72220964380763575,44,1]
["2013-05-27T08:00:00","2013-05-27T08:00:00",37.48639,37.15316,36.767060000000001,37.09599,37.148739999999997,36.859340000000003,36.695749999999997,37.008009999999999,36.862340000000003,36.76117,36.876809999999999,36.987569999999998,36.911850000000001,37.154620000000001,37.503700000000002,36.87182,36.731459999999998,37.219819999999999,36.967660000000002,37.06926,37.311329999999998,36.829610000000002,36.842570000000002,36.334310000000002,36.687159999999999,36.580019999999998,7478.96,13369.49,20848.45,52.612009999999998,36.35671,51,51,762815.03760000004,763117.24661033624,3389.3524876000092,74,69,108662.5353985,44,14.07535545708885,14.682495457088852,669982.11085931398,15440.112433362907,481.60097951814225,-6997.3590204818574,0.13368090368290891,7478.9600000000009,5408.3375666370939,0.65093898184572041,0.65093898184572041,1.0786398339409187,1,14801.644000650675,6046.8059993493262,0.78579065235184276,0.78579065235184276,44,1]
["2013-05-27T09:00:00","2013-05-27T09:00:00",37.401009999999999,37.14378,36.784739999999999,37.10275,37.146709999999999,36.858870000000003,36.688209999999998,37.002139999999997,36.852710000000002,36.748849999999997,36.853259999999999,36.966769999999997,36.888390000000001,37.108310000000003,37.41178,36.766739999999999,36.669919999999998,37.173169999999999,36.975740000000002,37.086239999999997,37.323149999999998,36.848379999999999,36.853340000000003,36.341819999999998,36.699399999999997,36.589390000000002,7107,13615.75,20716.36,52.883679999999998,36.326419999999999,51,51,{"$f":"3.1416*(138/2)^2*AI3483","v":762815.03760000004},{"$f":"62.4*AJ3483*(AF3483-AB3483)/1000","v":775602.63699455478},2884.0916699999921,76,69,112719.7564225,44,14.21370669400725,14.820846694007251,676567.58246840956,{"$f":"AO3483*1000/(500*AQ3483)","v":15860.712317924026},405.81837406508123,-6701.1816259349189,{"$f":"AJ3483/$BK$7","v":0.13368090368290891},7100.6100000000006,{"$f":"AE3483-AT3483","v":4855.6476820759744},0.70199518851002418,0.70199518851002418,1.0746615560558188,1,15210.97394092576,5505.3860590742406,0.84367873377843783,0.84367873377843783,44,1]
["2013-05-27T10:00:00","2013-05-27T10:00:00",37.365499999999997,37.101550000000003,36.763469999999998,37.117249999999999,37.172040000000003,36.882429999999999,36.690809999999999,37.013280000000002,36.876130000000003,36.779119999999999,36.869979999999998,36.994030000000002,36.907119999999999,37.089149999999997,37.419220000000003,36.805129999999998,36.698749999999997,37.203490000000002,37.013640000000002,37.127009999999999,37.361989999999999,36.886130000000001,36.878160000000001,36.372489999999999,36.726700000000001,36.624879999999997,516.6173,13378.81,13804.33,53.404710000000001,37.976550000000003,51,51,762815.03760000004,798714.17510798853,191.30855236299996,77,70,103205.2106448,44,13.950107682987682,14.557247682987681,664020.35960347124,14796.331754579922,27.42753772378445,-489.18976227621556,0.13368090368290891,425.52000000000044,-992.00175457992191,0.69156447979527436,0.69156447979527436,1.0044742614131563,1,14179.220260902848,-374.89026090284824,0.83973683438821944,0.83973683438821944,44,1]
["2013-05-27T11:00:00","2013-05-27T11:00:00",37.369010000000003,37.095320000000001,36.756590000000003,37.106380000000001,37.151000000000003,36.882770000000001,36.700360000000003,37.018189999999997,36.884599999999999,36.781829999999999,36.858490000000003,36.98733,36.900979999999997,37.097099999999998,37.456420000000001,36.850020000000001,36.745559999999998,37.239849999999997,37.046970000000002,37.162399999999998,37.394060000000003,36.905360000000002,36.878010000000003,36.365110000000001,36.719349999999999,36.627119999999998,511.02600000000001,13908.37,13397.88,54.082929999999998,38.733710000000002,51,51,762815.03760000004,830890.59215687972,189.56253957000129,78,71,106741.31548569996,44,14.131535858062371,14.738675858062368,672656.27875140833,15106.824418493983,26.828299694240446,-484.19770030575955,0.13368090368290891,-510.4900000000016,-1708.9444184939839,0.67359525609510384,0.67359525609510384,0.99463229528858299,0.99463229528858299,14484.51903191971,-1086.6390319197108,0.82831103280298746,0.82831103280298746,44,1]
["2013-05-27T12:00:00","2013-05-27T12:00:00",37.39987,37.113509999999998,36.764519999999997,37.114330000000002,37.15119,36.885919999999999,36.696249999999999,37.016170000000002,36.886940000000003,36.785249999999998,36.842010000000002,36.992159999999998,36.914029999999997,37.152239999999999,37.550980000000003,36.933309999999999,36.845700000000001,37.352290000000004,37.165779999999998,37.301409999999997,37.521639999999998,36.996110000000002,36.903790000000001,36.363079999999997,36.73462,36.646320000000003,1210.502,14574.11,13363.6,54.480029999999999,38.913040000000002,51,51,762815.03760000004,848878.50304592354,456.08689104999826,80,72,113437.51231444998,44,14.420723169922745,15.027863169922744,686421.4959940298,15732.569161447635,63.254371597848461,-1147.2476284021516,0.13368090368290891,-1210.5100000000002,-2368.9691614476342,0.64868599846203723,0.64868599846203723,0.98190401416609785,0.98190401416609785,15096.958367505969,-1733.358367505969,0.8100851010984762,0.8100851010984762,44,1]
["2013-05-27T13:00:00","2013-05-27T13:00:00",37.5398,37.131950000000003,36.779159999999997,37.130249999999997,37.171579999999999,36.906109999999998,36.7012,37.028919999999999,36.9024,36.804270000000002,36.840580000000003,37.01923,36.934280000000001,37.130110000000002,37.622900000000001,36.974829999999997,36.884500000000003,37.351329999999997,37.169510000000002,37.293840000000003,37.484610000000004,36.98368,36.92353,36.399279999999997,36.745620000000002,36.649279999999997,1841.703,14937.15,13095.45,54.917009999999998,38.561160000000001,51,51,762815.03760000004,869537.70676135889,820.03667778000204,81,72,122154.89241374997,44,14.717985831308875,15.325125831308874,700571.0971151035,16599.403452868621,111.43327452260169,-1730.2697254773982,0.13368090368290891,-1841.6999999999989,-3503.9534528686199,0.61184259808681163,0.61184259808681163,0.96253889091781331,0.96253889091781331,15941.780022998621,-2846.3300229986198,0.78015648530835791,0.78015648530835791,44,1]
["2013-05-27T14:00:00","2013-05-27T14:00:00",39.56062,37.177129999999998,36.790390000000002,37.150939999999999,37.187339999999999,36.92324,36.699849999999998,37.020350000000001,36.897410000000001,36.810229999999997,36.830570000000002,37.018410000000003,36.935169999999999,37.150550000000003,37.623739999999998,37.033700000000003,36.965580000000003,37.422469999999997,37.238799999999998,37.36788,37.515270000000001,36.994320000000002,36.934310000000004,36.417070000000002,36.770650000000003,36.663249999999998,1898.144,15011.8,13113.66,54.884770000000003,38.108640000000001,49,49,732900.72239999997,833324.8666845056,2749.8127406400022,82,72,125919.954167,44,14.846374437094701,15.4535144370947,678969.31751797814,16963.05784291419,370.43559049263956,-1527.7084095073606,0.12843851530318698,-1898.1399999999994,-3849.3978429141898,0.57136691602148404,0.57136691602148404,0.94258031186449365,0.94258031186449365,16296.610674493702,-3182.9506744937025,0.74668836775132852,0.74668836775132852,44,0.98004142094668034]
["2013-05-27T15:00:00","2013-05-27T15:00:00",46.841450000000002,37.33914,36.838679999999997,37.173679999999997,37.201860000000003,36.940939999999998,36.720610000000001,37.034289999999999,36.900170000000003,36.804949999999998,36.822110000000002,37.014189999999999,36.935000000000002,37.128059999999998,37.561279999999996,37.037649999999999,37.009160000000001,37.450499999999998,37.280160000000002,37.424259999999997,37.599649999999997,37.048670000000001,36.97683,36.412199999999999,36.753639999999997,36.678449999999998,1798.232,14899.5,13101.26,54.939729999999997,38.209350000000001,49,49,732900.72239999997,835143.21096639708,9137.7159080000038,83,72,124637.14840499997,44,14.8026307606105,15.409770760610499,676968.78773920634,16839.864537681624,1234.6070176005849,-563.6249823994151,0.12843851530318698,-1798.2399999999998,-3738.6045376816237,0.53205620436985757,0.53205620436985757,0.92367216220385662,0.92367216220385662,16176.379303914075,-3075.1193039140744,0.71435407643163751,0.71435407643163751,44,0.96113327128604331]
["2013-05-27T16:00:00","2013-05-27T16:00:00",52.750190000000003,46.053989999999999,42.6556,38.844230000000003,37.343089999999997,36.969670000000001,36.740450000000003,37.064540000000001,36.929160000000003,36.82461,36.816319999999997,37.019289999999998,36.931510000000003,37.120910000000002,37.47419,36.98874,36.960850000000001,37.439880000000002,37.313940000000002,37.467230000000001,37.648240000000001,37.103549999999998,36.991149999999998,36.443550000000002,36.773339999999997,36.680480000000003,10023.07,15227.13,5204.0590000000002,54.99559,38.03125,45,45,673072.09200000006,769229.09874159144,80533.914104850002,84,73,129159.1052721,44,15.017676489778612,15.62481648977861,630737.88535396138,17200.943882365391,10725.216268929924,702.14626892992419,0.11795373854374315,-10023.071,-11996.88488236539,0.40591125440923026,0.40591125440923026,0.81828148769589848,0.81828148769589848,16532.559644024346,-11328.500644024345,0.59523705889903056,0.59523705889903056,44,0.85574259677808517]
["2013-05-27T17:00:00","2013-05-27T17:00:00",55.070489999999999,54.749740000000003,54.426819999999999,54.544620000000002,52.112430000000003,47.682879999999997,43.512880000000003,39.993899999999996,37.30359,36.93479,36.894390000000001,37.090919999999997,36.98122,37.143329999999999,37.493070000000003,36.878149999999998,36.797440000000002,37.238959999999999,37.135939999999998,37.386710000000001,37.716349999999998,37.378950000000003,37.258020000000002,36.545490000000001,36.795830000000002,36.720410000000001,15099.21,15099.21,0,55.117579999999997,37.133609999999997,35,35,523500.516,600969.90644743841,138535.85571840001,85,73,135771.86983185,44,15.243171761266087,15.850311761266084,497940.03682796413,17814.123196703109,18176.77552783717,3077.5655278371705,9.1741796645133558E-2,-15099.21,-17814.123196703109,0.21859915620415879,0.21859915620415879,0.65951618248781341,0.65951618248781341,17131.760166842909,-17131.760166842909,0.41509987744115767,0.41509987744115767,44,0.6969772915700001]
["2013-05-27T18:00:00","2013-05-27T18:00:00",55.512410000000003,55.196159999999999,54.862580000000001,55.272289999999998,55.230310000000003,55.02223,54.821420000000003,54.945259999999998,53.329630000000002,48.930489999999999,45.17886,41.218020000000003,37.716290000000001,37.305,37.626309999999997,36.994669999999999,36.9163,37.340299999999999,37.198860000000003,37.376849999999997,37.569479999999999,37.084989999999998,37.140050000000002,36.709609999999998,37.170430000000003,36.81183,15077.03,15077.03,0,55.015590000000003,37.162430000000001,27,27,403843.25520000001,458731.45938544418,140974.60283870003,84,73,134586.31445740003,44,15.202744322997344,15.809884322997341,383106.40713524824,17705.528896359843,18545.941422621487,3468.9114226214861,7.0772243126245887E-2,-15077.03,-17705.528896359843,3.2428906296968929E-2,3.2428906296968929E-2,0.50098409573748315,0.50098409573748315,17025.591295646402,-17025.591295646402,0.23607904135758656,0.23607904135758656,44,0.53844520481966973]
["2013-05-27T19:00:00","2013-05-27T19:00:00",55.622920000000001,55.314540000000001,54.973050000000001,55.382260000000002,55.328580000000002,55.11392,54.8979,55.197980000000001,55.072380000000003,54.942340000000002,54.830550000000002,54.902149999999999,54.025750000000002,50.437190000000001,44.709060000000001,37.668559999999999,37.008699999999997,37.450409999999998,37.279339999999998,37.447310000000002,37.645330000000001,37.133569999999999,36.988950000000003,36.466500000000003,36.95767,37.088859999999997,9201.8739999999998,14861.79,8303.2970000000005,54.868459999999999,39.123280000000001,21,21,314100.30960000004,348477.6587488036,85274.042414220021,83,72,117000.77933609998,44,14.54223057536101,15.14937057536101,285025.67346211791,16091.17373428738,11727.780270339043,2525.9062703390427,5.5045077987080138E-2,-6558.4930000000004,-7787.8767342873798,-4.9459128020196058E-2,0,0.43202279624896095,0.43202279624896095,15446.289171431381,-7142.9921714313805,0.16097184487536892,0.16097184487536892,43,0.46948390533114753]
["2013-05-27T20:00:00","2013-05-27T20:00:00",55.578090000000003,55.250349999999997,54.908070000000002,55.32,55.265790000000003,55.043210000000002,54.841030000000003,55.13532,54.979019999999998,54.849290000000003,54.808149999999998,54.891640000000002,54.351599999999998,49.954360000000001,40.640720000000002,37.159289999999999,37.013210000000001,37.44482,37.285609999999998,37.454799999999999,37.680190000000003,37.223390000000002,37.157679999999999,36.633369999999999,37.008209999999998,36.921500000000002,4768.4430000000002,15063.14,19831.59,54.858379999999997,37.37677,21,21,314100.30960000004,351560.32462250208,44481.442994685,82,71,131663.96942769998,44,14.981398357484569,15.58853835748457,293633.30020919448,17576.993320109119,5938.2231128594858,1169.7801128594856,5.5045077987080138E-2,4768.4500000000007,2254.5966798908812,2.3706652864885717E-2,2.3706652864885717E-2,0.48216213596405155,0.48216213596405155,16892.407281338699,2939.1827186613009,0.19187678900096161,0.19187678900096161,44,0.51962324504623814]
["2013-05-27T21:00:00","2013-05-27T21:00:00",55.566070000000003,55.245339999999999,54.909880000000001,55.307740000000003,55.237229999999997,55.005699999999997,54.806510000000003,55.085639999999998,54.901899999999998,54.724530000000001,54.548499999999997,53.279249999999998,45.208889999999997,38.186439999999997,37.780419999999999,37.107849999999999,37.021270000000001,37.473379999999999,37.313969999999998,37.478279999999998,37.712580000000003,37.257289999999998,37.189830000000001,36.673459999999999,37.034170000000003,36.918570000000003,5690.634,14107.93,19798.57,54.210439999999998,36.853299999999997,25,25,373928.94,403474.07067039062,53058.048757500001,81,71,122436.6580601,44,14.666747039849412,15.273887039849409,342221.64124880329,16695.816424383782,7235.1488183905794,1544.5148183905794,6.5529854746523966E-2,5690.6399999999994,3102.7535756162179,5.6331513266071345E-2,5.6331513266071345E-2,0.54199812714699003,0.54199812714699003,16032.154452977695,3766.415547022305,0.23147992809654827,0.23147992809654827,44,0.57945923622917661]
["2013-05-27T22:00:00","2013-05-27T22:00:00",55.53143,55.215000000000003,54.88541,55.27901,55.208289999999998,54.964280000000002,54.748420000000003,54.984610000000004,54.671419999999998,53.829830000000001,47.415140000000001,39.653660000000002,37.473390000000002,37.424109999999999,37.720080000000003,37.110030000000002,37.01925,37.477989999999998,37.30782,37.464039999999997,37.700290000000003,37.242959999999997,37.18526,36.66404,37.032470000000004,36.903799999999997,6383.75,13423.3,19807.05,53.61777,36.549729999999997,27,27,403843.25520000001,421189.02085198509,59457.066506250012,80,71,114554.71066600003,44,14.397972633710602,15.005112633710603,362826.30612872011,15912.616807978657,8259.0886951737339,1875.3386951737339,7.0772243126245887E-2,6383.75,3894.4331920213426,9.7280733413599954E-2,9.7280733413599954E-2,0.60912203741263393,0.60912203741263393,15268.75718461993,4538.2928153800694,0.27919920903624484,0.27919920903624484,44,0.64658314649482052]
["2013-05-27T23:00:00","2013-05-27T23:00:00",55.50076,55.184730000000002,54.842390000000002,55.229410000000001,55.150469999999999,54.853099999999998,54.528100000000002,54.019919999999999,48.250489999999999,40.779440000000001,37.305759999999999,37.379089999999998,37.213799999999999,37.338329999999999,37.667949999999998,37.046340000000001,36.960270000000001,37.414760000000001,37.256480000000003,37.406140000000001,37.64143,37.187570000000001,37.133560000000003,36.61412,36.980110000000003,36.855229999999999,7429.37,13189.18,20618.55,53.150440000000003,36.824559999999998,31,31,463671.88560000004,471471.35860955383,69262.270608050007,79,71,107662.48498920003,44,14.162947738131724,14.770087738131721,409778.34664377262,15203.400729826053,9780.7704848858812,2351.4004848858813,8.125701988568973E-2,7429.369999999999,5415.1492701739462,0.15421999226399713,0.15421999226399713,0.68724044198835621,0.68724044198835621,14578.448943299012,6040.1010567009871,0.34270971639092163,0.34270971639092163,44,0.72470155107054279]
["2013-05-28","2013-05-28",55.440840000000001,55.13749,54.775649999999999,55.095649999999999,54.84816,53.310580000000002,47.070259999999998,39.885730000000002,37.311300000000003,37.058190000000003,37.094099999999997,37.241979999999998,37.165610000000001,37.359180000000002,37.727989999999998,37.124360000000003,37.035510000000002,37.494500000000002,37.327809999999999,37.471449999999997,37.714300000000001,37.265740000000001,37.206949999999999,36.686889999999998,37.054819999999999,36.945149999999998,7663.8959999999997,12936.19,20600.09,53.053130000000003,36.63344,35,35,523500.516,526190.2365231833,70874.522304120022,78,70,106204.11479055003,44,14.052370314357757,14.659510314357757,459040.80210077658,15115.473391992506,10087.198204804672,2423.3022048046723,9.1741796645133558E-2,7663.9,5484.6166080074945,0.21188968688508275,0.21188968688508275,0.76782488465682985,0.76782488465682985,14489.449171645527,6110.6408283544733,0.40696193595278507,0.40696193595278507,44,0.80528599373901644]
["2013-05-28T01:00:00","2013-05-28T01:00:00",55.355350000000001,54.999569999999999,54.43929,53.09104,46.011740000000003,39.490409999999997,37.173729999999999,37.253030000000003,37.11721,37.00938,37.055230000000002,37.185200000000002,37.117629999999998,37.321779999999997,37.68045,37.073279999999997,36.979309999999998,37.444450000000003,37.273919999999997,37.411790000000003,37.645560000000003,37.192700000000002,37.142249999999997,36.619590000000002,36.986609999999999,36.868479999999998,7664.3329999999996,12833.33,20497.66,52.664340000000003,36.467379999999999,39,39,583329.14639999997,574965.17710032372,70844.763903855011,77,70,103930.46633840002,44,13.974838902139442,14.581978902139442,508680.48490662081,14873.94124056615,10138.902408815491,2474.5694088154914,0.10222657340457739,7664.33,5623.7187594338502,0.2710220140231217,0.2710220140231217,0.84841384869305969,0.84841384869305969,14254.645002010191,6243.0149979898088,0.47260604458989286,0.47260604458989286,44,0.88587495777524627]
["2013-05-28T02:00:00","2013-05-28T02:00:00",54.869250000000001,51.813090000000003,44.323129999999999,38.639789999999998,37.577800000000003,37.15654,36.923850000000002,37.23612,37.10257,36.968000000000004,37.007060000000003,37.100639999999999,37.028919999999999,37.230849999999997,37.589939999999999,36.98424,36.878639999999997,37.357329999999997,37.175150000000002,37.309840000000001,37.542850000000001,37.089680000000001,37.043080000000003,36.52516,36.884979999999999,36.779870000000003,8236.2070000000003,12647.82,20884.03,52.462859999999999,36.515450000000001,45,45,673072.09200000006,658680.8522183809,74493.939090829997,75,69,100849.98557309998,44,13.80894750804271,14.416087508042711,579971.63250352524,14606.469539313144,10789.227643517754,2553.0206435177533,0.11795373854374315,8236.2099999999991,6277.5604606868546,0.33702936159317043,0.33702936159317043,0.93501602154898278,0.93501602154898278,13991.311514561208,6892.7184854387906,0.54508166113235434,0.54508166113235434,44,0.97247713063116936]
["2013-05-28T03:00:00","2013-05-28T03:00:00",42.50882,38.381390000000003,36.984189999999998,37.281089999999999,37.328220000000002,37.066760000000002,36.900419999999997,37.207050000000002,37.035170000000001,36.853549999999998,36.90513,37.013739999999999,36.9358,37.152369999999998,37.508659999999999,36.897860000000001,36.798789999999997,37.28745,37.102179999999997,37.215290000000003,37.460520000000002,37.000709999999998,36.977179999999997,36.455039999999997,36.810749999999999,36.694479999999999,7950.2420000000002,12638.86,20589.099999999999,52.337090000000003,36.583579999999998,49,49,732900.72239999997,715383.56255941954,23112.705035140003,73,68,99553.203699300037,44,13.703880246146133,14.311020246146132,626719.62488201598,14529.19930868439,3373.1621438591983,-4577.0798561408019,0.12843851530318698,7950.239999999998,6059.9006913156081,0.40074805831885396,0.40074805831885396,1.0186112745507971,1,13912.803138701322,6676.296861298677,0.61528164569074284,0.61528164569074284,44,1]
["2013-05-28T04:00:00","2013-05-28T04:00:00",37.963079999999998,37.43497,37.000390000000003,37.268599999999999,37.316479999999999,37.04419,36.88261,37.179699999999997,37.022950000000002,36.883789999999998,36.951129999999999,37.03228,36.937379999999997,37.148110000000003,37.491129999999998,36.877719999999997,36.77355,37.269829999999999,37.07226,37.177880000000002,37.428420000000003,36.967860000000002,36.945450000000001,36.427529999999997,36.782919999999997,36.667310000000001,2363.8580000000002,12214.42,14578.28,52.966140000000003,36.321309999999997,51,51,762815.03760000004,775818.73944344698,1531.5081403299971,73,68,101653.47222430004,44,13.775499402848633,14.382639402848632,655709.06512442802,14758.589761657446,222.35246731066562,-2141.5055326893344,0.13368090368290891,2363.8600000000006,-180.30976165744505,0.39885213566187117,0.39885213566187117,1.0248555357776457,1,14135.579621660612,442.70037833938841,0.61993655549614246,0.61993655549614246,44,1]
["2013-05-28T05:00:00","2013-05-28T05:00:00",37.681319999999999,37.37068,36.990279999999998,37.256439999999998,37.302059999999997,37.03199,36.871429999999997,37.181440000000002,37.033279999999998,36.932659999999998,37.03069,37.11065,37.02637,37.213859999999997,37.522770000000001,36.884549999999997,36.74335,37.244869999999999,37.02364,37.110349999999997,37.35924,36.888629999999999,36.873060000000002,36.347709999999999,36.699179999999998,36.591560000000001,2100.4160000000002,12476.19,14576.61,53.63429,36.609079999999999,51,51,762815.03760000004,811228.12528721476,1144.4746700799983,73,68,106204.87737495001,44,13.930702318485798,14.537842318485795,663096.67088309745,15247.598426393477,164.30968718085381,-1936.1063128191463,0.13368090368290891,2100.42,-670.9884263934764,0.39179682069456806,0.39179682069456806,1.022085514564349,1,14610.817072888969,-34.207072888968469,0.61957687466731148,0.61957687466731148,44,1]
["2013-05-28T06:00:00","2013-05-28T06:00:00",37.594099999999997,37.34628,37.017270000000003,37.34731,37.33128,37.00338,36.815779999999997,37.119459999999997,36.966140000000003,36.854810000000001,36.964260000000003,37.069859999999998,37.002850000000002,37.198729999999998,37.538209999999999,36.914700000000003,36.801020000000001,37.284739999999999,37.046599999999998,37.103340000000003,37.339359999999999,36.871560000000002,36.860309999999998,36.333080000000002,36.690420000000003,36.579009999999997,1856.713,12734.14,14590.85,53.77272,36.751199999999997,51,51,762815.03760000004,818414.7217043303,942.36539958500066,73,68,108377.20934640002,44,14.004778838712243,14.611918838712242,666622.68793735455,15477.17541198465,134.57769100645825,-1722.1353089935417,0.13368090368290891,1856.7100000000009,-886.32541198464969,0.38247727851008129,0.38247727851008129,1.0195229505274053,1,14834.08312661438,-243.23312661437922,0.61701932486280853,0.61701932486280853,44,1]
["2013-05-28T07:00:00","2013-05-28T07:00:00",37.549280000000003,37.287190000000002,36.968260000000001,37.302259999999997,37.345829999999999,37.078710000000001,36.895910000000001,37.144820000000003,36.952309999999997,36.827599999999997,36.929319999999997,37.029879999999999,36.957149999999999,37.17915,37.538330000000002,36.918700000000001,36.803870000000003,37.29372,37.069600000000001,37.101379999999999,37.322310000000002,36.85528,36.841880000000003,36.316110000000002,36.678809999999999,36.571530000000003,1532.7919999999999,13074.87,14607.67,53.595610000000001,36.796149999999997,51,51,762815.03760000004,810340.39165905735,749.34368900000027,74,69,109825.37778510003,44,14.115008382471913,14.722148382471911,671869.57655997667,15561.5037283976,106.17686772762231,-1426.6151322723777,0.13368090368290891,1532.7999999999993,-953.83372839759977,0.37244789929045252,0.37244789929045252,1.0161170988298693,1,14919.74879370967,-312.07879370967021,0.61373787603652641,0.61373787603652641,44,1]
["2013-05-28T08:00:00","2013-05-28T08:00:00",37.596420000000002,37.315930000000002,36.950270000000003,37.286299999999997,37.33229,37.065640000000002,36.90401,37.185859999999998,37.02449,36.849400000000003,36.907550000000001,37.013019999999997,36.939990000000002,37.152299999999997,37.508270000000003,36.881050000000002,36.771639999999998,37.268389999999997,37.038069999999998,37.101419999999997,37.336979999999997,36.859630000000003,36.842910000000003,36.314309999999999,36.664070000000002,36.501869999999997,1393.7840000000001,13057.56,14451.35,54.086269999999999,36.821910000000003,51,51,762815.03760000004,837011.4322236228,762.78313860000367,75,70,112715.20828079997,44,14.27439860237528,14.881538602375279,679456.49657110905,15792.638474036166,106.87429430099779,-1286.9097056990024,0.13368090368290891,1393.7900000000009,-1341.288474036166,0.3583445075267484,0.3583445075267484,1.014655435267539,1,15148.32723853019,-696.97723853018942,0.60640929368034124,0.60640929368034124,44,1]
["2013-05-28T09:00:00","2013-05-28T09:00:00",37.685969999999998,37.332819999999998,36.93121,37.257129999999997,37.310400000000001,37.058430000000001,36.879930000000002,37.192100000000003,37.04862,36.905149999999999,36.938659999999999,37.027099999999997,36.946399999999997,37.165529999999997,37.516979999999997,36.885390000000001,36.770530000000001,37.252389999999998,37.056040000000003,37.156959999999998,37.355400000000003,36.876640000000002,36.847529999999999,36.318420000000003,36.657550000000001,36.467199999999998,854.33399999999995,13510.44,14364.77,54.431220000000003,37.199730000000002,51,51,762815.03760000004,855081.21452502254,520.6183245899997,78,71,116402.50587780001,44,14.460982450432983,15.06812245043298,688337.8239915825,16098.837859292851,72.003174939806613,-782.33082506019332,0.13368090368290891,854.32999999999993,-1734.0678592928507,0.34011111565179863,0.34011111565179863,1.0089831165470526,1,15450.167233603175,-1085.3972336031748,0.59499654936689572,0.59499654936689572,44,1]
["2013-05-28T10:00:00","2013-05-28T10:00:00",37.754219999999997,37.420099999999998,36.998629999999999,37.290140000000001,37.326549999999997,37.0535,36.86477,37.17174,37.032290000000003,36.910170000000001,36.96264,37.072009999999999,36.962820000000001,37.156419999999997,37.507370000000002,36.886200000000002,36.786879999999996,37.246130000000001,37.041200000000003,37.121009999999998,37.3459,36.87961,36.843519999999998,36.327680000000001,36.72345,36.607489999999999,872.22410000000002,14645.35,14303.52,54.959919999999997,38.068899999999999,51,51,762815.03760000004,873569.3978232852,500.10277109649911,80,71,123687.44987849999,44,14.709399040856852,15.316539040856849,700162.36882329639,16817.471541148014,67.997716250325766,-804.22638374967426,0.13368090368290891,-341.82999999999993,-2513.9515411480133,0.31367739602615596,0.31367739602615596,0.9964057229299228,0.9964057229299228,16150.835322335401,-1847.3153223354002,0.57557238207826589,0.57557238207826589,44,1]
["2013-05-28T11:00:00","2013-05-28T11:00:00",37.800139999999999,37.413119999999999,36.976649999999999,37.338619999999999,37.333779999999997,37.118139999999997,36.886839999999999,37.17801,37.039969999999997,36.917369999999998,36.958530000000003,37.095120000000001,36.983849999999997,37.166969999999999,37.524830000000001,36.91066,36.813470000000002,37.285409999999999,37.098990000000001,37.187370000000001,37.341180000000001,36.880220000000001,36.830359999999999,36.320140000000002,36.718829999999997,36.690539999999999,1066.2239999999999,15359.97,14293.74,55.604529999999997,38.743310000000001,51,51,762815.03760000004,900299.46196419979,591.54107520000025,81,71,129493.91668169996,44,14.90739955884597,15.514539558845968,709587.12583195709,17373.106043147407,79.362074232320808,-986.86192576767917,0.13368090368290891,-1066.2299999999996,-3079.3660431474073,0.28129845105567663,0.28129845105567663,0.9851945184118045,0.9851945184118045,16693.233620054943,-2399.4936200549437,0.55034216560118687,0.55034216560118687,44,1]
["2013-05-28T12:00:00","2013-05-28T12:00:00",37.706940000000003,37.488819999999997,37.014299999999999,37.287750000000003,37.344569999999997,37.088639999999998,36.935450000000003,37.199080000000002,37.087220000000002,36.936529999999998,36.931930000000001,37.10736,37.038809999999998,37.202649999999998,37.544939999999997,36.926990000000004,36.833309999999997,37.297669999999997,37.122199999999999,37.256100000000004,37.391930000000002,36.888019999999997,36.829120000000003,36.307690000000001,36.646880000000003,36.629809999999999,854.33619999999996,15147.38,14293.04,54.782080000000001,38.294849999999997,51,51,762815.03760000004,864041.85020870192,460.11557555300163,82,70,124869.16897870002,44,14.688848662173672,15.295988662173672,699184.17781909136,17001.900128532165,62.648283216080635,-791.68791678391938,0.13368090368290891,-854.33999999999833,-2708.8601285321638,0.25281530491277104,0.25281530491277104,0.97621129671666451,0.97621129671666451,16327.047794889671,-2034.0077948896705,0.52895496267127973,0.52895496267127973,44,1]
["2013-05-28T13:00:00","2013-05-28T13:00:00",37.946820000000002,37.44802,37.080159999999999,37.346620000000001,37.325870000000002,37.065190000000001,36.886270000000003,37.21904,37.112369999999999,36.949199999999998,36.92848,37.114319999999999,37.00779,37.198169999999998,37.555250000000001,36.940950000000001,36.84713,37.30415,37.130569999999999,37.216180000000001,37.435659999999999,36.946300000000001,36.834470000000003,36.288249999999998,36.643039999999999,36.67577,1129.3610000000001,15402.29,14272.93,54.685020000000002,38.107239999999997,51,51,762815.03760000004,857234.14707202278,717.73714952500143,83,71,127667.88755810003,44,14.845131965731213,15.45227196573121,706623.20967365196,17199.966676323394,96.696634449843842,-1032.6643655501562,0.13368090368290891,-1129.3600000000006,-2927.0366763233942,0.22203807409925547,0.22203807409925547,0.96433629232307017,0.96433629232307017,16524.157462570096,-2251.2274625700957,0.50528373648211067,0.50528373648211067,44,1]
["2013-05-28T14:00:00","2013-05-28T14:00:00",40.40146,37.597610000000003,37.100819999999999,37.450980000000001,37.43665,37.11,36.84796,37.193179999999998,37.118769999999998,37.001060000000003,36.952010000000001,37.142060000000001,37.034520000000001,37.229950000000002,37.58822,36.974249999999998,36.882770000000001,37.32403,37.159100000000002,37.2624,37.455249999999999,36.970309999999998,36.866549999999997,36.305239999999998,36.650979999999997,36.691360000000003,2356.0340000000001,16071.43,13715.4,53.722000000000001,37.141019999999997,49,49,732900.72239999997,778862.34559750243,4370.5608716999959,83,71,133240.02970070002,44,15.035142012793873,15.642282012793871,687602.22601594485,17723.813927041316,581.37939342121933,-1774.6546065787807,0.12843851530318698,-2356.0300000000007,-4008.4139270413161,0.17989036832345306,0.17989036832345306,0.93956308749782402,0.93956308749782402,17035.881285316631,-3320.4812853166313,0.47036951085699324,0.47036951085699324,44,0.97522679517475386]
["2013-05-28T15:00:00","2013-05-28T15:00:00",51.510980000000004,45.977829999999997,44.393790000000003,42.229759999999999,39.154710000000001,37.348300000000002,36.928570000000001,37.221730000000001,37.103209999999997,37.008369999999999,37.018320000000003,37.169240000000002,37.088200000000001,37.267449999999997,37.615160000000003,36.995249999999999,36.898719999999997,37.345089999999999,37.190260000000002,37.324629999999999,37.515639999999998,37.003689999999999,36.890949999999997,36.32159,36.658650000000002,36.57555,13001.51,16962.02,3960.51,52.511479999999999,37.314920000000001,43,43,643157.77679999999,639557.40014652244,97091.571249650035,85,72,128882.17732559999,44,14.947386246802962,15.554526246802959,599884.12894579663,17244.777808985313,12991.11023780717,-10.399762192830167,0.11271135016402123,-13001.51,-13284.267808985313,4.0208833119989268E-2,4.0208833119989268E-2,0.8028546965743274,0.8028546965743274,16571.662200523802,-12611.152200523802,0.33776565753342369,0.33776565753342369,44,0.83851840425125723]
["2013-05-28T16:00:00","2013-05-28T16:00:00",52.452770000000001,52.11309,51.764270000000003,52.174010000000003,51.785760000000003,49.780670000000001,46.670789999999997,44.134880000000003,40.990090000000002,38.517119999999998,37.272109999999998,37.321820000000002,37.170250000000003,37.329979999999999,37.701070000000001,37.07929,36.988010000000003,37.433689999999999,37.271819999999998,37.421419999999998,37.652679999999997,37.138779999999997,37.01343,36.414209999999997,36.692909999999998,36.58672,17086.990000000002,17086.990000000002,0,52.385590000000001,37.077919999999999,33,33,493586.20079999999,486601.7033425452,135551.51884475001,83,71,130781.00210665,44,14.951289171836766,15.558429171836764,460496.40120987903,17494.27766443013,18132.418855236079,{"$f":"AU3514-AC3514","v":1045.4288552360777},8.6499408265411637E-2,{"$f":"AE3514-AD3514","v":-17086.990000000002},-17494.27766443013,-0.14374015048830779,0,0.62318826485786682,0.62318826485786682,{"$f":"AO3514*1000/(500*AR3514)","v":16811.594623367822},{"$f":"AE3514-BD3514","v":-16811.594623367822},0.16099495552890861,0.16099495552890861,42,0.65885197253479677]
["2013-05-28T17:00:00","2013-05-28T17:00:00",52.769129999999997,52.466290000000001,52.133139999999997,52.528129999999997,52.501240000000003,52.2911,52.084980000000002,52.259279999999997,51.751980000000003,51.16281,49.734839999999998,46.924129999999998,43.586109999999998,41.49297,38.795079999999999,37.277949999999997,37.099690000000002,37.502940000000002,37.369109999999999,37.536160000000002,37.782989999999998,37.313969999999998,37.215049999999998,36.587339999999998,36.822589999999998,36.664499999999997,16889.02,16889.02,0,52.290660000000003,37.150620000000004,23,23,344014.62479999999,335439.16033460165,{"$f":"500*AC3515*(C3515-AB3515)/1000","v":135995.70908129998},84,71,127850.2191804,44,{"$f":"19.5286-0.30357*AP3515+0.0000341*AO3515+0.060847*AN3515","v":14.851349474051641},{"$f":"19.5286-0.30357*42+0.0000341*AO3515+0.060847*AN3515","v":15.458489474051639},{"$f":"62.4*AJ3515*AQ3515/1000","v":318806.68042638811},17217.320136972143,{"$f":"AL3515*1000/(500*AQ3515)","v":18314.256131257625},1425.2361312576249,6.0287466366802052E-2,-16889.02,-17217.320136972143,-0.18103682817920216,0,0.44560344982678551,0.44560344982678551,16541.101172272651,-16541.101172272651,-1.2931559573118673E-2,{"$f":"IF(BF3515>1,1,IF(BF3515<0,0,BF3515))","v":0},41,0.48126715750371546]
["2013-05-28T18:00:00","2013-05-28T18:00:00",52.956850000000003,52.643909999999998,52.268909999999998,52.636139999999997,52.601700000000001,52.378799999999998,52.17295,52.455539999999999,52.308529999999998,52.12124,52.067889999999998,52.114660000000001,51.791849999999997,51.634790000000002,51.225439999999999,47.872120000000002,40.761429999999997,37.90607,37.588479999999997,37.712150000000001,37.934019999999997,37.456829999999997,37.327950000000001,36.719729999999998,36.963079999999998,36.76126,7294.8860000000004,17184.189999999999,12749.93,52.533709999999999,38.503889999999998,17,17,254271.67920000001,250254.4104277177,59072.49137637001,84,71,120545.5462729,44,14.60226012790589,15.209400127905891,231687.53105708104,16510.532645905885,8090.8696131879688,795.98361318796833,4.4560301227636302E-2,-4434.2599999999984,-3760.6026459058849,-3.9542017552148763E-2,0,0.39897805404303238,0.39897805404303238,15851.453082850459,-3101.5230828504591,{"$f":"IF(BF3515>1,1+BE3516*60/$BK$7,IF(BF3515<0,BE3516*60/$BK$7,BF3515+BE3516*60/$BK$7))","v":-3.2611922005103183E-2},0,41,0.43464176171996233]
["2013-05-28T19:00:00","2013-05-28T19:00:00",52.903469999999999,52.581339999999997,52.225169999999999,52.610349999999997,52.56382,52.325629999999997,52.107680000000002,52.36056,52.201180000000001,52.060090000000002,51.978760000000001,51.96152,51.685960000000001,51.382779999999997,50.583509999999997,43.126460000000002,38.47448,37.799259999999997,37.559570000000001,37.546660000000003,37.609270000000002,37.128860000000003,37.072620000000001,36.543810000000001,36.891770000000001,36.777790000000003,4442.4210000000003,16776.240000000002,21218.66,52.340760000000003,36.865870000000001,19,19,284185.99440000003,275981.3537686838,35818.52973563999,82,70,129805.23430680003,44,14.857168489861882,15.464308489861882,263465.23015860812,17473.751394200786,4821.7168379131672,379.29583791316691,4.9802689607358223E-2,4442.4199999999983,3744.9086057992135,3.9376997722138873E-2,3.9376997722138873E-2,0.44568925066606768,0.44568925066606768,16787.719204114168,4430.9407958858319,4.6590494987338374E-2,4.6590494987338374E-2,44,0.48135295834299763]
["2013-05-28T20:00:00","2013-05-28T20:00:00",52.865870000000001,52.557839999999999,52.201479999999997,52.585160000000002,52.525849999999998,52.275300000000001,52.063580000000002,52.307519999999997,52.109439999999999,51.864220000000003,51.710030000000003,51.633499999999998,50.852469999999997,48.26811,42.193040000000003,37.636020000000002,37.325040000000001,37.671080000000003,37.407380000000003,37.331119999999999,37.56279,37.104419999999998,37.05724,36.538229999999999,36.892429999999997,36.763919999999999,4940.1530000000002,16266.22,21206.37,51.83887,36.678910000000002,21,21,314100.30960000004,295466.89924156206,39773.04829917501,79,70,123297.62227559999,44,14.635258919597961,15.24239891959796,286849.01592184539,16849.39404939302,5435.236713976441,495.08371397644078,5.5045077987080138E-2,4940.1499999999996,4356.9759506069786,8.5189766508214665E-2,8.5189766508214665E-2,0.49763398304105427,0.49763398304105427,16178.243716882347,5028.1262831176518,9.9460281152572744E-2,9.9460281152572744E-2,44,0.53329769071798427]
["2013-05-28T21:00:00","2013-05-28T21:00:00",52.822800000000001,52.519449999999999,52.169139999999999,52.531779999999998,52.490029999999997,52.232109999999999,51.99286,52.171939999999999,51.864550000000001,51.591810000000002,51.196069999999999,50.148220000000002,45.236229999999999,39.137320000000003,38.062989999999999,37.339469999999999,37.115650000000002,37.547130000000003,37.197380000000003,37.277700000000003,37.514299999999999,37.056460000000001,37.015860000000004,36.49492,36.83916,36.710529999999999,5172.6610000000001,16041.77,21214.44,51.349890000000002,36.51305,25,25,373928.94,341582.61490569223,41671.655325235006,80,70,119004.58740340002,44,14.488866430455943,15.09600643045594,338071.1234872592,16427.03906128219,5752.231277063911,579.57027706391091,6.5529854746523966E-2,5172.6699999999983,4787.4009387178085,0.13552837171928239,0.13552837171928239,0.55202361874323369,0.55202361874323369,15766.366813849556,5448.0731861504428,0.1567457286822885,0.1567457286822885,44,0.58768732642016375]
["2013-05-28T22:00:00","2013-05-28T22:00:00",52.787730000000003,52.47146,52.124740000000003,52.479469999999999,52.41028,52.09319,51.7928,51.863030000000002,51.454410000000003,50.686489999999999,47.485259999999997,41.272320000000001,37.80471,37.604680000000002,37.910899999999998,37.223210000000002,36.951149999999998,37.309139999999999,37.105939999999997,37.24098,37.485689999999998,37.02402,36.982779999999998,36.460430000000002,36.800960000000003,36.6965,6158.9989999999998,15545.6,21704.6,50.752249999999997,36.432740000000003,27,27,403843.25520000001,354202.35765890969,49552.934739385011,80,70,111302.68732799996,44,14.226231637884799,14.833371637884799,358498.46409765183,15647.52917864745,6966.417530756964,807.41853075696417,7.0772243126245887E-2,6158.9999999999982,6057.0708213525486,0.19921731290355785,0.19921731290355785,0.61678432574555997,0.61678432574555997,15007.065156209008,6697.5348437909906,0.22716902656451288,0.22716902656451288,44,0.65244803342249003]
["2013-05-28T23:00:00","2013-05-28T23:00:00",52.723120000000002,52.418300000000002,52.063670000000002,52.385629999999999,52.229179999999999,51.836939999999998,51.375,51.19059,48.990720000000003,42.979140000000001,38.219189999999998,37.43139,37.249099999999999,37.410269999999997,37.758389999999999,37.035530000000001,36.819809999999997,37.283799999999999,37.107770000000002,37.242199999999997,37.483170000000001,37.034700000000001,36.983490000000003,36.457180000000001,36.799079999999996,36.709769999999999,5768.902,16036.9,21805.8,50.932169999999999,36.544989999999999,31,31,463671.88560000004,411498.48640726431,46189.723420850009,78,71,115362.88347099999,44,14.425531326361099,15.0326713263611,417375.71059864492,15994.264732583792,6403.8852193185121,634.98321931851206,8.125701988568973E-2,5768.9,5811.5352674162077,0.26032449470041241,0.26032449470041241,0.67744320586014362,0.67744320586014362,15348.287867998701,6457.5121320012986,0.29506853154007773,0.29506853154007773,44,0.71310691353707367]
["2013-05-29","2013-05-29",52.669829999999997,52.3508,51.911720000000003,52.122140000000002,51.90063,51.298180000000002,49.895539999999997,45.63252,39.692270000000001,37.468829999999997,37.281410000000001,37.307769999999998,37.141379999999998,37.367820000000002,37.679940000000002,36.9298,36.807549999999999,37.27308,37.10098,37.230820000000001,37.474960000000003,37.032020000000003,36.979529999999997,36.446820000000002,36.789929999999998,36.708640000000003,5799.6379999999999,16007.33,21806.97,50.901479999999999,36.528840000000002,33,33,493586.20079999999,437136.33438772563,46284.562024609986,77,71,115033.79572559998,44,14.414309434242959,15.02144943424296,443957.54400214338,15961.055401283822,6422.0297525534361,622.39175255343616,8.6499408265411637E-2,5799.6400000000012,5845.9145987161792,0.32179316859034268,0.32179316859034268,0.73842531119525845,0.73842531119525845,15315.938216104292,6491.0317838957089,0.36332048924419491,0.36332048924419491,44,0.77408901887218851]
["2013-05-29T01:00:00","2013-05-29T01:00:00",52.539749999999998,52.135719999999999,51.608510000000003,51.648429999999998,50.849420000000002,47.125109999999999,40.785609999999998,37.909770000000002,37.463749999999997,37.202719999999999,37.115009999999998,37.190809999999999,37.075319999999998,37.27064,37.557169999999999,36.897269999999999,36.798960000000001,37.268929999999997,37.099969999999999,37.221159999999998,37.476709999999997,37.026760000000003,36.97795,36.442830000000001,36.796410000000002,36.705910000000003,6101.0510000000004,15589.13,21690.19,50.681040000000003,36.480089999999997,37,37,553414.83120000002,482604.35870075872,48301.532682919984,76,71,110690.22783675004,44,14.266193769233176,14.873333769233177,492655.68872000021,15517.836029322314,6771.4673534139511,670.41635341395067,9.6984185024855479E-2,6101.0599999999995,6172.3539706776846,0.38669429004020517,0.38669429004020517,0.80257679017944628,0.80257679017944628,14884.386991398351,6805.8030086016479,0.43488220617155365,0.43488220617155365,44,0.83824049785637644]
["2013-05-29T02:00:00","2013-05-29T02:00:00",52.206989999999998,51.674190000000003,50.733159999999998,48.41948,42.4131,37.957990000000002,37.288469999999997,37.465479999999999,37.226210000000002,37.058019999999999,36.993859999999998,37.10951,37.025559999999999,37.213590000000003,37.538200000000003,36.893470000000001,36.791490000000003,37.265709999999999,37.090130000000002,37.208820000000003,37.46264,37.007550000000002,36.967570000000002,36.438079999999999,36.794350000000001,36.689320000000002,6365.3220000000001,15408.36,21773.69,50.500570000000003,36.468229999999998,41,41,613243.46160000004,528506.70656303526,49387.483119869983,76,70,108107.67318120004,44,14.117281655478923,14.724421655478922,540217.43385717575,15315.650111612445,6996.741203460042,631.4192034600419,0.10746896178429931,6365.3299999999981,6458.0398883875532,0.45459934427323045,0.45459934427323045,0.86950701766818106,0.86950701766818106,14684.13167059413,7089.5583294058688,0.50942755602486678,0.50942755602486678,44,0.90517072534511123]
["2013-05-29T03:00:00","2013-05-29T03:00:00",51.418219999999998,48.880499999999998,42.825749999999999,38.608919999999998,37.680819999999997,37.330170000000003,37.071579999999997,37.279429999999998,37.057729999999999,36.853639999999999,36.919089999999997,37.049379999999999,36.96219,37.146940000000001,37.499409999999997,36.878630000000001,36.773240000000001,37.252519999999997,37.077269999999999,37.196750000000002,37.453969999999998,37.001109999999997,36.958829999999999,36.430030000000002,36.781689999999998,36.667079999999999,6719.8270000000002,15058.62,21778.45,50.358199999999997,36.408000000000001,45,45,673072.09200000006,575022.91268591769,49562.554426390001,75,70,105035.38036199995,44,14.012516470344199,14.6196564703442,588521.4675524513,14991.651297508863,7074.0404881996992,354.21348819969899,0.11795373854374315,6719.83,6786.7987024911381,0.52596123455668509,0.52596123455668509,0.94016474485367263,0.94016474485367263,14369.062717043042,7409.3872829569591,0.5873358461528646,0.5873358461528646,44,0.9758284525306028]
["2013-05-29T04:00:00","2013-05-29T04:00:00",43.436160000000001,38.907490000000003,37.248690000000003,37.419699999999999,37.405709999999999,37.093400000000003,36.902279999999998,37.159790000000001,36.892389999999999,36.787129999999998,36.864550000000001,36.997199999999999,36.899239999999999,37.101140000000001,37.465350000000001,36.8613,36.756790000000002,37.243650000000002,37.062710000000003,37.171010000000003,37.428330000000003,36.976599999999998,36.942889999999998,36.414740000000002,36.763669999999998,36.655790000000003,6795.64,14994.21,21789.85,50.522129999999997,36.427320000000002,49,49,732900.72239999997,634149.39762994624,23038.476793399994,75,70,105670.27052504997,44,14.034166224904205,14.641306224904206,641824.59522567177,15059.002270834408,3283.1985063020375,-3512.4414936979629,0.12843851530318698,6795.6399999999994,6730.8477291655909,0.59673481105705306,0.59673481105705306,1.0116195996894071,1,14434.541413430665,7355.3085865693338,0.66467550913167806,0.66467550913167806,44,1]
["2013-05-29T05:00:00","2013-05-29T05:00:00",37.970999999999997,37.394480000000001,36.990389999999998,37.290680000000002,37.347320000000003,37.04768,36.888689999999997,37.075369999999999,36.859439999999999,36.766089999999998,36.85989,36.97007,36.891109999999998,37.090499999999999,37.461919999999999,36.850409999999997,36.741160000000001,37.22871,37.049770000000002,37.14978,37.40681,36.953040000000001,36.927999999999997,36.395589999999999,36.744779999999999,36.641080000000002,6269.5529999999999,15715.33,21984.880000000001,51.272500000000001,36.441630000000004,51,51,762815.03760000004,696450.5931203427,4169.0019628799819,74,69,116536.00811854997,44,14.343840876842556,14.950980876842554,682761.92511053733,16248.926507082462,581.29506576033418,-5688.2579342396657,0.13368090368290891,6269.5500000000011,5735.9534929175388,0.65704726495115973,0.65704726495115973,1.0659231191080427,1,15589.078613437543,6395.801386562458,0.7319261374220245,0.7319261374220245,44,1]
["2013-05-29T06:00:00","2013-05-29T06:00:00",37.661340000000003,37.31044,37.025599999999997,37.283259999999999,37.25367,36.916029999999999,36.67568,36.960630000000002,36.831479999999999,36.735729999999997,36.819279999999999,36.93721,36.856029999999997,37.072369999999999,37.44164,36.833840000000002,36.726439999999997,37.217970000000001,37.03201,37.142850000000003,37.397190000000002,36.950150000000001,36.916179999999997,36.388509999999997,36.738370000000003,36.632660000000001,3969.703,15154.07,19099.04,51.063429999999997,36.53734,51,51,762815.03760000004,686899.72167316964,2041.7770410200026,75,70,110064.69234314997,44,14.184016008901416,14.791156008901414,675154.31600130606,15519.53865168751,287.89829900624073,-3681.8047009937591,0.13368090368290891,3944.9700000000012,3579.5013483124912,{"$f":"IF(AZ3527>1,1+AY3528*60/$BK$7,IF(AZ3527<0,AY3528*60/$BK$7,AZ3527+AY3528*60/$BK$7))","v":0.69468503699735185},0.69468503699735185,{"$f":"IF(BB3527>1,1+AX3528*60/$BK$7,BB3527+AX3528*60/$BK$7)","v":1.04148060501753},1,14882.500363989444,4216.5396360105569,0.77626224522059173,0.77626224522059173,44,1]
["2013-05-29T07:00:00","2013-05-29T07:00:00",37.593980000000002,37.383319999999998,36.922130000000003,37.219540000000002,37.246339999999996,36.953409999999998,36.738779999999998,36.991230000000002,36.843310000000002,36.748040000000003,36.832299999999996,36.958089999999999,36.877220000000001,37.105379999999997,37.470770000000002,36.856529999999999,36.747329999999998,37.237270000000002,37.038310000000003,37.152090000000001,37.400010000000002,36.952289999999998,36.924759999999999,36.394680000000001,36.7468,36.629570000000001,167.96899999999999,14856.55,14801.72,51.559910000000002,36.794049999999999,51,51,762815.03760000004,710679.08299320086,80.995491645000072,75,70,109684.86869150003,44,14.171064022380152,14.778204022380152,674537.80586798885,15480.117585846247,11.43110940958069,-156.53789059041929,0.13368090368290891,-54.829999999999927,-678.39758584624724,0.68755181613551153,0.68755181613551153,0.99942347303702916,0.99942347303702916,14844.140536345683,-42.420536345684013,0.77581620139445695,0.77581620139445695,44,1]
["2013-05-29T08:00:00","2013-05-29T08:00:00",37.717359999999999,37.358260000000001,36.956699999999998,37.203919999999997,37.197670000000002,36.911709999999999,36.753729999999997,37.074890000000003,36.888449999999999,36.789769999999997,36.868139999999997,36.996969999999997,36.917639999999999,37.12838,37.497500000000002,36.89996,36.783839999999998,37.267670000000003,37.074869999999997,37.171169999999996,37.417230000000004,36.958199999999998,36.923090000000002,36.392090000000003,36.747920000000001,36.64331,543.1816,15099.74,14568.48,52.126379999999997,37.454650000000001,51,51,762815.03760000004,736988.84215091798,291.70209873999994,76,71,110769.65417509997,44,14.26890220737091,14.876042207370908,679194.87004676508,15526.02331493722,40.886410811521976,-502.29518918847805,0.13368090368290891,-531.26000000000022,-957.5433149372202,0.67748343132293065,0.67748343132293065,0.99383737574817455,0.99383737574817455,14892.355457315773,-323.87545731577302,0.77241071290663887,0.77241071290663887,44,1]
["2013-05-29T09:00:00","2013-05-29T09:00:00",37.586379999999998,37.292140000000003,36.998710000000003,37.265039999999999,37.199620000000003,36.942639999999997,36.738950000000003,37.062820000000002,36.920430000000003,36.84469,36.931240000000003,37.048470000000002,36.974260000000001,37.182400000000001,37.551850000000002,36.945749999999997,36.835749999999997,37.320160000000001,37.124429999999997,37.220280000000002,37.449710000000003,36.971919999999997,36.920389999999998,36.392020000000002,36.747300000000003,36.638399999999997,393.3954,14480.24,14503.67,52.889530000000001,37.640389999999996,51,51,762815.03760000004,773548.23574033147,186.46548564600025,76,71,110405.60349680003,44,14.256488079240881,14.863628079240883,678603.96178910928,15488.471337841405,26.158684328087205,-367.2367156719128,0.13368090368290891,23.430000000000291,-984.80133784140526,0.66712843361300267,0.66712843361300267,0.99408373771684877,0.99408373771684877,14855.808138928982,-352.13813892898179,0.76870804772730383,0.76870804772730383,44,1]
["2013-05-29T10:00:00","2013-05-29T10:00:00",37.586840000000002,37.289009999999998,36.967199999999998,37.287779999999998,37.303640000000001,36.940669999999997,36.723379999999999,37.138449999999999,36.939529999999998,36.867150000000002,36.950789999999998,37.070500000000003,36.987250000000003,37.194229999999997,37.56194,36.957070000000002,36.851399999999998,37.337269999999997,37.133319999999998,37.226329999999997,37.47043,37.000030000000002,36.96969,36.440669999999997,36.766469999999998,36.636969999999998,479.60239999999999,14289.73,13817.67,53.982779999999998,38.230429999999998,51,51,762815.03760000004,825654.62973879324,227.77996584400097,77,72,112548.41418275,44,14.390404923631776,14.997544923631775,684978.35782892234,15642.146941664463,31.657200343256925,-447.94519965674306,0.13368090368290891,-472.05999999999949,-1824.4769416644631,0.64794440752895777,0.64794440752895777,0.98912011710513936,0.98912011710513936,15008.911759338209,-1191.2417593382088,0.75618236847004816,0.75618236847004816,44,1]
["2013-05-29T11:00:00","2013-05-29T11:00:00",37.752299999999998,37.401510000000002,36.96705,37.313830000000003,37.268970000000003,36.922840000000001,36.692920000000001,37.046050000000001,36.98554,36.885120000000001,36.945839999999997,37.096159999999998,37.02572,37.2318,37.602679999999999,36.986530000000002,36.880650000000003,37.358879999999999,37.154420000000002,37.233510000000003,37.457720000000002,36.99286,36.955509999999997,36.426519999999996,36.76585,36.644219999999997,2598.4189999999999,15106.34,12507.92,54.11974,37.245069999999998,51,51,762815.03760000004,831828.7814228842,1439.6280627600013,78,72,127457.25120390001,44,14.898796266052992,15.50593626605299,709177.61203435867,17109.738119489855,193.25427867487571,-2405.164721325124,0.13368090368290891,-2598.42,-4601.8181194898552,0.59955717016667831,0.59955717016667831,0.96179822779048041,0.96179822779048041,16439.800733986125,-3931.8807339861251,0.71483939458114298,0.71483939458114298,44,1]
["2013-05-29T12:00:00","2013-05-29T12:00:00",40.920879999999997,37.49982,37.001579999999997,37.389679999999998,37.36103,37.012560000000001,36.748739999999998,37.04533,36.939720000000001,36.877940000000002,36.948889999999999,37.102379999999997,37.023710000000001,37.23001,37.601779999999998,36.99098,36.886780000000002,37.361759999999997,37.16142,37.27037,37.486179999999997,37.00338,36.960340000000002,36.423310000000001,36.774729999999998,36.649819999999998,3312.018,15427.3,12115.29,53.681750000000001,36.709299999999999,49,49,732900.72239999997,778921.34117405291,7072.9137995399969,78,71,130919.5389425,44,14.956013277939253,15.56315327793925,683983.43118304177,17507.277709576767,945.82876707830178,-2366.189232921698,0.12843851530318698,-3312.0099999999984,-5391.9877095767661,0.54286145069597758,0.54286145069597758,0.92697307611021174,0.92697307611021174,16824.294743415307,-4709.0047434153057,0.66532511036927688,0.66532511036927688,44,0.96517484831973133]
["2013-05-29T13:00:00","2013-05-29T13:00:00",50.418230000000001,40.421460000000003,37.086919999999999,37.379980000000003,37.430250000000001,37.044359999999998,36.844619999999999,37.036320000000003,36.920780000000001,36.855409999999999,36.966740000000001,37.12594,37.048720000000003,37.25573,37.626640000000002,37.009950000000003,36.911000000000001,37.374200000000002,37.155470000000001,37.255629999999996,37.502560000000003,37.034210000000002,36.97842,36.424779999999998,36.78313,36.668709999999997,3296.9569999999999,15393.32,12096.37,53.648429999999998,36.70158,47,47,702986.40720000002,744838.37114306784,22665.788105320007,80,73,130434.14252099999,44,15.0611552599661,15.668295259966101,660677.93528786092,17320.602605791551,3009.8339355902804,-287.12306440971952,0.12319612692346506,-3296.9499999999989,-5224.2326057915507,0.48792964405599276,0.48792964405599276,0.89230627744950064,0.89230627744950064,16649.436375413592,-4553.0663754135912,0.61745048827148441,0.61745048827148441,44,0.93050804965902023]
["2013-05-29T14:00:00","2013-05-29T14:00:00",53.24868,49.297699999999999,39.483060000000002,37.548409999999997,37.439349999999997,37.147089999999999,36.977229999999999,37.20261,36.903959999999998,36.78801,36.914720000000003,37.14423,37.06908,37.272150000000003,37.641309999999997,37.027749999999997,36.930810000000001,37.402079999999998,37.211739999999999,37.296169999999996,37.509520000000002,37.04786,36.994430000000001,36.455959999999997,36.795090000000002,36.678019999999997,4907.3410000000003,15563.74,10656.4,53.548470000000002,36.829540000000001,47,47,702986.40720000002,740045.0948808681,40658.93960753001,83,73,130104.53979909999,44,15.049915807149311,15.657055807149309,660184.90149645589,17289.736562817867,5403.2115698900316,495.87056989003122,0.12319612692346506,-4907.34,-6633.3365628178672,0.41818137881935269,{"$f":"IF(AZ3536>1,1,IF(AZ3536<0,0,AZ3536))","v":0.41818137881935269},0.84070653594912781,{"$f":"IF(BB3536>1,1,BB3536)","v":0.84070653594912781},16619.285439308685,-5962.8854393086858,0.55475188836508604,0.55475188836508604,44,0.8789083081586474]
["2013-05-29T15:00:00","2013-05-29T15:00:00",53.523650000000004,53.225380000000001,52.877839999999999,52.098770000000002,49.208269999999999,45.367100000000001,41.779600000000002,38.577930000000002,37.230670000000003,37.046250000000001,36.972949999999997,37.106029999999997,37.004860000000001,37.232250000000001,37.614910000000002,37.050600000000003,36.96313,37.440519999999999,37.276629999999997,37.398000000000003,37.611199999999997,37.106549999999999,37.025399999999998,36.479680000000002,36.803910000000002,36.694719999999997,16036.79,16036.79,0,53.922159999999998,37.122880000000002,37,37,553414.83120000002,594916.65789554722,134941.00816735005,83,73,134703.26275559998,44,15.20673225996596,15.813872259965962,525135.38480536581,17716.266776160297,17747.535218016932,1710.7452180169312,9.6984185024855479E-2,-16036.79,-17716.266776160297,0.2318982221598356,0.2318982221598356,0.67208275636675452,0.67208275636675452,17036.088383818766,-17036.088383818766,0.37562067740710225,0.37562067740710225,44,0.71028452857627411]
["2013-05-29T16:00:00","2013-05-29T16:00:00",53.995289999999997,53.694159999999997,53.365130000000001,53.76117,53.742040000000003,53.51708,53.280529999999999,53.173940000000002,51.395510000000002,47.365200000000002,44.967509999999997,40.844360000000002,38.593760000000003,37.55986,37.757109999999997,37.090560000000004,36.964500000000001,37.435699999999997,37.282240000000002,37.46613,37.740740000000002,37.253660000000004,37.116370000000003,36.507390000000001,36.82479,36.733330000000002,16476.39,16476.39,0,54.270809999999997,37.155140000000003,27,27,403843.25520000001,441941.3238991854,142207.39256219994,84,74,141002.22701564996,44,15.482373941233664,16.089513941233662,390153.02293665096,18214.548692707085,18370.230960959285,1893.8409609592854,7.0772243126245887E-2,-16476.39,-18214.548692707085,4.0375726451439775E-2,4.0375726451439775E-2,0.49883666686422823,0.49883666686422823,17527.220216925783,-17527.220216925783,0.19132530916005216,0.19132530916005216,44,0.53703843907374782]
["2013-05-29T17:00:00","2013-05-29T17:00:00",54.593179999999997,54.303049999999999,53.962409999999998,54.353920000000002,54.332540000000002,54.100830000000002,53.890140000000002,54.062890000000003,53.77169,53.501829999999998,53.436419999999998,53.487879999999997,53.168080000000003,49.673160000000003,48.169199999999996,43.833080000000002,39.77563,38.57985,37.444490000000002,37.500610000000002,37.762360000000001,37.434950000000001,37.310079999999999,36.722580000000001,36.922809999999998,36.766480000000001,16493.990000000002,16493.990000000002,0,54.626919999999998,37.222709999999999,19,19,284185.99440000003,316722.86267366377,147016.70576649997,82,73,143532.43284895,44,15.507806960149196,16.114946960149197,275003.13621663419,18510.990395713452,18960.347668021986,2466.3576680219849,4.9802689607358223E-2,-16493.990000000002,-18510.990395713452,-0.15426379706531226,0,0.32540551672795598,0.32540551672795598,17813.578065617305,-17813.578065617305,4.0189429040837221E-3,4.0189429040837221E-3,41,0.36360728893747557]
["2013-05-29T18:00:00","2013-05-29T18:00:00",54.969369999999998,54.728279999999998,54.416179999999997,54.78257,54.7958,54.531280000000002,54.388480000000001,54.631900000000002,54.416699999999999,54.165730000000003,54.111699999999999,54.038310000000003,53.869579999999999,53.963090000000001,54.154769999999999,53.330089999999998,52.93141,52.889209999999999,49.065069999999999,45.782649999999997,43.122779999999999,38.797499999999999,37.797730000000001,37.038739999999997,37.228900000000003,36.901290000000003,15217.19,15912.13,694.9325,54.335320000000003,37.673380000000002,9,9,134614.4184,146444.80087025266,137472.70314759997,73,69,132563.47766610002,44,14.890377588414012,15.497517588414013,125078.27397441459,17805.254014410722,18464.636283577591,3247.4462835775903,2.3590747708748628E-2,-15217.197499999998,-17110.321514410723,-0.17991175812800025,0,0.16539959552418382,0.16539959552418382,17107.704754625327,-16412.772254625328,-0.16855821817364025,0,41,0.20360136773370341]
["2013-05-29T19:00:00","2013-05-29T19:00:00",54.948059999999998,54.729709999999997,54.417529999999999,54.786140000000003,54.806060000000002,54.526159999999997,54.406730000000003,54.656019999999998,54.475250000000003,54.354660000000003,54.495820000000002,54.473880000000001,54.262970000000003,54.376330000000003,54.533549999999998,53.784610000000001,53.591079999999998,53.980170000000001,53.556620000000002,53.536279999999998,53.385240000000003,51.767890000000001,46.366129999999998,38.207740000000001,37.557949999999998,37.117400000000004,3574.8380000000002,15477.42,11902.3,53.688220000000001,38.24689,5,5,74785.788,77329.938285984361,31870.860466539991,72,68,119495.97488430001,44,14.383928743554632,14.991068743554631,67124.519006849179,16615.206737289431,4431.4541645405698,856.61616454056957,1.3105970949304794E-2,-3575.1200000000008,-4712.9067372894315,-4.9555312931139905E-2,0,0.12780789251750141,0.12780789251750141,15942.288962643437,-4039.9889626434378,-4.2479711235977276E-2,0,41,0.166009664727021]
["2013-05-29T20:00:00","2013-05-29T20:00:00",54.963270000000001,54.732030000000002,54.414740000000002,54.785310000000003,54.804270000000002,54.53098,54.401339999999998,54.655830000000002,54.493630000000003,54.37677,54.504249999999999,54.536839999999998,54.391689999999997,54.410600000000002,54.562469999999998,53.899639999999998,53.696759999999998,54.068809999999999,53.726089999999999,53.709960000000002,53.462000000000003,52.461150000000004,50.382510000000003,39.538829999999997,37.720039999999997,37.302610000000001,988.31460000000004,15197.35,14209.04,53.243340000000003,37.884120000000003,5,5,74785.788,74389.539391142986,8727.1440618180004,73,71,116709.7210335,44,14.471458487242352,15.078598487242349,67532.988212208933,16129.641823785509,1206.1181075164768,217.80350751647677,1.3105970949304794E-2,-988.30999999999949,-1920.6018237855078,-2.0194760834276161E-2,0,0.11741600189605814,0.11741600189605814,15480.181547674392,-1271.1415476743914,-1.3365810249622486E-2,0,41,0.15561777410557773]
["2013-05-29T21:00:00","2013-05-29T21:00:00",54.95205,54.724350000000001,54.410269999999997,54.794429999999998,54.823729999999998,54.550020000000004,54.418410000000002,54.662030000000001,54.517449999999997,54.410989999999998,54.52899,54.542160000000003,54.403320000000001,54.478670000000001,54.622410000000002,53.899940000000001,53.649709999999999,54.042119999999997,53.712719999999997,53.735399999999998,53.601590000000002,52.937910000000002,50.488860000000003,40.510100000000001,37.770969999999998,37.36036,1087.242,15286.18,14198.94,53.325470000000003,38.066769999999998,3,3,44871.472800000003,44701.987144714112,9563.2121094899994,75,72,116623.61738300003,44,14.529369352760302,15.136509352760301,40681.942186924738,16053.500265769453,1316.3974123451094,229.15541234510943,7.8635825695828766E-3,-1087.2399999999998,-1854.5602657694526,-1.9500346483138819E-2,0,0.10598388124640572,0.10598388124640572,15409.578875162852,-1210.638875162851,-1.2729636220173297E-2,0,41,0.14418565345592529]
["2013-05-29T22:00:00","2013-05-29T22:00:00",54.964750000000002,54.738570000000003,54.407510000000002,54.792819999999999,54.81767,54.554070000000003,54.416640000000001,54.675220000000003,54.527769999999997,54.418439999999997,54.50909,54.56617,54.449089999999998,54.445920000000001,54.606670000000001,53.890250000000002,53.672989999999999,54.021329999999999,53.713039999999999,53.72466,53.516440000000003,52.756410000000002,50.57311,41.572659999999999,38.531930000000003,37.392960000000002,3202.4580000000001,15155.25,17629.86,53.499400000000001,37.83126,3,3,44871.472800000003,45097.708304365515,28136.459729910002,75,72,118727.28936750001,44,14.601104567431753,15.20824456743175,40882.799346322114,16262.781876423947,3854.0179751426899,651.55997514268984,7.8635825695828766E-3,2474.6100000000006,1367.0781235760533,1.437456499597319E-2,1.437456499597319E-2,0.13200393209151479,0.13200393209151479,15613.542883411134,2016.3171165888671,2.1201188831171797E-2,2.1201188831171797E-2,44,0.17020570430103438]
["2013-05-29T23:00:00","2013-05-29T23:00:00",54.956829999999997,54.715730000000001,54.353879999999997,54.764850000000003,54.816180000000003,54.554659999999998,54.401960000000003,54.652270000000001,54.492089999999997,54.381439999999998,54.4193,54.420969999999997,54.218940000000003,54.259720000000002,54.442439999999998,53.679729999999999,53.445210000000003,53.7744,53.41872,53.328319999999998,52.552300000000002,47.727029999999999,40.436970000000002,37.215609999999998,37.523130000000002,37.401690000000002,5329.7790000000005,14613.68,19943.46,53.39696,37.148000000000003,5,5,74785.788,74644.057564300208,46782.508257029986,75,71,118728.55088639997,44,14.540300585226241,15.147440585226239,67854.249030235544,16330.96237460659,6434.8749852618084,1105.095985261808,1.3105970949304794E-2,5329.7799999999988,3612.4976253934092,5.2359286584656786E-2,5.2359286584656786E-2,0.18804554939413839,0.18804554939413839,15676.384431862311,4267.0755681376886,6.6068672290329145E-2,6.6068672290329145E-2,44,0.22624732160365799]
["2013-05-30","2013-05-30",54.900669999999998,54.663240000000002,54.362850000000002,54.793080000000003,54.802779999999998,54.522449999999999,54.376890000000003,54.616709999999998,54.428379999999997,54.243180000000002,54.215209999999999,54.140099999999997,53.962940000000003,54.037880000000001,54.233809999999998,53.458350000000003,53.161090000000002,53.3474,52.62623,50.761069999999997,43.195650000000001,37.627510000000001,37.26267,36.752279999999999,37.082940000000001,36.95487,5203.2870000000003,14908.33,20111.62,52.37865,36.829129999999999,9,9,134614.4184,129558.82207192405,46688.573922299998,74,71,115908.68775080002,44,14.444143252302283,15.05128325230228,121329.93245536527,16049.22988178272,6464.7065743907242,1261.4195743907239,2.3590747708748628E-2,5203.2899999999991,4062.3901182172795,9.5074541686948566E-2,9.5074541686948566E-2,0.24275714853980077,0.24275714853980077,15401.834622050626,4709.7853779493726,0.11559116472501338,0.11559116472501338,44,0.28095892074932038]
["2013-05-30T01:00:00","2013-05-30T01:00:00",54.864989999999999,54.675449999999998,54.402239999999999,54.774560000000001,54.772030000000001,54.487479999999998,54.315480000000001,54.520989999999998,54.251330000000003,54.000959999999999,53.929000000000002,53.909149999999997,53.72269,53.814839999999997,53.921680000000002,53.07441,52.574509999999997,51.862220000000001,45.767470000000003,40.369129999999998,37.316659999999999,36.81823,36.769390000000001,36.254649999999998,36.5807,36.473120000000002,5660.86,14715.07,20375.93,51.927390000000003,36.782249999999998,11,11,{"$f":"3.1416*(138/2)^2*AI3547","v":164528.73360000001},{"$f":"62.4*AJ3547*(AF3547-AB3547)/1000","v":158662.69984109828},52056.900604099988,74,71,111430.89762990004,44,14.291450609179591,14.898590609179593,146724.50645020066,{"$f":"AO3547*1000/(500*AQ3547)","v":15594.063986524428},7285.0408300278687,1624.180830027869,{"$f":"AJ3547/$BK$7","v":2.8833136088470546E-2},5660.8600000000006,{"$f":"AE3547-AT3547","v":4781.8660134755719},0.14535494821772854,0.14535494821772854,0.30228000871859428,0.30228000871859428,14958.582399229521,5417.3476007704794,0.17255353860117065,0.17255353860117065,44,0.34048178092811388]
["2013-05-30T02:00:00","2013-05-30T02:00:00",54.937869999999997,54.722630000000002,54.381619999999998,54.745199999999997,54.732089999999999,54.426380000000002,54.179589999999997,54.293889999999998,53.941670000000002,53.700769999999999,53.702950000000001,53.689959999999999,53.470219999999998,53.470759999999999,53.42445,52.089350000000003,48.241610000000001,41.757860000000001,38.198830000000001,36.906419999999997,36.97898,36.517150000000001,36.479799999999997,35.961379999999998,36.298900000000003,36.201099999999997,5665.2470000000003,14649.44,20314.689999999999,51.591749999999998,36.507300000000001,15,15,224357.364,215467.55344898783,53074.215016094997,74,71,110489.37260399997,44,14.2593446057964,14.866484605796398,199629.3916109438,15497.1179473545,7444.1310569800553,1778.884056980055,3.9317912847914381E-2,5665.2499999999982,4817.5720526454988,0.19601079692108478,0.19601079692108478,0.36184902890773685,0.36184902890773685,14864.223188435617,5450.4668115643817,0.22986415464429855,0.22986415464429855,44,0.40005080111725644]
["2013-05-30T03:00:00","2013-05-30T03:00:00",54.954729999999998,54.692320000000002,54.343739999999997,54.678220000000003,54.587859999999999,54.177010000000003,53.826569999999997,53.982439999999997,53.721080000000001,53.514899999999997,53.444659999999999,53.326450000000001,52.94361,52.492780000000003,49.602809999999998,42.942729999999997,37.778219999999997,37.554969999999997,36.59243,36.618789999999997,36.873919999999998,36.420070000000003,36.392620000000001,35.869979999999998,36.212589999999999,36.113379999999999,6396.3270000000002,14612.76,21009.09,51.524070000000002,36.87303,19,19,284185.99440000003,273280.94115130452,60257.717860724995,75,70,107046.06563520001,44,14.081080838160322,14.688220838160321,249702.70791768911,15204.239911058627,8558.6779244138761,2162.3509244138759,4.9802689607358223E-2,6396.33,5804.8500889413735,0.2570476853449134,0.2570476853449134,0.42910521546727409,0.42910521546727409,14575.770178657986,6433.3198213420146,0.29750928210040972,0.29750928210040972,44,0.46730698767679368]
["2013-05-30T04:00:00","2013-05-30T04:00:00",54.900309999999998,54.60924,54.200960000000002,54.42362,54.274889999999999,53.856900000000003,53.567309999999999,53.697940000000003,53.424019999999999,53.124899999999997,52.954410000000003,52.464449999999999,49.486730000000001,43.140770000000003,39.05415,37.227229999999999,36.475520000000003,36.728990000000003,36.51896,36.628729999999997,36.884,36.428370000000001,36.39808,35.871369999999999,36.220889999999997,36.113489999999999,6444.2420000000002,14680.09,21124.33,51.491860000000003,36.88946,23,23,344014.62479999999,330119.97318054002,60533.407245219998,75,70,107182.27310800002,44,14.085725512982801,14.692865512982802,302371.40402879694,15218.566201536472,8595.000263128286,2150.7582631282858,6.0287466366802052E-2,6444.2400000000016,5905.7637984635294,0.31914566212316353,0.31914566212316353,0.49686516651333212,0.49686516651333212,14589.70314718969,6534.6268528103119,0.36621963361597759,0.36621963361597759,44,0.53506693872285171]
["2013-05-30T05:00:00","2013-05-30T05:00:00",54.802100000000003,54.431289999999997,53.900579999999998,54.118499999999997,54.001930000000002,53.631360000000001,53.356119999999997,53.41648,52.992269999999998,52.334580000000003,50.626869999999997,44.359760000000001,38.736930000000001,37.38156,37.515079999999998,36.755409999999998,36.286720000000003,36.769750000000002,36.565060000000003,36.668239999999997,36.928019999999997,36.464649999999999,36.438740000000003,35.916629999999998,36.271039999999999,36.161239999999999,5784.7520000000004,15320.39,21105.14,52.280619999999999,37.17606,27,27,403843.25520000001,406205.46039876045,53916.37608336001,75,70,115703.87498919999,44,14.376312137131722,14.983452137131721,362280.46553278586,16096.461162714371,7500.7241869912677,1715.9721869912673,7.0772243126245887E-2,5784.75,5008.6788372856281,0.37181096211507897,0.37181096211507897,0.55769070634637441,0.55769070634637441,15444.221255589657,5660.9187444103427,0.42574311148101013,0.42574311148101013,44,0.595892478555894]
["2013-05-30T06:00:00","2013-05-30T06:00:00",54.594760000000001,54.126449999999998,53.639270000000003,53.948230000000002,53.795670000000001,53.375019999999999,52.98574,52.90381,51.794080000000001,47.582509999999999,40.103729999999999,38.027320000000003,36.665080000000003,36.8581,37.204509999999999,36.525750000000002,36.323979999999999,36.817570000000003,36.613770000000002,36.696820000000002,36.931220000000003,36.46566,36.432299999999998,35.906199999999998,36.250100000000003,36.144750000000002,4962.2470000000003,15206.33,20168.57,52.508929999999999,36.848869999999998,29,29,433757.57040000003,442920.62620342808,45776.753386234996,75,71,119066.02008990002,44,14.55180828506559,15.158948285065591,393866.11721537443,16364.429458859291,6291.5553159417759,1329.3083159417756,7.6014631505967808E-2,4962.24,3804.1405411407086,0.41181077230837082,0.41181077230837082,0.60986771084632951,0.60986771084632951,15709.008019666166,4459.5619803338341,0.4726345527486045,0.4726345527486045,44,0.6480694830558491]
["2013-05-30T07:00:00","2013-05-30T07:00:00",54.255679999999998,53.927689999999998,53.484630000000003,53.710270000000001,53.509700000000002,52.94941,52.291730000000001,50.168979999999998,43.56438,38.154319999999998,37.426569999999998,36.625660000000003,36.478009999999998,36.694220000000001,37.043329999999997,36.39508,36.262520000000002,36.756039999999999,36.533529999999999,36.604390000000002,36.836379999999998,36.335340000000002,36.269820000000003,35.738770000000002,36.079619999999998,35.961060000000003,5229.2979999999998,14668.17,19897.46,53.479370000000003,37.260919999999999,33,33,493586.20079999999,539560.0752258068,47834.00988837998,75,71,118947.49086825002,44,14.547766438607326,15.154906438607327,448067.99023321521,16352.680855884981,6576.1311319154211,1346.8331319154213,8.6499408265411637E-2,5229.2899999999991,3544.7791441150184,0.44908344701854941,0.44908344701854941,0.66485269501911648,0.66485269501911648,15697.555290111157,4199.9047098888423,0.5167957474806717,0.5167957474806717,44,0.70305446722863607]
["2013-05-30T08:00:00","2013-05-30T08:00:00",54.09487,53.735660000000003,53.26352,53.396070000000002,53.006450000000001,51.842529999999996,47.328069999999997,40.748370000000001,37.367890000000003,37.026780000000002,36.726309999999998,36.483820000000001,36.407389999999999,36.614660000000001,36.997669999999999,36.387369999999997,36.244109999999999,36.710030000000003,36.47972,36.604770000000002,36.88261,36.390830000000001,36.221870000000003,35.682270000000003,36.033099999999997,35.926020000000001,4831.2780000000002,14955.03,19786.310000000001,53.877079999999999,37.23189,35,35,523500.516,586397.08437941025,43889.382645149999,77,72,124464.65790285,44,14.796748834487186,15.403888834487185,483356.99255852983,16823.243983537363,5932.300823118092,1101.0228231180918,9.1741796645133558E-2,4831.2800000000007,2963.0660164626388,0.48023951945249765,0.48023951945249765,0.7156526801670624,0.7156526801670624,16160.160494561709,3626.1495054382922,0.5549240159769081,0.5549240159769081,44,0.753854452376582]
["2013-05-30T09:00:00","2013-05-30T09:00:00",53.913609999999998,53.461570000000002,52.862729999999999,52.821019999999997,51.107230000000001,44.413400000000003,38.862450000000003,37.196190000000001,36.789209999999997,36.625639999999997,36.628390000000003,36.55077,36.369689999999999,36.563499999999998,36.932090000000002,36.304569999999998,36.19782,36.699219999999997,36.47786,36.59545,36.761870000000002,36.247999999999998,36.177869999999999,35.640250000000002,35.99192,35.887839999999997,4539.2920000000004,15254.37,19793.66,53.945099999999996,37.218589999999999,39,39,583329.14639999997,657279.54627646657,40912.116777420008,78,73,127576.18617434998,44,14.963698948545336,15.570838948545333,544674.73224163125,17051.423797423035,5468.1822880962454,928.89028809624506,0.10222657340457739,4539.2899999999991,2742.2362025769653,0.50907360863032824,0.50907360863032824,0.76338244631231167,0.76338244631231167,16386.552657301545,3407.1073426984549,0.59074909802691122,0.59074909802691122,44,0.80158421852183126]
["2013-05-30T10:00:00","2013-05-30T10:00:00",53.681800000000003,53.128790000000002,52.109180000000002,50.217320000000001,42.550060000000002,38.221060000000001,37.036589999999997,36.931609999999999,36.612870000000001,36.41442,36.420160000000003,36.552039999999998,36.345660000000002,36.541179999999997,36.920740000000002,36.29,36.182429999999997,36.642749999999999,36.458440000000003,36.59637,36.752859999999998,36.271920000000001,36.215159999999997,35.676139999999997,36.023180000000004,35.924129999999998,3886.5070000000001,15864.85,19751.36,54.347059999999999,37.590859999999999,41,41,613243.46160000004,704979.06123930402,34507.654379345004,83,74,132917.29978500001,44,15.206677922668501,15.8138179226685,581904.69846497208,17481.438149861911,4538.4869140819583,651.97991408195821,0.10746896178429931,3886.51,2269.9218501380892,0.53294140272920332,0.53294140272920332,0.8042483556111607,0.8042483556111607,16810.27319714718,2941.0868028528203,0.6216740632335942,0.6216740632335942,44,0.84245012782068029]
["2013-05-30T11:00:00","2013-05-30T11:00:00",53.325099999999999,52.443280000000001,49.623179999999998,42.360489999999999,38.156120000000001,37.213439999999999,36.651859999999999,36.741489999999999,36.497970000000002,36.317689999999999,36.377299999999998,36.494210000000002,36.336030000000001,36.556260000000002,36.905290000000001,36.270180000000003,36.132919999999999,36.616990000000001,36.426789999999997,36.741509999999998,36.878619999999998,36.403680000000001,36.312530000000002,35.76679,36.11835,36.033050000000003,3490.268,16106.76,19597.03,54.652079999999998,37.615279999999998,43,43,643157.77679999999,747238.37391668418,30176.944384699993,83,74,137203.82438400001,44,15.352848411494401,15.9599884114944,616156.560357571,17873.403124501376,3931.1199558392123,440.85195583921222,0.11271135016402123,3490.2699999999986,1723.6268754986231,0.5510650096565457,0.5510650096565457,0.84094787709663066,0.84094787709663066,17193.474186382951,2403.5558136170475,0.64694699289902557,0.64694699289902557,44,0.87914964930615025]
["2013-05-30T12:00:00","2013-05-30T12:00:00",52.74362,49.836410000000001,40.95561,37.731819999999999,37.429009999999998,36.847520000000003,36.451079999999997,36.629069999999999,36.470739999999999,36.329279999999997,36.341740000000001,36.420360000000002,36.336239999999997,36.52037,36.856310000000001,36.22766,36.127209999999998,36.652999999999999,36.548029999999997,36.665880000000001,36.837890000000002,36.36504,36.300629999999998,35.767359999999996,36.135860000000001,36.033149999999999,3311.89,16282.68,19594.57,55.020090000000003,37.823619999999998,45,45,673072.09200000006,797445.75621225743,27671.619244150002,84,75,140002.30906980005,44,15.509123739280183,16.116263739280186,651378.52168173261,18054.186867464879,3568.4310357348804,256.54103573488055,0.11795373854374315,3311.8899999999994,1540.3831325351202,0.56726184367463839,0.56726184367463839,0.87577176699985104,0.87577176699985104,17374.040451891127,2220.5295481088724,0.67029543638905431,0.67029543638905431,44,0.91397353920937063]
["2013-05-30T13:00:00","2013-05-30T13:00:00",50.250929999999997,42.404730000000001,38.006489999999999,37.194659999999999,37.078110000000002,36.678150000000002,36.421590000000002,36.564210000000003,36.437550000000002,36.303040000000003,36.251530000000002,36.430509999999998,36.335979999999999,36.480640000000001,36.81335,36.24776,36.155929999999998,36.666849999999997,36.464509999999997,36.603630000000003,36.843530000000001,36.378799999999998,36.301780000000001,35.76746,36.134480000000003,36.014209999999999,3263.8139999999999,16326.66,19590.47,54.998710000000003,37.799300000000002,47,47,702986.40720000002,832780.7559232763,23233.003025039998,84,74,140404.45963530001,44,15.461990073563731,16.069130073563731,678261.09623854188,18161.240431185859,3005.1762954838291,-258.63770451617074,0.12319612692346506,3263.8100000000013,1429.2295688141421,0.58228991922992879,0.58228991922992879,0.91009010489906561,0.91009010489906561,17475.054217936493,2115.4157820635082,0.69253862873364136,0.69253862873364136,44,0.9482918771085852]
["2013-05-30T14:00:00","2013-05-30T14:00:00",43.553179999999998,38.88015,37.514850000000003,37.02413,37.158929999999998,36.59684,36.238720000000001,36.52525,36.393419999999999,36.305190000000003,36.216500000000003,36.411409999999997,36.304740000000002,36.433529999999998,36.826000000000001,36.241959999999999,36.182310000000001,36.626350000000002,36.448219999999999,36.61121,36.857089999999999,36.388469999999998,36.304340000000003,35.760420000000003,36.127139999999997,36.024079999999998,4846.8739999999998,16664.080000000002,16927.48,55.415050000000001,37.855110000000003,49,49,732900.72239999997,886807.32947269187,18246.299516700001,86,75,146310.1224776,44,15.724220176486162,16.331360176486161,719115.84117505781,18609.523503924305,2320.7891153782402,-2526.0848846217596,0.12843851530318698,263.39999999999782,-1682.0435039243057,0.56460355350127023,0.56460355350127023,0.91285970552001261,0.91285970552001261,17917.689757189586,-990.20975718958653,0.68212676252870552,0.68212676252870552,44,0.9510614777295322]
["2013-05-30T15:00:00","2013-05-30T15:00:00",53.07985,52.644869999999997,49.598010000000002,45.860970000000002,42.554679999999998,38.611960000000003,36.841419999999999,36.912179999999999,36.638280000000002,36.446379999999998,36.378740000000001,36.559480000000001,36.422089999999997,36.521070000000002,36.857880000000002,36.240839999999999,36.150170000000003,36.575710000000001,36.463090000000001,36.69529,36.950090000000003,36.474530000000001,36.355649999999997,35.766829999999999,36.136760000000002,36.095770000000002,16428.669999999998,16428.669999999998,0,55.3401,36.47786,41,41,613243.46160000004,736411.07563125808,139512.92278679996,88,75,154940.75821039997,44,16.018524854974643,16.625664854974637,612971.15142371389,19345.196840929115,17418.947630932875,990.27763093287649,0.10746896178429931,-16428.669999999998,-19345.196840929115,0.3611925087671024,0.3611925087671024,0.74011538269034727,0.74011538269034727,18638.744322340826,-18638.744322340826,0.48614393090824959,0.48614393090824959,44,0.77831715489986686]
["2013-05-30T16:00:00","2013-05-30T16:00:00",55.144390000000001,54.831200000000003,54.507899999999999,54.908520000000003,54.681019999999997,53.770330000000001,51.117489999999997,47.86674,44.243250000000003,40.926020000000001,38.185279999999999,37.134999999999998,36.771430000000002,36.808070000000001,37.126159999999999,36.477780000000003,36.289839999999998,36.722909999999999,36.493470000000002,36.64949,36.886830000000003,36.461170000000003,36.389389999999999,35.894089999999998,36.227040000000002,36.122970000000002,16445.59,16445.59,0,55.289279999999998,36.52534,31,31,463671.88560000004,554541.25569611392,156409.2372689,89,75,154292.03201229998,44,15.996403291619432,16.603543291619431,462825.94656749745,19290.840472012114,19555.550634415838,3109.9606344158383,8.125701988568973E-2,-16445.59,-19290.840472012114,0.15835301085565651,0.15835301085565651,0.56719314929687625,0.56719314929687625,18585.43436209526,-18585.43436209526,0.29072164332347622,0.29072164332347622,44,0.60539492150639584]
["2013-05-30T17:00:00","2013-05-30T17:00:00",55.773699999999998,55.468910000000001,55.135379999999998,55.546109999999999,55.517850000000003,55.29918,55.046329999999998,55.212780000000002,54.56559,54.036290000000001,53.007399999999997,50.46969,47.056260000000002,43.245130000000003,40.670969999999997,37.891170000000002,36.885890000000003,37.078310000000002,36.750799999999998,36.942709999999998,37.133220000000001,36.649290000000001,36.48574,35.821390000000001,36.142560000000003,36.29598,16627.11,16627.11,0,55.416319999999999,36.502659999999999,21,21,314100.30960000004,374755.97413221322,161929.09649459997,88,75,157239.75266130001,44,16.096920565750331,16.704060565750332,315497.37855846831,19536.625284200192,20119.263909289461,3492.15390928946,5.5045077987080138E-2,-16627.11,-19536.625284200192,-4.7070867346053064E-2,0,0.39236226782172601,0.39236226782172601,18826.530476511944,-18826.530476511944,9.2764276208724239E-2,9.2764276208724239E-2,43,0.4305640400312456]
["2013-05-30T18:00:00","2013-05-30T18:00:00",56.015920000000001,55.653060000000004,55.289000000000001,55.66507,55.586959999999998,55.322510000000001,55.081789999999998,55.384430000000002,55.212299999999999,55.045290000000001,54.958939999999998,55.04871,54.593649999999997,54.294519999999999,53.997709999999998,50.961939999999998,45.804729999999999,39.573329999999999,37.322429999999997,37.379809999999999,37.481819999999999,37.017040000000001,36.874339999999997,36.200229999999998,36.409779999999998,36.146700000000003,6746.7020000000002,17122.41,10259.41,55.676879999999997,39.854280000000003,15,15,224357.364,273420.55748252035,67025.853156219993,87,75,135460.52223299994,44,15.354248808145298,15.961388808145299,214957.94042084672,17644.695474927994,8730.5935957822112,1983.891595782211,3.9317912847914381E-2,-6863,-7385.2854749279941,-7.7654864226392006E-2,0,0.32019913546956402,0.32019913546956402,16973.525782903394,-6714.1157829033946,2.216663292307694E-2,2.216663292307694E-2,42,0.35840090767908361]
["2013-05-30T19:00:00","2013-05-30T19:00:00",56.190399999999997,55.723039999999997,55.285440000000001,55.699350000000003,55.638849999999998,55.384909999999998,55.144100000000002,55.426699999999997,55.24736,55.110169999999997,55.037930000000003,55.1723,54.989750000000001,54.898769999999999,54.835039999999999,53.893340000000002,51.62238,48.670740000000002,41.170279999999998,37.916899999999998,37.694029999999998,37.280909999999999,37.021850000000001,36.345399999999998,36.440829999999998,36.243839999999999,5136.62,18397.810000000001,13261.19,54.715049999999998,38.057580000000002,13,13,194443.04880000002,224115.739375323,51228.94951359999,85,74,153230.48407034995,44,15.899357506798935,16.506497506798933,192910.81976918867,19275.053599470928,6444.1534183621325,1307.5334183621326,3.4075524468192467E-2,-5136.6200000000008,-6013.8635994709275,-6.3234625510195222E-2,0,0.26618855862230156,0.26618855862230156,18566.080903260696,-5304.8909032606953,-3.3613280287732E-2,0,41,0.30439033083182115]
["2013-05-30T20:00:00","2013-05-30T20:00:00",55.816699999999997,55.50797,55.17783,55.6036,55.57291,55.332590000000003,55.131689999999999,55.447330000000001,55.303719999999998,55.21331,55.17022,55.328659999999999,55.147539999999999,55.208599999999997,55.382559999999998,54.352020000000003,53.812910000000002,53.569949999999999,50.284100000000002,44.197989999999997,38.435949999999998,37.451099999999997,37.326909999999998,36.53537,36.687159999999999,36.378,4875.2820000000002,18064.73,13189.45,53.847099999999998,37.294089999999997,11,11,164528.73360000001,179348.13936822183,47384.572106699998,84,74,149512.82816865001,44,15.772585440550966,16.379725440550967,161930.71490741489,18958.569440905467,6008.4723947508719,1133.1903947508717,2.8833136088470546E-2,-4875.2799999999988,-5769.119440905466,-6.0661187493733344E-2,0,0.21492592188999088,0.21492592188999088,18255.840576973776,-5066.3905769737758,-5.3272127896532843E-2,0,41,0.25312769409951047]
["2013-05-30T21:00:00","2013-05-30T21:00:00",55.768050000000002,55.449910000000003,55.112430000000003,55.522399999999998,55.478940000000001,55.252270000000003,55.072690000000001,55.412860000000002,55.300060000000002,55.21848,55.198059999999998,55.367489999999997,55.234229999999997,55.271790000000003,55.41093,54.628749999999997,54.193649999999998,53.903700000000001,52.291600000000003,48.437640000000002,40.504730000000002,37.84084,37.492339999999999,36.57714,36.592799999999997,36.482689999999998,3156.1379999999999,17182.03,19161.2,54.161540000000002,38.16733,9,9,134614.4184,148501.27410960445,30433.628769840005,83,74,137406.49802315002,44,15.359759582589415,15.966899582589416,129021.0544255839,17891.751141587261,3962.7741054407015,806.63610544070161,2.3590747708748628E-2,1979.1700000000019,1269.4488584127394,1.3348011945787478E-2,1.3348011945787478E-2,0.23573651589515313,0.23573651589515313,17211.41882460142,1949.7811753985807,2.0501576135515336E-2,2.0501576135515336E-2,44,0.27393828810467274]
["2013-05-30T22:00:00","2013-05-30T22:00:00",55.77364,55.477089999999997,55.147150000000003,55.552250000000001,55.489899999999999,55.26229,55.103000000000002,55.450969999999998,55.292380000000001,55.187910000000002,55.163290000000003,55.298540000000003,55.15569,55.152999999999999,55.220689999999998,54.250100000000003,53.631659999999997,52.731940000000002,48.538780000000003,41.54072,38.32,37.663310000000003,37.151040000000002,36.530909999999999,36.905650000000001,36.782789999999999,3015.2190000000001,16702.86,19250.64,53.865850000000002,38.708680000000001,11,11,164528.73360000001,175384.82381551978,28630.785873075001,82,74,126584.0442531,44,14.99071390903071,15.597853909030711,153903.55813327426,16888.327670217655,3819.8028521946821,804.58385219468209,2.8833136088470546E-2,2547.7799999999988,2362.312329782344,3.8187274267108683E-2,3.8187274267108683E-2,0.26252593529544327,0.26252593529544327,16230.956513807514,3019.6834861924854,5.2252970434764387E-2,5.2252970434764387E-2,44,0.30072770750496286]
["2013-05-30T23:00:00","2013-05-30T23:00:00",55.757750000000001,55.46219,55.13711,55.539020000000001,55.492420000000003,55.324590000000001,55.154110000000003,55.441920000000003,55.261969999999998,55.152369999999998,55.13485,55.235529999999997,55.000540000000001,54.947769999999998,54.95073,53.741199999999999,52.531480000000002,49.719520000000003,42.259450000000001,38.253050000000002,38.132869999999997,37.525840000000002,37.190440000000002,36.621220000000001,36.998950000000001,36.878929999999997,3451.098,16698.72,20149.82,53.656289999999998,37.669789999999999,13,13,194443.04880000002,203563.84022302652,32576.32897218001,81,74,133477.04364000002,44,15.225765188124001,15.832905188124002,184737.95829788435,17533.049011436382,4279.1056567179076,828.00765671790759,3.4075524468192467E-2,3451.0999999999985,2616.7709885636177,6.5702120716622625E-2,6.5702120716622625E-2,0.29881359172274125,0.29881359172274125,16860.714070355065,3289.1059296449348,8.6837290195983713E-2,8.6837290195983713E-2,44,0.33701536393226084]
["2013-05-31","2013-05-31",55.739939999999997,55.450949999999999,55.13138,55.545929999999998,55.550240000000002,55.355139999999999,55.127699999999997,55.39385,55.21349,55.089950000000002,55.038629999999998,55.087060000000001,54.793610000000001,54.5672,54.268070000000002,52.41048,49.001609999999999,42.463999999999999,37.88655,37.89913,38.07029,37.421610000000001,37.226089999999999,36.692230000000002,37.059730000000002,36.95599,4146.1909999999998,16248.46,20394.66,53.075339999999997,37.237920000000003,15,15,224357.364,225669.2802245481,38940.922217224994,80,74,128666.84268659995,44,15.06173733561306,15.668877335613058,210862.80919882024,17085.259133071027,5170.8407004483161,1024.6497004483163,3.9317912847914381E-2,4146.2000000000007,3309.4008669289724,0.10049983786168383,0.10049983786168383,0.34241009170212844,0.34241009170212844,16423.236959569414,3971.4230404305854,0.12859604387411541,0.12859604387411541,44,0.38061186391164803]
["2013-05-31T01:00:00","2013-05-31T01:00:00",55.734540000000003,55.455939999999998,55.150419999999997,55.602049999999998,55.571629999999999,55.308430000000001,55.087600000000002,55.350569999999998,55.154600000000002,54.96725,54.854550000000003,54.784669999999998,54.275500000000001,53.745809999999999,52.373109999999997,47.631180000000001,40.368029999999997,38.10577,37.6736,37.82161,37.866439999999997,37.429879999999997,37.339680000000001,36.806530000000002,37.176740000000002,37.070869999999999,4600.5370000000003,16108.63,20709.169999999998,52.955820000000003,37.341819999999998,17,17,254271.67920000001,252039.39761570178,42931.45219539501,79,74,125760.07441000004,44,14.962616537381003,15.569756537381002,237405.14504837876,16809.904082727044,5738.4952809743745,1137.9582809743742,4.4560301227636302E-2,4600.5399999999991,3899.2659172729545,0.14149987319090465,0.14149987319090465,0.39078388988243085,0.39078388988243085,16154.404740763432,4554.7652592365666,0.17648852941037038,0.17648852941037038,44,0.42898566209195044]
["2013-05-31T02:00:00","2013-05-31T02:00:00",55.719900000000003,55.496079999999999,55.204129999999999,55.596879999999999,55.534930000000003,55.255690000000001,55.028320000000001,55.250529999999998,54.993519999999997,54.725830000000002,54.51258,54.190199999999997,53.159390000000002,51.218510000000002,45.859050000000003,39.18506,37.5518,37.816270000000003,37.60633,37.693190000000001,37.907910000000001,37.482729999999997,37.396680000000003,36.873919999999998,37.240119999999997,37.126190000000001,4640.71,16053.76,20694.47,52.874510000000001,37.22081,21,21,314100.30960000004,308664.856511224,43144.007967049998,78,73,125650.37145599999,44,14.898028666649601,15.505168666649599,291999.26599735726,16868.053387127406,5791.9083030939828,1151.1983030939828,5.5045077987080138E-2,4640.7100000000009,3826.4166128725956,0.18173391201783698,0.18173391201783698,0.43958006792964077,0.43958006792964077,16207.546548818149,4486.9234511818522,0.22366767131065532,0.22366767131065532,44,0.47778184013916036]
["2013-05-31T03:00:00","2013-05-31T03:00:00",55.756979999999999,55.538449999999997,55.176450000000003,55.538690000000003,55.46801,55.187269999999998,54.940309999999997,55.096730000000001,54.712960000000002,54.30001,53.794400000000003,52.82246,49.438470000000002,43.033279999999998,38.809359999999998,37.49389,37.083739999999999,37.720779999999998,37.547849999999997,37.702590000000001,37.930050000000001,37.50085,37.424239999999998,36.898589999999999,37.268520000000002,37.159039999999997,4850.6580000000004,15931.53,20782.189999999999,52.780529999999999,37.22936,23,23,344014.62479999999,335338.91172081779,45106.123222260008,77,73,123876.96569504999,44,14.837555530201207,15.444695530201205,318510.57255709119,16697.759336826573,6079.9938548433302,1229.3358548433298,6.0287466366802052E-2,4850.659999999998,4084.4306631734253,0.22468091923477018,0.22468091923477018,0.49058383007088191,0.49058383007088191,16041.360666879547,4740.8293331204513,0.27351658499635878,0.27351658499635878,44,0.5287856022804015]
["2013-05-31T04:00:00","2013-05-31T04:00:00",55.776490000000003,55.483199999999997,55.122100000000003,55.47851,55.391919999999999,55.035029999999999,54.71555,54.753070000000001,54.197719999999997,53.369799999999998,51.658740000000002,47.383560000000003,40.256450000000001,38.172939999999997,38.061340000000001,37.294409999999999,37.245310000000003,37.759869999999999,37.568710000000003,37.71949,37.955689999999997,37.517809999999997,37.44453,36.926279999999998,37.290419999999997,37.178489999999996,4996.2860000000001,15908.48,20904.77,52.869860000000003,37.273890000000002,25,25,373928.94,366129.33871786285,46460.46351400001,77,72,124054.08841280002,44,14.782748414876481,15.389888414876481,344928.32057183405,16783.629800255458,6285.76800606915,1289.48200606915,6.5529854746523966E-2,4996.2900000000009,4121.1401997445428,0.2680139202075198,0.2680139202075198,0.543118863808283,0.543118863808283,16121.505896414996,4783.2641035850047,0.32381169217723449,0.32381169217723449,44,0.58132063601780259]
["2013-05-31T05:00:00","2013-05-31T05:00:00",55.714289999999998,55.429130000000001,55.050649999999997,55.38409,55.226010000000002,54.807740000000003,54.35736,54.14922,53.01923,50.66527,45.021230000000003,38.871400000000001,37.619439999999997,37.494169999999997,38.006590000000003,37.414169999999999,37.32696,37.817570000000003,37.601489999999998,37.734699999999997,37.966320000000003,37.531359999999999,37.454129999999999,36.941020000000002,37.303759999999997,37.184809999999999,4486.4210000000003,16306.34,20792.759999999998,53.384500000000003,37.45767,29,29,433757.57040000003,438468.46215951029,41565.52409554,78,73,129854.15255110002,44,15.041377601992512,15.648517601992513,407117.03161641723,17266.257916947503,5526.8240975525896,1040.4030975525893,7.6014631505967808E-2,4486.4199999999983,3526.5020830524954,0.30509441511637775,0.30509441511637775,0.59029271201568301,0.59029271201568301,16596.351917010437,4196.4080829895611,0.36793612054623609,0.36793612054623609,44,0.6284944842252026]
["2013-05-31T06:00:00","2013-05-31T06:00:00",55.663040000000002,55.354439999999997,54.948819999999998,55.195979999999999,54.942830000000001,54.365360000000003,53.596409999999999,52.621180000000003,49.276949999999999,42.251710000000003,38.408610000000003,37.479309999999998,37.132899999999999,37.615870000000001,37.950360000000003,37.45431,37.372259999999997,37.850439999999999,37.62059,37.771929999999998,37.999929999999999,37.565539999999999,37.491230000000002,36.971550000000001,37.343310000000002,37.21931,5001.9359999999997,15495.27,20497.2,54.099769999999999,37.765329999999999,31,31,463671.88560000004,488404.47040291142,46127.178530640005,77,72,126553.27904940001,44,14.86797081558454,15.475110815584541,430176.86793793004,17023.611442221481,6204.9057134669256,1202.9697134669259,8.125701988568973E-2,5001.93,3473.5885577785193,0.34161853442745554,0.34161853442745554,0.64288704927435258,0.64288704927435258,16355.718619081139,4141.4813809188618,0.41148300514848912,0.41148300514848912,44,0.68108882148387218]
["2013-05-31T07:00:00","2013-05-31T07:00:00",55.576529999999998,55.222740000000002,54.726939999999999,54.89011,54.398139999999998,53.399880000000003,51.590069999999997,47.245269999999998,40.43385,37.800939999999997,37.049120000000002,37.269840000000002,37.398260000000001,37.63982,38.035690000000002,37.461599999999997,37.367739999999998,37.864750000000001,37.650039999999997,37.79683,38.02908,37.593409999999999,37.51641,37.001919999999998,37.367649999999998,37.244399999999999,4676.5919999999996,15537.83,20214.419999999998,54.253140000000002,37.661050000000003,33,33,493586.20079999999,523865.43187648756,42865.946250479996,77,73,128902.53688235,44,15.008927507688135,15.616067507688136,462271.64921198972,17176.781860838662,5712.0598695039935,1035.4678695039938,8.6499408265411637E-2,4676.5899999999983,3037.6381391613359,0.37355871846858546,0.37355871846858546,0.69206049865899444,0.69206049865899444,16508.962556532035,3705.4574434679635,0.45044518144431928,0.45044518144431928,44,0.73026227086851403]
["2013-05-31T08:00:00","2013-05-31T08:00:00",55.423879999999997,54.97448,54.357550000000003,54.285739999999997,53.31935,50.724339999999998,44.817410000000002,39.142119999999998,37.768380000000001,37.062069999999999,37.162669999999999,37.238059999999997,37.609929999999999,37.708779999999997,38.080640000000002,37.487290000000002,37.386809999999997,37.887779999999999,37.654249999999998,37.786189999999998,38.012340000000002,37.578279999999999,37.493920000000003,36.97842,37.342619999999997,37.212809999999998,4525.1369999999997,15684.63,20209.77,54.250509999999998,37.503489999999999,37,37,553414.83120000002,588364.35025906144,41203.793333294998,77,74,131335.40615130001,44,15.152735349759331,15.75987534975933,523270.70489025279,17334.877580817247,5438.4627438173311,{"$f":"AU3578-AC3578","v":913.32574381733139},9.6984185024855479E-2,{"$f":"AE3578-AD3578","v":4525.1400000000012},2874.8924191827537,0.40378766239160924,0.40378766239160924,0.73964148026063548,0.73964148026063548,{"$f":"AO3578*1000/(500*AR3578)","v":16667.061539075643},{"$f":"AE3578-BD3578","v":3542.7084609243575},0.48769608331679609,0.48769608331679609,44,0.77784325247015507]
["2013-05-31T09:00:00","2013-05-31T09:00:00",55.18806,54.601779999999998,53.685429999999997,52.957239999999999,50.005339999999997,43.284019999999998,38.273380000000003,37.792140000000003,37.197560000000003,37.172890000000002,37.184249999999999,37.496870000000001,37.460790000000003,37.684620000000002,38.047339999999998,37.501159999999999,37.425249999999998,37.926549999999999,37.680160000000001,37.761659999999999,37.985570000000003,37.545679999999997,37.472470000000001,36.951819999999998,37.318919999999999,37.193010000000001,4355.1180000000004,15851.8,20206.919999999998,54.466889999999999,37.658250000000002,39,39,583329.14639999997,628764.71894596028,{"$f":"500*AC3579*(C3579-AB3579)/1000","v":39185.283082949994},79,74,133223.59977599999,44,{"$f":"19.5286-0.30357*AP3579+0.0000341*AO3579+0.060847*AN3579","v":15.2171227523616},{"$f":"19.5286-0.30357*42+0.0000341*AO3579+0.060847*AN3579","v":15.8242627523616},{"$f":"62.4*AJ3579*AQ3579/1000","v":553899.29248986451},17509.696405034854,{"$f":"AL3579*1000/(500*AQ3579)","v":5150.1566650461164},795.03866504611597,0.10222657340457739,4355.119999999999,2697.223594965144,0.43214845260971269,0.43214845260971269,0.78543473408105624,0.78543473408105624,16837.890252563939,3369.0297474360596,0.52312078673550499,{"$f":"IF(BF3579>1,1,IF(BF3579<0,0,BF3579))","v":0.52312078673550499},44,0.82363650629057583]
["2013-05-31T10:00:00","2013-05-31T10:00:00",54.775019999999998,53.93374,52.304229999999997,49.384790000000002,42.164230000000003,38.050400000000003,37.276879999999998,37.354730000000004,37.255549999999999,37.23095,37.273899999999998,37.547330000000002,37.53087,37.740600000000001,38.148330000000001,37.550150000000002,37.462209999999999,37.934519999999999,37.706919999999997,37.77948,37.99492,37.561079999999997,37.47551,36.961930000000002,37.334449999999997,37.213850000000001,3868.1860000000001,16286.85,20155.04,54.830849999999998,37.849809999999998,41,41,613243.46160000004,674139.02793164924,33964.935968809994,83,75,138283.82566199999,44,15.450523455074201,16.057663455074199,591235.78719639371,17900.21238621341,4396.6065056074667,528.42050560746657,0.10746896178429931,3868.1900000000005,2254.8276137865905,0.45585753370034232,0.45585753370034232,0.82610801208386986,0.82610801208386986,17223.40564041433,2931.6343595856706,{"$f":"IF(BF3579>1,1+BE3580*60/$BK$7,IF(BF3579<0,BE3580*60/$BK$7,BF3579+BE3580*60/$BK$7))","v":0.55394636130915009},0.55394636130915009,44,0.86430978429338945]
["2013-05-31T11:00:00","2013-05-31T11:00:00",54.196930000000002,52.677639999999997,49.091279999999998,42.327300000000001,38.742510000000003,37.277610000000003,36.816929999999999,37.50797,37.437840000000001,37.281660000000002,37.250300000000003,37.529269999999997,37.450769999999999,37.746200000000002,38.122129999999999,37.53745,37.459719999999997,37.913559999999997,37.712310000000002,37.81073,38.023099999999999,37.588090000000001,37.490569999999998,36.972180000000002,37.335009999999997,37.232399999999998,3174.6709999999998,16703.66,19878.330000000002,55.189279999999997,37.963230000000003,43,43,643157.77679999999,720664.27798961755,26928.400709815007,83,75,143869.04117149994,44,15.640979303948148,16.248119303948151,627720.13050877117,18396.42369901788,3443.3138982566966,268.64289825669675,0.11271135016402123,3174.6700000000019,1481.906300982122,0.47143949501919352,0.47143949501919352,0.85948905993239644,0.85948905993239644,17709.008468018943,2169.3215319810588,0.57675636230386729,0.57675636230386729,44,0.89769083214191603]
["2013-05-31T12:00:00","2013-05-31T12:00:00",53.371839999999999,50.623530000000002,43.74492,38.769489999999998,37.865540000000003,36.975520000000003,36.962949999999999,37.615839999999999,37.443219999999997,37.289009999999998,37.276850000000003,37.523739999999997,37.435409999999997,37.834919999999997,38.104410000000001,37.520890000000001,37.437559999999998,37.905140000000003,37.743369999999999,37.835459999999998,38.049289999999999,37.615079999999999,37.510660000000001,36.990349999999999,37.35248,37.246279999999999,2576.5889999999999,16918.46,19495.04,55.443759999999997,37.885350000000003,45,45,673072.09200000006,764288.67420223728,20774.470257419998,85,76,148530.62862429995,44,15.860786436088631,16.467926436088629,666148.24893573229,18729.289272358241,2619.6015362959661,43.012536295966129,0.11795373854374315,2576.5800000000017,765.75072764176002,0.47949121745946405,0.47949121745946405,0.88658130582427075,0.88658130582427075,18038.777280277689,1456.2627197223119,0.59206868627047671,0.59206868627047671,44,0.92478307803379034]
["2013-05-31T13:00:00","2013-05-31T13:00:00",51.967770000000002,46.630189999999999,39.250129999999999,38.10971,37.558810000000001,37.104309999999998,37.07103,37.664920000000002,37.561929999999997,37.384059999999998,37.327159999999999,37.529049999999998,37.477249999999998,37.865049999999997,38.134419999999999,37.493960000000001,37.420110000000001,37.911290000000001,37.720680000000002,37.854779999999998,38.070839999999997,37.639389999999999,37.52901,37.006349999999998,37.374319999999997,37.266199999999998,2394.8629999999998,17112.04,19506.900000000001,55.690829999999998,38.056759999999997,47,47,702986.40720000002,808221.30153581465,17604.123017455004,87,76,150877.45560140003,44,15.940813236007742,16.547953236007743,699265.32153674285,18929.706203519407,2208.6856870877969,-186.17731291220298,0.12319612692346506,2394.8600000000006,577.19379648059476,0.4855602998328104,0.4855602998328104,0.91176280067271875,0.91176280067271875,18235.180321043714,1271.7196789562877,0.60544057545995233,0.60544057545995233,44,0.94996457288223835]
["2013-05-31T14:00:00","2013-05-31T14:00:00",49.621479999999998,42.320860000000003,38.099719999999998,37.681919999999998,37.49832,37.185360000000003,37.333750000000002,37.580089999999998,37.495669999999997,37.453659999999999,37.439390000000003,37.563699999999997,37.488109999999999,37.706420000000001,38.156410000000001,37.526829999999997,37.421039999999998,37.908990000000003,37.714550000000003,37.89555,38.115369999999999,37.676740000000002,37.558540000000001,37.032200000000003,37.398539999999997,37.281779999999998,3731.663,17317.57,17510.919999999998,55.887149999999998,38.171169999999996,47,47,702986.40720000002,816149.70596182381,23023.800960550001,89,76,153398.86188430001,44,16.026793190254633,16.633933190254631,703036.94845828274,19142.801690056978,2873.163793559153,-858.49920644084705,0.12319612692346506,193.34999999999854,-1631.88169005698,0.46840137598279558,0.46840137598279558,0.91379583894173966,0.91379583894173966,18444.08777283923,-933.16777283923147,0.5956284948103574,0.5956284948103574,44,0.95199761115125925]
["2013-05-31T15:00:00","2013-05-31T15:00:00",55.005670000000002,54.643799999999999,52.811309999999999,48.676760000000002,44.531109999999998,40.81532,37.934829999999998,37.648299999999999,37.435789999999997,37.464469999999999,37.455919999999999,37.633420000000001,37.608640000000001,37.74,38.069409999999998,37.522790000000001,37.448889999999999,37.876089999999998,37.75703,37.994109999999999,38.240090000000002,37.795099999999998,37.61739,37.035769999999999,37.416930000000001,37.305239999999998,16927.91,16927.91,0,56.652360000000002,37.71772,39,39,583329.14639999997,704230.11328165827,149815.64300065004,89,76,160261.94090120003,44,16.260824184730922,16.867964184730923,591889.75194582879,19711.416725320432,18426.574360397852,1498.6643603978519,0.10222657340457739,-16927.91,-19711.416725320432,0.26113959920909346,0.26113959920909346,0.73580210299893234,0.73580210299893234,19001.930422198904,-19001.930422198904,0.39582683081447911,0.39582683081447911,44,0.77400387520845193]
["2013-05-31T16:00:00","2013-05-31T16:00:00",57.001609999999999,56.695729999999998,56.350209999999997,56.779589999999999,56.623620000000003,55.74944,54.100090000000002,51.170639999999999,47.175829999999998,43.616129999999998,40.359310000000001,38.071869999999997,37.52084,37.653550000000003,38.078380000000003,37.582549999999998,37.482280000000003,37.90746,37.740430000000003,37.95337,38.234520000000003,37.909660000000002,37.869529999999997,37.168700000000001,37.473750000000003,37.320839999999997,16763.04,16763.04,0,57.132989999999999,37.730080000000001,29,29,433757.57040000003,536245.01102018252,164954.76737040002,89,76,162625.87822319998,44,16.341434447411121,16.948574447411122,442304.98433221865,19903.500974354658,20188.529703588272,3425.4897035882714,7.6014631505967808E-2,-16763.04,-19903.500974354658,5.1858093295682389E-2,5.1858093295682389E-2,0.5595419435723572,0.5595419435723572,19190.508172566799,-19190.508172566799,0.19404230784169982,0.19404230784169982,44,0.59774371578187679]
["2013-05-31T17:00:00","2013-05-31T17:00:00",57.631079999999997,57.327710000000003,56.979680000000002,57.39866,57.345109999999998,57.150590000000001,56.932659999999998,57.063679999999998,56.527360000000002,55.96902,55.258830000000003,53.835509999999999,50.162379999999999,46.595239999999997,43.743720000000003,39.773119999999999,37.557429999999997,37.869900000000001,37.768639999999998,38.104889999999997,38.314149999999998,38.018050000000002,37.896630000000002,37.287779999999998,37.689,37.42933,16634.72,16634.72,0,57.260150000000003,37.697780000000002,19,19,284185.99440000003,351664.01721156633,{"$f":"500*AC3587*(C3587-AB3587)/1000","v":168025.22738},89,76,162707.27374320003,44,16.344210034643122,16.951350034643124,289835.2442779569,19910.081111087824,20560.825763234123,3926.1057632341217,4.9802689607358223E-2,-16634.72,-19910.081111087824,-0.15749260149693178,0,0.38463104440272933,0.38463104440272933,19196.969375380548,-19196.969375380548,-7.8101534428677011E-3,0,41,0.42283281661224892]
["2013-05-31T18:00:00","2013-05-31T18:00:00",57.830269999999999,57.507219999999997,57.14575,57.544719999999998,57.460419999999999,57.211689999999997,56.946809999999999,57.231900000000003,57.055759999999999,56.926169999999999,56.833970000000001,56.943519999999999,56.515340000000002,56.136020000000002,55.857280000000003,54.103079999999999,50.57396,43.67445,38.548349999999999,37.890709999999999,38.034730000000003,38.171199999999999,38.202199999999998,37.561230000000002,37.760429999999999,37.597569999999997,6097.3530000000001,17670.07,11574.88,56.918750000000003,39.766959999999997,15,15,224357.364,270494.57848417811,61682.957021550006,87,75,151536.66496265007,44,15.902445275226368,16.509585275226371,222632.63587369226,19058.284727911818,7757.6694595066874,1660.3164595066874,3.9317912847914381E-2,-6095.1900000000005,-7483.4047279118186,-7.8686569404793141E-2,0,0.32054128734581921,0.32054128734581921,18357.416305307193,-6782.5363053071942,-7.131707199231048E-2,0,41,0.35874305955533881]
["2013-05-31T19:00:00","2013-05-31T19:00:00",57.73612,57.443309999999997,57.110259999999997,57.527670000000001,57.45966,57.23216,57.004570000000001,57.2761,57.104730000000004,56.978560000000002,56.911749999999998,57.054810000000003,56.879910000000002,56.782060000000001,56.763359999999999,55.704349999999998,54.171709999999997,53.139200000000002,46.335929999999998,39.883870000000002,38.268140000000002,38.037390000000002,38.320709999999998,37.643140000000002,37.835160000000002,37.600639999999999,4303.46,18102.07,13798.61,56.387599999999999,38.551189999999998,13,13,194443.04880000002,227946.81187721965,43326.116380400003,86,75,161437.97118435003,44,16.240079817386338,16.847219817386339,197044.88746475187,19881.425830372755,5335.7023940259014,1032.2423940259014,3.4075524468192467E-2,-4303.4599999999991,-6082.8158303727541,-6.3959645030018247E-2,0,0.27529122854467758,0.27529122854467758,19164.939133487882,-5366.3291334878813,-5.6425924450699216E-2,0,40,0.31349300075419717]
["2013-05-31T20:00:00","2013-05-31T20:00:00",57.683509999999998,57.395470000000003,57.059049999999999,57.46987,57.411940000000001,57.216450000000002,57.004100000000001,57.279319999999998,57.127249999999997,57.019579999999998,56.973059999999997,57.121389999999998,56.954149999999998,56.923110000000001,56.927149999999997,55.896320000000003,55.008670000000002,54.110909999999997,50.570340000000002,41.998840000000001,38.68289,38.392060000000001,38.355609999999999,37.583159999999999,37.830010000000001,37.691299999999998,2278.5010000000002,17955.669999999998,19834.79,56.422559999999997,39.464680000000001,11,11,164528.73360000001,192306.22235961776,22776.135238604998,85,75,152245.04858979996,44,15.926601156912179,16.533741156912178,163511.93157930108,19118.33505339277,2860.1375791620312,581.63657916203101,2.8833136088470546E-2,1879.1200000000026,716.45494660723125,7.5333867312223201E-3,7.5333867312223201E-3,0.29504981593584689,0.29504981593584689,18416.28547887985,1418.5045211201505,1.4915303730108347E-2,1.4915303730108347E-2,43,0.33325158814536648]
["2013-05-31T21:00:00","2013-05-31T21:00:00",57.696669999999997,57.408160000000002,57.057600000000001,57.467829999999999,57.417180000000002,57.206589999999998,56.991860000000003,57.266100000000002,57.09599,56.987549999999999,56.94285,57.073590000000003,56.828919999999997,56.772979999999997,56.702469999999998,55.358910000000002,54.239490000000004,52.37574,45.196440000000003,39.044310000000003,38.796550000000003,38.553899999999999,38.206670000000003,37.623649999999998,37.960030000000003,37.81026,2693.0520000000001,17206.939999999999,19899.990000000002,56.168509999999998,38.947240000000001,13,13,194443.04880000002,222745.16787947423,26777.568111659995,84,75,148162.67980689998,44,15.787392381415291,16.394532381415289,191552.31933204317,18769.746925567659,3392.2724493985711,699.22044939857096,3.4075524468192467E-2,2693.0500000000029,1130.2430744323428,1.9417676483571969E-2,1.9417676483571969E-2,0.32336672160115215,0.32336672160115215,18074.645419573662,1825.3445804263392,3.4108452869785963E-2,3.4108452869785963E-2,44,0.36156849381067174]
["2013-05-31T22:00:00","2013-05-31T22:00:00",57.686390000000003,57.397840000000002,57.056179999999998,57.466520000000003,57.4131,57.205440000000003,56.981879999999997,57.222619999999999,57.053260000000002,56.945639999999997,56.886040000000001,56.94012,56.679470000000002,56.458100000000002,56.093649999999997,54.499110000000002,52.611870000000003,47.340519999999998,39.504460000000002,38.440829999999998,38.929470000000002,38.393549999999998,38.178249999999998,37.63447,38.01,37.875770000000003,3270.1410000000001,16883.810000000001,20153.95,54.998089999999998,38.419040000000003,15,15,224357.364,239710.75943970346,32391.760348710002,83,75,139958.76509024994,44,15.507638889577525,16.114778889577522,217105.38614728081,18050.299737675006,4177.5231651131708,907.38216511317069,3.9317912847914381E-2,3270.1399999999994,2103.6502623249944,{"$f":"IF(AZ3591>1,1+AY3592*60/$BK$7,IF(AZ3591<0,AY3592*60/$BK$7,AZ3591+AY3592*60/$BK$7))","v":4.1537156638434103E-2},4.1537156638434103E-2,{"$f":"IF(BB3591>1,1+AX3592*60/$BK$7,BB3591+AX3592*60/$BK$7)","v":0.35775161823966284},0.35775161823966284,17370.237103379732,2783.712896620269,6.3378661552465354E-2,6.3378661552465354E-2,44,0.39595339044918243]
["2013-05-31T23:00:00","2013-05-31T23:00:00",57.672330000000002,57.393380000000001,57.051259999999999,57.461640000000003,57.413530000000002,57.177430000000001,56.938800000000001,57.194380000000002,57.008119999999998,56.87236,56.774540000000002,56.780540000000002,56.390090000000001,55.890720000000002,55.23901,53.072119999999998,47.74483,39.799860000000002,38.199399999999997,38.582880000000003,38.910080000000001,38.488779999999998,38.006700000000002,37.44473,37.799900000000001,37.668109999999999,3147.5,17037.22,20184.72,54.172559999999997,37.940800000000003,17,17,254271.67920000001,261868.72706420021,31481.641225000007,83,74,138272.03305359997,44,15.38927432712776,15.996414327127759,244174.73338928126,17969.922442653206,4091.374363182947,943.87436318294704,4.4560301227636302E-2,3147.5,2214.7975573467957,{"$f":"IF(AZ3592>1,1+AY3593*60/$BK$7,IF(AZ3592<0,AY3593*60/$BK$7,AZ3592+AY3593*60/$BK$7))","v":6.4825329341925558E-2},6.4825329341925558E-2,{"$f":"IF(BB3592>1,1+AX3593*60/$BK$7,BB3592+AX3593*60/$BK$7)","v":0.3908469787348442},0.3908469787348442,17287.878423992715,2896.8415760072858,9.3838396661405948E-2,9.3838396661405948E-2,44,0.42904875094436379]

{"sheet":"tank level pred","index":1,"n_rows":3590,"n_cols":27,"rows_kept":3590,"cut":false,"hidden":false,"merged":[]}
[null,null,null,"dT 44","dT 43","dT 42","dT 41","dT 40","dT 39","dT 38","dT 37","dT 36",null,"ratio 44","ratio 43","ratio 42","ratio 41","ratio 40","ratio 39","ratio 38","ratio 37","ratio 36"]
[1,2,3,4,5,6,7,8,9,10,11,12,13,1,1,1,1,1,1,1,1,1,null,null,1,1]
["2013-01-01","2013-01-01",null,9.8698584845736939,10.173430686229594,10.477002887885494,10.780575089541394,11.084147291197294,11.387719492853194,11.691291694509093,11.994863896164993,12.298436097820893,null,1,1,1,1,1,1,1,1,1,null,1,1,1,{"$f":"COUNTIF(X3:X3590,\"<0\")","v":137}]
["2013-01-01T01:00:00","2013-01-01T01:00:00",null,9.8541894059876292,10.157761607643529,10.461333809299429,10.764906010955329,11.068478212611229,11.372050414267129,11.675622615923029,11.979194817578929,12.282767019234829,null,1,1,1,1,1,1,1,1,1,null,1,1,1,{"$f":"COUNTIF(Y3:Y3590,\"<0\")","v":56}]
["2013-01-01T02:00:00","2013-01-01T02:00:00",null,9.7963421180752981,10.099914319731198,10.403486521387098,10.707058723042998,11.010630924698898,11.314203126354798,11.617775328010698,11.921347529666598,12.224919731322498,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T03:00:00","2013-01-01T03:00:00",null,9.7603590209760647,10.063931222631965,10.367503424287865,10.671075625943764,10.974647827599664,11.278220029255564,11.581792230911464,11.885364432567364,12.188936634223264,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T04:00:00","2013-01-01T04:00:00",null,9.7688289955263166,10.072401197182216,10.375973398838116,10.679545600494016,10.983117802149916,11.286690003805816,11.590262205461716,11.893834407117616,12.197406608773516,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T05:00:00","2013-01-01T05:00:00",null,9.7171270886842329,10.020699290340133,10.324271491996033,10.627843693651933,10.931415895307833,11.234988096963733,11.538560298619633,11.842132500275532,12.145704701931432,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T06:00:00","2013-01-01T06:00:00",null,9.6268508682703615,9.9304230699262614,10.233995271582161,10.537567473238061,10.841139674893961,11.144711876549861,11.448284078205761,11.751856279861661,12.055428481517561,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T07:00:00","2013-01-01T07:00:00",null,9.5281698714271528,9.8317420730830527,10.135314274738953,10.438886476394851,10.742458678050751,11.046030879706651,11.349603081362551,11.653175283018451,11.95674748467435,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T08:00:00","2013-01-01T08:00:00",null,9.4966532340927614,9.8002254357486613,10.103797637404561,10.407369839060461,10.710942040716361,11.014514242372261,11.318086444028161,11.621658645684061,11.925230847339961,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T09:00:00","2013-01-01T09:00:00",null,9.501957677853003,9.805529879508903,10.109102081164803,10.412674282820701,10.716246484476601,11.019818686132501,11.323390887788401,11.626963089444301,11.930535291100201,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T10:00:00","2013-01-01T10:00:00",null,9.5138087271552543,9.8173809288111542,10.120953130467054,10.424525332122952,10.728097533778852,11.031669735434752,11.335241937090652,11.638814138746552,11.942386340402452,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T11:00:00","2013-01-01T11:00:00",null,9.4987423532445696,9.8023145549004695,10.105886756556369,10.409458958212269,10.713031159868169,11.016603361524069,11.320175563179969,11.623747764835869,11.927319966491769,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T12:00:00","2013-01-01T12:00:00",null,9.6073037107106156,9.9108759123665155,10.214448114022415,10.518020315678314,10.821592517334214,11.125164718990113,11.428736920646013,11.732309122301913,12.035881323957813,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T13:00:00","2013-01-01T13:00:00",null,9.5860749224562838,9.8896471241121837,10.193219325768084,10.496791527423984,10.800363729079884,11.103935930735783,11.407508132391683,11.711080334047583,12.014652535703483,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T14:00:00","2013-01-01T14:00:00",null,9.4324944063003588,9.7360666079562588,10.039638809612159,10.343211011268059,10.646783212923959,10.950355414579859,11.253927616235758,11.557499817891658,11.861072019547558,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T15:00:00","2013-01-01T15:00:00",null,9.4210285730501138,9.7246007747060137,10.028172976361914,10.331745178017814,10.635317379673713,10.938889581329613,11.242461782985513,11.546033984641413,11.849606186297313,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T16:00:00","2013-01-01T16:00:00",null,9.3455735569930916,9.6491457586489915,9.9527179603048914,10.256290161960791,10.559862363616691,10.863434565272591,11.167006766928491,11.470578968584391,11.774151170240291,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T17:00:00","2013-01-01T17:00:00",null,9.2666790400954699,9.5702512417513699,9.8738234434072698,10.17739564506317,10.48096784671907,10.78454004837497,11.08811225003087,11.391684451686769,11.695256653342669,null,0.99963198169425538,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T18:00:00","2013-01-01T18:00:00",null,9.3274458736641108,9.6310180753200108,9.9345902769759107,10.238162478631811,10.541734680287711,10.84530688194361,11.14887908359951,11.45245128525541,11.75602348691131,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T19:00:00","2013-01-01T19:00:00",null,9.2536955656870798,9.5572677673429798,9.8608399689988797,10.16441217065478,10.46798437231068,10.77155657396658,11.075128775622479,11.378700977278379,11.682273178934279,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T20:00:00","2013-01-01T20:00:00",null,9.242467879621298,9.5460400812771979,9.8496122829330979,10.153184484589,10.4567566862449,10.760328887900799,11.063901089556699,11.367473291212599,11.671045492868499,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T21:00:00","2013-01-01T21:00:00",null,9.1896488996312833,9.4932211012871832,9.7967933029430831,10.100365504598983,10.403937706254883,10.707509907910783,11.011082109566683,11.314654311222583,11.618226512878483,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T22:00:00","2013-01-01T22:00:00",null,9.1168400060431587,9.4204122076990586,9.7239844093549586,10.027556611010858,10.331128812666758,10.634701014322658,10.938273215978558,11.241845417634458,11.545417619290358,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-01T23:00:00","2013-01-01T23:00:00",null,9.0714101246184171,9.374982326274317,9.678554527930217,9.9821267295861169,10.285698931242019,10.589271132897919,10.892843334553818,11.196415536209718,11.499987737865618,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02","2013-01-02",null,9.0444587298441093,9.3480309315000092,9.6516031331559091,9.9551753348118091,10.258747536467709,10.562319738123609,10.865891939779509,11.169464141435409,11.473036343091309,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T01:00:00","2013-01-02T01:00:00",null,8.9785526737455488,9.2821248754014487,9.5856970770573486,9.8892692787132486,10.192841480369148,10.496413682025048,10.799985883680948,11.103558085336848,11.407130286992748,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T02:00:00","2013-01-02T02:00:00",null,8.9424143012737698,9.2459865029296697,9.5495587045855697,9.8531309062414696,10.15670310789737,10.460275309553269,10.763847511209169,11.067419712865069,11.370991914520969,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T03:00:00","2013-01-02T03:00:00",null,8.889917059983798,9.1934892616396979,9.4970614632955979,9.8006336649514978,10.104205866607398,10.407778068263298,10.711350269919198,11.014922471575098,11.318494673230997,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T04:00:00","2013-01-02T04:00:00",null,8.8095154382234071,9.113087639879307,9.416659841535207,9.7202320431911069,10.023804244847007,10.327376446502907,10.630948648158807,10.934520849814707,11.238093051470607,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T05:00:00","2013-01-02T05:00:00",null,8.8550151148976646,9.1585873165535645,9.4621595182094644,9.7657317198653644,10.069303921521264,10.372876123177164,10.676448324833064,10.980020526488964,11.283592728144864,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T06:00:00","2013-01-02T06:00:00",null,8.7925856853460882,9.0961578870019881,9.3997300886578881,9.703302290313788,10.006874491969688,10.310446693625588,10.614018895281488,10.917591096937388,11.221163298593288,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T07:00:00","2013-01-02T07:00:00",null,8.8875297782535441,9.191101979909444,9.4946741815653439,9.7982463832212439,10.101818584877144,10.405390786533044,10.708962988188944,11.012535189844844,11.316107391500744,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T08:00:00","2013-01-02T08:00:00",null,8.8971171499629023,9.2006893516188022,9.5042615532747021,9.8078337549306021,10.111405956586502,10.414978158242402,10.718550359898302,11.022122561554202,11.325694763210102,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T09:00:00","2013-01-02T09:00:00",null,8.9699543107012332,9.2735265123571331,9.577098714013033,9.880670915668933,10.184243117324833,10.487815318980733,10.791387520636633,11.094959722292533,11.398531923948433,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T10:00:00","2013-01-02T10:00:00",null,8.9899212362824255,9.2934934379383254,9.5970656395942253,9.9006378412501235,10.204210042906023,10.507782244561923,10.811354446217823,11.114926647873723,11.418498849529623,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T11:00:00","2013-01-02T11:00:00",null,9.0727649835742419,9.3763371852301418,9.6799093868860417,9.9834815885419417,10.287053790197842,10.590625991853742,10.894198193509641,11.197770395165541,11.501342596821441,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T12:00:00","2013-01-02T12:00:00",null,9.0233548248620785,9.3269270265179784,9.6304992281738784,9.9340714298297783,10.23764363148568,10.54121583314158,10.84478803479748,11.14836023645338,11.45193243810928,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T13:00:00","2013-01-02T13:00:00",null,9.0826500059314981,9.386222207587398,9.6897944092432979,9.9933666108991979,10.296938812555098,10.600511014210998,10.904083215866898,11.207655417522798,11.511227619178698,null,0.99966352612046205,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T14:00:00","2013-01-02T14:00:00",null,9.1517833423707025,9.4553555440266024,9.7589277456825023,10.062499947338402,10.366072148994302,10.669644350650202,10.973216552306102,11.276788753962002,11.580360955617902,null,0.99910624125747727,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T15:00:00","2013-01-02T15:00:00",null,9.2413424555480166,9.5449146572039165,9.8484868588598165,10.152059060515716,10.455631262171616,10.759203463827516,11.062775665483416,11.366347867139316,11.669920068795216,null,0.99727666453748953,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T16:00:00","2013-01-02T16:00:00",null,9.2483470065007047,9.5519192081566047,9.8554914098125046,10.159063611468405,10.462635813124304,10.766208014780204,11.069780216436104,11.373352418092004,11.676924619747904,null,0.99505803989428598,0.99978970382528876,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T17:00:00","2013-01-02T17:00:00",null,9.2539893798971633,9.5575615815530632,9.8611337832089632,10.164705984864863,10.468278186520763,10.771850388176663,11.075422589832563,11.378994791488463,11.682566993144363,null,0.99253448579775105,0.99928499300598173,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T18:00:00","2013-01-02T18:00:00",null,9.1089208151386636,9.4124930167945635,9.7160652184504634,10.019637420106363,10.323209621762263,10.626781823418163,10.930354025074063,11.233926226729963,11.537498428385863,null,0.9905892461816721,0.99936911147586627,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T19:00:00","2013-01-02T19:00:00",null,9.1214861397356568,9.4250583413915567,9.7286305430474567,10.032202744703357,10.335774946359257,10.639347148015156,10.942919349671056,11.246491551326956,11.550063752982856,null,0.98788694033663271,0.99871719333426145,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T20:00:00","2013-01-02T20:00:00",null,8.9998394814200005,9.3034116830759004,9.6069838847318003,9.9105560863877002,10.2141282880436,10.5177004896995,10.8212726913554,11.1248448930113,11.4284170946672,null,0.98431190536654167,0.99724512011128275,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T21:00:00","2013-01-02T21:00:00",null,8.98655810452032,9.2901303061762199,9.5937025078321199,9.8972747094880198,10.20084691114392,10.50441911279982,10.80799131445572,11.11156351611162,11.415135717767519,null,0.98151496624288215,0.99653011311726458,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T22:00:00","2013-01-02T22:00:00",null,9.0094292918207923,9.3130014934766923,9.6165736951325922,9.9201458967884921,10.223718098444392,10.527290300100292,10.830862501756192,11.134434703412092,11.438006905067992,null,0.9814518773904688,0.99845432311587246,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-02T23:00:00","2013-01-02T23:00:00",null,8.9157642815732423,9.2193364832291422,9.5229086848850422,9.8264808865409421,10.130053088196842,10.433625289852742,10.737197491508642,11.040769693164542,11.344341894820442,null,0.98299755427459645,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03","2013-01-03",null,8.8448822765117399,9.1484544781676398,9.4520266798235397,9.7555988814794397,10.05917108313534,10.36274328479124,10.666315486447139,10.969887688103039,11.273459889758939,null,0.98487970503826205,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T01:00:00","2013-01-03T01:00:00",null,8.7961004617814638,9.0996726634373637,9.4032448650932636,9.7068170667491636,10.010389268405063,10.313961470060963,10.617533671716863,10.921105873372763,11.224678075028663,null,0.98975857629156283,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T02:00:00","2013-01-03T02:00:00",null,8.6648170230836019,8.9683892247395018,9.2719614263954018,9.5755336280513017,9.8791058297072016,10.182678031363102,10.486250233019001,10.789822434674901,11.093394636330801,null,0.99452178464877239,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T03:00:00","2013-01-03T03:00:00",null,8.6289370770203107,8.9325092786762106,9.2360814803321105,9.5396536819880104,9.8432258836439104,10.14679808529981,10.45037028695571,10.75394248861161,11.05751469026751,null,0.99724512011128297,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T04:00:00","2013-01-03T04:00:00",null,8.7719935447440545,9.0755657463999544,9.3791379480558543,9.6827101497117543,9.9862823513676542,10.289854553023554,10.593426754679454,10.896998956335354,11.200571157991254,null,0.99943220032827984,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T05:00:00","2013-01-03T05:00:00",null,8.6932635917998713,8.9968357934557712,9.3004079951116712,9.6039801967675711,9.907552398423471,10.211124600079371,10.514696801735271,10.818269003391171,11.121841205047071,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T06:00:00","2013-01-03T06:00:00",null,8.757656033704917,9.0612282353608169,9.3648004370167168,9.6683726386726168,9.9719448403285167,10.275517041984417,10.579089243640317,10.882661445296216,11.186233646952116,null,0.99883285623035267,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T07:00:00","2013-01-03T07:00:00",null,8.7135209400456013,9.0170931417015012,9.3206653433574012,9.6242375450133011,9.927809746669201,10.231381948325101,10.534954149981001,10.838526351636901,11.142098553292801,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T08:00:00","2013-01-03T08:00:00",null,8.8591340267611844,9.1627062284170844,9.4662784300729843,9.7698506317288842,10.073422833384782,10.376995035040682,10.680567236696582,10.984139438352482,11.287711640008382,null,1,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T09:00:00","2013-01-03T09:00:00",null,9.0305731477154598,9.3341453493713598,9.6377175510272597,9.9412897526831596,10.24486195433906,10.548434155994959,10.852006357650859,11.155578559306759,11.459150760962659,null,0.99873822295173253,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T10:00:00","2013-01-03T10:00:00",null,9.2397746523238613,9.5433468539797612,9.8469190556356612,10.150491257291561,10.454063458947461,10.757635660603361,11.061207862259261,11.364780063915161,11.668352265571061,null,0.99707688317151377,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T11:00:00","2013-01-03T11:00:00",null,9.3803610376557494,9.6839332393116493,9.9875054409675492,10.291077642623449,10.594649844279349,10.898222045935249,11.201794247591149,11.505366449247049,11.808938650902949,null,0.99507906951175695,0.99997897038252892,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-03T12:00:00","2013-01-03T12:00:00",null,9.5139436622632445,9.8175158639191444,10.121088065575044,10.424660267230944,10.728232468886844,11.031804670542744,11.335376872198644,11.638949073854544,11.942521275510444,null,0.98920129142857782,0.99616209481151996,0.99812836404506999,0.99995794076505773,1,1,1,1,1,null,0.99812836404506999,0.99812836404506999,0.99812836404506999]
["2013-01-03T13:00:00","2013-01-03T13:00:00",null,9.5839009832846553,9.8874731849405553,10.191045386596455,10.494617588252355,10.798189789908255,11.101761991564155,11.405334193220055,11.708906394875955,12.012478596531855,null,0.98326042449298534,0.99228213038809754,0.99618312442899104,0.99983176306023103,1,1,1,1,1,null,0.99618312442899104,0.99618312442899104,0.99618312442899104]
["2013-01-03T14:00:00","2013-01-03T14:00:00",null,9.6895724894582589,9.9931446911141588,10.296716892770059,10.600289094425959,10.903861296081859,11.207433497737759,11.511005699393658,11.814577901049558,12.118150102705458,null,0.971336631386858,0.98256644711643826,0.98854937328697301,0.99416428115176314,0.99619363923772652,0.99794961229656542,0.99961095207678419,1,1,null,0.98854937328697301,0.98854937328697301,0.98854937328697301]
["2013-01-03T15:00:00","2013-01-03T15:00:00",null,9.6924726259288612,9.9960448275847611,10.299617029240661,10.603189230896561,10.906761432552461,11.210333634208361,11.513905835864261,11.817478037520161,12.121050239176061,null,0.95926563095843287,0.97271407133121668,0.98078944444012828,0.98837062153846844,0.99226110077062635,0.99577304688830404,0.99910624125747716,1,1,null,0.98078944444012828,0.98078944444012828,0.98078944444012828]
["2013-01-03T16:00:00","2013-01-03T16:00:00",null,9.710153308958267,10.013725510614167,10.317297712270067,10.620869913925965,10.924442115581865,11.228014317237765,11.531586518893665,11.835158720549565,12.138730922205465,null,0.9461641792739226,0.96186278871611675,0.97205163838087627,0.98162011433023766,0.98739274432606117,0.99268169312004884,0.99770777169564739,1,1,null,0.97205163838087627,0.97205163838087627,0.97205163838087627]
["2013-01-03T17:00:00","2013-01-03T17:00:00",null,9.7034363725897208,10.007008574245621,10.310580775901521,10.614152977557421,10.917725179213321,11.22129738086922,11.52486958252512,11.82844178418102,12.13201398583692,null,0.93349383474757042,0.95143209845043919,0.96372390986231116,0.97526916985395817,0.98292395061344728,0.98997938727500945,0.99668783524829785,1,1,null,0.96372390986231116,0.96372390986231116,0.96372390986231116]
["2013-01-03T18:00:00","2013-01-03T18:00:00",null,9.5681293903054261,9.871701591961326,10.175273793617226,10.478845995273124,10.782418196929024,11.085990398584924,11.389562600240824,11.693134801896724,11.996707003552624,null,0.92063422366397807,0.94084368605372826,0.95528051844765483,0.96883410690779426,0.97838155323968445,0.98723502219502779,0.99564686918347722,1,1,null,0.95528051844765483,0.95528051844765483,0.95528051844765483]
["2013-01-03T19:00:00","2013-01-03T19:00:00",null,9.4776796671434518,9.7812518687993517,10.084824070455252,10.388396272111152,10.691968473767052,10.995540675422951,11.299112877078851,11.602685078734751,11.906257280390651,null,0.90899433039371091,0.93145396185287144,0.94801478561138153,0.96355567292254218,0.97498527001809798,0.98561574164975119,0.99570995803589057,1,1,null,0.94801478561138153,0.94801478561138153,0.94801478561138153]
["2013-01-03T20:00:00","2013-01-03T20:00:00",null,9.5018726684756913,9.8054448701315913,10.109017071787491,10.412589273443391,10.716161475099291,11.019733676755191,11.323305878411091,11.626878080066991,11.930450281722891,null,0.89984644679377201,0.92447212885245822,0.9430728255056674,0.96052740800670033,0.97377606701350838,0.98610993766032262,0.9978234345917385,1,1,null,0.9430728255056674,0.9430728255056674,0.9430728255056674]
["2013-01-03T21:00:00","2013-01-03T21:00:00",null,9.5494511381245779,9.8530233397804778,10.156595541436378,10.460167743092279,10.763739944748179,11.067312146404079,11.370884348059979,11.674456549715879,11.978028751371779,null,0.89201291428577834,0.91876258770904806,0.93936109802201406,0.958687316477977,0.97371297816109503,0.98771870339686363,1,1,1,null,0.93936109802201406,0.93936109802201406,0.93936109802201406]
["2013-01-03T22:00:00","2013-01-03T22:00:00",null,9.4312655134847514,9.7348377151406513,10.038409916796551,10.341982118452451,10.645554320108351,10.949126521764251,11.252698723420151,11.556270925076051,11.859843126731951,null,0.88701838013638634,0.91582895607182624,0.93836219119213571,0.95950747155935079,0.97624704706636545,0.99187205284741065,1,1,1,null,0.93836219119213571,0.93836219119213571,0.93836219119213571]
["2013-01-03T23:00:00","2013-01-03T23:00:00",null,9.4020254889504926,9.7055976906063925,10.009169892262292,10.312742093918192,10.616314295574092,10.919886497229992,11.223458698885892,11.527030900541792,11.830603102197692,null,0.88367467095847763,0.91449357536240983,0.93891947605512049,0.96184175909864555,0.98025318919461457,0.99746593109472959,1,1,1,null,0.93891947605512049,0.93891947605512049,0.93891947605512049]
["2013-01-04","2013-01-04",null,9.4198890341911188,9.7234612358470187,10.027033437502919,10.330605639158817,10.634177840814717,10.937750042470617,11.241322244126517,11.544894445782417,11.848466647438316,null,0.88333819707893968,0.91607079667274416,0.94229472965923589,0.96690989690918638,0.98691957793296092,1,1,1,1,null,0.94229472965923589,0.94229472965923589,0.94229472965923589]
["2013-01-04T01:00:00","2013-01-04T01:00:00",null,9.2639562465394221,9.567528448195322,9.8711006498512219,10.174672851507122,10.478245053163022,10.781817254818922,11.085389456474822,11.388961658130722,11.692533859786622,null,0.88429504467387587,0.91893082464881704,0.94694227512035434,0.97323981176799468,0.99483722891083914,1,1,1,1,null,0.94694227512035434,0.94694227512035434,0.94694227512035434]
["2013-01-04T02:00:00","2013-01-04T02:00:00",null,9.2333805857991749,9.5369527874550748,9.8405249891109747,10.144097190766875,10.447669392422775,10.751241594078675,11.054813795734574,11.358385997390474,11.661958199046374,null,0.88701838013638645,0.92350476644878654,0.95326167517042715,0.98118900717207957,1,1,1,1,1,null,0.95326167517042715,0.95326167517042715,0.95326167517042715]
["2013-01-04T03:00:00","2013-01-04T03:00:00",null,9.2308859538946635,9.5344581555505634,9.8380303572064633,10.141602558862363,10.445174760518261,10.748746962174161,11.052319163830061,11.355891365485961,11.659463567141861,null,0.8899204673474016,0.92824694518852502,0.95973879735153333,0.98930643951593344,1,1,1,1,1,null,0.95973879735153333,0.95973879735153333,0.95973879735153333]
["2013-01-04T04:00:00","2013-01-04T04:00:00",null,9.2594970102654592,9.5630692119213592,9.8666414135772591,10.170213615233159,10.473785816889061,10.777358018544961,11.080930220200861,11.384502421856761,11.68807462351266,null,0.89114018516072679,0.9313698433829869,0.96463869822230519,0.99588870978439525,1,1,1,1,1,null,0.96463869822230519,0.96463869822230519,0.96463869822230519]
["2013-01-04T05:00:00","2013-01-04T05:00:00",null,9.223728996893108,9.5273011985490079,9.8308734002049079,10.134445601860808,10.438017803516708,10.741590005172608,11.045162206828508,11.348734408484408,11.652306610140307,null,0.89039363374050184,0.93258956119631209,0.96769850756435372,1,1,1,1,1,1,null,0.96769850756435372,0.96769850756435372,0.96769850756435372]
["2013-01-04T06:00:00","2013-01-04T06:00:00",null,9.2704921987567115,9.5740644004126114,9.8776366020685114,10.181208803724413,10.484781005380313,10.788353207036213,11.091925408692113,11.395497610348013,11.699069812003913,null,0.88689220243155975,0.93112800278206898,0.96816115914871848,1,1,1,1,1,1,null,0.96816115914871848,0.96816115914871848,0.96816115914871848]
["2013-01-04T07:00:00","2013-01-04T07:00:00",null,9.2921699894996426,9.5957421911555425,9.8993143928114424,10.202886594467344,10.506458796123244,10.810030997779144,11.113603199435044,11.417175401090944,11.720747602746844,null,0.88204487560446565,0.92836260808461613,0.96735151887608017,1,1,1,1,1,1,null,0.96735151887608017,0.96735151887608017,0.96735151887608017]
["2013-01-04T08:00:00","2013-01-04T08:00:00",null,9.3516041341907972,9.6551763358466971,9.958748537502597,10.262320739158497,10.565892940814397,10.869465142470297,11.173037344126197,11.476609545782097,11.780181747437997,null,0.87776534844909193,0.92614398344141258,0.96705710423148439,1,1,1,1,1,1,null,0.96705710423148439,0.96705710423148439,0.96705710423148439]
["2013-01-04T09:00:00","2013-01-04T09:00:00",null,9.3615054947604222,9.6650776964163221,9.968649898072222,10.272222099728122,10.575794301384022,10.879366503039922,11.182938704695822,11.486510906351722,11.790083108007622,null,0.87289699200452675,0.92333652950901757,0.96619488991516833,1,1,1,1,1,1,null,0.96619488991516833,0.96619488991516833,0.96619488991516833]
["2013-01-04T10:00:00","2013-01-04T10:00:00",null,9.4775222998188777,9.7810945014747777,10.084666703130678,10.388238904786578,10.691811106442477,10.995383308098377,11.298955509754277,11.602527711410177,11.906099913066077,null,0.86524221124503764,0.91781625492284746,0.96267242898875505,0.99837020464598791,1,1,1,1,1,null,0.96267242898875505,0.96267242898875505,0.96267242898875505]
["2013-01-04T11:00:00","2013-01-04T11:00:00",null,9.5707420200726894,9.8743142217285893,10.177886423384489,10.481458625040389,10.785030826696289,11.088603028352189,11.392175230008089,11.695747431663989,11.999319633319889,null,0.85623102015866104,0.91096059962726106,0.95783561697039654,0.99544708781750169,0.99887491546529483,1,1,1,1,null,0.95783561697039654,0.95783561697039654,0.95783561697039654]
["2013-01-04T12:00:00","2013-01-04T12:00:00",null,9.627722336406638,9.9312945380625379,10.234866739718438,10.538438941374336,10.842011143030236,11.145583344686136,11.449155546342036,11.752727747997936,12.056299949653836,null,0.84787174721388925,0.9047148032383372,0.9535876342412295,0.99308125585200024,0.99828608617610337,1,1,1,1,null,0.9535876342412295,0.9535876342412295,0.9535876342412295]
["2013-01-04T13:00:00","2013-01-04T13:00:00",null,9.6864143275996035,9.9899865292555035,10.293558730911403,10.597130932567303,10.900703134223203,11.204275335879103,11.507847537535003,11.811419739190903,12.114991940846803,null,0.83606361700385312,0.89511478286276913,0.94606954599530269,0.98752943683962346,0.99458487350118552,0.99804424557518545,0.99970558535540421,1,1,null,0.94606954599530269,0.94606954599530269,0.94606954599530269]
["2013-01-04T14:00:00","2013-01-04T14:00:00",null,9.7500772257502781,10.053649427406178,10.357221629062078,10.660793830717978,10.964366032373878,11.267938234029778,11.571510435685678,11.875082637341578,12.178654838997478,null,0.82460247548209054,0.88584072155800342,0.93885638720270714,0.98226151766310688,0.99114653104465678,0.99634084656002442,0.99965301131172646,1,1,null,0.93885638720270714,0.93885638720270714,0.93885638720270714]
["2013-01-04T15:00:00","2013-01-04T15:00:00",null,9.8682366631666785,10.171808864822578,10.475381066478478,10.778953268134378,11.082525469790278,11.386097671446178,11.689669873102078,11.993242074757978,12.296814276413878,null,0.81040748368908189,0.8738853840256694,0.92901452622622116,0.9744174703463776,0.9851846344915931,0.99216646749200632,0.99716100164139831,0.99911675606621275,1,null,0.92901452622622116,0.92901452622622116,0.92901452622622116]
["2013-01-04T16:00:00","2013-01-04T16:00:00",null,9.8637606096689172,10.167332811324817,10.470905012980717,10.774477214636617,11.078049416292517,11.381621617948417,11.685193819604317,11.988766021260217,12.292338222916117,null,0.79649639173193332,0.86221394632919557,0.91944605027685977,0.96683629324803744,0.97948560815691854,0.98824444383364174,0.99492134738072358,0.99848586754207902,1,null,0.91944605027685977,0.91944605027685977,0.91944605027685977]
["2013-01-04T17:00:00","2013-01-04T17:00:00",null,9.8044792806585672,10.108051482314467,10.411623683970367,10.715195885626267,11.018768087282167,11.322340288938067,11.625912490593967,11.929484692249867,12.233056893905767,null,0.78199647048559329,0.84998522376973695,0.90935183389072027,0.95875040533039024,0.97330290062040814,0.9838597685909124,0.99224007115315527,0.9974238718597872,1,null,0.90935183389072027,0.90935183389072027,0.90935183389072027]
["2013-01-04T18:00:00","2013-01-04T18:00:00",null,9.7205471199134728,10.024119321569373,10.327691523225273,10.631263724881173,10.934835926537072,11.238408128192972,11.541980329848872,11.845552531504772,12.149124733160672,null,0.76833773393809823,0.83858717110038772,0.90007777258595456,0.95148467249411695,0.96792983335653593,0.98027421881208576,0.99035792038948967,0.99715048683266261,1,null,0.90007777258595456,0.90007777258595456,0.90007777258595456]
["2013-01-04T19:00:00","2013-01-04T19:00:00",null,9.7308017263334872,10.034373927989387,10.337946129645287,10.641518331301187,10.945090532957087,11.248662734612987,11.552234936268887,11.855807137924787,12.159379339580687,null,0.75795961771609854,0.83036459066917823,0.89388455024070856,0.94721566014747882,0.96546936811241446,0.97952766739186081,0.99123064951454132,0.99955837803310632,1,null,0.89388455024070856,0.89388455024070856,0.89388455024070856]
["2013-01-04T20:00:00","2013-01-04T20:00:00",null,9.6729014951785679,9.9764736968344678,10.280045898490368,10.583618100146268,10.887190301802168,11.190762503458068,11.494334705113967,11.797906906769867,12.101479108425767,null,0.74694009816122953,0.82153215133130619,0.88711301341500659,0.94238936293785591,0.96247264762277929,0.97826589034359335,0.99160918262902153,1,1,null,0.88711301341500659,0.88711301341500659,0.88711301341500659]
["2013-01-04T21:00:00","2013-01-04T21:00:00",null,9.6448982893034945,9.9484704909593944,10.252042692615294,10.555614894271194,10.859187095927094,11.162759297582994,11.466331499238894,11.769903700894794,12.073475902550694,null,0.73753985915163711,0.81427693330376838,0.88187663866469668,0.93905616856868279,0.96093748554738723,0.97843412728336232,0.99338618530533151,1,1,null,0.88187663866469668,0.88187663866469668,0.88187663866469668]
["2013-01-04T22:00:00","2013-01-04T22:00:00",null,9.6215353359943503,9.9251075376502502,10.22867973930615,10.53225194096205,10.83582414261795,11.13939634427385,11.44296854592975,11.74654074758565,12.05011294924155,null,0.72945397123398992,0.80829400713323363,0.87788101134518315,0.93693217720409927,0.96059049685911368,0.97975899318404314,0.99628827251634666,1,1,null,0.87788101134518315,0.87788101134518315,0.87788101134518315]
["2013-01-04T23:00:00","2013-01-04T23:00:00",null,9.5440800455615289,9.8476522472174288,10.151224448873329,10.454796650529227,10.758368852185127,11.061941053841027,11.365513255496927,11.669085457152827,11.972657658808727,null,0.7258473918376922,0.80667472658795703,0.87813336675483666,0.93895102048132717,0.96427067991656035,0.98501639755182413,1,1,1,null,0.87813336675483666,0.87813336675483666,0.87813336675483666]
["2013-01-05","2013-01-05",null,9.5927209075700315,9.8962931092259314,10.199865310881831,10.503437512537731,10.807009714193631,11.110581915849531,11.414154117505431,11.717726319161331,12.021298520817231,null,0.7232922933149506,0.80607538249002997,0.87936359937689745,0.94190568173602007,0.96885513652526534,0.99113601623592118,1,1,1,null,0.87936359937689745,0.87936359937689745,0.87936359937689745]
["2013-01-05T01:00:00","2013-01-05T01:00:00",null,9.6209252382874766,9.9244974399433765,10.228069641599276,10.531641843255175,10.835214044911075,11.138786246566974,11.442358448222874,11.745930649878774,12.049502851534674,null,0.72310302675771043,0.80775775188771992,0.88281245664216179,0.94701587878150317,0.97553204007234717,0.99929550781471732,1,1,1,null,0.88281245664216179,0.88281245664216179,0.88281245664216179]
["2013-01-05T02:00:00","2013-01-05T02:00:00",null,9.5253910420963113,9.8289632437522112,10.132535445408111,10.436107647064011,10.739679848719911,11.043252050375811,11.346824252031711,11.650396453687611,11.953968655343511,null,0.72450149631954019,0.81100682778700861,0.88778596117408259,0.95361917866743606,0.98367050203367212,1,1,1,1,null,0.88778596117408259,0.88778596117408259,0.88778596117408259]
["2013-01-05T03:00:00","2013-01-05T03:00:00",null,9.5444793311711269,9.8480515328270268,10.151623734482927,10.455195936138825,10.758768137794725,11.062340339450625,11.365912541106525,11.669484742762425,11.973056944418325,null,0.72476436653792919,0.81314133396032773,0.8916764404062405,0.95917099767981284,0.99077851273891204,1,1,1,1,null,0.8916764404062405,0.8916764404062405,0.8916764404062405]
["2013-01-05T04:00:00","2013-01-05T04:00:00",null,9.4359991490723871,9.7395713507282871,10.043143552384187,10.346715754040087,10.650287955695987,10.953860157351887,11.257432359007787,11.561004560663687,11.864576762319587,null,0.72627849899585017,0.81634835062467415,0.89647119318965673,0.96546936811241446,0.99848586754207902,1,1,1,1,null,0.89647119318965673,0.89647119318965673,0.89647119318965673]
["2013-01-05T05:00:00","2013-01-05T05:00:00",null,9.31539773249267,9.6189699341485699,9.9225421358044699,10.22611433746037,10.52968653911627,10.83325874077217,11.13683094242807,11.44040314408397,11.743975345739869,null,0.72816064975951578,0.82010213734326975,0.90197043815835565,0.97261943805259665,1,1,1,1,1,null,0.90197043815835565,0.90197043815835565,0.90197043815835565]
["2013-01-05T06:00:00","2013-01-05T06:00:00",null,9.2930792688256876,9.5966514704815875,9.9002236721374874,10.203795873793387,10.507368075449287,10.810940277105187,11.114512478761087,11.418084680416987,11.721656882072887,null,0.7273089502519352,0.82120619226050373,0.90491458460431295,0.97728801313118618,1,1,1,1,1,null,0.90491458460431295,0.90491458460431295,0.90491458460431295]
["2013-01-05T07:00:00","2013-01-05T07:00:00",null,9.4166877414104739,9.7202599430663739,10.023832144722274,10.327404346378174,10.630976548034074,10.934548749689974,11.238120951345874,11.541693153001773,11.845265354657673,null,0.72720380216457958,0.82300422455428479,0.90851064919187519,0.98256644711643826,1,1,1,1,1,null,0.90851064919187519,0.90851064919187519,0.90851064919187519]
["2013-01-05T08:00:00","2013-01-05T08:00:00",null,9.4566531465774553,9.7602253482333552,10.063797549889255,10.367369751545153,10.670941953201053,10.974514154856953,11.278086356512853,11.581658558168753,11.885230759824653,null,0.72474333692045811,0.82251002854371336,0.90987757432749827,0.98567883050216465,1,1,1,1,1,null,0.90987757432749827,0.90987757432749827,0.90987757432749827]
["2013-01-05T09:00:00","2013-01-05T09:00:00",null,9.5237880981171337,9.8273602997730336,10.130932501428934,10.434504703084833,10.738076904740733,11.041649106396633,11.345221308052533,11.648793509708433,11.952365711364333,null,0.72231441610254332,0.8220473769593486,0.91125501427185684,0.98879121388789104,1,1,1,1,1,null,0.91125501427185684,0.91125501427185684,0.91125501427185684]
["2013-01-05T10:00:00","2013-01-05T10:00:00",null,9.5909723022670725,9.8945445039229725,10.198116705578872,10.501688907234772,10.805261108890672,11.108833310546572,11.412405512202472,11.715977713858372,12.019549915514272,null,0.71598450124373503,0.81777836461271047,0.90893124154129767,0.98829701787731961,1,1,1,1,1,null,0.90893124154129767,0.90893124154129767,0.90893124154129767]
["2013-01-05T11:00:00","2013-01-05T11:00:00",null,9.7371937660801837,10.040765967736084,10.344338169391984,10.647910371047884,10.951482572703783,11.255054774359683,11.558626976015583,11.862199177671483,12.165771379327383,null,0.70908678671320635,0.81293103778561637,0.90601863952154704,0.98720347776882111,1,1,1,1,1,null,0.90601863952154704,0.90601863952154704,0.90601863952154704]
["2013-01-05T12:00:00","2013-01-05T12:00:00",null,9.8588619862664579,10.162434187922358,10.466006389578258,10.769578591234158,11.073150792890058,11.376722994545958,11.680295196201858,11.983867397857757,12.287439599513657,null,0.69916080726683583,0.80512904970382937,0.90020395029078126,0.98327093930172094,0.9978444642092098,0.99952683360689976,1,1,1,null,0.90020395029078126,0.90020395029078126,0.90020395029078126]
["2013-01-05T13:00:00","2013-01-05T13:00:00",null,9.985587180283348,10.289159381939248,10.592731583595148,10.896303785251046,11.199875986906946,11.503448188562846,11.807020390218746,12.110592591874646,12.414164793530546,null,0.68617501847841678,0.79433034113240719,0.89146614423152926,0.97646785804981229,0.9928814744860246,0.99630930213381774,0.99843329349840126,1,1,null,0.89146614423152926,0.89146614423152926,0.89146614423152926]
["2013-01-05T14:00:00","2013-01-05T14:00:00",null,10.127791474338261,10.431363675994161,10.734935877650059,11.038508079305959,11.342080280961859,11.645652482617759,11.949224684273659,12.252796885929559,12.556369087585459,null,0.66922514679669087,0.77964115332882711,0.87892197741000377,0.9659425345055147,0.98426984613159929,0.98951673569064469,0.99335464087912484,0.99656165754347126,0.9981178492363344,null,0.87892197741000377,0.87892197741000377,0.87892197741000377]
["2013-01-05T15:00:00","2013-01-05T15:00:00",null,10.269717997162374,10.573290198818274,10.876862400474174,11.180434602130074,11.484006803785974,11.787579005441874,12.091151207097774,12.394723408753674,12.698295610409573,null,0.64846891435269149,0.76124023804159358,0.86272917195723831,0.95184217599112608,0.97215678646823189,0.97928582679094289,0.98491124946446851,0.98982166514397607,0.9929971373821157,null,0.86272917195723831,0.86272917195723831,0.86272917195723831]
["2013-01-05T16:00:00","2013-01-05T16:00:00",null,10.298519070023014,10.602091271678914,10.905663473334815,11.209235674990715,11.512807876646615,11.816380078302515,12.119952279958415,12.423524481614315,12.727096683270215,null,0.62988924731695339,0.74493176969273689,0.84857623939917182,0.93971860151902309,0.96196793680347237,0.9709265538461711,0.97828691996106443,0.98484816061205527,0.98960085416052923,null,0.84857623939917182,0.84857623939917182,0.84857623939917182]
["2013-01-05T17:00:00","2013-01-05T17:00:00",null,10.210047995359677,10.513620197015577,10.817192398671477,11.120764600327377,11.424336801983277,11.727909003639176,12.031481205295076,12.335053406950976,12.638625608606876,null,0.61227694268488708,0.72959066374755188,0.83538015443604152,0.92854135983312069,0.95270439030744225,0.96348206926139324,0.97257737881765427,0.98077892963139279,0.9870878148727299,null,0.83538015443604152,0.83538015443604152,0.83538015443604152]
["2013-01-05T18:00:00","2013-01-05T18:00:00",null,9.9519751146766033,10.255547316332503,10.559119517988403,10.862691719644303,11.166263921300203,11.469836122956103,11.773408324612003,12.076980526267903,12.380552727923803,null,0.59730385504544681,0.71686774517752183,0.82477071242185951,0.91992973147869539,0.94598542752541814,0.95856113877315019,0.96934933253583677,0.97917016389485179,0.98701421121158095,null,0.82477071242185951,0.82477071242185951,0.82477071242185951]
["2013-01-05T19:00:00","2013-01-05T19:00:00",null,9.8554292736513815,10.159001475307281,10.462573676963181,10.766145878619081,11.069718080274981,11.373290281930881,11.676862483586781,11.980434685242681,12.284006886898581,null,0.58387644429013419,0.70565895906541276,0.81566488805686277,0.91280069115598439,0.94071750834890155,0.95507022227294358,0.96753027062458452,0.97894935291140495,0.98830753268605509,null,0.81566488805686277,0.81566488805686277,0.81566488805686277]
["2013-01-05T20:00:00","2013-01-05T20:00:00",null,9.7450390628057075,10.048611264461607,10.352183466117507,10.655755667773407,10.959327869429307,11.262900071085207,11.566472272741107,11.870044474397007,12.173616676052907,null,0.57272023222170287,0.69667931240524283,0.80873562910012742,0.9078061570065924,0.93755255091949741,0.95364020828490714,0.96773005199056017,0.98070532597024385,0.99154609377660818,null,0.80873562910012742,0.80873562910012742,0.80873562910012742]
["2013-01-05T21:00:00","2013-01-05T21:00:00",null,9.716527485841409,10.020099687497309,10.323671889153209,10.627244090809109,10.930816292465009,11.234388494120909,11.537960695776809,11.841532897432709,12.145105099088608,null,0.56316227108107697,0.68926637224667164,0.80333101741004853,0.90429421088891471,0.93583863709560078,0.95361917866743606,0.96931778810962999,0.98381770935597024,0.9960990059591065,null,0.80333101741004853,0.80333101741004853,0.80333101741004853]
["2013-01-05T22:00:00","2013-01-05T22:00:00",null,9.6674508602826439,9.9710230619385438,10.274595263594444,10.578167465250344,10.881739666906244,11.185311868562144,11.488884070218043,11.792456271873943,12.096028473529843,null,0.55633816021169724,0.68450316388946209,0.80051304866891793,0.90330581886777184,0.93657467370709013,0.9559955254416731,0.97323981176799457,0.98921180623731353,1,null,0.80051304866891793,0.80051304866891793,0.80051304866891793]
["2013-01-05T23:00:00","2013-01-05T23:00:00",null,9.5372987759633254,9.8408709776192254,10.144443179275125,10.448015380931023,10.751587582586923,11.055159784242823,11.358731985898723,11.662304187554623,11.965876389210523,null,0.55308908431240855,0.68324138684119462,0.80111239276684498,0.90566113602453768,0.94058081583533926,0.96156837407152096,0.98029524842955662,0.99766571246070535,1,null,0.80111239276684498,0.80111239276684498,0.80111239276684498]
["2013-01-06","2013-01-06",null,9.2165138450388859,9.5200860466947859,9.8236582483506858,10.127230450006586,10.430802651662486,10.734374853318386,11.037947054974286,11.341519256630185,11.645091458286085,null,0.54876749792209256,0.68100173258051988,0.80082849293098479,0.90721732771740082,0.94386143616083462,0.96648930455976401,0.98676185580192721,1,1,null,0.80082849293098479,0.80082849293098479,0.80082849293098479]
["2013-01-06T01:00:00","2013-01-06T01:00:00",null,9.3601729945303802,9.6637451961862801,9.9673173978421801,10.270889599498078,10.574461801153978,10.878034002809878,11.181606204465778,11.485178406121678,11.788750607777578,null,0.54799991688439653,0.6821793911589028,0.80382521342061997,0.91192796203093263,0.95019135101964292,0.97434386668522877,0.99605694672416401,1,1,null,0.80382521342061997,0.80382521342061997,0.80382521342061997]
["2013-01-06T02:00:00","2013-01-06T02:00:00",null,9.0607190387730618,9.3642912404289618,9.6678634420848617,9.9714356437407616,10.275007845396662,10.578580047052561,10.882152248708461,11.185724450364361,11.489296652020261,null,0.54896727928806821,0.68509199317865344,0.80855687735162285,0.91837353978583214,0.95824569451108343,0.98392285744332575,1,1,1,null,0.80855687735162285,0.80855687735162285,0.80855687735162285]
["2013-01-06T03:00:00","2013-01-06T03:00:00",null,9.145174878246694,9.4487470799025939,9.7523192815584938,10.055891483214394,10.359463684870295,10.663035886526195,10.966608088182095,11.270180289837995,11.573752491493895,null,0.55304702507746628,0.69100131568803924,0.81618011368490528,0.92760554185565558,0.96899182903882775,0.99610952076784209,1,1,1,null,0.81618011368490528,0.81618011368490528,0.81618011368490528]
["2013-01-06T04:00:00","2013-01-06T04:00:00",null,8.9425311571512509,9.2461033588071508,9.5496755604630508,9.8532477621189507,10.156819963774851,10.460392165430751,10.76396436708665,11.06753656874255,11.37110877039845,null,0.5572003745280133,0.69701578628478067,0.82394004253175002,0.93700578086524799,0.97993774493254782,1,1,1,1,null,0.82394004253175002,0.82394004253175002,0.82394004253175002]
["2013-01-06T05:00:00","2013-01-06T05:00:00",null,9.0367259870243419,9.3402981886802419,9.6438703903361418,9.9474425919920417,10.251014793647942,10.554586995303842,10.858159196959742,11.161731398615641,11.465303600271541,null,0.55966083977213477,0.70137943191003893,0.83009120564205374,0.94482879856450608,0.98933798394214023,1,1,1,1,null,0.83009120564205374,0.83009120564205374,0.83009120564205374]
["2013-01-06T06:00:00","2013-01-06T06:00:00",null,8.9725405757971668,9.2761127774530667,9.5796849791089667,9.8832571807648666,10.186829382420767,10.490401584076666,10.793973785732566,11.097545987388466,11.401118189044366,null,0.56193203845901618,0.70557484059552822,0.83608464662132409,0.95250460894146638,0.99860153043817035,1,1,1,1,null,0.83608464662132409,0.83608464662132409,0.83608464662132409]
["2013-01-06T07:00:00","2013-01-06T07:00:00",null,8.9183256608541548,9.2218978625100547,9.5254700641659547,9.8290422658218546,10.132614467477755,10.436186669133654,10.739758870789554,11.043331072445454,11.346903274101354,null,0.56339359687325929,0.70900266824332148,0.84134205098910508,0.9594864419418796,1,1,1,1,1,null,0.84134205098910508,0.84134205098910508,0.84134205098910508]
["2013-01-06T08:00:00","2013-01-06T08:00:00",null,8.9669890877862528,9.2705612894421527,9.5741334910980527,9.8777056927539526,10.181277894409853,10.484850096065752,10.788422297721652,11.091994499377552,11.395566701033452,null,0.56183740518039615,0.70949686425389291,0.8437499421895488,0.96369236543610437,1,1,1,1,1,null,0.8437499421895488,0.8437499421895488,0.8437499421895488]
["2013-01-06T09:00:00","2013-01-06T09:00:00",null,9.1662196386534696,9.4697918403093695,9.7733640419652694,10.076936243621169,10.380508445277069,10.684080646932969,10.987652848588869,11.291225050244769,11.594797251900669,null,0.56053356889718642,0.71019084163044,0.84632607032976148,0.96802446663515596,1,1,1,1,1,null,0.84632607032976148,0.84632607032976148,0.84632607032976148]
["2013-01-06T10:00:00","2013-01-06T10:00:00",null,9.3960505847928424,9.6996227864487423,10.003194988104642,10.30676718976054,10.61033939141644,10.91391159307234,11.21748379472824,11.52105599638414,11.82462819804004,null,0.55761045206870019,0.70926553846171059,0.84728291792469768,0.97074780209766653,1,1,1,1,1,null,0.84728291792469768,0.84728291792469768,0.84728291792469768]
["2013-01-06T11:00:00","2013-01-06T11:00:00",null,9.5890812404689409,9.8926534421248409,10.196225643780741,10.499797845436641,10.803370047092541,11.106942248748441,11.410514450404341,11.71408665206024,12.01765885371614,null,0.55136465567977633,0.70508064458495689,0.84504326366402294,0.97033772455697964,1,1,1,1,1,null,0.84504326366402294,0.84504326366402294,0.84504326366402294]
["2013-01-06T12:00:00","2013-01-06T12:00:00",null,9.7738505699448801,10.07742277160078,10.38099497325668,10.68456717491258,10.98813937656848,11.29171157822438,11.59528377988028,11.89885598153618,12.20242818319208,null,0.54243758306328416,0.69825653371557717,0.84020645164566443,0.96736203368481555,0.99880131180414589,1,1,1,1,null,0.84020645164566443,0.84020645164566443,0.84020645164566443]
["2013-01-06T13:00:00","2013-01-06T13:00:00",null,9.8640737222047452,10.167645923860645,10.471218125516545,10.774790327172445,11.078362528828345,11.381934730484245,11.685506932140145,11.989079133796045,12.292651335451945,null,0.52844237263625116,0.68649046274048331,0.8305538572264185,0.95969673811659084,0.99301816699958678,0.99599385787175088,0.99767622726944083,0.99928499300598184,1,null,0.8305538572264185,0.8305538572264185,0.8305538572264185]
["2013-01-06T14:00:00","2013-01-06T14:00:00",null,10.164543911782218,10.468116113438118,10.771688315094018,11.075260516749918,11.378832718405818,11.682404920061717,11.985977121717617,12.289549323373517,12.593121525029417,null,0.50215535079734619,0.66273750980684876,0.80918776587575647,0.94059133064407474,0.97604726570038969,0.98105231465851728,0.98464837924607951,0.98808672170260836,0.99054718694672972,null,0.80918776587575647,0.80918776587575647,0.80918776587575647]
["2013-01-06T15:00:00","2013-01-06T15:00:00",null,10.106230951121493,10.409803152777393,10.713375354433293,11.016947556089193,11.320519757745092,11.624091959400992,11.927664161056892,12.231236362712792,12.534808564368692,null,0.48263986578414314,0.64556682714167601,0.79422519304505179,0.92772120475174691,0.96516443865908297,0.97204112357214068,0.97741419083601289,0.98254541749896718,0.98662516328836514,null,0.79422519304505179,0.79422519304505179,0.79422519304505179]
["2013-01-06T16:00:00","2013-01-06T16:00:00",null,10.165354073682671,10.468926275338571,10.772498476994471,11.076070678650371,11.379642880306271,11.683215081962171,11.986787283618071,12.290359485273971,12.593931686929871,null,0.45996993815027148,0.62532582032571915,0.77626589972471194,0.91192796203093274,0.95142158364170348,0.96023299336210455,0.96745666696343569,0.97433335187649328,0.9800849522548456,null,0.77626589972471194,0.77626589972471194,0.77626589972471194]
["2013-01-06T17:00:00","2013-01-06T17:00:00",null,10.024178912599432,10.327751114255332,10.631323315911231,10.934895517567131,11.238467719223031,11.542039920878931,11.845612122534831,12.149184324190731,12.452756525846631,null,0.44114843051361552,0.60884911503709349,0.76200781907928983,0.89975181351515199,0.94122221916820836,0.95190526484353943,0.96090594112118055,0.96947551024066358,0.97683587635555691,null,0.76200781907928983,0.76200781907928983,0.76200781907928983]
["2013-01-06T18:00:00","2013-01-06T18:00:00",null,9.7763512477242784,10.079923449380178,10.383495651036078,10.687067852691978,10.990640054347878,11.294212256003778,11.597784457659678,11.901356659315578,12.204928860971478,null,0.42057094981812071,0.59073209958572015,0.74620406154974017,0.88612462139386361,0.92965592955909016,0.94229472965923577,0.95314601227433582,0.96346103964392216,0.97249326034776984,null,0.74620406154974017,0.74620406154974017,0.74620406154974017]
["2013-01-06T19:00:00","2013-01-06T19:00:00",null,9.7035049030825604,10.00707710473846,10.31064930639436,10.614221508050262,10.917793709706162,11.221365911362062,11.524938113017962,11.828510314673862,12.132082516329762,null,0.40397858163340389,0.57649504855776923,0.7341856351649928,0.87618812713875749,0.92169621934626977,0.9361961405926098,0.94881391107528423,0.96080079303382493,0.97143126466547802,null,0.7341856351649928,0.7341856351649928,0.7341856351649928]
["2013-01-06T20:00:00","2013-01-06T20:00:00",null,9.6202388574615902,9.9238110591174902,10.22738326077339,10.53095546242929,10.83452766408519,11.13809986574109,11.44167206739699,11.74524426905289,12.04881647070879,null,0.3881537944863831,0.56301506375877874,0.72291376020047038,0.86699818430387632,0.91447254574493864,0.93083358813747319,0.94520733167898652,0.95886606822648157,0.97108427597720448,null,0.72291376020047038,0.72291376020047038,0.72291376020047038]
["2013-01-06T21:00:00","2013-01-06T21:00:00",null,9.5769172719060514,9.8804894735619513,10.184061675217851,10.487633876873751,10.791206078529651,11.094778280185551,11.398350481841451,11.701922683497351,12.005494885153251,null,0.37476844296601269,0.5519114257340253,0.71395514315777153,0.86006892534714097,0.90944646716933997,0.92761605666439118,0.94370371402980113,0.95898173112257279,0.97273510094868776,null,0.71395514315777153,0.71395514315777153,0.71395514315777153]
["2013-01-06T22:00:00","2013-01-06T22:00:00",null,9.3658732573089196,9.6694454589648196,9.9730176606207195,10.276589862276619,10.580162063932519,10.883734265588419,11.187306467244319,11.490878668900219,11.794450870556119,null,0.36562055936607374,0.54497165196855435,0.70907627190447076,0.85713529370991914,0.90835292706084148,0.92824694518852491,0.94597491271668255,0.96280912150231734,0.97803456455141102,null,0.70907627190447076,0.70907627190447076,0.70907627190447076]
["2013-01-06T23:00:00","2013-01-06T23:00:00",null,9.4022467304589235,9.7058189321148234,10.009391133770723,10.312963335426621,10.616535537082521,10.920107738738421,11.223679940394321,11.527252142050221,11.830824343706121,null,0.35837585614727152,0.53987196973180673,0.70597440332747996,0.85592609070532955,0.90892072673256186,0.93049711425793513,0.9498128179051627,0.96815064433998288,0.984806101377113,null,0.70597440332747996,0.70597440332747996,0.70597440332747996]
["2013-01-07","2013-01-07",null,9.1673380190865323,9.4709102207424323,9.7744824223983322,10.078054624054232,10.381626825710132,10.685199027366032,10.988771229021932,11.292343430677832,11.595915632333732,null,0.35286609636983701,0.53649671612769134,0.70459696338312139,0.85642028671590098,0.91118141061070768,0.93442965272503531,0.95532257768259721,0.97515350695786718,0.99321794836556254,null,0.70459696338312139,0.70459696338312139,0.70459696338312139]
["2013-01-07T01:00:00","2013-01-07T01:00:00",null,9.0043474480854826,9.3079196497413825,9.6114918513972825,9.9150640530531824,10.218636254709082,10.522208456364982,10.825780658020882,11.129352859676782,11.432925061332682,null,0.34892304309400124,0.53466713940770361,0.70474417070541928,0.85842861518439328,0.91494571213803888,0.93984477922384979,0.96229389587427483,0.98359689837252351,1,null,0.70474417070541928,0.70474417070541928,0.70474417070541928]
["2013-01-07T02:00:00","2013-01-07T02:00:00",null,8.901248375808235,9.204820577464135,9.5083927791200349,9.8119649807759348,10.115537182431833,10.419109384087733,10.722681585743633,11.026253787399533,11.329825989055433,null,0.34721964407884021,0.53503515771344823,0.70704691381850737,0.86255042020873363,0.92077091617754026,0.94727874899989217,0.97124199810823808,0.9939750145945232,1,null,0.70704691381850737,0.70704691381850737,0.70704691381850737]
["2013-01-07T03:00:00","2013-01-07T03:00:00",null,9.0506182515788911,9.354190453234791,9.657762654890691,9.9613348565465909,10.264907058202491,10.568479259858391,10.872051461514291,11.175623663170191,11.479195864826091,null,0.34882840981538121,0.53856813344859711,0.71238843665617291,0.8695848272528246,0.92940357414943664,0.95741502462097394,0.98279777290862069,1,1,null,0.71238843665617291,0.71238843665617291,0.71238843665617291]
["2013-01-07T04:00:00","2013-01-07T04:00:00",null,8.9062764415568658,9.2098486432127658,9.5134208448686657,9.8169930465245656,10.120565248180466,10.424137449836365,10.727709651492265,11.031281853148165,11.334854054804065,null,0.34679905172941777,0.53862070749227486,0.71438625031592973,0.87340170282383356,0.93493436354434223,0.96456509456115613,0.99147249011545935,1,1,null,0.71438625031592973,0.71438625031592973,0.71438625031592973]
["2013-01-07T05:00:00","2013-01-07T05:00:00",null,8.8471864953462624,9.1507586970021624,9.4543308986580623,9.7579031003139622,10.061475301969862,10.365047503625762,10.668619705281662,10.972191906937562,11.275764108593462,null,0.34422292358920509,0.5381580559079101,0.71588986796511511,0.87675592681047787,0.94003404578108984,0.97129457215191584,0.9997476445903466,1,1,null,0.71588986796511511,0.71588986796511511,0.71588986796511511]
["2013-01-07T06:00:00","2013-01-07T06:00:00",null,8.7359664169492337,9.0395386186051336,9.3431108202610336,9.6466830219169335,9.9502552235728334,10.253827425228733,10.557399626884633,10.860971828540533,11.164544030196433,null,0.34006957413865813,0.53619178667435996,0.71596347162626406,0.87874322566149909,0.94381937692589213,0.97677278750314367,1,1,1,null,0.71596347162626406,0.71596347162626406,0.71596347162626406]
["2013-01-07T07:00:00","2013-01-07T07:00:00",null,8.7900881318979707,9.0936603335538706,9.3972325352097705,9.7008047368656705,10.00437693852157,10.30794914017747,10.61152134183337,10.91509354348927,11.21866574514517,null,0.33251994146652464,0.53092386749784337,0.71284057343180218,0.87761814112679393,0.94458695796358816,0.97930685640841408,1,1,1,null,0.71284057343180218,0.71284057343180218,0.71284057343180218]
["2013-01-07T08:00:00","2013-01-07T08:00:00",null,8.9485169203132777,9.2520891219691777,9.5556613236250776,9.8592335252809775,10.162805726936877,10.466377928592777,10.769950130248677,11.073522331904577,11.377094533560477,null,0.32366647251118141,0.52436262684685264,0.70842435376286617,0.87521024992635021,0.94407173233554564,0.98057914826541703,1,1,1,null,0.70842435376286617,0.70842435376286617,0.70842435376286617]
["2013-01-07T09:00:00","2013-01-07T09:00:00",null,9.3032659679923686,9.6068381696482685,9.9104103713041685,10.213982572960068,10.517554774615968,10.821126976271868,11.124699177927768,11.428271379583668,11.731843581239568,null,0.31416108541423338,0.51708637920184375,0.70323003824749852,0.8719927184532682,0.94270480719992256,0.98095768137989725,1,1,1,null,0.70323003824749852,0.70323003824749852,0.70323003824749852]
["2013-01-07T10:00:00","2013-01-07T10:00:00",null,9.4750190484435706,9.7785912500994705,10.08216345175537,10.38573565341127,10.68930785506717,10.99288005672307,11.29645225837897,11.60002446003487,11.90359666169077,null,0.30267891427499966,0.50785437713202031,0.69611151273352301,0.86686149179031391,0.93945573130063387,0.97948560815691854,1,1,1,null,0.69611151273352301,0.69611151273352301,0.69611151273352301]
["2013-01-07T11:00:00","2013-01-07T11:00:00",null,9.9143057636530472,10.217877965308947,10.521450166964847,10.825022368620747,11.128594570276647,11.432166771932547,11.735738973588447,12.039311175244347,12.342883376900247,null,0.28599191281166275,0.49348063359050703,0.68390381979153558,0.85671470136049654,0.93124366567815997,0.97311363406316798,0.99537348415635274,0.99702430912783591,0.99859101562943464,null,0.68390381979153558,0.68390381979153558,0.68390381979153558]
["2013-01-07T12:00:00","2013-01-07T12:00:00",null,10.008575108194218,10.312147309850118,10.615719511506018,10.919291713161918,11.222863914817818,11.526436116473718,11.830008318129618,12.133580519785518,12.437152721441418,null,0.26794850102143836,0.4777715093395774,0.67038177575760283,0.84526407464746955,0.92174879338994753,0.96547988292114995,0.98949570607317361,0.99281838563361113,0.99597282825427969,null,0.67038177575760283,0.67038177575760283,0.67038177575760283]
["2013-01-07T13:00:00","2013-01-07T13:00:00",null,10.415480008577308,10.719052210233208,11.022624411889108,11.326196613545008,11.629768815200908,11.933341016856808,12.236913218512708,12.540485420168608,12.844057621824508,null,0.23615171940509888,0.44860342990712843,0.64369519118674645,0.82092229242464354,0.89963615061906066,0.945480716706111,0.97150486832662708,0.97674124307693688,0.98172526241759317,null,0.64369519118674645,0.64369519118674645,0.64369519118674645]
["2013-01-07T14:00:00","2013-01-07T14:00:00",null,11.059551065174993,11.363123266830893,11.666695468486793,11.970267670142693,12.273839871798593,12.577412073454493,12.880984275110393,13.184556476766293,13.488128678422193,null,0.17044467961657195,0.38628215853145248,0.58459145128415246,0.764857332246627,0.84647327765205915,0.89507272362782675,0.92372557743223338,0.93146447666160692,0.93883535758523573,null,0.58459145128415246,0.58459145128415246,0.58459145128415246]
["2013-01-07T15:00:00","2013-01-07T15:00:00",null,11.04150929420549,11.34508149586139,11.64865369751729,11.95222589917319,12.255798100829089,12.559370302484989,12.862942504140889,13.166514705796789,13.470086907452689,null,0.10892253370479871,0.3280406329451746,0.52946230908360092,0.71267233649203277,0.79709573582986004,0.84836594322446035,0.8795528659341374,0.88972068598142584,0.89940482482687822,null,0.52946230908360092,0.52946230908360092,0.52946230908360092]
["2013-01-07T16:00:00","2013-01-07T16:00:00",null,10.551519315756725,10.855091517412625,11.158663719068525,11.462235920724424,11.765808122380324,12.069380324036224,12.372952525692124,12.676524727348024,12.980096929003924,null,5.5454731284465951E-2,0.27746440292712138,0.48160941452805828,0.6674060848854384,0.75426891984991606,0.80787341478381114,0.84126844732795614,0.85353922912235702,0.86523169643630171,null,0.48160941452805828,0.48160941452805828,0.48160941452805828]
["2013-01-07T17:00:00","2013-01-07T17:00:00",null,10.426741011756716,10.730313213412618,11.033885415068518,11.337457616724418,11.641029818380318,11.944602020036218,12.248174221692118,12.551746423348018,12.855318625003918,null,1.959923349619954E-2,0.24444790349745671,0.45128470613469746,0.63962596020608364,0.72889668637100491,0.78479340960925259,0.82036500756165887,0.83470720667696552,0.84836594322446024,null,0.45128470613469746,0.45128470613469746,0.45128470613469746]
["2013-01-07T18:00:00","2013-01-07T18:00:00",null,10.156807380944301,10.460379582600201,10.763951784256099,11.067523985911999,11.371096187567899,11.674668389223799,11.978240590879699,12.281812792535598,12.585384994191498,null,0,0.21969604373394377,0.42900382642404156,0.61968988284345805,0.71117923365158298,0.76917891863694299,0.80674833024910608,0.82299370974554942,0.83845047858682531,null,0.42900382642404156,0.42900382642404156,0.42900382642404156]
["2013-01-07T19:00:00","2013-01-07T19:00:00",null,9.9505993540572728,10.254171555713173,10.557743757369073,10.861315959024973,11.164888160680873,11.468460362336772,11.772032563992672,12.075604765648572,12.379176967304472,null,0,0.201757780031075,0.41338933545173201,0.60627298689688092,0.69983375502591161,0.75981022405355725,0.79924075681191487,0.81726313898466818,0.83440227722363391,null,0.41338933545173201,0.41338933545173201,0.41338933545173201]
["2013-01-07T20:00:00","2013-01-07T20:00:00",null,9.9586276780086322,10.262199879664532,10.565772081320432,10.869344282976332,11.172916484632232,11.476488686288132,11.780060887944032,12.083633089599932,12.387205291255832,null,0,0.18678469239163473,0.40065590207296642,0.59564251526522771,0.69120109705401522,0.75305971684532647,0.79428828189746514,0.81400354827664401,0.83276196706088623,null,0.40065590207296642,0.40065590207296642,0.40065590207296642]
["2013-01-07T21:00:00","2013-01-07T21:00:00",null,9.8662368828680957,10.169809084523996,10.473381286179896,10.776953487835796,11.080525689491695,11.384097891147595,11.687670092803495,11.991242294459395,12.294814496115295,null,0,0.17288411524322175,0.38897394956775705,0.58605300969839513,0.68358837552946838,0.74731863127570963,0.79032419900415829,0.81172183478102711,0.83207850449307474,null,0.38897394956775705,0.38897394956775705,0.38897394956775705]
["2013-01-07T22:00:00","2013-01-07T22:00:00",null,9.8042916623877758,10.107863864043676,10.411436065699576,10.715008267355476,11.018580469011376,11.322152670667275,11.625724872323175,11.929297073979075,12.232869275634975,null,0,0.16237982131639531,0.38060416181424972,0.57970206522211565,0.67914061143432569,0.744668899474348,0.78937786621795769,0.81239478254010311,0.83428661432754281,null,0.38060416181424972,0.38060416181424972,0.38060416181424972]
["2013-01-07T23:00:00","2013-01-07T23:00:00",null,9.6638332942577385,9.9674054959136384,10.270977697569538,10.574549899225438,10.878122100881338,11.181694302537238,11.485266504193138,11.788838705849038,12.092410907504938,null,0,0.15597630279643804,0.37625103099772705,0.57728365921293634,0.67854126733639863,0.74579398400905317,0.79213274610667495,0.81669533931294802,0.84005924432336632,null,0.37625103099772705,0.37625103099772705,0.37625103099772705]
["2013-01-08","2013-01-08",null,9.7029887491105917,10.006560950766492,10.310133152422392,10.61370535407829,10.91727755573419,11.22084975739009,11.52442195904599,11.827994160701889,12.131566362357789,null,0,0.15097125383831053,0.37323328089062074,0.57614805986949569,0.67918267066926796,0.74810724193087685,0.79604425495630404,0.8221104658117625,0.84690438481021713,null,0.37323328089062074,0.37323328089062074,0.37323328089062074]
["2013-01-08T01:00:00","2013-01-08T01:00:00",null,9.5983890098698019,9.9019612115257019,10.205533413181602,10.509105614837502,10.812677816493402,11.116250018149302,11.419822219805202,11.723394421461101,12.026966623117001,null,0,0.14810071105350212,0.37231849253062688,0.5770733630382251,0.68184291727936519,0.75241831351245725,0.80190100342201209,0.82944980230918475,0.85564219086946913,null,0.37231849253062688,0.37231849253062688,0.37231849253062688]
["2013-01-08T02:00:00","2013-01-08T02:00:00",null,9.6638736071478988,9.9674458088037987,10.271018010459699,10.574590212115599,10.878162413771499,11.181734615427398,11.485306817083298,11.788879018739198,12.092451220395098,null,0,0.14531428673857819,0.3714773078317819,0.57805124025063237,0.68454522312440458,0.75675041471150883,0.80777878150519122,0.83678913880660699,0.86436948211998554,null,0.3714773078317819,0.3714773078317819,0.3714773078317819]
["2013-01-08T03:00:00","2013-01-08T03:00:00",null,9.7289832696386505,10.03255547129455,10.33612767295045,10.63969987460635,10.94327207626225,11.24684427791815,11.55041647957405,11.85398868122995,12.15756088288585,null,0,0.14258043646733207,0.3706676675591436,0.57905014708051072,0.68724752896944397,0.76107200110182482,0.81363552997089927,0.84409693087782256,0.8730547141355598,null,0.3706676675591436,0.3706676675591436,0.3706676675591436]
["2013-01-08T04:00:00","2013-01-08T04:00:00",null,9.7411534303222034,10.044725631978103,10.348297833634003,10.651870035289903,10.955442236945803,11.259014438601703,11.562586640257603,11.866158841913503,12.169731043569403,null,0,0.13932084575930784,0.36934280165846278,0.57955485789981775,0.68947666842138311,0.76493093590777606,0.81905065646971376,0.85097361579088016,0.88132986861044704,null,0.36934280165846278,0.36934280165846278,0.36934280165846278]
["2013-01-08T05:00:00","2013-01-08T05:00:00",null,9.7978195075998631,10.101391709255763,10.404963910911663,10.708536112567563,11.012108314223463,11.315680515879363,11.619252717535263,11.922824919191163,12.226397120847063,null,0,0.13287526800440833,0.36491606718079117,0.57703130380328282,0.68875114661862935,0.76590881312018333,0.82163729941866204,0.8550954208152205,0.8869027172402949,null,0.36491606718079117,0.36491606718079117,0.36491606718079117]
["2013-01-08T06:00:00","2013-01-08T06:00:00",null,9.9174908042767296,10.22106300593263,10.524635207588529,10.828207409244431,11.131779610900331,11.435351812556231,11.738924014212131,12.042496215868031,12.346068417523931,null,0,0.12360120669964264,0.35771342319693122,0.57178441424423743,0.68535486339704288,0.76425798814870005,0.82164781422739763,0.85668315693429031,0.8899940710085501,null,0.35771342319693122,0.35771342319693122,0.35771342319693122]
["2013-01-08T07:00:00","2013-01-08T07:00:00",null,9.9968556735022993,10.300427875158199,10.604000076814099,10.907572278469999,11.211144480125899,11.514716681781799,11.818288883437699,12.121861085093599,12.425433286749499,null,0,0.11367522725327212,0.34986937588020195,0.5658961213523227,0.68131717684258708,0.76197627465308315,0.8210274405119995,0.85764000452922651,0.89245453625267157,null,0.34986937588020195,0.34986937588020195,0.34986937588020195]
["2013-01-08T08:00:00","2013-01-08T08:00:00",null,10.028698530776047,10.332270732431947,10.635842934087847,10.939415135743747,11.242987337399647,11.546559539055547,11.850131740711447,12.153703942367347,12.457276144023247,null,0,0.10219305611403841,0.34050068129681621,0.55852524042869378,0.67583896149135925,0.75828557678690089,0.81902962685224268,0.85726147141474629,0.89361116521358341,null,0.34050068129681621,0.34050068129681621,0.34050068129681621]
["2013-01-08T09:00:00","2013-01-08T09:00:00",null,10.028679469528683,10.332251671184583,10.635823872840483,10.939396074496383,11.242968276152283,11.546540477808183,11.850112679464083,12.153684881119982,12.457257082775882,null,0,9.0816033062160323E-2,0.33123713480078609,0.55125950759242048,0.67046589422748704,0.75470002700807426,0.81713696127984148,0.85698808638762169,0.89487294226185088,null,0.33123713480078609,0.33123713480078609,0.33123713480078609]
["2013-01-08T10:00:00","2013-01-08T10:00:00",null,10.137467141070283,10.441039342726183,10.744611544382083,11.048183746037983,11.351755947693883,11.655328149349783,11.958900351005683,12.262472552661583,12.566044754317483,null,0,8.0826964763376419E-2,0.32329845420543679,0.54525555180441454,0.66630202996820453,0.75227110619015947,0.81635886543340985,0.8577766970427888,0.89715465575746778,null,0.32329845420543679,0.32329845420543679,0.32329845420543679]
["2013-01-08T11:00:00","2013-01-08T11:00:00",null,10.275602750182482,10.579174951838382,10.882747153494282,11.186319355150182,11.489891556806082,11.793463758461982,12.097035960117882,12.400608161773782,12.704180363429682,null,0,6.7325950346914812E-2,0.31192143115355869,0.5358868572210288,0.65883651576595548,0.74661413909042706,0.81241581215757408,0.85546343912096512,0.89638707471977175,null,0.31192143115355869,0.31192143115355869,0.31192143115355869]
["2013-01-08T12:00:00","2013-01-08T12:00:00",null,10.232154066486489,10.535726268142389,10.839298469798289,11.142870671454189,11.446442873110088,11.750015074765988,12.053587276421888,12.357159478077788,12.660731679733688,null,0,5.6138193852276849E-2,0.30280509197982641,0.52872627247211113,0.65352653735449662,0.7430601337378071,0.81053366139390848,0.85516902447636933,0.89759627772436135,null,0.30280509197982641,0.30280509197982641,0.30280509197982641]
["2013-01-08T13:00:00","2013-01-08T13:00:00",null,10.317660663220176,10.621232864876076,10.924805066531976,11.228377268187876,11.531949469843775,11.835521671499675,12.139093873155575,12.442666074811475,12.746238276467375,null,0,4.402513418890943E-2,0.29276344963736473,0.52065089936319953,0.64731228539177943,0.73861236964266441,0.80776826669645563,0.85399136589798641,0.89794326641263489,null,0.29276344963736473,0.29276344963736473,0.29276344963736473]
["2013-01-08T14:00:00","2013-01-08T14:00:00",null,10.333379981284773,10.636952182940673,10.940524384596573,11.244096586252473,11.547668787908373,11.851240989564273,12.154813191220173,12.458385392876073,12.761957594531973,null,0,3.1060375017961488E-2,0.2818911374047936,0.51176588598164963,0.64029890796515954,0.73338650970109009,0.80423529096130675,0.85206715589937854,0.89755421848941908,null,0.2818911374047936,0.2818911374047936,0.2818911374047936]
["2013-01-08T15:00:00","2013-01-08T15:00:00",null,10.400926822310627,10.704499023966527,11.008071225622427,11.311643427278327,11.615215628934227,11.918787830590126,12.222360032246026,12.525932233901926,12.829504435557826,null,0,1.8190249125633603E-2,0.27110294364210696,0.50294396145251308,0.63333810458221751,0.72820270899445805,0.80073385965236465,0.85016397551824185,0.89717568537493886,null,0.27110294364210696,0.27110294364210696,0.27110294364210696]
["2013-01-08T16:00:00","2013-01-08T16:00:00",null,10.332205706749065,10.635777908404965,10.939350110060865,11.242922311716764,11.546494513372664,11.850066715028564,12.153638916684464,12.457211118340364,12.760783319996264,null,0,5.236004763421221E-3,0.26024114621827144,0.49406946287969877,0.62633524196433321,0.72298736386161933,0.79720088391721577,0.84825028032836958,0.89678663745172305,null,0.26024114621827144,0.26024114621827144,0.26024114621827144]
["2013-01-08T17:00:00","2013-01-08T17:00:00",null,10.310992679537959,10.614564881193859,10.918137082849759,11.221709284505659,11.525281486161559,11.828853687817459,12.132425889473359,12.435998091129258,12.739570292785158,null,0,0,0.25051494813787661,0.48629901922411845,0.62042591945494741,0.71883401441107231,0.79471938905562312,0.84735652158584684,0.89740701116712118,null,0.25051494813787661,0.25051494813787661,0.25051494813787661]
["2013-01-08T18:00:00","2013-01-08T18:00:00",null,10.22659970307849,10.53017190473439,10.833744106390292,11.137316308046191,11.440888509702091,11.744460711357991,12.048032913013891,12.351605114669791,12.655177316325691,null,0,0,0.24151427186023555,0.47924358256255634,0.61522108913084417,0.71537464233707238,0.79293187157057754,0.8471462254111356,0.89870033264159532,null,0.24151427186023555,0.24151427186023555,0.24151427186023555]
["2013-01-08T19:00:00","2013-01-08T19:00:00",null,10.228917253631712,10.532489455287612,10.836061656943514,11.139633858599414,11.443206060255314,11.746778261911214,12.050350463567113,12.353922665223013,12.657494866878913,null,0,0,0.23242947711270998,0.47211454223984528,0.60994265514559209,0.71185218141065909,0.79107075042438302,0.84686232557527541,0.89993056526365611,null,0.23242947711270998,0.23242947711270998,0.23242947711270998]
["2013-01-08T20:00:00","2013-01-08T20:00:00",null,10.215739827925781,10.51931202958168,10.82288423123758,11.12645643289348,11.43002863454938,11.73360083620528,12.03717303786118,12.34074523951708,12.64431744117298,null,0,0,0.22402814493299594,0.46564793486747463,0.60530562449320924,0.70896060900837954,0.78983000299358674,0.84718828464607787,0.90174962717490836,null,0.22402814493299594,0.22402814493299594,0.22402814493299594]
["2013-01-08T21:00:00","2013-01-08T21:00:00",null,10.123670697345093,10.427242899000992,10.730815100656892,11.034387302312792,11.337959503968692,11.641531705624592,11.945103907280492,12.248676108936392,12.552248310592292,null,0,0,0.21683601575787154,0.4603800156909581,0.6018462524192093,0.70722566556701183,0.78973536971496672,0.84864984306032099,0.90468325881213019,null,0.21683601575787154,0.21683601575787154,0.21683601575787154]
["2013-01-08T22:00:00","2013-01-08T22:00:00",null,10.144553508447006,10.448125710102905,10.751697911758805,11.055270113414705,11.358842315070605,11.662414516726505,11.965986718382405,12.269558920038305,12.573131121694205,null,0,0,0.21190457046089295,0.45729917673143844,0.60052138651852849,0.70756213944654978,0.79164906490483899,0.85205664109064305,0.90952007083048869,null,0.21190457046089295,0.21190457046089295,0.21190457046089295]
["2013-01-08T23:00:00","2013-01-08T23:00:00",null,10.080063974556836,10.383636176212736,10.687208377868636,10.990780579524536,11.294352781180436,11.597924982836336,11.901497184492236,12.205069386148136,12.508641587804036,null,0,0,0.21051661570779875,0.45767770984591866,0.60257177422196306,0.71120026326905428,0.79679080637652877,0.85862839655036927,0.91745875142583799,null,0.21051661570779875,0.21051661570779875,0.21051661570779875]
["2013-01-09","2013-01-09",null,10.155225385548448,10.458797587204348,10.762369788860248,11.06594199051615,11.36951419217205,11.673086393827949,11.976658595483849,12.280230797139749,12.583802998795649,null,0,0,0.2085398316655131,0.45746741367120741,0.60403333263620618,0.71424955780236721,0.80134371855902709,0.86461132272090402,0.92480860273199583,null,0.2085398316655131,0.2085398316655131,0.2085398316655131]
["2013-01-09T01:00:00","2013-01-09T01:00:00",null,10.192591353886124,10.496163555542024,10.799735757197924,11.103307958853824,11.406880160509724,11.710452362165624,12.014024563821524,12.317596765477424,12.621168967133324,null,0,0,0.2082349022121818,0.45888691285050826,0.60707211236078362,0.7188340144110722,0.80738973358197519,0.87205580730568188,0.93357795321745451,null,0.2082349022121818,0.2082349022121818,0.2082349022121818]
["2013-01-09T02:00:00","2013-01-09T02:00:00",null,10.143109679533531,10.446681881189431,10.750254082845331,11.053826284501231,11.35739848615713,11.66097068781303,11.96454288946893,12.26811509112483,12.57168729278073,null,0,0,0.20695209554644323,0.45936007924360855,0.60919610372536714,0.72253522708599005,0.81258404909734283,0.87866962200035037,0.9415376634302749,null,0.20695209554644323,0.20695209554644323,0.20695209554644323]
["2013-01-09T03:00:00","2013-01-09T03:00:00",null,10.165139457115,10.4687116587709,10.7722838604268,11.0758560620827,11.3794282637386,11.6830004653945,11.9865726670504,12.2901448687063,12.593717070362199,null,0,0,0.20815078374229729,0.46224113683715257,0.61367541224671651,0.7285286680652604,0.82000750406464962,0.88746000210328024,0.9516213650076788,null,0.20815078374229729,0.20815078374229729,0.20815078374229729]
["2013-01-09T04:00:00","2013-01-09T04:00:00",null,10.214747454449631,10.518319656105531,10.821891857761431,11.125464059417331,11.429036261073231,11.73260846272913,12.03618066438503,12.33975286604093,12.64332506769683,null,0,0,0.20668922532805417,0.46252503667301276,0.61561013705405987,0.73203009937420249,0.82500203821404161,0.89386352062323748,0.95937077904578794,null,0.20668922532805417,0.20668922532805417,0.20668922532805417]
["2013-01-09T05:00:00","2013-01-09T05:00:00",null,10.325424870845541,10.628997072501441,10.932569274157341,11.236141475813241,11.539713677469141,11.843285879125041,12.146858080780941,12.450430282436841,12.754002484092741,null,0,0,0.20304058669681416,0.46066391552681829,0.6154419001142909,0.73347062817097453,0.82796721427747011,0.8982797402921735,0.96517495346781812,null,0.20304058669681416,0.20304058669681416,0.20304058669681416]
["2013-01-09T06:00:00","2013-01-09T06:00:00",null,10.465675389364584,10.769247591020484,11.072819792676384,11.376391994332284,11.679964195988184,11.983536397644084,12.287108599299984,12.590680800955884,12.894253002611784,null,0,0,0.19593257599157424,0.45541702596777284,0.61196149842281988,0.73166208106845787,0.82774640329402327,0.89957306176664764,0.96791931854779978,null,0.19593257599157424,0.19593257599157424,0.19593257599157424]
["2013-01-09T07:00:00","2013-01-09T07:00:00",null,10.50031498848435,10.80388719014025,11.10745939179615,11.41103159345205,11.71460379510795,12.01817599676385,12.321748198419749,12.625320400075649,12.928892601731549,null,0,0,0.1870580774187599,0.44843519296735967,0.60678821252492343,0.72820270899445794,0.82590631176529994,0.89928916193078745,0.9691074919349183,null,0.1870580774187599,0.1870580774187599,0.1870580774187599]
["2013-01-09T08:00:00","2013-01-09T08:00:00",null,10.502773746139171,10.806345947795071,11.109918149450971,11.413490351106871,11.717062552762771,12.020634754418671,12.324206956074571,12.627779157730471,12.931351359386371,null,0,0,0.17812048999353219,0.4414007859232687,0.60156235258334911,0.72469076287678025,0.82402416100163434,0.8989526880512495,0.97025360608709454,null,0.17812048999353219,0.17812048999353219,0.17812048999353219]
["2013-01-09T09:00:00","2013-01-09T09:00:00",null,10.609206793459327,10.912778995115227,11.216351196771125,11.519923398427025,11.823495600082925,12.127067801738825,12.430640003394725,12.734212205050625,13.037784406706525,null,0,0,0.16742692950946564,0.43264195024654556,0.59463309362661376,0.7195069621701482,0.82050170007522105,0.89700744843517055,0.96981198412020098,null,0.16742692950946564,0.16742692950946564,0.16742692950946564]
["2013-01-09T10:00:00","2013-01-09T10:00:00",null,10.662895390995326,10.966467592651226,11.270039794307126,11.573611995963025,11.877184197618925,12.180756399274825,12.484328600930725,12.787900802586625,13.091473004242525,null,0,0,0.1574483760194173,0.4245770919463695,0.58837678242895441,0.71496456479638537,0.8175996128642059,0.89566155291701866,0.96994867663376327,null,0.1574483760194173,0.1574483760194173,0.1574483760194173]
["2013-01-09T11:00:00","2013-01-09T11:00:00",null,10.715745272966478,11.019317474622378,11.322889676278278,11.626461877934178,11.930034079590078,12.233606281245978,12.537178482901878,12.840750684557777,13.144322886213677,null,0,0,0.14816379990591605,0.41717466659653385,0.5827513597554288,0.71103202632928519,0.81528635494238222,0.89488345707058703,0.97063213920157476,null,0.14816379990591605,0.14816379990591605,0.14816379990591605]
["2013-01-09T12:00:00","2013-01-09T12:00:00",null,10.73726842262141,11.04084062427731,11.34441282593321,11.64798502758911,11.95155722924501,12.25512943090091,12.55870163255681,12.86227383421271,13.16584603586861,null,0,0,0.13775413925770968,0.40866818632946417,0.57605342659087577,0.7060480069886288,0.81193213095573791,0.89308542477680597,0.9703166949395079,null,0.13775413925770968,0.13775413925770968,0.13775413925770968]
["2013-01-09T13:00:00","2013-01-09T13:00:00",null,10.82802373226826,11.13159593392416,11.43516813558006,11.73874033723596,12.04231253889186,12.34588474054776,12.64945694220366,12.95302914385956,13.25660134551546,null,0,0,0.12641917544077386,0.39924691770240062,0.56845121987506442,0.70017022890544967,0.80769466303530646,0.89041466335797326,0.96913903636112497,null,0.12641917544077386,0.12641917544077386,0.12641917544077386]
["2013-01-09T14:00:00","2013-01-09T14:00:00",null,10.961913484096163,11.265485685752063,11.569057887407965,11.872630089063865,12.176202290719765,12.479774492375665,12.783346694031565,13.086918895687464,13.390491097343364,null,0,0,0.11188770976822718,0.38669223607213959,0.55775765939099786,0.69126418590642869,0.80048150424271092,0.88482078511065432,0.96508032018919809,null,0.11188770976822718,0.11188770976822718,0.11188770976822718]
["2013-01-09T15:00:00","2013-01-09T15:00:00",null,10.985435072165439,11.289007273821339,11.59257947547724,11.89615167713314,12.19972387878904,12.50329608044494,12.80686828210084,13.11044048375674,13.41401268541264,null,0,0,9.6178585517297549E-2,0.37298092548096673,0.54593901437222614,0.68124357318143813,0.79217480534161688,0.87815439637230797,0.95998063795245048,null,9.6178585517297549E-2,9.6178585517297549E-2,9.6178585517297549E-2]
["2013-01-09T16:00:00","2013-01-09T16:00:00",null,10.990384153583708,11.293956355239608,11.597528556895508,11.901100758551408,12.204672960207308,12.508245161863208,12.811817363519108,13.115389565175008,13.418961766830908,null,0,0,8.0532550118781299E-2,0.35933270374220727,0.53419397301460336,0.67130707892633201,0.78395222491040739,0.87157212610384616,0.9549650741855874,null,8.0532550118781299E-2,8.0532550118781299E-2,8.0532550118781299E-2]
["2013-01-09T17:00:00","2013-01-09T17:00:00",null,10.999810901594426,11.303383103250326,11.606955304906226,11.910527506562126,12.214099708218026,12.517671909873926,12.821244111529825,13.124816313185725,13.428388514841625,null,0,0,6.4287170622338019E-2,0.34508513790552076,0.52186010236778912,0.66079227019077003,0.77516184480747752,0.86443257097239956,0.94940274036447514,null,6.4287170622338019E-2,6.4287170622338019E-2,6.4287170622338019E-2]
["2013-01-09T18:00:00","2013-01-09T18:00:00",null,10.987329406704706,11.290901608360606,11.594473810016506,11.898046011672406,12.201618213328306,12.505190414984206,12.808762616640106,13.112334818296006,13.415907019951906,null,0,0,4.865165003255733E-2,0.33144743097549684,0.51011506101016635,0.65084526112692842,0.76693926437626803,0.85785030070393775,0.94437666178887647,null,4.865165003255733E-2,4.865165003255733E-2,4.865165003255733E-2]
["2013-01-09T19:00:00","2013-01-09T19:00:00",null,10.991119135097744,11.294691336753644,11.598263538409544,11.901835740065444,12.205407941721344,12.508980143377244,12.812552345033144,13.116124546689043,13.419696748344943,null,0,0,3.301612944277664E-2,0.31780972404547292,0.49838053446127917,0.6409192816805579,0.75872719875379413,0.85128906005294702,0.93938212763948448,null,3.301612944277664E-2,3.301612944277664E-2,3.301612944277664E-2]
["2013-01-09T20:00:00","2013-01-09T20:00:00",null,10.900247176267911,11.203819377923811,11.507391579579711,11.810963781235611,12.11453598289151,12.41810818454741,12.72168038620331,13.02525258785921,13.32882478951511,null,0,0,1.8179734316898663E-2,0.30497114257935171,0.48742410375882356,0.6317608832718834,0.75128271416901626,0.84547437082218124,0.93512363010158184,null,1.8179734316898663E-2,1.8179734316898663E-2,1.8179734316898663E-2]
["2013-01-09T21:00:00","2013-01-09T21:00:00",null,10.882129083036498,11.185701284692398,11.489273486348296,11.792845688004196,12.096417889660096,12.399990091315995,12.703562292971895,13.007134494627795,13.310706696283695,null,0,0,4.3107015946923875E-3,0.2930683790906955,0.47739297622509741,0.62350675841446723,0.74473198832676113,0.84053241071646712,0.93172734687999537,null,4.3107015946923875E-3,4.3107015946923875E-3,4.3107015946923875E-3]
["2013-01-09T22:00:00","2013-01-09T22:00:00",null,10.857094585937411,11.160666787593311,11.46423898924921,11.76781119090511,12.07138339256101,12.37495559421691,12.67852779587281,12.98209999752871,13.28567219918461,null,0,0,0,0.28562389450591763,0.47171497950789393,0.6195111310949537,0.74233461193505301,0.83965968159141546,0.93230566136045123,null,-4.99490413627998E-3,-4.99490413627998E-3,-4.99490413627998E-3]
["2013-01-09T23:00:00","2013-01-09T23:00:00",null,10.81987870526941,11.12345090692531,11.42702310858121,11.73059531023711,12.03416751189301,12.33773971354891,12.64131191520481,12.94488411686071,13.24845631851661,null,0,0,0,0.27983023489262299,0.46764574852723145,0.6170927250857744,0.74147239761873696,0.8402905701155492,0.93435604906388581,null,-7.6127215245468862E-3,-7.6127215245468862E-3,-7.6127215245468862E-3]
["2013-01-10","2013-01-10",null,10.802072396328736,11.105644597984636,11.409216799640536,11.712789001296436,12.016361202952336,12.319933404608236,12.623505606264136,12.927077807920035,13.230650009575935,null,0,0,0,0.27478312669955324,0.46430203934932274,0.61537881126187777,0.74130416067896798,0.84159440639875893,0.93706886971766079,null,-6.8556552955864221E-3,-6.8556552955864221E-3,-6.8556552955864221E-3]
["2013-01-10T01:00:00","2013-01-10T01:00:00",null,10.761401865534891,11.064974067190791,11.368546268846689,11.672118470502589,11.975690672158489,12.279262873814389,12.582835075470289,12.886407277126189,13.189979478782089,null,0,0,0,0.27157611003520682,0.46276687727393068,0.61542087049682004,0.74284983756309564,0.84458061207965851,0.94142200053418346,null,-4.9629897231852627E-3,-4.9629897231852627E-3,-4.9629897231852627E-3]
["2013-01-10T02:00:00","2013-01-10T02:00:00",null,10.769647781068759,11.073219982724659,11.376792184380559,11.680364386036459,11.983936587692359,12.287508789348259,12.591080991004159,12.894653192660058,13.198225394315958,null,0,0,0,0.26814828238741362,0.46102141902382737,0.61526314836578666,0.74420624788998313,0.84738806601205352,0.94560689441093715,null,-5.1838007066320651E-3,-5.1838007066320651E-3,-5.1838007066320651E-3]
["2013-01-10T03:00:00","2013-01-10T03:00:00",null,10.750852777500246,11.054424979156146,11.357997180812045,11.661569382467945,11.965141584123845,12.268713785779745,12.572285987435645,12.875858189091545,13.179430390747445,null,0,0,0,0.26551958020352312,0.4600435418114201,0.61586249246371372,0.74629869482835998,0.8509105269384668,0.95048576566423792,null,-4.3741604339937908E-3,-4.3741604339937908E-3,-4.3741604339937908E-3]
["2013-01-10T04:00:00","2013-01-10T04:00:00",null,10.79812813772249,11.10170033937839,11.405272541034289,11.708844742690189,12.012416944346089,12.315989146001989,12.619561347657889,12.923133549313789,13.226705750969689,null,0,0,0,0.26050401643666005,0.45673137705971806,0.61416960825728828,0.74615148750606208,0.85223539283914762,0.9532091011267485,null,-6.8135960606441745E-3,-6.8135960606441745E-3,-6.8135960606441745E-3]
["2013-01-10T05:00:00","2013-01-10T05:00:00",null,10.868169535852036,11.171741737507936,11.475313939163836,11.778886140819736,12.082458342475636,12.386030544131536,12.689602745787436,12.993174947443336,13.296747149099236,null,0,0,0,0.25237606928407064,0.45038043258343863,0.60951154798743434,0.74310219297274915,0.85072126038122664,0.95315652708307075,null,-9.9995831075194597E-3,-9.9995831075194597E-3,-9.9995831075194597E-3]
["2013-01-10T06:00:00","2013-01-10T06:00:00",null,10.933931377143846,11.237503578799746,11.541075780455646,11.844647982111546,12.148220183767446,12.451792385423346,12.755364587079246,13.058936788735146,13.362508990391046,null,0,0,0,0.24128294606805273,0.44112740089614405,0.60201448935897861,0.73726647412451229,0.84648379246079519,0.95043319162056017,null,-1.3038362832096877E-2,-1.3038362832096877E-2,-1.3038362832096877E-2]
["2013-01-10T07:00:00","2013-01-10T07:00:00",null,10.906452277688576,11.210024479344476,11.513596681000376,11.817168882656276,12.120741084312176,12.424313285968076,12.727885487623976,13.031457689279875,13.335029890935775,null,0,0,0,0.23133593700421107,0.43299945374355464,0.59561097083902137,0.73250326576730274,0.84328729060518437,0.94874030741413473,null,-1.1860704253713933E-2,-1.1860704253713933E-2,-1.1860704253713933E-2]
["2013-01-10T08:00:00","2013-01-10T08:00:00",null,10.720987220279666,11.024559421935566,11.328131623591464,11.631703825247364,11.935276026903264,12.238848228559164,12.542420430215063,12.845992631870963,13.149564833526863,null,0,0,0,0.22037950630175546,0.42391465899602909,0.5883031787678058,0.72687784309377712,0.83928114847693525,0.94626932736127767,null,-1.2922699936005696E-2,-1.2922699936005696E-2,-1.2922699936005696E-2]
["2013-01-10T09:00:00","2013-01-10T09:00:00",null,10.802600769049278,11.106172970705178,11.409745172361077,11.713317374016977,12.016889575672877,12.320461777328777,12.624033978984677,12.927606180640577,13.231178382296477,null,0,0,0,0.20894990920619957,0.41435669785540324,0.58052222030348988,0.72078976883588675,0.83481235476432136,0.94333569572405584,null,-1.3395866329105985E-2,-1.3395866329105985E-2,-1.3395866329105985E-2]
["2013-01-10T10:00:00","2013-01-10T10:00:00",null,10.862578531368412,11.166150733024311,11.469722934680211,11.773295136336111,12.076867337992011,12.380439539647911,12.684011741303811,12.987583942959711,13.291156144615611,null,0,0,0,0.19466028413457082,0.40200179759111787,0.5699968967591923,0.71202041835042806,0.82770434405908144,0.93781542113788574,null,-1.6318983157592219E-2,-1.6318983157592219E-2,-1.6318983157592219E-2]
["2013-01-10T11:00:00","2013-01-10T11:00:00",null,10.793796132317921,11.09736833397382,11.40094053562972,11.70451273728562,12.00808493894152,12.31165714059742,12.61522934225332,12.91880154390922,13.22237374556512,null,0,0,0,0.18049683676776881,0.38977307503165926,0.55961878053719261,0.70339827518726727,0.8207645702936105,0.93247389830022021,null,-1.6213835070236601E-2,-1.6213835070236601E-2,-1.6213835070236601E-2]
["2013-01-10T12:00:00","2013-01-10T12:00:00",null,10.772873253321595,11.076445454977495,11.380017656633393,11.683589858289293,11.987162059945193,12.290734261601093,12.594306463256993,12.897878664912893,13.201450866568793,null,0,0,0,0.16690118907268714,0.37818575580506991,0.54993464169174,0.69552268344433132,0.81462392199204225,0.92797356016139965,null,-1.5698609442194061E-2,-1.5698609442194061E-2,-1.5698609442194061E-2]
["2013-01-10T13:00:00","2013-01-10T13:00:00",null,10.962507158311547,11.266079359967447,11.569651561623347,11.873223763279247,12.176795964935147,12.480368166591047,12.783940368246947,13.087512569902847,13.391084771558747,null,0,0,0,0.14982513968613445,0.36338090510539861,0.5372853267828589,0.6849237562388848,0.80598074921141027,0.92120202333569767,null,-1.9452396160789694E-2,-1.9452396160789694E-2,-1.9452396160789694E-2]
["2013-01-10T14:00:00","2013-01-10T14:00:00",null,10.92747786949122,11.23105007114712,11.53462227280302,11.83819447445892,12.14176667611482,12.44533887777072,12.74891107942662,13.05248328108252,13.356055482738419,null,0,0,0,0.13755435789173359,0.35326565910178798,0.52922046848268289,0.67880413755478775,0.80172225167350764,0.91872052847410501,null,-1.4541980481282243E-2,-1.4541980481282243E-2,-1.4541980481282243E-2]
["2013-01-10T15:00:00","2013-01-10T15:00:00",null,10.760536329226534,11.064108530882434,11.367680732538334,11.671252934194234,11.974825135850134,12.278397337506034,12.581969539161934,12.885541740817834,13.189113942473734,null,0,0,0,0.1296367069138554,0.34741942544481552,0.52535101886799607,0.67680632389503093,0.80151195549879639,0.9202136313145548,null,-1.0094216386139518E-2,-1.0094216386139518E-2,-1.0094216386139518E-2]
["2013-01-10T16:00:00","2013-01-10T16:00:00",null,10.607640741589734,10.911212943245634,11.214785144901535,11.518357346557435,11.821929548213335,12.125501749869235,12.429073951525135,12.732646153181035,13.036218354836935,null,0,0,0,0.12564107959434184,0.34542161178505876,0.52525638558937604,0.67852023771892755,0.80495029795532513,0.92529228393383123,null,-6.1091038753615205E-3,-6.1091038753615205E-3,-6.1091038753615205E-3]
["2013-01-10T17:00:00","2013-01-10T17:00:00",null,10.585169372864829,10.888741574520729,11.192313776176629,11.495885977832529,11.799458179488429,12.103030381144329,12.406602582800229,12.710174784456129,13.013746986112029,null,0,0,0,0.12272847757459117,0.34448579380759375,0.52620271837557664,0.68125408799017373,0.80937703243299675,0.93134881376551493,null,-4.9945341493919486E-3,-4.9945341493919486E-3,-4.9945341493919486E-3]
["2013-01-10T18:00:00","2013-01-10T18:00:00",null,10.522806650998904,10.826378852654804,11.129951054310704,11.433523255966604,11.737095457622504,12.040667659278403,12.344239860934303,12.647812062590203,12.951384264246103,null,0,0,0,0.12268641833964893,0.34635742976252382,0.5298829014330233,0.68666921448898821,0.8164324690945588,0.93997095692867572,null,-2.0609025121701516E-3,-2.0609025121701516E-3,-2.0609025121701516E-3]
["2013-01-10T19:00:00","2013-01-10T19:00:00",null,10.448936513481343,10.752508715137242,11.056080916793142,11.359653118449042,11.663225320104942,11.966797521760842,12.270369723416742,12.573941925072642,12.877514126728542,null,0,0,0,0.12287568489688905,0.3484709063183718,0.53381543990012348,0.69232618158872061,0.82374026116577437,0.94884545550149002,null,-1.8295767199877876E-3,-1.8295767199877876E-3,-1.8295767199877876E-3]
["2013-01-10T20:00:00","2013-01-10T20:00:00",null,10.4312403673979,10.734812569053799,11.038384770709699,11.341956972365599,11.645529174021499,11.949101375677399,12.252673577333299,12.556245778989199,12.859817980645099,null,0,0,0,0.12399025462285862,0.35148865642547811,0.5386312223010109,0.69885587781350467,0.83189975274457051,0.9585611387731493,null,-8.8324393378720785E-4,-8.8324393378720785E-4,-8.8324393378720785E-4]
["2013-01-10T21:00:00","2013-01-10T21:00:00",null,10.106891844719362,10.410464046375262,10.714036248031162,11.017608449687062,11.321180651342962,11.624752852998862,11.928325054654762,12.231897256310662,12.535469457966562,null,0,0,0,0.11831225790565514,0.34751405872343566,0.53627590514424506,0.69803572273213088,0.83254115607743984,0.9605904968591128,null,-7.4865438197201425E-3,-7.4865438197201425E-3,-7.4865438197201425E-3]
["2013-01-10T22:00:00","2013-01-10T22:00:00",null,10.322262368471897,10.625834570127797,10.929406771783697,11.232978973439597,11.536551175095497,11.840123376751396,12.143695578407296,12.447267780063196,12.750839981719096,null,0,0,1.0094216386139518E-3,0.12129846358655474,0.35236138555052976,0.54290023464764914,0.7063424216332248,0.84244610590633928,0.97202009395466871,null,1.0094216386139518E-3,1.0094216386139518E-3,1.0094216386139518E-3]
["2013-01-10T23:00:00","2013-01-10T23:00:00",null,10.19169209039538,10.49526429205128,10.79883649370718,11.10240869536308,11.40598089701898,11.709553098674879,12.013125300330779,12.316697501986679,12.620269703642579,null,7.3603661148933987E-5,2.2186246432035813E-3,5.2468895590454369E-3,0.12743911188812296,0.36031058095461466,0.55256334387563066,0.71763532621521842,0.85528468737246044,0.98632023383503298,null,5.2468895590454369E-3,5.2468895590454369E-3,5.2468895590454369E-3]
["2013-01-11","2013-01-11",null,10.21256293674249,10.51613513839839,10.81970734005429,11.12327954171019,11.42685174336609,11.73042394502199,12.03399614667789,12.337568348333789,12.641140549989689,null,2.6287021838904993E-3,6.8346256781152987E-3,1.1808130210036124E-2,0.13584044406783699,0.37044685657569643,0.56435044446819571,0.7309891333093822,0.87013159730707401,1,null,1.1808130210036124E-2,1.1808130210036124E-2,1.1808130210036124E-2]
["2013-01-11T01:00:00","2013-01-11T01:00:00",null,10.102556200175339,10.406128401831239,10.709700603487139,11.013272805143039,11.316845006798939,11.620417208454839,11.923989410110739,12.227561611766639,12.531133813422539,null,7.4865438197201425E-3,1.3711310591172844E-2,2.0587995504230391E-2,0.14641834165581236,0.38272815317883285,0.57824050680787309,0.74641435772445164,0.88700786532765097,1,null,2.0587995504230391E-2,2.0587995504230391E-2,2.0587995504230391E-2]
["2013-01-11T02:00:00","2013-01-11T02:00:00",null,10.040574783334128,10.344146984990028,10.647719186645928,10.951291388301827,11.254863589957727,11.558435791613627,11.862007993269527,12.165580194925427,12.469152396581327,null,1.1913278297391743E-2,2.0177917963543471E-2,2.8978812875208863E-2,0.15662822093804304,0.39465194628496014,0.59179409526801252,0.76151362306871861,0.90357920389489665,1,null,2.8978812875208863E-2,2.8978812875208863E-2,2.8978812875208863E-2]
["2013-01-11T03:00:00","2013-01-11T03:00:00",null,10.005887147533189,10.309459349189089,10.613031550844989,10.91660375250089,11.22017595415679,11.52374815581269,11.82732035746859,12.13089255912449,12.43446476078039,null,1.8127530260108882E-2,2.8379468777281827E-2,3.9062514452612815E-2,0.16847841038302142,0.40818450512762844,0.60691439022975069,0.77813753567964217,0.92163313049385664,1,null,3.9062514452612815E-2,3.9062514452612815E-2,3.9062514452612815E-2]
["2013-01-11T04:00:00","2013-01-11T04:00:00",null,10.069474269522077,10.373046471177977,10.676618672833877,10.980190874489777,11.283763076145677,11.587335277801577,11.890907479457477,12.194479681113377,12.498051882769277,null,2.4720315337306255E-2,3.6949037896764854E-2,4.9493204718290315E-2,0.18066507370753776,0.4220325082323636,0.62232909983608453,0.79504534812642591,0.93996044211994123,1,null,4.9493204718290315E-2,4.9493204718290315E-2,4.9493204718290315E-2]
["2013-01-11T05:00:00","2013-01-11T05:00:00",null,9.9688591222569656,10.272431323912866,10.576003525568765,10.879575727224665,11.183147928880565,11.486720130536465,11.790292332192365,12.093864533848265,12.397436735504165,null,2.9451979268309156E-2,4.373108953120234E-2,5.8209981160071214E-2,0.19120091206057088,0.43429277521802889,0.63621916217576191,0.81049160215896654,0.95687876937546046,1,null,5.8209981160071214E-2,5.8209981160071214E-2,5.8209981160071214E-2]
["2013-01-11T06:00:00","2013-01-11T06:00:00",null,10.135129705859148,10.438701907515048,10.742274109170948,11.045846310826848,11.349418512482748,11.652990714138648,11.956562915794548,12.260135117450448,12.563707319106348,null,3.2427670140473201E-2,4.8767682915536535E-2,6.5191814160484376E-2,0.2000228365897074,0.44484964318853315,0.64842685511774933,0.82426600160255281,0.97213575685076092,1,null,6.5191814160484376E-2,6.5191814160484376E-2,6.5191814160484376E-2]
["2013-01-11T07:00:00","2013-01-11T07:00:00",null,10.212670929843833,10.516243131499733,10.819815333155633,11.123387534811533,11.426959736467433,11.730531938123333,12.034104139779233,12.337676341435133,12.641248543091033,null,3.4993283471950326E-2,5.3394198759183817E-2,7.1763569620210632E-2,0.208434683578157,0.45499643361835046,0.66022447051904987,0.83763032350545208,0.98699318159410998,1,null,7.1763569620210632E-2,7.1763569620210632E-2,7.1763569620210632E-2]
["2013-01-11T08:00:00","2013-01-11T08:00:00",null,10.095583878579646,10.399156080235546,10.702728281891446,11.006300483547347,11.309872685203247,11.613444886859147,11.917017088515047,12.220589290170947,12.524161491826847,null,3.6454841886193447E-2,5.6969233729274898E-2,7.7336418250058492E-2,0.21588968297167047,0.46423895049690944,0.67115987160403434,0.85016397551824197,1,1,null,7.7336418250058492E-2,7.7336418250058492E-2,7.7336418250058492E-2]
["2013-01-11T09:00:00","2013-01-11T09:00:00",null,10.407329526829185,10.710901728485085,11.014473930140985,11.318046131796885,11.621618333452785,11.925190535108685,12.228762736764585,12.532334938420485,12.835907140076385,null,3.2322522053117579E-2,5.5055538539402614E-2,7.7504655189827479E-2,0.21803470395372512,0.46825560743389411,0.67695353121732904,0.8576505193379621,1,1,null,7.7504655189827479E-2,7.7504655189827479E-2,7.7504655189827479E-2]
["2013-01-11T10:00:00","2013-01-11T10:00:00",null,10.659364803200244,10.962937004856144,11.266509206512044,11.570081408167944,11.873653609823844,12.177225811479744,12.480798013135644,12.784370214791544,13.087942416447444,null,2.2480661076631547E-2,4.7526935484740226E-2,7.2173647160897553E-2,0.21477511324570089,0.46697280076815556,0.6775423605065205,0.86001635130346354,1,1,null,7.2173647160897553E-2,7.2173647160897553E-2,7.2173647160897553E-2]
["2013-01-11T11:00:00","2013-01-11T11:00:00",null,11.053339791699008,11.356911993354908,11.660484195010808,11.964056396666708,12.267628598322608,12.571200799978508,12.874773001634408,13.178345203290307,13.481917404946207,null,3.9009940408934983E-3,3.1418248501859244E-2,5.8409762526046898E-2,0.20322985325405382,0.45754101733235647,0.67012942034794931,0.85451710633476463,0.99633033175128882,0.99807579000139213,null,5.8409762526046898E-2,5.8409762526046898E-2,5.8409762526046898E-2]
["2013-01-11T12:00:00","2013-01-11T12:00:00",null,11.2321507960876,11.535722997743502,11.839295199399402,12.142867401055302,12.446439602711202,12.750011804367102,13.053584006023002,13.357156207678901,13.660728409334801,null,0,1.3711310591172841E-2,4.3047626963390817E-2,0.19010737195207245,0.44654252739495864,0.66114977368777939,0.84747218448193806,0.99112550142718558,0.99462693273612779,null,4.3047626963390817E-2,4.3047626963390817E-2,4.3047626963390817E-2]
["2013-01-11T13:00:00","2013-01-11T13:00:00",null,11.413693906666801,11.717266108322701,12.0208383099786,12.3244105116345,12.6279827132904,12.9315549149463,13.2351271166022,13.5386993182581,13.842271519914,null,0,0,2.5887459106953638E-2,0.17518685835630998,0.43375651997251524,0.65040363916003507,0.83866077476153711,0.98417521285297915,0.98944313202949574,null,2.5887459106953638E-2,2.5887459106953638E-2,2.5887459106953638E-2]
["2013-01-11T14:00:00","2013-01-11T14:00:00",null,11.547244139801936,11.850816341457836,12.154388543113736,12.457960744769636,12.761532946425536,13.065105148081436,13.368677349737336,13.672249551393236,13.975821753049136,null,0,0,6.0355002142125878E-3,0.15761661295918589,0.41836283998365248,0.63708137649207808,0.82731529613586574,0.97472239979970887,0.98180938088747771,null,6.0355002142125878E-3,6.0355002142125878E-3,6.0355002142125878E-3]
["2013-01-11T15:00:00","2013-01-11T15:00:00",null,11.635909926231896,11.939482127887796,12.243054329543696,12.546626531199596,12.850198732855496,13.153770934511396,13.457343136167296,13.760915337823196,14.064487539479096,null,0,0,0,0.13947856789034144,0.40240136032306939,0.62320182896113629,0.81541253264720959,0.9647123018834538,0.9736183448824749,null,-1.4384258350248813E-2,-1.4384258350248813E-2,-1.4384258350248813E-2]
["2013-01-11T16:00:00","2013-01-11T16:00:00",null,11.680804330460711,11.984376532116611,12.287948733772511,12.591520935428411,12.895093137084311,13.198665338740211,13.502237540396111,13.805809742052011,14.109381943707911,null,0,0,0,0.11938476839668247,0.38452618547261397,0.60744013066652891,0.8016696776298301,0.95289365686468208,0.9636503062011621,null,-2.2417572224218179E-2,-2.2417572224218179E-2,-2.2417572224218179E-2]
["2013-01-11T17:00:00","2013-01-11T17:00:00",null,11.57043989624867,11.87401209790457,12.17758429956047,12.48115650121637,12.78472870287227,13.08830090452817,13.39187310618407,13.69544530783997,13.99901750949587,null,0,0,0,0.10076304212600216,0.36810205422766612,0.59310844635995785,0.78933580698301586,0.94246296659900453,0.95504919265547239,null,-2.0924469383768376E-2,-2.0924469383768376E-2,-2.0924469383768376E-2]
["2013-01-11T18:00:00","2013-01-11T18:00:00",null,11.509495231459121,11.813067433115023,12.116639634770923,12.420211836426823,12.723784038082723,13.027356239738623,13.330928441394523,13.634500643050423,13.938072844706323,null,0,0,0,8.5663776781735132E-2,0.35514780986545375,0.58220458970118005,0.78037718994031702,0.9353654707025002,0.94973921424401353,null,-1.7349434413677298E-2,-1.7349434413677298E-2,-1.7349434413677298E-2]
["2013-01-11T19:00:00","2013-01-11T19:00:00",null,11.68841941629813,11.99199161795403,12.29556381960993,12.59913602126583,12.90270822292173,13.20628042457763,13.509852626233529,13.813424827889429,14.116997029545329,null,0,0,0,7.1100766682981764E-2,0.34274033555749062,0.57184750309665144,0.77197585776060296,0.92883577447771615,0.94500755031301065,null,-1.6813179168163633E-2,-1.6813179168163633E-2,-1.6813179168163633E-2]
["2013-01-11T20:00:00","2013-01-11T20:00:00",null,11.603859259622704,11.907431461278604,12.211003662934504,12.514575864590403,12.818148066246303,13.121720267902203,13.425292469558103,13.728864671214003,14.032436872869903,null,0,0,0,6.0007643466963856E-2,0.33372914447111396,0.56482361086129607,0.76684463109764867,0.92551309491727851,0.94341981419394083,null,-1.3280203433014804E-2,-1.3280203433014804E-2,-1.3280203433014804E-2]
["2013-01-11T21:00:00","2013-01-11T21:00:00",null,11.634590045460369,11.938162247116269,12.241734448772169,12.545306650428069,12.848878852083969,13.152451053739869,13.456023255395769,13.759595457051669,14.063167658707568,null,0,0,0,5.0586374839900305E-2,0.32633723393001385,0.55937693993627491,0.76324856651008643,0.92369403300602626,0.94329363648911413,null,-1.1555774800382635E-2,-1.1555774800382635E-2,-1.1555774800382635E-2]
["2013-01-11T22:00:00","2013-01-11T22:00:00",null,11.558954622699742,11.862526824355642,12.166099026011542,12.469671227667442,12.773243429323342,13.076815630979242,13.380387832635142,13.683960034291042,13.987532235946942,null,0,0,0,4.3057771785237918E-2,0.32085901857878607,0.55584396420112603,0.76157671192113208,0.92379918109338188,0.94509166878289519,null,-9.6631092279814753E-3,-9.6631092279814753E-3,-9.6631092279814753E-3]
["2013-01-11T23:00:00","2013-01-11T23:00:00",null,11.762627357397456,12.066199559053354,12.369771760709254,12.673343962365154,12.976916164021054,13.280488365676954,13.584060567332854,13.887632768988754,14.191204970644653,null,5.0576230018053212E-2,5.2973606409761342E-2,5.5255319905378297E-2,0.10048965709887756,0.38036232121333141,0.61732405087795705,0.8249389493616287,0.98896996563639517,1,null,5.5255319905378297E-2,5.5255319905378297E-2,5.5255319905378297E-2]
["2013-01-12","2013-01-12",null,11.838571955922607,12.142144157578507,12.445716359234407,12.749288560890307,13.052860762546207,13.356432964202106,13.660005165858006,13.963577367513906,14.267149569169806,null,0.10012200878002134,0.10490624675470205,0.1094591589372004,0.15685954673022542,0.43879311335684945,0.67773162706376078,0.88722867631109803,1,1,null,0.1094591589372004,0.1094591589372004,0.1094591589372004]
["2013-01-12T01:00:00","2013-01-12T01:00:00",null,11.878346979132461,12.181919180788361,12.485491382444261,12.789063584100161,13.092635785756061,13.396207987411961,13.699780189067861,14.00335239072376,14.30692459237966,null,0.14942594694107153,0.1566285909249315,0.1634947610292535,0.213092743848011,0.49711875741301187,0.73805508477967996,0.94946582921688949,1,1,null,0.1634947610292535,0.1634947610292535,0.1634947610292535]
["2013-01-12T02:00:00","2013-01-12T02:00:00",null,11.898130474229118,12.201702675885018,12.505274877540918,12.808847079196818,13.112419280852718,13.415991482508618,13.719563684164518,14.023135885820418,14.326708087476318,null,0.20153733903451679,0.2111058149838782,0.22022215415761048,0.27196515795842263,0.55803104441812257,0.80092312620960515,1,1,1,null,0.22022215415761048,0.22022215415761048,0.22022215415761048]
["2013-01-12T03:00:00","2013-01-12T03:00:00",null,11.902207444576865,12.205779646232765,12.509351847888665,12.812924049544565,13.116496251200465,13.420068452856365,13.723640654512264,14.027212856168164,14.330785057824064,null,0.25339637571830853,0.26533068363317142,0.27670770668504951,0.33059573146791632,0.61870149082231529,0.86354932703861242,1,1,1,null,0.27670770668504951,0.27670770668504951,0.27670770668504951]
["2013-01-12T04:00:00","2013-01-12T04:00:00",null,11.869731381786332,12.173303583442232,12.476875785098132,12.780447986754032,13.084020188409932,13.387592390065832,13.691164591721732,13.994736793377632,14.298308995033532,null,0.30378333917912165,0.31813605310316379,0.33180530445939438,0.38789092426799365,0.67807861575203388,0.92492426562808783,1,1,1,null,0.33180530445939438,0.33180530445939438,0.33180530445939438]
["2013-01-12T05:00:00","2013-01-12T05:00:00",null,11.949064533350709,12.252636735006609,12.556208936662509,12.859781138318409,13.163353339974309,13.466925541630209,13.770497743286109,14.074069944942009,14.377642146597909,null,0.35067938613972816,0.36751359492536295,0.38354867824709499,0.44189498193384008,0.73422769439993496,0.98313424678815908,1,1,1,null,0.38354867824709499,0.38354867824709499,0.38354867824709499]
["2013-01-12T06:00:00","2013-01-12T06:00:00",null,11.96548813248144,12.26906033413734,12.57263253579324,12.87620473744914,13.179776939105039,13.483349140760939,13.786921342416839,14.090493544072739,14.394065745728639,null,0.39364289463323449,0.41306374636781751,0.43154878012493553,0.49223988615971093,0.78680173807774501,1,1,1,1,null,0.43154878012493553,0.43154878012493553,0.43154878012493553]
["2013-01-12T07:00:00","2013-01-12T07:00:00",null,11.942408874010438,12.245981075666338,12.549553277322238,12.853125478978138,13.156697680634037,13.460269882289937,13.763842083945837,14.067414285601737,14.370986487257637,null,0.43493454853778646,0.45691049879511103,0.47783496817887944,0.54083933213547852,0.83761980869671615,1,1,1,1,null,0.47783496817887944,0.47783496817887944,0.47783496817887944]
["2013-01-12T08:00:00","2013-01-12T08:00:00",null,11.924862082031572,12.228434283687472,12.532006485343372,12.835578686999272,13.139150888655172,13.442723090311071,13.746295291966971,14.049867493622871,14.353439695278771,null,0.40720699790210946,0.43172753187344004,0.4550704072663877,0.52038802914481042,0.81936610073178051,0.9838492537821768,0.98585758225066911,0.98777127744054138,0.98961136896926472,null,0.4550704072663877,0.4550704072663877,0.4550704072663877]
["2013-01-12T09:00:00","2013-01-12T09:00:00",null,12.067577013985925,12.371149215641825,12.674721417297725,12.978293618953625,13.281865820609525,13.585438022265425,13.889010223921325,14.192582425577225,14.496154627233125,null,0.37608316404484593,0.40319034096512479,0.42900419641092952,0.49666662063738254,0.79788434648502737,0.96451252051747827,0.96856072188066966,0.97244068630409197,0.97615241378774531,null,0.42900419641092952,0.42900419641092952,0.42900419641092952]
["2013-01-12T10:00:00","2013-01-12T10:00:00",null,12.182859375027462,12.486431576683362,12.790003778339262,13.093575979995162,13.397148181651062,13.700720383306962,14.004292584962862,14.307864786618762,14.611436988274662,null,0.34410763068000189,0.37382248016670011,0.40211783047409749,0.47214608666605196,0.77562449639184261,0.9444082062150837,0.95052782489918086,0.9563845733648888,0.96198896642094334,null,0.40211783047409749,0.40211783047409749,0.40211783047409749]
["2013-01-12T11:00:00","2013-01-12T11:00:00",null,11.901810155490244,12.205382357146144,12.508954558802044,12.812526760457944,13.116098962113844,13.419671163769744,13.723243365425644,14.026815567081544,14.330387768737443,null,0.32153233632475026,0.35368662143809887,0.38431625928479102,0.45655262531121349,0.76214451159285213,0.93294706469332112,0.94100140818476175,0.94869824817919302,0.95606912910282194,null,0.38431625928479102,0.38431625928479102,0.38431625928479102]
["2013-01-12T12:00:00","2013-01-12T12:00:00",null,11.128059005051856,11.431631206707756,11.735203408363656,12.038775610019556,12.342347811675456,12.645920013331356,12.949492214987256,13.253064416643156,13.556636618299056,null,0.30781051092484185,0.34234114281242745,0.37522094972852987,0.44959182192827146,0.75721306629587359,0.92993982939495035,0.9398447792238499,0.94929759227712007,0.95834032778970335,null,0.37522094972852987,0.37522094972852987,0.37522094972852987]
["2013-01-12T13:00:00","2013-01-12T13:00:00",null,10.733271630441799,11.036843832097698,11.340416033753598,11.643988235409498,11.947560437065398,12.251132638721298,12.554704840377198,12.858277042033098,13.161849243688998,null,0.29627576574193032,0.33320377402122409,0.36835477962420787,0.44488118761473971,0.75455281968577637,0.92922482240093218,0.94098037856729055,0.95218916467939962,0.96291426958967286,null,0.36835477962420787,0.36835477962420787,0.36835477962420787]
["2013-01-12T14:00:00","2013-01-12T14:00:00",null,10.611777174589388,10.915349376245288,11.218921577901188,11.522493779557088,11.826065981212988,12.129638182868888,12.433210384524788,12.736782586180688,13.040354787836588,null,0.28715942656819804,0.32644275200425771,0.36383341186791623,0.442473296414296,0.75414274214508947,0.93072844005011757,0.94429254331899259,0.95722575806373378,0.96959117313675469,null,0.36383341186791623,0.36383341186791623,0.36383341186791623]
["2013-01-12T15:00:00","2013-01-12T15:00:00",null,10.505844246317363,10.809416447973263,11.112988649629161,11.416560851285061,11.720133052940961,12.023705254596861,12.327277456252761,12.63084965790866,12.93442185956456,null,0.2798095752620402,0.32141667342865909,0.36101544312678563,0.44173725980280665,0.75539400438462134,0.93385133824457944,0.94920295899850005,0.96383957275840226,0.97782426837669978,null,0.36101544312678563,0.36101544312678563,0.36101544312678563]
["2013-01-12T16:00:00","2013-01-12T16:00:00",null,10.246166271852278,10.549738473508178,10.853310675164078,11.156882876819978,11.460455078475878,11.764027280131778,12.067599481787678,12.371171683443578,12.674743885099478,null,0.27863191668365728,0.32244712468474418,0.36412782651251197,0.44682642723081867,0.76235480776756337,0.94257862949509585,0.95961261964670641,0.97585799914314963,0.99136734202810362,null,0.36412782651251197,0.36412782651251197,0.36412782651251197]
["2013-01-12T17:00:00","2013-01-12T17:00:00",null,9.8296215765959758,10.133193778251876,10.436765979907776,10.740338181563676,11.043910383219576,11.347482584875475,11.651054786531375,11.954626988187275,12.258199189843175,null,0.28128164848501891,0.32728393670310268,0.37102554104304064,0.4556693813774263,0.77303785344289433,0.95499661861179452,0.97368143373488836,0.99149351973293032,1,null,0.37102554104304064,0.37102554104304064,0.37102554104304064]
["2013-01-12T18:00:00","2013-01-12T18:00:00",null,9.6553177166739115,9.9588899183298114,10.262462119985711,10.566034321641611,10.869606523297511,11.173178724953411,11.476750926609311,11.780323128265211,12.083895329921111,null,0.28598176798981512,0.33415010680742468,0.37992106923332608,0.46648911956631961,0.78566613873430424,0.96933881772710107,0.9896429133954715,1,1,null,0.37992106923332608,0.37992106923332608,0.37992106923332608]
["2013-01-12T19:00:00","2013-01-12T19:00:00",null,9.4025556560623862,9.7061278577182861,10.009700059374186,10.313272261030086,10.616844462685986,10.920416664341886,11.223988865997786,11.527561067653686,11.831133269309586,null,0.29337367853091523,0.34367652352184386,0.39145581441623761,0.47991653032163228,0.80087055216592684,0.98622560055641362,1,1,1,null,0.39145581441623761,0.39145581441623761,0.39145581441623761]
["2013-01-12T20:00:00","2013-01-12T20:00:00",null,9.3439136084326009,9.6474858100885008,9.9510580117444007,10.254630213400301,10.558202415056201,10.861774616712101,11.165346818368,11.4689190200239,11.7724912216798,null,0.30425650557222189,0.35659922345784956,0.40629220954211559,0.49656147255002692,0.81920837860074691,1,1,1,1,null,0.40629220954211559,0.40629220954211559,0.40629220954211559]
["2013-01-12T21:00:00","2013-01-12T21:00:00",null,9.2870371026989105,9.5906093043548104,9.8941815060107103,10.19775370766661,10.50132590932251,10.80489811097841,11.10847031263431,11.41204251429021,11.71561471594611,null,0.3144032960020392,0.36881743120857258,0.42045565690891762,0.51255449663681674,0.83692583132016884,1,1,1,1,null,0.42045565690891762,0.42045565690891762,0.42045565690891762]
["2013-01-12T22:00:00","2013-01-12T22:00:00",null,9.270487956814824,9.5740601584707239,9.8776323601266238,10.181204561782526,10.484776763438425,10.788348965094325,11.091921166750225,11.395493368406125,11.699065570062025,null,0.3205965183472852,0.3770610412572532,0.43062347695620606,0.52452034897788624,0.85059508267639949,1,1,1,1,null,0.43062347695620606,0.43062347695620606,0.43062347695620606]
["2013-01-12T23:00:00","2013-01-12T23:00:00",null,9.2241662132617126,9.5277384149176125,9.8313106165735125,10.134882818229414,10.438455019885314,10.742027221541214,11.045599423197114,11.349171624853014,11.652743826508914,null,0.3218688102042882,0.38031011715654184,0.43571264438421808,0.53134445984726597,0.85905950370852691,1,1,1,1,null,0.43571264438421808,0.43571264438421808,0.43571264438421808]
["2013-01-13","2013-01-13",null,9.0659557507998194,9.3695279524557193,9.6731001541116193,9.9766723557675192,10.280244557423419,10.583816759079319,10.887388960735219,11.190961162391119,11.494533364047019,null,0.32406640523002067,0.38446346660708886,0.44169557055475284,0.53905181465043295,0.86838613905697037,1,1,1,1,null,0.44169557055475284,0.44169557055475284,0.44169557055475284]
["2013-01-13T01:00:00","2013-01-13T01:00:00",null,8.9679399414615446,9.2715121431174445,9.5750843447733445,9.8786565464292444,10.182228748085146,10.485800949741046,10.789373151396946,11.092945353052846,11.396517554708746,null,0.32681077031000233,0.38912152687694285,0.44815166311838789,0.5471902766117579,0.87810182232862966,1,1,1,1,null,0.44815166311838789,0.44815166311838789,0.44815166311838789]
["2013-01-13T02:00:00","2013-01-13T02:00:00",null,8.9638726019042689,9.2674448035601689,9.5710170052160688,9.8745892068719687,10.178161408527869,10.481733610183769,10.785305811839669,11.088878013495568,11.392450215151468,null,0.32949204653757064,0.39371649829438343,0.45452363721213845,0.55524462010319842,0.88772287232166891,1,1,1,1,null,0.45452363721213845,0.45452363721213845,0.45452363721213845]
["2013-01-13T03:00:00","2013-01-13T03:00:00",null,8.8880242364058049,9.1915964380617048,9.4951686397176047,9.7987408413735047,10.102313043029405,10.405885244685305,10.709457446341204,11.013029647997104,11.316601849653004,null,0.33284627052421489,0.39898441747089997,0.46156855906496497,0.56396139654497934,0.89800635526504857,1,1,1,1,null,0.46156855906496497,0.46156855906496497,0.46156855906496497]
["2013-01-13T04:00:00","2013-01-13T04:00:00",null,8.8805817280692647,9.1841539297251646,9.4877261313810646,9.7912983330369645,10.094870534692863,10.398442736348763,10.702014938004663,11.005587139660562,11.309159341316462,null,0.33665263128648831,0.40468344380557458,0.46903407326721397,0.57308825052744716,0.90868940094037953,1,1,1,1,null,0.46903407326721397,0.46903407326721397,0.46903407326721397]
["2013-01-13T05:00:00","2013-01-13T05:00:00",null,8.8366002176414824,9.1401724192973823,9.4437446209532823,9.7473168226091822,10.050889024265082,10.354461225920982,10.658033427576882,10.961605629232782,11.265177830888682,null,0.33900794844325421,0.40898400057841944,0.47515369195131107,0.58092178303544084,0.91812118437617862,1,1,1,1,null,0.47515369195131107,0.47515369195131107,0.47515369195131107]
["2013-01-13T06:00:00","2013-01-13T06:00:00",null,8.8367526487304495,9.1403248503863495,9.4438970520422494,9.7474692536981493,10.051041455354049,10.354613657009949,10.658185858665849,10.961758060321749,11.265330261977649,null,0.3414473840699046,0.41336867582114878,0.48136794391402821,0.58883943401331906,0.92764760109059774,1,1,1,1,null,0.48136794391402821,0.48136794391402821,0.48136794391402821]
["2013-01-13T07:00:00","2013-01-13T07:00:00",null,8.7899963255578957,9.0935685272137956,9.3971407288696955,9.7007129305255955,10.004285132181495,10.307857333837395,10.611429535493295,10.915001737149195,11.218573938805095,null,0.34254092417840304,0.41646002958940398,0.48633093363721347,0.59555839679534317,0.93601738884410512,1,1,1,1,null,0.48633093363721347,0.48633093363721347,0.48633093363721347]
["2013-01-13T08:00:00","2013-01-13T08:00:00",null,8.7312371900056274,9.0348093916615273,9.3383815933174272,9.6419537949733272,9.9455259966292253,10.249098198285125,10.552670399941025,10.856242601596925,11.159814803252825,null,0.3431402682763301,0.41908873177329448,0.4908628162022407,0.60187779684541598,0.94400864348313229,1,1,1,1,null,0.4908628162022407,0.4908628162022407,0.4908628162022407]
["2013-01-13T09:00:00","2013-01-13T09:00:00",null,8.7188566109956245,9.0224288126515244,9.3260010143074243,9.6295732159633243,9.9331454176192242,10.236717619275124,10.540289820931024,10.843862022586924,11.147434224242824,null,0.34447564898574645,0.42243244095120319,0.49608867614381502,0.6088596298458292,0.95264130145502868,1,1,1,1,null,0.49608867614381502,0.49608867614381502,0.49608867614381502]
["2013-01-13T10:00:00","2013-01-13T10:00:00",null,8.7971604432555637,9.1007326449114636,9.4043048465673635,9.7078770482232635,10.011449249879163,10.315021451535063,10.618593653190963,10.922165854846863,11.225738056502763,null,0.34524323002344248,0.42521886526612712,0.50075725122240455,0.61529469279199311,0.96073770418141147,1,1,1,1,null,0.50075725122240455,0.50075725122240455,0.50075725122240455]
["2013-01-13T11:00:00","2013-01-13T11:00:00",null,8.8462338388938111,9.149806040549711,9.453378242205611,9.7569504438615109,10.060522645517411,10.364094847173311,10.667667048829211,10.971239250485111,11.274811452141011,null,0.34278276477932096,0.42486136176911804,0.50237653176768116,0.61875406486599305,0.9659425345055147,1,1,1,1,null,0.50237653176768116,0.50237653176768116,0.50237653176768116]
["2013-01-13T12:00:00","2013-01-13T12:00:00",null,9.0149388349724919,9.3185110366283919,9.6220832382842918,9.92565543994019,10.22922764159609,10.53279984325199,10.83637204490789,11.13994424656379,11.44351644821969,null,0.33817727855314478,0.42237986690752538,0.50190336537458091,0.62015253442782281,0.96910749193491885,1,1,1,1,null,0.50190336537458091,0.50190336537458091,0.50190336537458091]
["2013-01-13T13:00:00","2013-01-13T13:00:00",null,9.1080482184791425,9.4116204201350424,9.7151926217909423,10.018764823446842,10.322337025102742,10.625909226758642,10.929481428414542,11.233053630070442,11.536625831726342,null,0.33215229314766775,0.41852093210157415,0.50007378865459318,0.62022613808897176,0.97096861308111337,1,1,1,1,null,0.50007378865459318,0.50007378865459318,0.50007378865459318]
["2013-01-13T14:00:00","2013-01-13T14:00:00",null,9.2757245882022179,9.5792967898581178,9.8828689915140178,10.186441193169918,10.490013394825818,10.793585596481718,11.097157798137617,11.400729999793517,11.704302201449417,null,0.3244239087270297,0.41297962789793297,0.49657235734565103,0.61865943158737302,0.97121045368203129,1,1,1,1,null,0.49657235734565103,0.49657235734565103,0.49657235734565103]
["2013-01-13T15:00:00","2013-01-13T15:00:00",null,9.3844943788803974,9.6880665805362973,9.9916387821921973,10.295210983848097,10.598783185503997,10.902355387159897,11.205927588815797,11.509499790471697,11.813071992127597,null,0.3143191775321546,0.40510403615499702,0.49078921254109192,0.61485307082509955,0.96926521406595234,0.99981073344275984,1,1,1,null,0.49078921254109192,0.49078921254109192,0.49078921254109192]
["2013-01-13T16:00:00","2013-01-13T16:00:00",null,9.3715308644606345,9.6751030661165345,9.9786752677724344,10.282247469428334,10.585819671084234,10.889391872740134,11.192964074396034,11.496536276051934,11.800108477707834,null,0.30507666065359562,0.39806962911090604,0.4858367376266422,0.61185635033546437,0.9681085851050405,1,1,1,1,null,0.4858367376266422,0.4858367376266422,0.4858367376266422]
["2013-01-13T17:00:00","2013-01-13T17:00:00",null,9.2449488642448436,9.5485210659007436,9.8520932675566435,10.155665469212543,10.459237670868443,10.762809872524343,11.066382074180243,11.369954275836143,11.673526477492043,null,0.2950139886936628,0.39026764102911904,0.48015874090943872,0.60816565246928211,0.96630003800252384,0.99996845557379332,1,1,1,null,0.48015874090943872,0.48015874090943872,0.48015874090943872]
["2013-01-13T18:00:00","2013-01-13T18:00:00",null,9.13564454955584,9.43921675121174,9.7427889528676399,10.04636115452354,10.34993335617944,10.65350555783534,10.95707775949124,11.26064996114714,11.564222162803039,null,0.28736972274290923,0.38483148491283348,0.47679400211405887,0.60674615328998127,0.96672063035194633,1,1,1,1,null,0.47679400211405887,0.47679400211405887,0.47679400211405887]
["2013-01-13T19:00:00","2013-01-13T19:00:00",null,8.9958512194951226,9.2994234211510225,9.6029956228069224,9.9065678244628224,10.210140026118722,10.513712227774622,10.817284429430522,11.120856631086422,11.424428832742322,null,0.27992523815813131,0.37962665458873029,0.47368161872833253,0.60560003913780502,0.96742512253722901,1,1,1,1,null,0.47368161872833253,0.47368161872833253,0.47368161872833253]
["2013-01-13T20:00:00","2013-01-13T20:00:00",null,8.966140200630111,9.2697124022860109,9.5732846039419108,9.8768568055978108,10.180429007253711,10.484001208909611,10.787573410565511,11.09114561222141,11.39471781387731,null,0.27412106373610107,0.37600956038369698,0.4721149122267338,0.60594702782607857,0.96958065832801921,1,1,1,1,null,0.4721149122267338,0.4721149122267338,0.4721149122267338]
["2013-01-13T21:00:00","2013-01-13T21:00:00",null,8.9342557302482728,9.2378279319041727,9.5414001335600727,9.8449723352159708,10.148544536871871,10.452116738527771,10.755688940183671,11.059261141839571,11.36283334349547,null,0.27034624740003432,0.3743692502209493,0.47246190091500734,0.60816565246928211,0.97355525603006166,1,1,1,1,null,0.47246190091500734,0.47246190091500734,0.47246190091500734]
["2013-01-13T22:00:00","2013-01-13T22:00:00",null,8.7764422393718569,9.0800144410277568,9.3835866426836567,9.6871588443395567,9.9907310459954566,10.294303247651357,10.597875449307256,10.901447650963156,11.205019852619056,null,0.26816968199177299,0.37430616136853595,0.47437559610487962,0.61194046880534891,0.97907553061623176,1,1,1,1,null,0.47437559610487962,0.47437559610487962,0.47437559610487962]
["2013-01-13T23:00:00","2013-01-13T23:00:00",null,8.6610218927173737,8.9645940943732736,9.2681662960291735,9.5717384976850735,9.8753106993409734,10.178882900996873,10.482455102652773,10.786027304308673,11.089599505964573,null,0.26897932226441129,0.37715567453587323,0.47913880446208917,0.61849119464760405,0.98729811104744125,1,1,1,1,null,0.47913880446208917,0.47913880446208917,0.47913880446208917]
["2013-01-14","2013-01-14",null,8.3706176696675652,8.6741898713234651,8.977762072979365,9.2813342746352649,9.5849064762911649,9.8884786779470648,10.192050879602965,10.495623081258865,10.799195282914765,null,0.27591909602988218,0.38552546228938056,0.48885448773374846,0.6294581401587952,0.99943220032827984,1,1,1,1,null,0.48885448773374846,0.48885448773374846,0.48885448773374846]
["2013-01-14T01:00:00","2013-01-14T01:00:00",null,8.3810399087862582,8.6846121104421581,8.988184312098058,9.2917565137539579,9.5953287154098579,9.8989009170657578,10.202473118721658,10.506045320377558,10.809617522033458,null,0.29107093541782703,0.40229658222260195,0.50712922531615523,0.64914186211176728,1,1,1,1,1,null,0.50712922531615523,0.50712922531615523,0.50712922531615523]
["2013-01-14T02:00:00","2013-01-14T02:00:00",null,8.3630788903471789,8.6666510920030788,8.9702232936589787,9.2737954953148787,9.5773676969707786,9.8809398986266785,10.184512100282578,10.488084301938478,10.791656503594378,null,0.30256362136579629,0.41551369680320338,0.52196562044203321,0.66549238969556623,1,1,1,1,1,null,0.52196562044203321,0.52196562044203321,0.52196562044203321]
["2013-01-14T03:00:00","2013-01-14T03:00:00",null,8.3565066412424258,8.6600788428983257,8.9636510445542257,9.2672232462101256,9.5707954478660238,9.8743676495219237,10.177939851177824,10.481512052833724,10.785084254489623,null,0.31449792928065917,0.42916191854196284,0.53721209310859808,0.68224248001131649,1,1,1,1,1,null,0.53721209310859808,0.53721209310859808,0.53721209310859808]
["2013-01-14T04:00:00","2013-01-14T04:00:00",null,8.4349577494973484,8.7385299511532484,9.0421021528091483,9.3456743544650482,9.6492465561209464,9.9528187577768463,10.256390959432746,10.559963161088646,10.863535362744546,null,0.32564362654035489,0.44204255924302627,0.55171201435493811,0.69824601890684179,1,1,1,1,1,null,0.55171201435493811,0.55171201435493811,0.55171201435493811]
["2013-01-14T05:00:00","2013-01-14T05:00:00",null,8.385243980098867,8.6888161817547669,8.9923883834106668,9.2959605850665668,9.5995327867224685,9.9031049883783684,10.206677190034268,10.510249391690168,10.813821593346068,null,0.33564320964787436,0.45381914502685572,0.56514993991898632,0.71324013616375315,1,1,1,1,1,null,0.56514993991898632,0.56514993991898632,0.56514993991898632]
["2013-01-14T06:00:00","2013-01-14T06:00:00",null,8.4131273426371465,8.7166995442930464,9.0202717459489463,9.3238439476048462,9.6274161492607444,9.9309883509166443,10.234560552572544,10.538132754228444,10.841704955884344,null,0.34381321603540604,0.46382924294311073,0.57687395165913791,0.72657291364044574,1,1,1,1,1,null,0.57687395165913791,0.57687395165913791,0.57687395165913791]
["2013-01-14T07:00:00","2013-01-14T07:00:00",null,8.4215478862843725,8.7251200879402724,9.0286922895961723,9.3322644912520722,9.6358366929079722,9.9394088945638721,10.242981096219772,10.546553297875672,10.850125499531572,null,0.3506057824785791,0.47247241572374271,0.5872520678811376,0.73857031040772203,1,1,1,1,1,null,0.5872520678811376,0.5872520678811376,0.5872520678811376]
["2013-01-14T08:00:00","2013-01-14T08:00:00",null,8.5001437927769032,8.8037159944328032,9.1072881960887031,9.410860397744603,9.714432599400503,10.018004801056403,10.321577002712303,10.625149204368203,10.928721406024103,null,0.35526384274843309,0.47899159713979117,0.59551670754728936,0.74846474542788588,1,1,1,1,1,null,0.59551670754728936,0.59551670754728936,0.59551670754728936]
["2013-01-14T09:00:00","2013-01-14T09:00:00",null,8.5401002864008664,8.8436724880567663,9.1472446897126662,9.4508168913685662,9.7543890930244643,10.057961294680364,10.361533496336264,10.665105697992164,10.968677899648064,null,0.35731423045186766,0.48299773926804029,0.60134191158679073,0.75599334848254829,1,1,1,1,1,null,0.60134191158679073,0.60134191158679073,0.60134191158679073]
["2013-01-14T10:00:00","2013-01-14T10:00:00",null,8.7332074500359411,9.0367796516918411,9.340351853347741,9.6439240550036409,9.9474962566595408,10.251068458315441,10.554640659971341,10.858212861627241,11.161785063283141,null,0.35989035859208035,0.48746653298065412,0.6075877079757146,0.76388996984295532,1,1,1,1,1,null,0.6075877079757146,0.6075877079757146,0.6075877079757146]
["2013-01-14T11:00:00","2013-01-14T11:00:00",null,8.8753945987257588,9.1789668003816587,9.4825390020375586,9.7861112036934585,10.089683405349358,10.393255607005258,10.696827808661158,11.000400010317058,11.303972211972958,null,0.35674643078014734,0.48634144844594901,0.60835528901341063,0.76642403874822573,1,1,1,1,1,null,0.60835528901341063,0.60835528901341063,0.60835528901341063]
["2013-01-14T12:00:00","2013-01-14T12:00:00",null,9.3112054220063794,9.6147776236622793,9.9183498253181792,10.221922026974079,10.525494228629979,10.829066430285879,11.132638631941779,11.436210833597679,11.739783035253579,null,0.34078495111956425,0.47288249326442966,0.59724113617992158,0.75750748094046916,0.99316537432188468,0.99512112874669922,0.99697173508415815,0.99872770814299705,1,null,0.59724113617992158,0.59724113617992158,0.59724113617992158]
["2013-01-14T13:00:00","2013-01-14T13:00:00",null,9.3006392659970256,9.6042114676529255,9.9077836693088255,10.211355870964727,10.514928072620627,10.818500274276527,11.122072475932427,11.425644677588327,11.729216879244227,null,0.32950256134630623,0.46395542064793754,0.59052217339789748,0.75285993547935071,0.99047358328558077,0.99427994404785425,0.99787600863541648,1,1,null,0.59052217339789748,0.59052217339789748,0.59052217339789748]
["2013-01-14T14:00:00","2013-01-14T14:00:00",null,9.4370219799232942,9.7405941815791941,10.044166383235094,10.347738584890994,10.651310786546894,10.954882988202794,11.258455189858694,11.562027391514594,11.865599593170494,null,0.31826223080799043,0.45502834803144543,0.58377166618966669,0.7481493011658189,0.98769767377939244,0.99332309645291805,0.99864358967311251,1,1,null,0.58377166618966669,0.58377166618966669,0.58377166618966669]
["2013-01-14T15:00:00","2013-01-14T15:00:00",null,9.5342737066878946,9.8378459083437946,10.141418109999695,10.444990311655593,10.748562513311493,11.052134714967393,11.355706916623292,11.659279118279192,11.962851319935092,null,0.30347840972579027,0.44258932929727557,0.5735302424812293,0.73997929477828728,0.98148342181667525,0.98895945082765979,0.99602540229795755,0.99904315240506381,1,null,0.5735302424812293,0.5735302424812293,0.5735302424812293]
["2013-01-14T16:00:00","2013-01-14T16:00:00",null,9.5245368141804203,9.8281090158363202,10.13168121749222,10.43525341914812,10.73882562080402,11.04239782245992,11.34597002411582,11.64954222577172,11.95311442742762,null,0.2891677550366904,0.43061296214747047,0.56374095554842107,0.73224039554891363,0.97568976220338055,0.98500588274308853,0.993806777654754,0.99847535273334342,1,null,0.56374095554842107,0.56374095554842107,0.56374095554842107]
["2013-01-14T17:00:00","2013-01-14T17:00:00",null,9.4954216756707961,9.798993877326696,10.102566078982596,10.406138280638496,10.709710482294396,11.013282683950296,11.316854885606196,11.620427087262096,11.923999288917996,null,0.27650792531907376,0.42023484592547078,0.55550786030847599,0.72602614358619644,0.97137869062180016,0.9824928434552892,0.9929971373821157,0.99928499300598173,1,null,0.55550786030847599,0.55550786030847599,0.55550786030847599]
["2013-01-14T18:00:00","2013-01-14T18:00:00",null,9.3692645097777518,9.6728367114336518,9.9764089130895517,10.279981114745452,10.583553316401352,10.887125518057251,11.190697719713151,11.494269921369051,11.797842123024951,null,0.26716026035315915,0.41309529079402418,0.55043972249793516,0.72290324539173456,0.97009588395606161,0.98294498023091836,0.99508958432049255,1,1,null,0.55043972249793516,0.55043972249793516,0.55043972249793516]
["2013-01-14T19:00:00","2013-01-14T19:00:00",null,9.1430126172893331,9.4465848189452331,9.750157020601133,10.053729222257033,10.357301423912933,10.660873625568833,10.964445827224733,11.268018028880633,11.571590230536533,null,0.25901128358309861,0.40716493866716724,0.54660181730945501,0.72102109462806896,0.97005382472111934,0.9846378644373438,0.99842277868966567,1,1,null,0.54660181730945501,0.54660181730945501,0.54660181730945501]
["2013-01-14T20:00:00","2013-01-14T20:00:00",null,9.0987240799260611,9.4022962815819611,9.705868483237861,10.009440684893761,10.313012886549661,10.616585088205561,10.920157289861461,11.223729491517361,11.527301693173261,null,0.2535646126580775,0.4038632887242008,0.54531901064371646,0.72162043872599602,0.97243017149535638,0.98869658060927068,1,1,1,null,0.54531901064371646,0.54531901064371646,0.54531901064371646]
["2013-01-14T21:00:00","2013-01-14T21:00:00",null,9.0821313324637298,9.3857035341196298,9.6892757357755297,9.9928479374314296,10.29642013908733,10.599992340743229,10.903564542399129,11.207136744055029,11.510708945710929,null,0.24907478932799254,0.40149745675869936,0.54492996272050065,0.72310302675771021,0.97566873258590947,0.99358596667130705,1,1,1,null,0.54492996272050065,0.54492996272050065,0.54492996272050065]
["2013-01-14T22:00:00","2013-01-14T22:00:00",null,9.0223835535441381,9.3259557552000381,9.629527956855938,9.9331001585118379,10.236672360167738,10.540244561823638,10.843816763479538,11.147388965135438,11.450961166791338,null,0.24821257501167646,0.4026435709108756,0.54796874244507809,0.72790829434986204,0.98213533995828006,1,1,1,1,null,0.54796874244507809,0.54796874244507809,0.54796874244507809]
["2013-01-14T23:00:00","2013-01-14T23:00:00",null,8.7872835035376777,9.0908557051935777,9.3944279068494776,9.6980001085053775,10.001572310161276,10.305144511817176,10.608716713473076,10.912288915128975,11.215861116784875,null,0.24943229282500165,0.40586110238395756,0.55305790987309011,0.73474292002797736,0.99061027579914307,1,1,1,1,null,0.55305790987309011,0.55305790987309011,0.55305790987309011]
["2013-01-15","2013-01-15",null,8.7606842518086374,9.0642564534645373,9.3678286551204373,9.6714008567763372,9.9749730584322371,10.278545260088137,10.582117461744037,10.885689663399937,11.189261865055837,null,0.25231335041854563,0.41068739959358053,0.55970326899396527,0.74309167816401356,1,1,1,1,1,null,0.55970326899396527,0.55970326899396527,0.55970326899396527]
["2013-01-15T01:00:00","2013-01-15T01:00:00",null,8.6582741740647648,8.9618463757206648,9.2654185773765647,9.5689907790324646,9.8725629806883646,10.176135182344265,10.479707384000164,10.783279585656064,11.086851787311964,null,0.25744457708149987,0.41770077702020036,0.56848313428815955,0.7535328832384266,1,1,1,1,1,null,0.56848313428815955,0.56848313428815955,0.56848313428815955]
["2013-01-15T02:00:00","2013-01-15T02:00:00",null,8.7031880099588577,9.0067602116147576,9.3103324132706575,9.6139046149265575,9.9174768165824556,10.221049018238356,10.524621219894255,10.828193421550155,11.131765623206055,null,0.26400581773249054,0.42609159439117883,0.57858786548303465,0.7652463801698427,1,1,1,1,1,null,0.57858786548303465,0.57858786548303465,0.57858786548303465]
["2013-01-15T03:00:00","2013-01-15T03:00:00",null,8.6972529383880293,9.0008251400439292,9.3043973416998291,9.6079695433557291,9.911541745011629,10.215113946667529,10.518686148323429,10.822258349979329,11.125830551635229,null,0.27100868035037484,0.43491351892031532,0.58911318902733223,0.77736995464194569,1,1,1,1,1,null,0.58911318902733223,0.58911318902733223,0.58911318902733223]
["2013-01-15T04:00:00","2013-01-15T04:00:00",null,8.7068875695630261,9.0104597712189261,9.314031972874826,9.6176041745307259,9.9211763761866258,10.224748577842526,10.528320779498426,10.831892981154326,11.135465182810226,null,0.27745425810527435,0.44319918820393817,0.5991127721348517,0.78898881829474166,1,1,1,1,1,null,0.5991127721348517,0.5991127721348517,0.5991127721348517]
["2013-01-15T05:00:00","2013-01-15T05:00:00",null,8.7322335853010955,9.0358057869569954,9.3393779886128954,9.6429501902687953,9.9465223919246935,10.250094593580593,10.553666795236493,10.857238996892393,11.160811198548293,null,0.2821754072275417,0.44980248808987111,0.60748255988835909,0.7990199458284678,1,1,1,1,1,null,0.60748255988835909,0.60748255988835909,0.60748255988835909]
["2013-01-15T06:00:00","2013-01-15T06:00:00",null,8.731340508262468,9.0349127099183679,9.3384849115742679,9.6420571132301678,9.9456293148860677,10.249201516541968,10.552773718197868,10.856345919853768,11.159918121509667,null,0.28698067481969353,0.45650042125442408,0.6159469809204865,0.80913519183207849,1,1,1,1,1,null,0.6159469809204865,0.6159469809204865,0.6159469809204865]
["2013-01-15T07:00:00","2013-01-15T07:00:00",null,8.7015281578614569,9.0051003595173569,9.3086725611732568,9.6122447628291567,9.9158169644850567,10.219389166140957,10.522961367796857,10.826533569452756,11.130105771108656,null,0.29365757836677542,0.46500690152149377,0.62616737501145281,0.82095383685085022,1,1,1,1,1,null,0.62616737501145281,0.62616737501145281,0.62616737501145281]
["2013-01-15T08:00:00","2013-01-15T08:00:00",null,8.7079268399865679,9.0114990416424678,9.3150712432983678,9.6186434449542677,9.9222156466101676,10.225787848266068,10.529360049921968,10.832932251577867,11.136504453233767,null,0.29997697841684817,0.47316639310028985,0.63605129522288106,0.83244652279881948,1,1,1,1,1,null,0.63605129522288106,0.63605129522288106,0.63605129522288106]
["2013-01-15T09:00:00","2013-01-15T09:00:00",null,8.7801408258981191,9.083713027554019,9.3872852292099189,9.6908574308658189,9.9944296325217188,10.298001834177619,10.601574035833519,10.905146237489419,11.208718439145319,null,0.30588630092623403,0.48091580713839904,0.64551462308488683,0.84352913120610185,1,1,1,1,1,null,0.64551462308488683,0.64551462308488683,0.64551462308488683]
["2013-01-15T10:00:00","2013-01-15T10:00:00",null,8.871278507255127,9.1748507089110269,9.4784229105669269,9.7819951122228268,10.085567313878727,10.389139515534627,10.692711717190527,10.996283918846427,11.299856120502326,null,0.31027097616896337,0.48717211833605845,0.65351639253264948,0.85318172562534778,1,1,1,1,1,null,0.65351639253264948,0.65351639253264948,0.65351639253264948]
["2013-01-15T11:00:00","2013-01-15T11:00:00",null,8.9937077238937384,9.2972799255496383,9.6008521272055383,9.9044243288614382,10.207996530517338,10.511568732173238,10.815140933829138,11.118713135485038,11.422285337140938,null,0.31120679414642838,0.490063690738338,0.65824805646365236,0.85963781818898288,1,1,1,1,1,null,0.65824805646365236,0.65824805646365236,0.65824805646365236]
["2013-01-15T12:00:00","2013-01-15T12:00:00",null,9.0180549375151973,9.3216271391710972,9.6251993408269971,9.9287715424828971,10.232343744138797,10.535915945794697,10.839488147450597,11.143060349106497,11.446632550762397,null,0.31064950928344359,0.49151473434384557,0.66157073602409,0.8647269856169949,1,1,1,1,1,null,0.66157073602409,0.66157073602409,0.66157073602409]
["2013-01-15T13:00:00","2013-01-15T13:00:00",null,9.0857086836716743,9.3892808853275742,9.6928530869834741,9.9964252886393741,10.299997490295274,10.603569691951174,10.907141893607074,11.210714095262974,11.514286296918874,null,0.31010273922919435,0.49296577794935315,0.66488290077579204,0.86979512342753573,1,1,1,1,1,null,0.66488290077579204,0.66488290077579204,0.66488290077579204]
["2013-01-15T14:00:00","2013-01-15T14:00:00",null,9.1397958345667103,9.4433680362226102,9.7469402378785102,10.05051243953441,10.35408464119031,10.65765684284621,10.96122904450211,11.26480124615801,11.56837344781391,null,0.3062648340407142,0.49122031969924984,0.66509319695050328,0.87183499632223471,1,1,1,1,1,null,0.66509319695050328,0.66509319695050328,0.66509319695050328]
["2013-01-15T15:00:00","2013-01-15T15:00:00",null,9.1856036717278382,9.4891758733837381,9.7927480750396381,10.09632027669554,10.39989247835144,10.70346468000734,11.00703688166324,11.31060908331914,11.614181284975039,null,0.30374127994417932,0.49072612368867841,0.66650218132106864,0.87504201298658113,1,1,1,1,1,null,0.66650218132106864,0.66650218132106864,0.66650218132106864]
["2013-01-15T16:00:00","2013-01-15T16:00:00",null,9.2181744770520009,9.5217466787079008,9.8253188803638007,10.128891082019701,10.432463283675601,10.736035485331501,11.0396076869874,11.3431798886433,11.6467520902992,null,0.29925145661409436,0.48831823248823469,0.66605004454543948,0.8764299677396753,1,1,1,1,1,null,0.66605004454543948,0.66605004454543948,0.66605004454543948]
["2013-01-15T17:00:00","2013-01-15T17:00:00",null,9.1281502010460027,9.4317224027019027,9.7352946043578026,10.038866806013703,10.342439007669602,10.646011209325502,10.949583410981402,11.253155612637302,11.556727814293202,null,0.29611804361089689,0.48725623680594293,0.66692277367049113,0.8791217587759792,1,1,1,1,1,null,0.66692277367049113,0.66692277367049113,0.66692277367049113]
["2013-01-15T18:00:00","2013-01-15T18:00:00",null,9.1375456806749877,9.4411178823308877,9.7446900839867876,10.048262285642688,10.351834487298587,10.655406688954487,10.958978890610387,11.262551092266287,11.566123293922187,null,0.29241683093597909,0.48563695626066639,0.66725924755002908,0.88128780937550499,1,1,1,1,1,null,0.66725924755002908,0.66725924755002908,0.66725924755002908]
["2013-01-15T19:00:00","2013-01-15T19:00:00",null,9.1029272445993996,9.4064994462552995,9.7100716479111995,10.013643849567099,10.317216051222999,10.620788252878899,10.924360454534799,11.227932656190699,11.531504857846599,null,0.29075549115576027,0.48599445975767547,0.6695094166194393,0.8853149811212252,1,1,1,1,1,null,0.6695094166194393,0.6695094166194393,0.6695094166194393]
["2013-01-15T20:00:00","2013-01-15T20:00:00",null,9.0335451645421632,9.3371173661980631,9.640689567853963,9.944261769509863,10.247833971165763,10.551406172821663,10.854978374477563,11.158550576133463,11.462122777789363,null,0.28923084388910381,0.48649917057698244,0.67191730781988301,0.88951038980671449,1,1,1,1,1,null,0.67191730781988301,0.67191730781988301,0.67191730781988301]
["2013-01-15T21:00:00","2013-01-15T21:00:00",null,9.0174984768401281,9.321070678496028,9.6246428801519279,9.9282150818078279,10.23178728346373,10.535359485119629,10.838931686775529,11.142503888431429,11.446076090087329,null,0.2887051034523257,0.4879712437999611,0.67527153180652733,0.89462058685219759,1,1,1,1,1,null,0.67527153180652733,0.67527153180652733,0.67527153180652733]
["2013-01-15T22:00:00","2013-01-15T22:00:00",null,8.7794645664062454,9.0830367680621453,9.3866089697180453,9.6901811713739452,9.9937533730298451,10.297325574685745,10.600897776341645,10.904469977997545,11.208042179653445,null,0.29040850246748673,0.49165142685740781,0.68080232120143291,0.90189683449720648,1,1,1,1,1,null,0.68080232120143291,0.68080232120143291,0.68080232120143291]
["2013-01-15T23:00:00","2013-01-15T23:00:00",null,8.7738500953848018,9.0774222970407017,9.3809944986966016,9.6845667003525016,9.9881389020084015,10.291711103664301,10.595283305320201,10.898855506976101,11.202427708632001,null,0.29251146421459912,0.49572065783807029,0.68671164371081872,0.90953058563922451,1,1,1,1,1,null,0.68671164371081872,0.68671164371081872,0.68671164371081872]
["2013-01-16","2013-01-16",null,8.6509021900745626,8.9544743917304626,9.2580465933863625,9.5616187950422624,9.8651909966981624,10.168763198354062,10.472335400009962,10.775907601665862,11.079479803321762,null,0.29814740169686033,0.50322823127526151,0.69597519020684884,0.92043444229800231,1,1,1,1,1,null,0.69597519020684884,0.69597519020684884,0.69597519020684884]
["2013-01-16T01:00:00","2013-01-16T01:00:00",null,8.5754012668823432,8.8789734685382431,9.182545670194143,9.486117871850043,9.7896900735059411,10.093262275161841,10.396834476817741,10.700406678473641,11.003978880129541,null,0.30430907961589965,0.51126154514923083,0.70575396233092147,0.93185352458482262,1,1,1,1,1,null,0.70575396233092147,0.70575396233092147,0.70575396233092147]
["2013-01-16T02:00:00","2013-01-16T02:00:00",null,8.5726549963783256,8.8762271980342256,9.1797993996901255,9.4833716013460254,9.7869438030019236,10.090516004657824,10.394088206313723,10.697660407969623,11.001232609625523,null,0.31070208332712135,0.5195261848153826,0.71576406024717654,0.94349341785508978,1,1,1,1,1,null,0.71576406024717654,0.71576406024717654,0.71576406024717654]
["2013-01-16T03:00:00","2013-01-16T03:00:00",null,8.5711578953942666,8.8747300970501666,9.1783022987060665,9.4818745003619664,9.7854467020178646,10.089018903673765,10.392591105329664,10.696163306985564,10.999735508641464,null,0.31717920550822754,0.52786442814268331,0.72584776182458044,0.95520691478650588,1,1,1,1,1,null,0.72584776182458044,0.72584776182458044,0.72584776182458044]
["2013-01-16T04:00:00","2013-01-16T04:00:00",null,8.4269894254259015,8.7305616270818014,9.0341338287377013,9.3377060303936013,9.6412782320495012,9.9448504337054011,10.248422635361301,10.551994837017201,10.855567038673101,null,0.32438184949208748,0.53692819327273777,0.73665698520473821,0.96764593352067574,1,1,1,1,1,null,0.73665698520473821,0.73665698520473821,0.73665698520473821]
["2013-01-16T05:00:00","2013-01-16T05:00:00",null,8.3769154372678436,8.6804876389237435,8.9840598405796435,9.2876320422355434,9.5912042438914433,9.8947764455473433,10.198348647203243,10.501920848859143,10.805493050515043,null,0.33046992374997786,0.54494047752923602,0.74645678694628204,0.97911758985117392,1,1,1,1,1,null,0.74645678694628204,0.74645678694628204,0.74645678694628204]
["2013-01-16T06:00:00","2013-01-16T06:00:00",null,8.4287925488340711,8.7323647504899711,9.035936952145871,9.3395091538017709,9.6430813554576709,9.9466535571135708,10.250225758769471,10.553797960425371,10.857370162081271,null,0.33315119997754616,0.54965111184276783,0.75306008683221493,0.9874873776046813,1,1,1,1,1,null,0.75306008683221493,0.75306008683221493,0.75306008683221493]
["2013-01-16T07:00:00","2013-01-16T07:00:00",null,8.4054224678319152,8.7089946694878151,9.012566871143715,9.316139072799615,9.6197112744555149,9.9232834761114148,10.226855677767315,10.530427879423215,10.834000081079115,null,0.33736763828050653,0.55584433418801382,0.76110391551491985,0.99725563492001845,1,1,1,1,1,null,0.76110391551491985,0.76110391551491985,0.76110391551491985]
["2013-01-16T08:00:00","2013-01-16T08:00:00",null,8.4413862359264655,8.7449584375823655,9.0485306392382654,9.3521028408941653,9.6556750425500653,9.9592472442059652,10.262819445861865,10.566391647517765,10.869963849173665,null,0.33913412614808097,0.55966120975902278,0.76684500108453668,1,1,1,1,1,1,null,0.76684500108453668,0.76684500108453668,0.76684500108453668]
["2013-01-16T09:00:00","2013-01-16T09:00:00",null,8.6618689954820205,8.9654411971379204,9.2690133987938204,9.5725856004497203,9.8761578021056202,10.17973000376152,10.48330220541742,10.78687440707332,11.09044660872922,null,0.33974398505474357,0.56232145636912001,0.77141894288450619,1,1,1,1,1,1,null,0.77141894288450619,0.77141894288450619,0.77141894288450619]
["2013-01-16T10:00:00","2013-01-16T10:00:00",null,8.8618927259381426,9.1654649275940425,9.4690371292499425,9.7726093309058424,10.076181532561742,10.379753734217642,10.683325935873542,10.986898137529442,11.290470339185342,null,0.33630564259821477,0.56101762008591027,0.77211292026105327,1,1,1,1,1,1,null,0.77211292026105327,0.77211292026105327,0.77211292026105327]
["2013-01-16T11:00:00","2013-01-16T11:00:00",null,9.0776714414148074,9.3812436430707073,9.6848158447266073,9.9883880463825072,10.291960248038407,10.595532449694307,10.899104651350207,11.202676853006107,11.506249054662007,null,0.32797791407964966,0.55494006063675538,0.76813832255901082,0.9979916715315077,0.99985279267770211,1,1,1,1,null,0.76813832255901082,0.76813832255901082,0.76813832255901082]
["2013-01-16T12:00:00","2013-01-16T12:00:00",null,9.2574468931079394,9.5610190947638394,9.8645912964197393,10.168163498075639,10.471735699731539,10.775307901387439,11.078880103043339,11.382452304699239,11.686024506355139,null,0.31709508703834299,0.54633894709106567,0.76167171518664023,0.993543907436365,0.9972976941549605,0.99923241896230397,1,1,1,null,0.76167171518664023,0.76167171518664023,0.76167171518664023]
["2013-01-16T13:00:00","2013-01-16T13:00:00",null,9.4108153524469262,9.7143875541028262,10.017959755758726,10.321531957414626,10.625104159070526,10.928676360726426,11.232248562382326,11.535820764038226,11.839392965694126,null,0.30536056048945581,0.53687561922905991,0.75434289349795347,0.98822341421617066,0.99386986650716724,0.99760262360829188,1,1,1,null,0.75434289349795347,0.75434289349795347,0.75434289349795347]
["2013-01-16T14:00:00","2013-01-16T14:00:00",null,9.5189159839406354,9.8224881855965354,10.126060387252435,10.429632588908335,10.733204790564235,11.036776992220135,11.340349193876035,11.643921395531935,11.947493597187835,null,0.29130226121000941,0.52514109268017273,0.74478493235732757,0.98071584077897944,0.98829701787731938,0.99385935169843176,0.9979916715315077,0.99963198169425538,1,null,0.74478493235732757,0.74478493235732757,0.74478493235732757]
["2013-01-16T15:00:00","2013-01-16T15:00:00",null,9.6565118241794039,9.9600840258353038,10.263656227491202,10.567228429147102,10.870800630803002,11.174372832458902,11.477945034114802,11.781517235770702,12.085089437426602,null,0.27338502712461177,0.50963174979521875,0.73153627335051941,0.9695911731367548,0.97919119351232264,0.98664619290583622,0.99258705984142881,0.99593076901933753,0.99792858267909423,null,0.73153627335051941,0.73153627335051941,0.73153627335051941]
["2013-01-16T16:00:00","2013-01-16T16:00:00",null,9.6713121152048735,9.9748843168607735,10.278456518516673,10.582028720172573,10.885600921828473,11.189173123484373,11.492745325140273,11.796317526796173,12.099889728452073,null,0.25472124161898924,0.49338637029877547,0.71757260734969308,0.95778304292671868,0.96941242138825001,0.97878111597163586,0.98654104481848071,0.99160918262902153,0.99524730645152593,null,0.71757260734969308,0.71757260734969308,0.71757260734969308]
["2013-01-16T17:00:00","2013-01-16T17:00:00",null,9.640028214644115,9.9436004163000149,10.247172617955915,10.550744819611815,10.854317021267715,11.157889222923615,11.461461424579515,11.765033626235414,12.068605827891314,null,0.23782394398094112,0.4788759342436999,0.70529131074655671,0.94761522287943023,0.96123190019198279,0.97248274553903424,0.98203019187092466,0.98879121388789093,0.99402758863820073,null,0.70529131074655671,0.70529131074655671,0.70529131074655671]
["2013-01-16T18:00:00","2013-01-16T18:00:00",null,9.430286039560988,9.7338582412168879,10.037430442872788,10.341002644528688,10.644574846184588,10.948147047840488,11.251719249496388,11.555291451152288,11.858863652808187,null,0.22088458710795073,0.46436549818862433,0.69306258818709809,0.93753152130202633,0.95317755670054227,0.966342097237466,0.97769809067187308,0.98617302651273597,0.99303919661705786,null,0.69306258818709809,0.69306258818709809,0.69306258818709809]
["2013-01-16T19:00:00","2013-01-16T19:00:00",null,9.3031704008048148,9.6067426024607148,9.9103148041166147,10.213887005772515,10.517459207428415,10.821031409084314,11.124603610740214,11.428175812396114,11.731748014052014,null,0.20738357269148913,0.45321980092892861,0.68412500076187044,0.93067586600643992,0.94827765582977042,0.96329280270415307,0.97640476919739894,0.98653053000974511,0.99496340661566574,null,0.68412500076187044,0.68412500076187044,0.68412500076187044]
["2013-01-16T20:00:00","2013-01-16T20:00:00",null,9.1882114747417667,9.4917836763976666,9.7953558780535666,10.098928079709466,10.402500281365366,10.706072483021266,11.009644684677166,11.313216886333066,11.616789087988966,null,0.19659537892880252,0.44473435027933006,0.67779508590306214,0.92636479442485953,0.9458802794380623,0.96269345860622602,0.97750882411463291,0.98924335066352009,0.99920087453609718,null,0.67779508590306214,0.67779508590306214,0.67779508590306214]
["2013-01-16T21:00:00","2013-01-16T21:00:00",null,9.2054969050239528,9.5090691066798527,9.8126413083357527,10.116213509991653,10.419785711647553,10.723357913303452,11.026930114959352,11.330502316615252,11.634074518271152,null,0.19212658521618867,0.44246315159244864,0.6775847897283509,0.92808922305749164,0.94942376998194666,0.9679613777827426,0.98440653864516159,0.99767622726944083,1,null,0.6775847897283509,0.6775847897283509,0.6775847897283509]
["2013-01-16T22:00:00","2013-01-16T22:00:00",null,9.2697713682872873,9.5733435699431872,9.8769157715990872,10.180487973254987,10.484060174910887,10.787632376566787,11.091204578222687,11.394776779878587,11.698348981534487,null,0.20140064652095435,0.45390326349674009,0.69106477452734139,0.94349341785509,0.96662599707332608,0.98686700388928306,1,1,1,null,0.69106477452734139,0.69106477452734139,0.69106477452734139]
["2013-01-16T23:00:00","2013-01-16T23:00:00",null,9.2422066793292394,9.5457788809851394,9.8493510826410393,10.152923284296939,10.456495485952839,10.760067687608739,11.063639889264639,11.367212090920539,11.670784292576439,null,0.21237810684088107,0.46700471518125036,0.70616403987160836,0.96046431915428709,0.98537390104883316,1,1,1,1,null,0.70616403987160836,0.70616403987160836,0.70616403987160836]
["2013-01-17","2013-01-17",null,9.2811844670971748,9.5847566687530747,9.8883288704089747,10.191901072064875,10.495473273720775,10.799045475376674,11.102617677032574,11.406189878688474,11.709762080344374,null,0.22102127962151302,0.47783496817887922,0.71905519538140739,0.97529019947142948,1,1,1,1,1,null,0.71905519538140739,0.71905519538140739,0.71905519538140739]
["2013-01-17T01:00:00","2013-01-17T01:00:00",null,9.1692512692271659,9.4728234708830659,9.7763956725389658,10.079967874194866,10.383540075850766,10.687112277506666,10.990684479162566,11.294256680818465,11.597828882474365,null,0.23221955092488655,0.49116774565557181,0.73439630132659239,0.99250294137154449,1,1,1,1,1,null,0.73439630132659239,0.73439630132659239,0.73439630132659239]
["2013-01-17T02:00:00","2013-01-17T02:00:00",null,9.1231383397833632,9.4267105414392631,9.7302827430951631,10.033854944751065,10.337427146406965,10.640999348062865,10.944571549718765,11.248143751374664,11.551715953030564,null,0.24621476135191958,0.50721334378603944,0.75237662426440344,1,1,1,1,1,1,null,0.75237662426440344,0.75237662426440344,0.75237662426440344]
["2013-01-17T03:00:00","2013-01-17T03:00:00",null,9.1378246810728232,9.4413968827287231,9.7449690843846231,10.048541286040523,10.352113487696423,10.655685689352323,10.959257891008223,11.262830092664123,11.566402294320023,null,0.25929518341895869,0.52236518317398428,0.76948421807716283,1,1,1,1,1,1,null,0.76948421807716283,0.76948421807716283,0.76948421807716283]
["2013-01-17T04:00:00","2013-01-17T04:00:00",null,9.0726911445361971,9.376263346192097,9.6798355478479969,9.9834077495038986,10.286979951159799,10.590552152815699,10.894124354471598,11.197696556127498,11.501268757783398,null,0.27224942778117106,0.5374223892833091,0.78650769342003768,1,1,1,1,1,1,null,0.78650769342003768,0.78650769342003768,0.78650769342003768]
["2013-01-17T05:00:00","2013-01-17T05:00:00",null,9.1570554070456804,9.4606276087015804,9.7641998103574803,10.067772012013382,10.371344213669282,10.674916415325182,10.978488616981082,11.282060818636982,11.585633020292882,null,0.28417322088729835,0.55145965894528437,0.80252174712429858,1,1,1,1,1,1,null,0.80252174712429858,0.80252174712429858,0.80252174712429858]
["2013-01-17T06:00:00","2013-01-17T06:00:00",null,9.026016283163349,9.329588484819249,9.6331606864751489,9.9367328881310506,10.240305089786951,10.54387729144285,10.84744949309875,11.15102169475465,11.45459389641055,null,0.28197562586156588,0.5514175997103421,0.80449853116658421,1,1,1,1,1,1,null,0.80449853116658421,0.80449853116658421,0.80449853116658421]
["2013-01-17T07:00:00","2013-01-17T07:00:00",null,9.1132961335070828,9.4168683351629827,9.7204405368188826,10.024012738474783,10.327584940130683,10.631157141786582,10.934729343442482,11.238301545098382,11.541873746754282,null,0.27563519619402199,0.547243220642324,0.80236402499326509,0.99977918901655316,1,1,1,1,1,null,0.80236402499326509,0.80236402499326509,0.80236402499326509]
["2013-01-17T08:00:00","2013-01-17T08:00:00",null,9.2110207429975191,9.514592944653419,9.8181651463093189,10.121737347965219,10.425309549621119,10.728881751277019,11.032453952932919,11.336026154588819,11.639598356244719,null,0.27162905406577287,0.54530849583498064,0.80237453980200069,1,1,1,1,1,1,null,0.80237453980200069,0.80237453980200069,0.80237453980200069]
["2013-01-17T09:00:00","2013-01-17T09:00:00",null,9.4123616786735731,9.715933880329473,10.019506081985373,10.323078283641273,10.626650485297173,10.930222686953073,11.233794888608973,11.537367090264873,11.840939291920773,null,0.26780166368602831,0.54349994873246399,0.80246917308062071,1,1,1,1,1,1,null,0.80246917308062071,0.80246917308062071,0.80246917308062071]
["2013-01-17T10:00:00","2013-01-17T10:00:00",null,9.8031051685896546,10.106677370245555,10.410249571901455,10.713821773557354,11.017393975213254,11.320966176869154,11.624538378525054,11.928110580180954,12.231682781836854,null,0.25722376609805292,0.53506707212654325,0.79606565456066347,0.99549966186117944,0.9973082089636961,0.99901160797885713,1,1,1,null,0.79606565456066347,0.79606565456066347,0.79606565456066347]
["2013-01-17T11:00:00","2013-01-17T11:00:00",null,9.9387597918061736,10.242331993462074,10.545904195117974,10.849476396773873,11.153048598429773,11.456620800085673,11.760193001741573,12.063765203397473,12.367337405053373,null,0.24298671507010197,0.52305916055053148,0.78616070473176403,0.98758201088330122,0.99126219394074799,0.99474259563221901,0.99741335705105172,0.99901160797885713,1,null,0.78616070473176403,0.78616070473176403,0.78616070473176403]
["2013-01-17T12:00:00","2013-01-17T12:00:00",null,10.168873048366695,10.472445250022595,10.776017451678495,11.079589653334395,11.383161854990295,11.686734056646195,11.990306258302095,12.293878459957995,12.597450661613895,null,0.22390233721505695,0.50629855542604563,0.77158717982427505,0.97507990329671801,0.98071584077897933,0.98605736361664476,0.99049461290305196,0.99376471841981173,0.99635136136876001,null,0.77158717982427505,0.77158717982427505,0.77158717982427505]
["2013-01-17T13:00:00","2013-01-17T13:00:00",null,10.299690081244771,10.603262282900671,10.906834484556571,11.210406686212471,11.513978887868371,11.817551089524271,12.121123291180171,12.42469549283607,12.72826769449197,null,0.20160042788692994,0.48637299287215563,0.75392230114853087,0.95953901598555735,0.96719379674504657,0.97444901477258428,0.98070532597024374,0.98569986011963573,0.98993732804006718,null,0.75392230114853087,0.75392230114853087,0.75392230114853087]
["2013-01-17T14:00:00","2013-01-17T14:00:00",null,10.456870040714023,10.760442242369923,11.064014444025824,11.367586645681724,11.671158847337624,11.974731048993524,12.278303250649424,12.581875452305324,12.885447653961224,null,0.17499796178595808,0.46224150682404086,0.73212510263971087,0.9399604421199409,0.94970766981780697,0.95896070150510149,0.96710967827516203,0.9739022447183352,0.97986414127139876,null,0.73212510263971087,0.73212510263971087,0.73212510263971087]
["2013-01-17T15:00:00","2013-01-17T15:00:00",null,10.495078422684175,10.798650624340075,11.102222825995977,11.405795027651877,11.709367229307777,12.012939430963677,12.316511632619576,12.620083834275476,12.923656035931376,null,0.14635562279028719,0.43612272192490487,0.70838266451481191,0.91847868787318776,0.93036042174437283,0.94164281151763085,0.95172651309503487,0.96034865625819577,0.96806652587009823,null,0.70838266451481191,0.70838266451481191,0.70838266451481191]
["2013-01-17T16:00:00","2013-01-17T16:00:00",null,10.510472432372026,10.814044634027926,11.117616835683826,11.421189037339726,11.724761238995626,12.028333440651526,12.331905642307426,12.635477843963326,12.939050045619226,null,0.11694570275692028,0.40924687079680838,0.6839041897784236,0.89627141182368086,0.91030868148565613,0.92364145896234873,0.93567040015583169,0.94614314965645152,0.95561699232719277,null,0.6839041897784236,0.6839041897784236,0.6839041897784236]
["2013-01-17T17:00:00","2013-01-17T17:00:00",null,10.407290068570791,10.710862270226691,11.014434471882591,11.318006673538491,11.621578875194391,11.925151076850291,12.228723278506191,12.532295480162091,12.835867681817991,null,8.9155063268829909E-2,0.38396927059651736,0.66100293635236962,0.87562032746703711,0.8917921033023315,0.90714372405625199,0.92109687524834272,0.93339920146895039,0.94461850238979495,null,0.66100293635236962,0.66100293635236962,0.66100293635236962]
["2013-01-17T18:00:00","2013-01-17T18:00:00",null,10.220659940746957,10.524232142402857,10.827804344058755,11.131376545714655,11.434948747370555,11.738520949026455,12.042093150682355,12.345665352338255,12.649237553994155,null,6.3562018806472012E-2,0.36086823580448768,0.64025721871710584,0.85710374928371247,0.87538900167485478,0.89273843608853209,0.90858425285302391,0.92269512617614824,0.93562834092088942,null,0.64025721871710584,0.64025721871710584,0.64025721871710584]
["2013-01-17T19:00:00","2013-01-17T19:00:00",null,10.017394398063944,10.320966599719844,10.624538801375744,10.928111003031644,11.231683204687544,11.535255406343444,11.838827607999344,12.142399809655243,12.445972011311143,null,4.1333713139493952E-2,0.34108988057289558,0.62278160659860182,0.84180470257346973,0.86215085747678222,0.88145604631527408,0.8991629842259603,0.91502983060792353,0.92963489994161908,null,0.62278160659860182,0.62278160659860182,0.62278160659860182]
["2013-01-17T20:00:00","2013-01-17T20:00:00",null,9.9099593988681125,10.213531600524012,10.517103802179911,10.820676003835811,11.12424820549171,11.42782040714761,11.73139260880351,12.03496481045941,12.33853701211531,null,2.1113735941008231E-2,0.32327779457485356,0.60725123409617676,0.82841935105309927,0.85079486404237525,0.87202426287947499,0.89155026270141347,0.9091520525247444,0.92539743202118763,null,0.60725123409617676,0.60725123409617676,0.60725123409617676]
["2013-01-17T21:00:00","2013-01-17T21:00:00",null,9.8555430416898737,10.159115243345774,10.462687445001672,10.766259646657572,11.069831848313472,11.373404049969372,11.676976251625272,11.980548453281171,12.284120654937071,null,3.8904792321576807E-3,0.30839934021403331,0.59457037476108898,0.81782042384765274,0.84216220607047887,0.86525272605377301,0.88653469893455039,0.90581885815557128,0.92365197377108432,null,0.59457037476108898,0.59457037476108898,0.59457037476108898]
["2013-01-17T22:00:00","2013-01-17T22:00:00",null,9.7208616554689939,10.024433857124894,10.328006058780794,10.631578260436694,10.935150462092594,11.238722663748494,11.542294865404394,11.845867067060293,12.149439268716193,null,0,0.29701180235341967,0.58531734307379446,0.81057572062885053,0.83681016842407785,0.86168820589241746,0.88467357778835587,0.90556650274591777,0.92493478043682287,null,0.58531734307379446,0.58531734307379446,0.58531734307379446]
["2013-01-17T23:00:00","2013-01-17T23:00:00",null,9.5407931469842637,9.8443653486401637,10.147937550296064,10.451509751951965,10.755081953607865,11.058654155263765,11.362226356919665,11.665798558575565,11.969370760231465,null,0,0.28784288913600964,0.57824087679476122,0.80547603839210291,0.83357160733352476,0.86021613266943875,0.88486284434559603,0.90733299061349215,0.92820488595358264,null,0.57824087679476122,0.57824087679476122,0.57824087679476122]
["2013-01-18","2013-01-18",null,9.4238362928844079,9.7274084945403079,10.030980696196208,10.334552897852108,10.638125099508008,10.941697301163908,11.245269502819808,11.548841704475707,11.852413906131607,null,0,0.2814393706160524,0.57387723116950295,0.80303660276545252,0.83294071880939102,0.86128864316046605,0.88755463538189994,0.91155994372518812,0.93388288267078612,null,0.57387723116950295,0.57387723116950295,0.57387723116950295]
["2013-01-18T01:00:00","2013-01-18T01:00:00",null,9.4514073148424878,9.7549795164983877,10.058551718154288,10.362123919810188,10.665696121466087,10.969268323121987,11.272840524777887,11.576412726433787,11.879984928089687,null,0,0.27731756559171211,0.57172169537871276,0.80273167331212125,0.83437073279742746,0.86436948211998577,0.89219166603428279,0.91766904760054968,0.94140097091671293,null,0.57172169537871276,0.57172169537871276,0.57172169537871276]
["2013-01-18T02:00:00","2013-01-18T02:00:00",null,9.4286269302077734,9.7321991318636734,10.035771333519573,10.339343535175473,10.642915736831373,10.946487938487273,11.250060140143173,11.553632341799073,11.857204543454973,null,0,0.27457320051173045,0.57091205510607446,0.8037410949507352,0.83708355345120244,0.86870158331903735,0.89805892930872644,0.92497683967176525,0.95008620293228718,null,0.57091205510607446,0.57091205510607446,0.57091205510607446]
["2013-01-18T03:00:00","2013-01-18T03:00:00",null,9.4082023173530889,9.7117745190089888,10.015346720664889,10.318918922320789,10.622491123976689,10.926063325632589,11.229635527288488,11.533207728944388,11.836779930600288,null,0,0.27292237554024723,0.57115389570699238,0.8057704530366987,0.84079528093485578,0.87400104692176062,0.90486201056063509,0.93320993491171034,0.95967570849911976,null,0.57115389570699238,0.57115389570699238,0.57115389570699238]
["2013-01-18T04:00:00","2013-01-18T04:00:00",null,9.2289920220903721,9.532564223746272,9.8361364254021719,10.139708627058072,10.443280828713972,10.746853030369872,11.050425232025772,11.353997433681672,11.657569635337572,null,0,0.2699361698593476,0.57014447406837843,0.80661163773554367,0.84339243869253955,0.87824902965092766,0.91066618498266527,0.94048618255671923,0.96835042570595842,null,0.57014447406837843,0.57014447406837843,0.57014447406837843]
["2013-01-18T05:00:00","2013-01-18T05:00:00",null,9.3139700656680375,9.6175422673239375,9.9211144689798374,10.224686670635739,10.528258872291639,10.831831073947539,11.135403275603439,11.438975477259339,11.742547678915239,null,0,0.26591951292236293,0.56811511598241493,0.8064539156045103,0.84499068962034496,0.88150862035895183,0.91550299700102378,0.94681609741552752,0.97608932493533207,null,0.56811511598241493,0.56811511598241493,0.56811511598241493]
["2013-01-18T06:00:00","2013-01-18T06:00:00",null,9.3297958131691523,9.6333680148250522,9.9369402164809522,10.240512418136854,10.544084619792754,10.847656821448654,11.151229023104554,11.454801224760454,11.758373426416354,null,0,0.26714974554442367,0.57135367707296802,0.81158514226746459,0.85190943376834471,0.89010973390464154,0.9257023614745189,0.95851907953820803,0.98922232104604901,null,0.57135367707296802,0.57135367707296802,0.57135367707296802]
["2013-01-18T07:00:00","2013-01-18T07:00:00",null,8.9873864125813903,9.2909586142372902,9.5945308158931901,9.8981030175490901,10.20167521920499,10.50524742086089,10.80881962251679,11.11239182417269,11.41596402582859,null,4.978761936288606E-2,0.31929268206407563,0.62570472342708794,0.86800760594249027,0.91028765186818494,0.95031752872446951,0.98764509973571468,1,1,null,0.62570472342708794,0.62570472342708794,0.62570472342708794]
["2013-01-18T08:00:00","2013-01-18T08:00:00",null,9.0729677937618192,9.3765399954177191,9.680112197073619,9.983684398729519,10.287256600385419,10.590828802041319,10.894401003697219,11.197973205353119,11.501545407009019,null,9.8670965174513792E-2,0.3705523746499404,0.67918304065615631,0.92356785530119989,0.9678141704604446,1,1,1,1,null,0.67918304065615631,0.67918304065615631,0.67918304065615631]
["2013-01-18T09:00:00","2013-01-18T09:00:00",null,9.6245792832287371,9.9281514848846371,10.231723686540537,10.535295888196439,10.838868089852339,11.142440291508239,11.446012493164138,11.749584694820038,12.053156896475938,null,0.14756482579487706,0.42167537472224281,0.73240900247557117,0.97878111597163597,1,1,1,1,1,null,0.73240900247557117,0.73240900247557117,0.73240900247557117]
["2013-01-18T10:00:00","2013-01-18T10:00:00",null,9.9044430333441351,10.208015235000035,10.511587436655935,10.815159638311835,11.118731839967735,11.422304041623635,11.725876243279535,12.029448444935435,12.333020646591335,null,0.19242099986078454,0.46882377709250278,0.78171294063662133,1,1,1,1,1,1,null,0.78171294063662133,0.78171294063662133,0.78171294063662133]
["2013-01-18T11:00:00","2013-01-18T11:00:00",null,11.212919205126987,11.516491406782887,11.820063608438787,12.123635810094687,12.427208011750587,12.730780213406486,13.034352415062386,13.337924616718286,13.641496818374186,null,0.14982550967302288,0.42965611455253433,0.74580486880467711,0.96717276712757549,0.9701169135735328,0.97291385269719233,0.97558461411602504,0.97812919783003105,0.98056863345668144,null,0.74580486880467711,0.74580486880467711,0.74580486880467711]
["2013-01-18T12:00:00","2013-01-18T12:00:00",null,11.335801653181278,11.639373854837178,11.942946056493078,12.246518258148978,12.550090459804878,12.853662661460778,13.157234863116678,13.460807064772577,13.764379266428477,null,0.14296985437743645,0.42615468324359218,0.74549993935134584,0.96989610259008607,0.97572130662958734,0.98126261083322852,0.98655155962721619,0.99159866782028594,0.99642496502990896,null,0.74549993935134584,0.74549993935134584,0.74549993935134584]
["2013-01-18T13:00:00","2013-01-18T13:00:00",null,10.978110688564007,11.281682890219907,11.585255091875807,11.888827293531707,12.192399495187606,12.495971696843506,12.799543898499406,13.103116100155306,13.406688301811206,null,0.15218082682978876,0.43840443542052193,0.7606307491218196,0.9877502478230703,0.99617260962025544,1,1,1,1,null,0.7606307491218196,0.7606307491218196,0.7606307491218196]
["2013-01-18T14:00:00","2013-01-18T14:00:00",null,10.887603748111635,11.191175949767535,11.494748151423435,11.798320353079335,12.101892554735235,12.405464756391135,12.709036958047035,13.012609159702935,13.316181361358835,null,0.16895194676301015,0.4580250685210806,0.78295368806741772,1,1,1,1,1,1,null,0.78295368806741772,0.78295368806741772,0.78295368806741772]
["2013-01-18T15:00:00","2013-01-18T15:00:00",null,10.848891230649407,11.152463432305309,11.456035633961209,11.759607835617109,12.063180037273009,12.366752238928909,12.670324440584809,12.973896642240708,13.277468843896608,null,0.18765779150357495,0.47953836719404047,0.80713774815921036,1,1,1,1,1,1,null,0.80713774815921036,0.80713774815921036,0.80713774815921036]
["2013-01-18T16:00:00","2013-01-18T16:00:00",null,10.899629367026581,11.203201568682481,11.506773770338381,11.81034597199428,12.11391817365018,12.41749037530608,12.72106257696198,13.02463477861788,13.32820698027378,null,0.20729945422160476,0.50194542460952307,0.83217350775858345,1,1,1,1,1,1,null,0.83217350775858345,0.83217350775858345,0.83217350775858345]
["2013-01-18T17:00:00","2013-01-18T17:00:00",null,10.749432125329541,11.053004326985441,11.356576528641341,11.660148730297241,11.963720931953141,12.267293133609041,12.570865335264941,12.874437536920841,13.178009738576741,null,0.23068438884949463,0.52804317989118799,0.86083687637172546,1,1,1,1,1,1,null,0.86083687637172546,0.86083687637172546,0.86083687637172546]
["2013-01-18T18:00:00","2013-01-18T18:00:00",null,10.426018018808813,10.729590220464715,11.033162422120615,11.336734623776515,11.640306825432415,11.943879027088315,12.247451228744215,12.551023430400114,12.854595632056014,null,0.25936878708010774,0.5593773099231627,0.89466301607402843,1,1,1,1,1,1,null,0.89466301607402843,0.89466301607402843,0.89466301607402843]
["2013-01-18T19:00:00","2013-01-18T19:00:00",null,10.267873159874398,10.571445361530298,10.875017563186198,11.178589764842098,11.482161966497998,11.785734168153898,12.089306369809798,12.392878571465697,12.696450773121597,null,0.29243786055345022,0.59500148191924673,0.93269507927055617,1,1,1,1,1,1,null,0.93269507927055617,0.93269507927055617,0.93269507927055617]
["2013-01-18T20:00:00","2013-01-18T20:00:00",null,10.168816673362659,10.472388875018559,10.775961076674459,11.079533278330359,11.383105479986259,11.686677681642159,11.990249883298059,12.293822084953959,12.597394286609859,null,0.32691591839735801,0.63201360866842493,0.97210458241144249,1,1,1,1,1,1,null,0.97210458241144249,0.97210458241144249,0.97210458241144249]
["2013-01-18T21:00:00","2013-01-18T21:00:00",null,10.146975714408793,10.450547916064693,10.754120117720593,11.057692319376493,11.361264521032393,11.664836722688293,11.968408924344192,12.271981126000092,12.575553327655992,null,0.37001611940442664,0.67740603797984611,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-18T22:00:00","2013-01-18T22:00:00",null,9.8129955682845527,10.116567769940453,10.420139971596353,10.723712173252251,11.027284374908151,11.330856576564051,11.63442877821995,11.93800097987585,12.24157318153175,null,0.4092363559880729,0.71889747325037379,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-18T23:00:00","2013-01-18T23:00:00",null,9.7498223599249823,10.053394561580882,10.356966763236782,10.660538964892682,10.964111166548582,11.267683368204482,11.571255569860382,11.874827771516282,12.178399973172182,null,0.40980415565979322,0.72165235313909104,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19","2013-01-19",null,9.7285977138096289,10.032169915465529,10.335742117121429,10.639314318777327,10.942886520433227,11.246458722089127,11.550030923745027,11.853603125400927,12.157175327056827,null,0.4115811583361032,0.72558489160619122,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T01:00:00","2013-01-19T01:00:00",null,9.634951495717802,9.9385236973737019,10.242095899029602,10.5456681006855,10.8492403023414,11.1528125039973,11.4563847056532,11.7599569073091,12.063529108965,null,0.41470405653056513,0.73084229597397221,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T02:00:00","2013-01-19T02:00:00",null,9.5986675892805344,9.9022397909364344,10.205811992592334,10.509384194248234,10.812956395904134,11.116528597560034,11.420100799215934,11.723673000871834,12.027245202527734,null,0.4200035201332884,0.73822369170633673,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T03:00:00","2013-01-19T03:00:00",null,9.7046157376976829,10.008187939353583,10.311760141009483,10.615332342665383,10.918904544321283,11.222476745977183,11.526048947633083,11.829621149288982,12.133193350944882,null,0.42695380870749489,0.74718230874903557,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T04:00:00","2013-01-19T04:00:00",null,9.632438815185024,9.9360110168409239,10.239583218496824,10.543155420152724,10.846727621808624,11.150299823464524,11.453872025120424,11.757444226776324,12.061016428432223,null,0.43415645269135483,0.75639328120138793,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T05:00:00","2013-01-19T05:00:00",null,9.5838300070282347,9.8874022086841347,10.190974410340035,10.494546611995935,10.798118813651834,11.101691015307734,11.405263216963634,11.708835418619534,12.012407620275434,null,0.43767891361776812,0.76196612983123579,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T06:00:00","2013-01-19T06:00:00",null,9.5521187304898838,9.8556909321457837,10.159263133801684,10.462835335457585,10.766407537113485,11.069979738769385,11.373551940425285,11.677124142081185,11.980696343737085,null,0.4360175738375493,0.76242878141560055,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T07:00:00","2013-01-19T07:00:00",null,9.5593541920307885,9.8629263936866884,10.166498595342588,10.470070796998488,10.773642998654388,11.077215200310288,11.380787401966188,11.684359603622088,11.987931805277988,null,0.43362019744584118,0.76216591119721155,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-19T08:00:00","2013-01-19T08:00:00",null,9.6872140597871059,9.9907862614430059,10.294358463098906,10.597930664754806,10.901502866410706,11.205075068066606,11.508647269722506,11.812219471378405,12.115791673034305,null,0.42678557176772586,0.75742373245747308,0.99722409049381167,0.99908521164000608,1,1,1,1,1,null,0.99722409049381167,0.99722409049381167,0.99722409049381167]
["2013-01-19T09:00:00","2013-01-19T09:00:00",null,9.9264084643995822,10.229980666055482,10.533552867711382,10.837125069367282,11.140697271023182,11.444269472679082,11.747841674334982,12.051413875990882,12.354986077646782,null,0.41805828051720939,0.750799402954069,0.99257654503269321,0.99630930213381774,0.99899057836138605,1,1,1,1,null,0.99257654503269321,0.99257654503269321,0.99257654503269321]
["2013-01-19T10:00:00","2013-01-19T10:00:00",null,10.165560294715453,10.469132496371353,10.772704698027255,11.076276899683155,11.379849101339055,11.683421302994955,11.986993504650854,12.290565706306754,12.594137907962654,null,0.40386328872420069,0.7388125209955283,0.98268211001252936,0.98838113634720404,0.99293404852970235,0.99570995803589069,0.99739232743358064,0.99898006355265045,1,null,0.98268211001252936,0.98268211001252936,0.98268211001252936]
["2013-01-19T11:00:00","2013-01-19T11:00:00",null,10.833671284038481,11.13724348569438,11.44081568735028,11.74438788900618,12.04796009066208,12.35153229231798,12.65510449397388,12.95867669562978,13.26224889728568,null,0.37016332672672447,0.7077202315644715,0.95406080063432963,0.96210462931703455,0.96887616614273653,0.97377606701350838,0.97746676487969064,0.98097871099736833,0.98382822416470561,null,0.95406080063432963,0.95406080063432963,0.95406080063432963]
["2013-01-19T12:00:00","2013-01-19T12:00:00",null,10.981060324358687,11.284632526014587,11.588204727670487,11.891776929326387,12.195349130982287,12.498921332638186,12.802493534294086,13.106065735949986,13.409637937605886,null,0.33636873145062823,0.67650176442858789,0.92528176912509641,0.93564937053836061,0.94461850238979506,0.95162136500767924,0.95730987653361832,0.96272500303243269,0.96739357811102222,null,0.92528176912509641,0.92528176912509641,0.92528176912509641]
["2013-01-19T13:00:00","2013-01-19T13:00:00",null,11.109913565991182,11.41348576764708,11.71705796930298,12.02063017095888,12.32420237261478,12.62777457427068,12.931346775926579,13.234918977582479,13.538491179238379,null,0.29989285994696369,0.64264408030007825,0.89390557985817942,0.90663901323694507,0.91784779934905425,0.92698516814025744,0.93471355256089561,0.94206340386705334,0.94859310009183739,null,0.89390557985817942,0.89390557985817942,0.89390557985817942]
["2013-01-19T14:00:00","2013-01-19T14:00:00",null,11.126154131983792,11.429726333639692,11.733298535295592,12.036870736951492,12.340442938607392,12.644015140263292,12.947587341919192,13.251159543575092,13.554731745230992,null,0.26268095183180978,0.60807138917755044,0.86182489840597976,0.87693467855898244,0.89040414854923744,0.90168653832249523,0.91146531044656798,0.92077091617754026,0.92917224835725443,null,0.86182489840597976,0.86182489840597976,0.86182489840597976]
["2013-01-19T15:00:00","2013-01-19T15:00:00",null,11.220564136603564,11.524136338259463,11.827708539915363,12.131280741571263,12.434852943227163,12.738425144883063,13.041997346538963,13.345569548194863,13.649141749850763,null,0.22437550360815742,0.57240515794652413,0.82867170646275279,0.84615783338999251,0.86189850206712881,0.87533642763117692,0.88716558745868423,0.89843746242320655,0.90872094536658632,null,0.82867170646275279,0.82867170646275279,0.82867170646275279]
["2013-01-19T16:00:00","2013-01-19T16:00:00",null,11.168355943948432,11.471928145604332,11.775500347260232,12.079072548916132,12.382644750572032,12.686216952227932,12.989789153883832,13.293361355539732,13.596933557195632,null,0.18850949101115544,0.53912578829847035,0.79785280205882059,0.81767321652535507,0.83563250984569493,0.85118391196559096,0.86502140026159069,0.87821748522472087,0.89034105969682398,null,0.79785280205882059,0.79785280205882059,0.79785280205882059]
["2013-01-19T17:00:00","2013-01-19T17:00:00",null,10.986958315671172,11.29053051732707,11.59410271898297,11.89767492063887,12.20124712229477,12.50481932395067,12.80839152560657,13.11196372726247,13.41553592891837,null,0.15779573469457883,0.51090404165222192,0.77199688737807359,0.79405695610528282,0.81415075559894179,0.83172100099606572,0.84749321409940881,0.86252939059126232,0.87640893812220433,null,0.77199688737807359,0.77199688737807359,0.77199688737807359]
["2013-01-19T18:00:00","2013-01-19T18:00:00",null,10.833327285634189,11.136899487290087,11.440471688945987,11.744043890601887,12.047616092257787,12.351188293913687,12.654760495569587,12.958332697225487,13.261904898881387,null,0.13113017974119362,0.48665689270801593,0.7500419667382201,0.77427860087369071,0.79643330287951986,0.81596981751019382,0.83360315175973143,0.85042684573663041,0.86599927747399796,null,0.7500419667382201,0.7500419667382201,0.7500419667382201]
["2013-01-19T19:00:00","2013-01-19T19:00:00",null,10.65876768992112,10.96233989157702,11.26591209323292,11.56948429488882,11.87305649654472,12.17662869820062,12.48020089985652,12.78377310151242,13.08734530316832,null,0.1094696737459359,0.46730964463458186,0.73288179888178295,0.75920036514689482,0.78332133638627399,0.80472948697187807,0.82413982389772567,0.84266691688978568,0.85985862917242972,null,0.73288179888178295,0.73288179888178295,0.73288179888178295]
["2013-01-19T20:00:00","2013-01-19T20:00:00",null,10.457784672959349,10.761356874615249,11.064929076271149,11.368501277927049,11.672073479582949,11.975645681238849,12.279217882894748,12.582790084550648,12.886362286206548,null,8.7378060592520138E-2,0.4475943782554031,0.71540618676327894,0.74384874439297433,0.7699885589095814,0.79329988987632216,0.81452928871342201,0.83479132514684973,0.85362334759224145,null,0.71540618676327894,0.71540618676327894,0.71540618676327894]
["2013-01-19T21:00:00","2013-01-19T21:00:00",null,10.379308390995558,10.682880592651458,10.986452794307358,11.290024995963257,11.593597197619157,11.897169399275057,12.200741600930957,12.504313802586857,12.807886004242757,null,6.9292589567353499E-2,0.43179062072585339,0.70174745021578389,0.73222988074017836,0.7602939052553932,0.78543481294212181,0.80840967002932496,0.83032253143423584,0.8507317751899619,null,0.70174745021578389,0.70174745021578389,0.70174745021578389]
["2013-01-19T22:00:00","2013-01-19T22:00:00",null,10.340413323762052,10.643985525417952,10.947557727073852,11.251129928729751,11.554702130385651,11.858274332041551,12.161846533697451,12.465418735353351,12.768990937009251,null,5.3268021054357018E-2,0.41799519166479604,0.69005498290183898,0.72252471227725468,0.75247088755613512,0.77940982753664478,0.80407756883027337,0.82760971078046086,0.84956463142031458,null,0.69005498290183898,0.69005498290183898,0.69005498290183898]
["2013-01-19T23:00:00","2013-01-19T23:00:00",null,10.179937891884562,10.483510093540461,10.787082295196361,11.090654496852261,11.394226698508161,11.697798900164061,12.001371101819961,12.304943303475861,12.608515505131761,null,4.2006660898570122E-2,0.40885782287359268,0.68291542777039238,0.71727782271820928,0.74902203029087078,0.77766436928654148,0.80394087631671107,0.82900818034229062,0.85242465939638745,null,0.68291542777039238,0.68291542777039238,0.68291542777039238]
["2013-01-20","2013-01-20",null,10.124476852805186,10.428049054461086,10.731621256116986,11.035193457772886,11.338765659428786,11.642337861084686,11.945910062740586,12.249482264396486,12.553054466052386,null,2.9967204896351636E-2,0.39897390266216443,0.67507138045366311,0.71134747059135228,0.74491074007526603,0.77527750770356896,0.80319432489648612,0.82981782061492892,0.85470637289200435,null,0.67507138045366311,0.67507138045366311,0.67507138045366311]
["2013-01-20T01:00:00","2013-01-20T01:00:00",null,10.05634053286197,10.35991273451787,10.66348493617377,10.96705713782967,11.27062933948557,11.57420154114147,11.87777374279737,12.18134594445327,12.48491814610917,null,2.1828742935026652E-2,0.39289634321300959,0.67093906062058728,0.70904472747826419,0.74435345521228125,0.77636053300333185,0.80584405669784775,0.83395014044800475,0.86024767709564554,null,0.67093906062058728,0.67093906062058728,0.67093906062058728]
["2013-01-20T02:00:00","2013-01-20T02:00:00",null,9.995439136579213,10.299011338235113,10.602583539891013,10.906155741546915,11.209727943202815,11.513300144858714,11.816872346514614,12.120444548170514,12.424016749826414,null,1.4121388131859708E-2,0.38727092053948392,0.6672799071806117,0.70724669518448313,0.74431139597733897,0.77797981354860846,0.80905107336219417,0.83865025995280096,0.86637781058847818,null,0.6672799071806117,0.6672799071806117,0.6672799071806117]
["2013-01-20T03:00:00","2013-01-20T03:00:00",null,9.799704518924937,10.103276720580837,10.406848922236737,10.710421123892637,11.013993325548537,11.317565527204437,11.621137728860337,11.924709930516237,12.228282132172136,null,9.6841388454525449E-3,0.38486302933904021,0.66678571117004026,0.70855053146769287,0.74731863127570974,0.78259581458352012,0.8152022364724979,0.84625246666861231,0.87535745724864811,null,0.66678571117004026,0.66678571117004026,0.66678571117004026]
["2013-01-20T04:00:00","2013-01-20T04:00:00",null,9.8268517405670757,10.130423942222976,10.433996143878876,10.737568345534775,11.041140547190675,11.344712748846575,11.648284950502475,11.951857152158375,12.255429353814275,null,3.6906978661822064E-3,0.38094100568067557,0.66480892712775463,0.70841383895413057,0.74891688220351516,0.78583437567407322,0.82000750406464973,0.85252980748374285,0.88304378243434389,null,0.66480892712775463,0.66480892712775463,0.66480892712775463]
["2013-01-20T05:00:00","2013-01-20T05:00:00",null,9.7247603935690918,10.028332595224992,10.331904796880892,10.635476998536792,10.939049200192692,11.242621401848591,11.546193603504491,11.849765805160391,12.153338006816291,null,0,0.37513683125864533,0.66103411079168783,0.70654220299920056,0.7488537933511018,0.7874746858368209,0.82325657996393842,0.8573140454584236,0.88928957882326776,null,0.66103411079168783,0.66103411079168783,0.66103411079168783]
["2013-01-20T06:00:00","2013-01-20T06:00:00",null,9.817300090032866,10.120872291688766,10.424444493344666,10.728016695000566,11.031588896656466,11.335161098312366,11.638733299968266,11.942305501624165,12.245877703280065,null,0,0.36806036497961209,0.65599751740735368,0.70342981961347417,0.74757098668536326,0.78791630780371447,0.82532799728484418,0.86094165447219251,0.89438926106001537,null,0.65599751740735368,0.65599751740735368,0.65599751740735368]
["2013-01-20T07:00:00","2013-01-20T07:00:00",null,9.6107667159783396,9.9143389176342396,10.21791111929014,10.521483320946038,10.825055522601938,11.128627724257838,11.432199925913737,11.735772127569637,12.039344329225537,null,0,0.36100492831804998,0.65102401287543288,0.7004225843151034,0.74641435772445142,0.78851565190164152,0.82757816635425441,0.86476904485193706,0.89970975428020972,null,0.65102401287543288,0.65102401287543288,0.65102401287543288]
["2013-01-20T08:00:00","2013-01-20T08:00:00",null,9.8165734464355072,10.120145648091407,10.423717849747307,10.727290051403207,11.030862253059107,11.334434454715007,11.638006656370907,11.941578858026807,12.245151059682707,null,0,0.353970521273959,0.64602947872604088,0.69735226016431928,0.74517361029365514,0.78899933310347736,0.82969164291010233,0.86842819829191265,0.90484098094316401,null,0.64602947872604088,0.64602947872604088,0.64602947872604088]
["2013-01-20T09:00:00","2013-01-20T09:00:00",null,10.078986838479221,10.382559040135121,10.686131241791021,10.989703443446921,11.29327564510282,11.59684784675872,11.90042004841462,12.20399225007052,12.50756445172642,null,0,0.34392887893149732,0.63805925370448491,0.69134830437631334,0.74103077565184372,0.78661247152050484,0.82897663591608417,0.8693009274169643,0.90721732771740105,null,0.63805925370448491,0.63805925370448491,0.63805925370448491]
["2013-01-20T10:00:00","2013-01-20T10:00:00",null,10.358187007364982,10.661759209020882,10.965331410676782,11.268903612332682,11.572475813988582,11.876048015644482,12.179620217300382,12.483192418956282,12.786764620612182,null,0,0.33027014238400226,0.62652450852157338,0.68182188766189422,0.73340753931856129,0.78079778228973906,0.8248863753179505,0.86684046217284283,0.90631305416614272,null,0.62652450852157338,0.62652450852157338,0.62652450852157338]
["2013-01-20T11:00:00","2013-01-20T11:00:00",null,10.842675078609693,11.146247280265593,11.449819481921493,11.753391683577393,12.056963885233293,12.360536086889192,12.664108288545092,12.967680490200992,13.271252691856892,null,0,0.30313142103751672,0.60177264875806047,0.65934122658526262,0.71308241403271999,0.76251252989859675,0.80855687735162274,0.85236157054397399,0.89361116521358386,null,0.60177264875806047,0.60177264875806047,0.60177264875806047]
["2013-01-20T12:00:00","2013-01-20T12:00:00",null,11.00532309400338,11.30889529565928,11.61246749731518,11.91603969897108,12.21961190062698,12.52318410228288,12.82675630393878,13.130328505594679,13.433900707250579,null,0,0.27186037985795536,0.57297258763135617,0.63287545299785308,0.6888457798972496,0.74039988712770988,0.78846307785796377,0.83419198104892289,0.8772711524385205,null,0.57297258763135617,0.57297258763135617,0.57297258763135617]
["2013-01-20T13:00:00","2013-01-20T13:00:00",null,11.2540342664867,11.5576064681426,11.8611786697985,12.1647508714544,12.4683230731103,12.7718952747662,13.0754674764221,13.379039678078,13.6826118797339,null,0,0.2357945858949777,0.53945137738238447,0.6017621339493251,0.66002468915307411,0.71376587660053137,0.76391099946042651,0.81162720150240686,0.85660955327314114,null,0.53945137738238447,0.53945137738238447,0.53945137738238447]
["2013-01-20T14:00:00","2013-01-20T14:00:00",null,11.292197808917877,11.595770010573776,11.899342212229676,12.202914413885576,12.506486615541476,12.810058817197376,13.113631018853276,13.417203220509176,13.720775422165076,null,0,0.20040173969107603,0.50663465931869545,0.57139536632102206,0.63198169425533024,0.68794150634599105,0.74020010576173423,0.78993515108094248,0.83684171285028464,null,0.50663465931869545,0.50663465931869545,0.50663465931869545]
["2013-01-20T15:00:00","2013-01-20T15:00:00",null,11.42698216766825,11.73055436932415,12.03412657098005,12.337698772635949,12.641270974291849,12.944843175947749,13.248415377603649,13.551987579259549,13.855559780915449,null,0,0.17036093113357539,0.47921203813634977,0.54645424000026899,0.60940639990007861,0.66761638106014976,0.72203051626668313,0.77381594928932596,0.82268878029221815,null,0.47921203813634977,0.47921203813634977,0.47921203813634977]
["2013-01-20T16:00:00","2013-01-20T16:00:00",null,11.443414250064443,11.746986451720343,12.050558653376243,12.354130855032142,12.657703056688042,12.961275258343942,13.264847459999842,13.568419661655742,13.871991863311642,null,0,0.13962614519952768,0.45110595438619255,0.52085068072917551,0.58617918740322217,0.64666036725017473,0.70324055305623379,0.75708688859104678,0.80793650363622471,null,0.45110595438619255,0.45110595438619255,0.45110595438619255]
["2013-01-20T17:00:00","2013-01-20T17:00:00",null,11.408905174255871,11.712477375911771,12.016049577567671,12.319621779223571,12.623193980879471,12.926766182535371,13.230338384191271,13.53391058584717,13.83748278750307,null,0,0.11041600653213646,0.42449297347648512,0.49670867987232514,0.56438198889440216,0.62710282300202946,0.68581751498140753,0.7417142382196551,0.79450909288091209,null,0.42449297347648512,0.42449297347648512,0.42449297347648512]
["2013-01-20T18:00:00","2013-01-20T18:00:00",null,11.034549303135071,11.338121504790971,11.641693706446871,11.945265908102771,12.248838109758671,12.552410311414571,12.855982513070471,13.159554714726371,13.46312691638227,null,0,8.4896565730927492E-2,0.40154966081548882,0.47622583245545036,0.54622291420808655,0.61116237295891751,0.6719905414941435,0.72990610800961897,0.78462517266948384,null,0.40154966081548882,0.40154966081548882,0.40154966081548882]
["2013-01-20T19:00:00","2013-01-20T19:00:00",null,10.87320838303873,11.17678058469463,11.480352786350529,11.783924988006429,12.087497189662329,12.391069391318229,12.694641592974129,12.998213794630029,13.301785996285929,null,0,6.3540989189001071E-2,0.38270712356136172,0.4597596419755603,0.53201740760634231,0.59911240214796346,0.66199095838662403,0.72185176451817845,0.77844246513297344,null,0.38270712356136172,0.38270712356136172,0.38270712356136172]
["2013-01-20T20:00:00","2013-01-20T20:00:00",null,10.609201548652688,10.912773750308588,11.216345951964488,11.519918153620388,11.823490355276288,12.127062556932188,12.430634758588088,12.734206960243988,13.037779161899888,null,0,4.4635363082460598E-2,0.366304021933885,0.44573288712232056,0.52024082182251286,0.58948083734618872,0.65439926647954827,0.71619479741844605,0.77463610437069996,null,0.366304021933885,0.366304021933885,0.366304021933885]
["2013-01-20T21:00:00","2013-01-20T21:00:00",null,10.552744273395815,10.856316475051717,11.159888676707617,11.463460878363517,11.767033080019417,12.070605281675316,12.374177483331216,12.677749684987116,12.981321886643016,null,0,3.2543333036564301E-2,0.35666194232337467,0.43840406543363386,0.51510959515955856,0.58644205762161128,0.65333727079725645,0.71702546730855543,0.77726480655459051,null,0.35666194232337467,0.35666194232337467,0.35666194232337467]
["2013-01-20T22:00:00","2013-01-20T22:00:00",null,10.306480580598482,10.610052782254382,10.913624983910282,11.217197185566182,11.520769387222082,11.824341588877981,12.127913790533881,12.431485992189781,12.735058193845681,null,0,2.5666648123506754E-2,0.35214057456708303,0.43612235193801691,0.51494135821978959,0.58827163434159901,0.65707002789838098,0.72256677151219662,0.78453053939086381,null,0.35214057456708303,0.35214057456708303,0.35214057456708303]
["2013-01-20T23:00:00","2013-01-20T23:00:00",null,10.205880696278337,10.509452897934237,10.813025099590135,11.116597301246035,11.420169502901935,11.723741704557835,12.027313906213735,12.330886107869635,12.634458309525535,null,0,2.3847586212254527E-2,0.35256116691650552,0.43865642084328732,0.51948375559355242,0.59470669728776293,0.66531363794706155,0.73252429538477382,0.7961178586174531,null,0.35256116691650552,0.35256116691650552,0.35256116691650552]
["2013-01-21","2013-01-21",null,10.23038831668458,10.53396051834048,10.83753271999638,11.14110492165228,11.44467712330818,11.74824932496408,12.05182152661998,12.35539372827588,12.65896592993178,null,0,2.4278693370412569E-2,0.35515832467418934,0.44329345149567018,0.52606602586201423,0.60312905908494807,0.67548145799435,0.74435345521228102,0.80953475456403023,null,0.35515832467418934,0.35515832467418934,0.35515832467418934]
["2013-01-21T01:00:00","2013-01-21T01:00:00",null,10.115710463462378,10.419282665118278,10.722854866774178,11.026427068430078,11.329999270085978,11.633571471741877,11.937143673397777,12.240715875053677,12.544288076709577,null,5.1522562804253791E-4,2.7044088067865374E-2,0.36004771073622566,0.45019116602619885,0.53486692077367959,0.6137279862903946,0.68779429902369305,0.75828557678690067,0.82501255302277754,null,0.36004771073622566,0.36004771073622566,0.36004771073622566]
["2013-01-21T02:00:00","2013-01-21T02:00:00",null,9.9439774585548619,10.247549660210762,10.551121861866662,10.854694063522562,11.158266265178462,11.461838466834362,11.765410668490262,12.068982870146161,12.372555071802061,null,2.7864243149239294E-3,3.1554941015421473E-2,0.36666152543089414,0.4588027943806241,0.5453606998917705,0.62599876808479549,0.70175796502451937,0.773858008524268,0.84210963202680134,null,0.36666152543089414,0.36666152543089414,0.36666152543089414]
["2013-01-21T03:00:00","2013-01-21T03:00:00",null,9.9067004441547937,10.210272645810694,10.513844847466594,10.817417049122493,11.120989250778393,11.424561452434293,11.728133654090193,12.031705855746093,12.335278057401993,null,7.0238922353554143E-3,3.7979489152849856E-2,0.37514697608049269,0.4692334846463016,0.55762096687743579,0.64000449332056408,0.71741451523177113,0.79107075042438302,0.86081547676736614,null,0.37514697608049269,0.37514697608049269,0.37514697608049269]
["2013-01-21T04:00:00","2013-01-21T04:00:00",null,9.9347295583947961,10.238301760050696,10.541873961706596,10.845446163362496,11.149018365018396,11.452590566674296,11.756162768330196,12.059734969986096,12.363307171641996,null,1.3543073651403854E-2,4.6612147124746255E-2,0.3857669329034103,0.48173559223288481,0.57190007714032898,0.65596597298114723,0.73497424582015969,0.81014461347069244,0.8813298686104476,null,0.3857669329034103,0.3857669329034103,0.3857669329034103]
["2013-01-21T05:00:00","2013-01-21T05:00:00",null,9.8358581806964676,10.139430382352367,10.443002584008267,10.746574785664166,11.050146987320066,11.353719188975965,11.657291390631865,11.960863592287765,12.264435793943665,null,1.7917234085397644E-2,5.3183902584472503E-2,0.39441010568404228,0.49232400462959575,0.58433909587449884,0.67015044996542039,0.75080954777591602,0.82755713673678311,0.90023549471698805,null,0.39441010568404228,0.39441010568404228,0.39441010568404228]
["2013-01-21T06:00:00","2013-01-21T06:00:00",null,9.5479127739113352,9.8514849755672351,10.155057177223135,10.458629378879035,10.762201580534935,11.065773782190835,11.369345983846735,11.672918185502635,11.976490387158535,null,2.3016916322145212E-2,6.0523239081894775E-2,0.40385240392857696,0.5037536017251516,0.59764032892498475,0.68521817088348069,0.76755963809166627,0.84589496317160318,0.9200769388009935,null,0.40385240392857696,0.40385240392857696,0.40385240392857696]
["2013-01-21T07:00:00","2013-01-21T07:00:00",null,9.4350837586737732,9.7386559603296732,10.042228161985573,10.345800363641473,10.649372565297373,10.952944766953273,11.256516968609173,11.560089170265073,11.863661371920973,null,2.437332664903271E-2,6.4192907330605911E-2,0.40968812277681388,0.51162919346808755,0.60745064547526406,0.69684754934501225,0.78091344518583006,0.86087856561977905,0.93660621813329692,null,0.40968812277681388,0.40968812277681388,0.40968812277681388]
["2013-01-21T08:00:00","2013-01-21T08:00:00",null,9.342010478446479,9.645582680102379,9.9491548817582789,10.252727083414179,10.556299285070079,10.859871486725979,11.163443688381879,11.467015890037779,11.770588091693678,null,1.5046691300589218E-2,5.7158500286514938E-2,0.4048092515235131,0.50876916549201467,0.60649379788032787,0.69768873404385723,0.78345802889983607,0.86504242987906155,0.942294729659236,null,0.4048092515235131,0.4048092515235131,0.4048092515235131]
["2013-01-21T09:00:00","2013-01-21T09:00:00",null,9.4631660553012527,9.7667382569571526,10.070310458613053,10.373882660268952,10.677454861924852,10.981027063580752,11.284599265236652,11.588171466892552,11.891743668548452,null,2.9441464459573422E-4,4.4761540787287342E-2,0.39463091666748906,0.50067276276563188,0.60036366438749522,0.69340920688848351,0.78093447480330114,0.86419073037148098,0.94302025146198976,null,0.39463091666748906,0.39463091666748906,0.39463091666748906]
["2013-01-21T10:00:00","2013-01-21T10:00:00",null,9.4909735861702114,9.7945457878261113,10.098117989482011,10.401690191137911,10.705262392793811,11.008834594449711,11.312406796105611,11.615978997761511,11.919551199417411,null,0,3.0839934021403257E-2,0.38295947897101523,0.49112531643374158,0.59281403171536173,0.68775223978875111,0.77706502518861431,0.86201416496321959,0.94245245179026937,null,0.38295947897101523,0.38295947897101523,0.38295947897101523]
["2013-01-21T11:00:00","2013-01-21T11:00:00",null,9.592438249859935,9.8960104515158349,10.199582653171735,10.503154854827635,10.806727056483535,11.110299258139435,11.413871459795335,11.717443661451235,12.021015863107134,null,0,1.5162354196680317E-2,0.36956361264190923,0.47988498589542578,0.58360305926300937,0.68046547733500662,0.77158680983738648,0.85826037824462398,0.94033897523442145,null,0.36956361264190923,0.36956361264190923,0.36956361264190923]
["2013-01-21T12:00:00","2013-01-21T12:00:00",null,9.7862547884339754,10.089826990089875,10.393399191745777,10.696971393401677,11.000543595057577,11.304115796713477,11.607687998369377,11.911260200025277,12.214832401681177,null,0,0,0.35326565910178814,0.46578462738103715,0.5715741180695264,0.6704028053750738,0.76337474421491258,0.85181480048972447,0.93557576687721189,null,0.35326565910178814,0.35326565910178814,0.35326565910178814]
["2013-01-21T13:00:00","2013-01-21T13:00:00",null,9.9694071032088036,10.272979304864704,10.576551506520603,10.880123708176503,11.183695909832403,11.487268111488303,11.790840313144203,12.094412514800103,12.397984716456003,null,0,0,0.33471753649225677,0.44946564422344493,0.55734758185031097,0.65816356800687958,0.75302817241911957,0.84325574617897703,0.92872011158162548,null,0.33471753649225677,0.33471753649225677,0.33471753649225677]
["2013-01-21T14:00:00","2013-01-21T14:00:00",null,10.173899930895134,10.477472132551034,10.781044334206936,11.084616535862835,11.388188737518735,11.691760939174635,11.995333140830535,12.298905342486435,12.602477544142335,null,0,0,0.31290982317470117,0.42992912959277074,0.53995608820169139,0.64281194725295909,0.73960076166380695,0.83166842695238774,0.9188782506051395,null,0.31290982317470117,0.31290982317470117,0.31290982317470117]
["2013-01-21T15:00:00","2013-01-21T15:00:00",null,10.484480193833324,10.788052395489224,11.091624597145124,11.395196798801024,11.698769000456924,12.002341202112824,12.305913403768724,12.609485605424624,12.913057807080524,null,0,0,0.28294261827834949,0.40239084551433385,0.51472054723634264,0.61975297169587162,0.71861320342762525,0.81265765275849167,0.90174962717490903,null,0.28294261827834949,0.28294261827834949,0.28294261827834949]
["2013-01-21T16:00:00","2013-01-21T16:00:00",null,10.488907727146703,10.792479928802603,11.096052130458503,11.399624332114403,11.703196533770303,12.006768735426203,12.310340937082103,12.613913138738003,12.917485340393903,null,0,0,0.25272305797234429,0.3746002060262435,0.48923265086134038,0.59645215553786624,0.69739431939926111,0.79341555277241316,0.88438967795249612,null,0.25272305797234429,0.25272305797234429,0.25272305797234429]
["2013-01-21T17:00:00","2013-01-21T17:00:00",null,10.453748195126707,10.757320396782607,11.060892598438507,11.364464800094407,11.668037001750307,11.971609203406206,12.275181405062106,12.578753606718006,12.882325808373906,null,0,0,0.25462623835348103,0.37890076279908835,0.49579389151233105,0.60516893197964716,0.70816148354447661,0.80612795653370761,0.8989526880512495,null,0.25462623835348103,0.25462623835348103,0.25462623835348103]
["2013-01-21T18:00:00","2013-01-21T18:00:00",null,10.215435956387697,10.519008158043597,10.822580359699497,11.126152561355397,11.429724763011297,11.733296964667197,12.036869166323097,12.340441367978997,12.644013569634897,null,3.6812345383202556E-2,3.9514651228241986E-2,0.29668547329572903,0.42336788894178001,0.54254273115063967,0.65408382221748163,0.75912676148574565,0.8590489888997912,0.9537348415635275,null,0.29668547329572903,0.29668547329572903,0.29668547329572903]
["2013-01-21T19:00:00","2013-01-21T19:00:00",null,9.9342311997251453,10.237803401381045,10.541375603036945,10.844947804692845,11.148520006348745,11.452092208004645,11.755664409660545,12.059236611316445,12.362808812972345,null,8.0879908793942884E-2,8.6137313161723877E-2,0.34572654123839019,0.47468015557132254,0.59601053357097245,0.70959149753251338,0.81656916160812087,0.91832096574215416,1,null,0.34572654123839019,0.34572654123839019,0.34572654123839019]
["2013-01-21T20:00:00","2013-01-21T20:00:00",null,9.8045518458077119,10.108124047463612,10.41169624911951,10.71526845077541,11.01884065243131,11.32241285408721,11.62598505574311,11.92955725739901,12.23312945905491,null,0.12817551848650074,0.1359354473333455,0.39786947775804216,0.5290417167341781,0.6524645416722048,0.76803280448476696,0.87689261932404006,0.98042142613438332,1,null,0.39786947775804216,0.39786947775804216,0.39786947775804216]
["2013-01-21T21:00:00","2013-01-21T21:00:00",null,9.7067167180393188,10.010288919695219,10.313861121351119,10.617433323007019,10.921005524662919,11.224577726318818,11.528149927974718,11.831722129630618,12.135294331286518,null,0.17698526063697953,0.18721616953668135,0.45148448750067277,0.58485432150254124,0.71034856376147359,0.8278725809988503,0.93859351698431781,1,1,null,0.45148448750067277,0.45148448750067277,0.45148448750067277]
["2013-01-21T22:00:00","2013-01-21T22:00:00",null,9.495379991712884,9.798952193368784,10.102524395024684,10.406096596680584,10.709668798336484,11.013240999992384,11.316813201648284,11.620385403304184,11.923957604960084,null,0.22836061611893543,0.24099941621908097,0.50752841806121818,0.64302224342767023,0.77052481415509488,0.88994149696487279,1,1,1,null,0.50752841806121818,0.50752841806121818,0.50752841806121818]
["2013-01-21T23:00:00","2013-01-21T23:00:00",null,9.4325989407244926,9.7361711423803925,10.039743344036292,10.343315545692192,10.646887747348092,10.950459949003992,11.254032150659892,11.557604352315792,11.861176553971692,null,0.27987266411445366,0.29481420732768726,0.56351977457808577,0.70105347283923691,0.83048025356526944,0.95171599828629949,1,1,1,null,0.56351977457808577,0.56351977457808577,0.56351977457808577]
["2013-01-22","2013-01-22",null,9.3711207306717164,9.6746929323276163,9.9782651339835162,10.281837335639416,10.585409537295316,10.888981738951216,11.192553940607116,11.496126142263016,11.799698343918916,null,0.33140574172744303,0.34855539477514463,0.6193428941551844,0.75882183203241449,0.89008870428717035,1,1,1,1,null,0.6193428941551844,0.6193428941551844,0.6193428941551844]
["2013-01-22T01:00:00","2013-01-22T01:00:00",null,9.2573801779540954,9.5609523796099953,9.8645245812658953,10.168096782921795,10.471668984577695,10.775241186233595,11.078813387889495,11.382385589545395,11.685957791201295,null,0.38567266961167851,0.40496734364143477,0.67777368629870238,0.81915580455706927,0.95221019429687059,1,1,1,1,null,0.67777368629870238,0.67777368629870238,0.67777368629870238]
["2013-01-22T02:00:00","2013-01-22T02:00:00",null,9.1811349753273479,9.4847071769832478,9.7882793786391478,10.091851580295049,10.395423781950949,10.698995983606849,11.002568185262749,11.306140386918649,11.609712588574549,null,0.44037070465407202,0.46182091447461848,0.73664610040911405,0.87992088423988202,1,1,1,1,1,null,0.73664610040911405,0.73664610040911405,0.73664610040911405]
["2013-01-22T03:00:00","2013-01-22T03:00:00",null,9.2185532013315559,9.5221254029874558,9.8256976046433557,10.129269806299256,10.432842007955156,10.736414209611056,11.039986411266955,11.343558612922855,11.647130814578755,null,0.49685625718151105,0.52039891394043436,0.79717985429974447,0.94229472965923577,1,1,1,1,1,null,0.79717985429974447,0.79717985429974447,0.79717985429974447]
["2013-01-22T04:00:00","2013-01-22T04:00:00",null,9.166943837354415,9.4705160390103149,9.7740882406662148,10.077660442322115,10.381232643978015,10.684804845633915,10.988377047289815,11.291949248945715,11.595521450601614,null,0.55241650654022068,0.57808315466372751,0.85686190868279433,1,1,1,1,1,1,null,0.85686190868279433,0.85686190868279433,0.85686190868279433]
["2013-01-22T05:00:00","2013-01-22T05:00:00",null,9.1212623008376212,9.4248345024935212,9.7284067041494211,10.031978905805321,10.335551107461221,10.639123309117121,10.942695510773021,11.246267712428921,11.549839914084821,null,0.57086999587113196,0.59872372421163567,0.87954235112540158,1,1,1,1,1,1,null,0.87954235112540158,0.87954235112540158,0.87954235112540158]
["2013-01-22T06:00:00","2013-01-22T06:00:00",null,9.2775081155638883,9.5810803172197883,9.8846525188756882,10.188224720531588,10.491796922187488,10.795369123843388,11.098941325499288,11.402513527155188,11.706085728811088,null,0.56289977084957599,0.59294057940707656,0.87580959402427705,0.99820196770621894,1,1,1,1,1,null,0.87580959402427705,0.87580959402427705,0.87580959402427705]
["2013-01-22T07:00:00","2013-01-22T07:00:00",null,9.2314114534920062,9.5349836551479061,9.8385558568038061,10.142128058459708,10.445700260115608,10.749272461771508,11.052844663427408,11.356416865083307,11.659989066739207,null,0.55351004664871917,0.58579050946689437,0.8707624858312073,0.99512112874669922,0.99878028218667481,1,1,1,1,null,0.8707624858312073,0.8707624858312073,0.8707624858312073]
["2013-01-22T08:00:00","2013-01-22T08:00:00",null,9.4050841086749948,9.7086563103308947,10.012228511986795,10.315800713642695,10.619372915298595,10.922945116954494,11.226517318610394,11.530089520266294,11.833661721922194,null,0.54204890512695658,0.57659005182327761,0.86369653436090965,0.99005299093615839,0.99560480994853506,0.99860153043817024,1,1,1,null,0.86369653436090965,0.86369653436090965,0.86369653436090965]
["2013-01-22T09:00:00","2013-01-22T09:00:00",null,9.6014979687083581,9.9050701703642581,10.20864237202016,10.51221457367606,10.81578677533196,11.11935897698786,11.42293117864376,11.726503380299659,12.030075581955559,null,0.52338511962133405,0.56036570194430546,0.84976441278629,0.97828691996106454,0.98587861186814019,0.99081005716511883,0.99403810344693633,0.99576253207956855,0.99741335705105172,null,0.84976441278629,0.84976441278629,0.84976441278629]
["2013-01-22T10:00:00","2013-01-22T10:00:00",null,10.142317834623274,10.445890036279174,10.749462237935074,11.053034439590974,11.356606641246874,11.660178842902774,11.963751044558673,12.267323246214573,12.570895447870473,null,0.49459557330336529,0.53418382819275612,0.82604300427886213,0.95689979899293143,0.96668908592573954,0.97371297816109503,0.97891780848519816,0.98252438788149599,0.98597324514676021,null,0.82604300427886213,0.82604300427886213,0.82604300427886213]
["2013-01-22T11:00:00","2013-01-22T11:00:00",null,10.452458850346961,10.756031052002861,11.059603253658761,11.363175455314661,11.666747656970561,11.970319858626461,12.27389206028236,12.57746426193826,12.88103646359416,null,0.46452322031965798,0.50668760334926144,0.80097570025328235,0.93413523808043974,0.94610109042150914,0.95519639997777039,0.96236749953542355,0.96784571488665139,0.97307157482822559,null,0.80097570025328235,0.80097570025328235,0.80097570025328235]
["2013-01-22T12:00:00","2013-01-22T12:00:00",null,10.812619564419039,11.116191766074939,11.419763967730839,11.723336169386739,12.026908371042639,12.330480572698539,12.634052774354439,12.937624976010339,13.241197177666239,null,0.43077068427850396,0.4755217102570557,0.77225975759646248,0.90774306815417916,0.9219170303297165,0.9331047868243546,0.94227370004176458,0.9496550957741291,0.95668950281821996,null,0.77225975759646248,0.77225975759646248,0.77225975759646248]
["2013-01-22T13:00:00","2013-01-22T13:00:00",null,10.936143763825818,11.239715965481718,11.543288167137618,11.846860368793518,12.150432570449418,12.454004772105318,12.757576973761218,13.061149175417118,13.364721377073018,null,0.39452613856702173,0.44190586672946397,0.74112540893046341,0.87897455145368153,0.89538816788989362,0.90871043055785072,0.9199087018612242,0.92922482240093218,0.93810983578248186,null,0.74112540893046341,0.74112540893046341,0.74112540893046341]
["2013-01-22T14:00:00","2013-01-22T14:00:00",null,11.056615411109718,11.360187612765618,11.663759814421518,11.967332016077417,12.270904217733317,12.574476419389217,12.878048621045117,13.181620822701017,13.485193024356917,null,0.35615760149095599,0.4061975762634954,0.70793015775229418,0.84817667666722041,0.86686149179031391,0.88234980505779681,0.89560897887334046,0.90689136864659847,0.91764801798307816,null,0.70793015775229418,0.70793015775229418,0.70793015775229418]
["2013-01-22T15:00:00","2013-01-22T15:00:00",null,11.248856896870363,11.552429098526263,11.856001300182163,12.159573501838063,12.463145703493963,12.766717905149862,13.070290106805762,13.373862308461662,13.677434510117562,null,0.31550735091927329,0.36821808711064546,0.67248473750471471,0.81512863281134906,0.83610567623879506,0.85378106972327483,0.86911166085972424,0.88238134948400349,0.89503066439288426,null,0.67248473750471471,0.67248473750471471,0.67248473750471471]
["2013-01-22T16:00:00","2013-01-22T16:00:00",null,11.354425085505373,11.657997287161272,11.961569488817172,12.265141690473072,12.568713892128972,12.872286093784872,13.175858295440772,13.479430497096672,13.783002698752572,null,0.27338502712461193,0.32877703954355242,0.63558827365162762,0.78066108977617688,0.80394087631671085,0.82381386482692309,0.84123690290174935,0.85650440518578541,0.87106741528453846,null,0.63558827365162762,0.63558827365162762,0.63558827365162762]
["2013-01-22T17:00:00","2013-01-22T17:00:00",null,11.329536278264566,11.633108479920466,11.936680681576366,12.240252883232266,12.543825084888166,12.847397286544066,13.150969488199966,13.454541689855866,13.758113891511766,null,0.2324403619083335,0.29049262093737116,0.59982740914198129,0.74729760165823866,0.77286961650312513,0.79490865561286317,0.81441362581733068,0.83165791214365237,0.84812410262354221,null,0.59982740914198129,0.59982740914198129,0.59982740914198129]
["2013-01-22T18:00:00","2013-01-22T18:00:00",null,11.091963012880774,11.395535214536674,11.699107416192573,12.002679617848473,12.306251819504373,12.609824021160273,12.913396222816173,13.216968424472073,13.520540626127973,null,0.19571213499501544,0.25637206659047246,0.56816732003920412,0.71798231490349185,0.74578346920031746,0.76994649967463902,0.79147031315633443,0.81063880948126399,0.82894509148987716,null,0.56816732003920412,0.56816732003920412,0.56816732003920412]
["2013-01-22T19:00:00","2013-01-22T19:00:00",null,10.879385810311302,11.182958011967202,11.486530213623102,11.790102415279001,12.093674616934901,12.397246818590801,12.700819020246701,13.004391221902601,13.307963423558501,null,0.16227504321592828,0.22550058814286245,0.53971424760077336,0.69184250038688477,0.72183073490070726,0.74806518269593447,0.7715762950286511,0.79263745692598186,0.8127417712283761,null,0.53971424760077336,0.53971424760077336,0.53971424760077336]
["2013-01-22T20:00:00","2013-01-22T20:00:00",null,10.754621322849273,11.058193524505173,11.361765726161073,11.665337927816973,11.968910129472873,12.272482331128773,12.576054532784672,12.879626734440572,13.183198936096472,null,0.1313930499595827,0.19714214898305174,0.51374267002393526,0.66814212149692809,0.70027537699280518,0.72854969768273137,0.75400604963152695,0.77691781786631664,0.79878862003628537,null,0.51374267002393526,0.51374267002393526,0.51374267002393526]
["2013-01-22T21:00:00","2013-01-22T21:00:00",null,10.689205418532714,10.992777620188614,11.296349821844514,11.599922023500413,11.903494225156313,12.207066426812213,12.510638628468113,12.814210830124013,13.117783031779913,null,0.10366549932390572,0.1718645487827607,0.49077832774546787,0.64737537424419311,0.68159056186971145,0.71185218141065887,0.73919068412312006,0.76388996984295532,0.78747468583682068,null,0.49077832774546787,0.49077832774546787,0.49077832774546787]
["2013-01-22T22:00:00","2013-01-22T22:00:00",null,10.611147846952097,10.914720048607997,11.218292250263897,11.521864451919797,11.825436653575697,12.129008855231596,12.432581056887496,12.736153258543396,13.039725460199296,null,7.978636868544442E-2,0.15034073530106529,0.47149416852444714,0.63020469157902037,0.66641769286429553,0.69858249278637963,0.72772954260135747,0.75416377176256044,0.77938879791917348,null,0.47149416852444714,0.47149416852444714,0.47149416852444714]
["2013-01-22T23:00:00","2013-01-22T23:00:00",null,10.534284798769853,10.837857000425753,11.141429202081653,11.445001403737553,11.748573605393453,12.052145807049353,12.355718008705253,12.659290210361153,12.962862412017053,null,5.9881835749025558E-2,0.13269688624279224,0.45599534044822876,0.61673522158876548,0.6548724328726484,0.68886680951472035,0.7197488027710659,0.74783385690375215,0.77463610437069941,null,0.45599534044822876,0.45599534044822876,0.45599534044822876]
["2013-01-23","2013-01-23",null,10.535918155953381,10.83949035760928,11.14306255926518,11.44663476092108,11.75020696257698,12.05377916423288,12.35735136588878,12.66092356754468,12.96449576920058,null,3.9966788003871136E-2,0.11504252237578365,0.44048599756327483,0.603255236789775,0.64332717288100127,0.67914061143432547,0.71176806294077433,0.74150394204494385,0.76988341082222533,null,0.44048599756327483,0.44048599756327483,0.44048599756327483]
["2013-01-23T01:00:00","2013-01-23T01:00:00",null,10.501125897632239,10.804698099288139,11.108270300944039,11.411842502599939,11.715414704255839,12.018986905911738,12.322559107567638,12.626131309223538,12.929703510879438,null,1.8232678347464486E-2,9.5632185449936208E-2,0.42327325566315982,0.58812442701930123,0.63017314715281325,0.66785822166106745,0.70227319065256189,0.73370195396315685,0.76370070328571493,null,0.42327325566315982,0.42327325566315982,0.42327325566315982]
["2013-01-23T02:00:00","2013-01-23T02:00:00",null,10.493767907083553,10.797340108739453,11.100912310395353,11.404484512051253,11.708056713707153,12.011628915363053,12.315201117018953,12.618773318674853,12.922345520330753,null,0,7.653729278615562E-2,0.40636544321637613,0.57329854670215885,0.6173135360692209,0.65685973172366963,0.69305170339147404,0.72617335090849444,0.75778086596759353,null,0.40636544321637613,0.40636544321637613,0.40636544321637613]
["2013-01-23T03:00:00","2013-01-23T03:00:00",null,10.476210311440074,10.779782513095974,11.083354714751874,11.386926916407774,11.690499118063673,11.994071319719573,12.297643521375473,12.601215723031373,12.904787924687273,null,0,5.8262555203748873E-2,0.39026727104223069,0.55925076223144798,0.60521099121458899,0.64660779320649664,0.68455573793313995,0.71934924003911471,0.75255500602601921,null,0.39026727104223069,0.39026727104223069,0.39026727104223069]
["2013-01-23T04:00:00","2013-01-23T04:00:00",null,10.471587059780653,10.775159261436553,11.078731463092453,11.382303664748353,11.685875866404253,11.989448068060153,12.293020269716052,12.596592471371952,12.900164673027852,null,0,4.0292747074673417E-2,0.37446351351268103,0.5454973924053329,0.59340286100455286,0.63663975452518384,0.67634367231066606,0.71280902900559517,0.74760253111156949,null,0.37446351351268103,0.37446351351268103,0.37446351351268103]
["2013-01-23T05:00:00","2013-01-23T05:00:00",null,10.617421624587273,10.920993826243173,11.224566027899074,11.528138229554974,11.831710431210874,12.135282632866774,12.438854834522674,12.742427036178574,13.045999237834474,null,0,1.8611211461944579E-2,0.35501111735189134,0.52816898760912678,0.57808278467683905,0.6232333733873423,0.66475635308407677,0.702946138411638,0.73939046548909559,null,0.35501111735189134,0.35501111735189134,0.35501111735189134]
["2013-01-23T06:00:00","2013-01-23T06:00:00",null,10.517970692064804,10.821542893720704,11.125115095376604,11.428687297032504,11.732259498688403,12.035831700344303,12.339403902000203,12.642976103656103,12.946548305312003,null,0,0,0.3335293631051382,0.50887431357937052,0.56087004277672403,0.60798690072077743,0.6513920311811775,0.6913693339937842,0.72950654527766734,null,0.3335293631051382,0.3335293631051382,0.3335293631051382]
["2013-01-23T07:00:00","2013-01-23T07:00:00",null,10.477954322580592,10.781526524236492,11.085098725892392,11.388670927548292,11.692243129204192,11.995815330860092,12.299387532515992,12.602959734171892,12.906531935827791,null,0,0,0.31403490770940623,0.49152487916569321,0.54556048125774581,0.59461206400914257,0.63984677118953037,0.68156953225224037,0.72137859812507787,null,0.31403490770940623,0.31403490770940623,0.31403490770940623]
["2013-01-23T08:00:00","2013-01-23T08:00:00",null,10.493087753811938,10.796659955467838,11.100232157123738,11.403804358779638,11.707376560435538,12.010948762091438,12.314520963747338,12.618093165403238,12.921665367059138,null,0,0,0.2938149305109205,0.47347095256673327,0.5295569423622204,0.58055376472969622,0.62763907824754295,0.67111781236909174,0.71260924763961919,null,0.2938149305109205,0.2938149305109205,0.2938149305109205]
["2013-01-23T09:00:00","2013-01-23T09:00:00",null,10.887188689352518,11.190760891008416,11.494333092664316,11.797905294320216,12.101477495976116,12.405049697632016,12.708621899287916,13.012194100943816,13.315766302599716,null,0,0,0.2715445656090002,0.45334560864686763,0.51146095652831824,0.56439250370313743,0.61332842355844308,0.65856313073883066,0.70172642059831247,null,0.2715445656090002,0.2715445656090002,0.2715445656090002]
["2013-01-23T10:00:00","2013-01-23T10:00:00",null,11.240860150054921,11.544432351710821,11.848004553366721,12.151576755022621,12.455148956678521,12.758721158334421,13.062293359990321,13.365865561646221,13.66943776330212,null,0,0,0.24278656371723814,0.42682726101578028,0.48707711507054996,0.54203802033133264,0.59290866499398165,0.63999397851182815,0.68492375623888435,null,0.24278656371723814,0.24278656371723814,0.24278656371723814]
["2013-01-23T11:00:00","2013-01-23T11:00:00",null,11.605782523190728,11.909354724846628,12.212926926502528,12.516499128158427,12.820071329814327,13.123643531470227,13.427215733126127,13.730787934782027,14.034360136437927,null,0,0,0.20753041002689876,0.39390539486473564,0.45638438837144446,0.51345877018807518,0.56635877293668757,0.61537881126187755,0.66215919532639267,null,0.20753041002689876,0.20753041002689876,0.20753041002689876]
["2013-01-23T12:00:00","2013-01-23T12:00:00",null,11.780522424002474,12.084094625658373,12.387666827314273,12.691239028970173,12.994811230626073,13.298383432281973,13.601955633937873,13.905527835593773,14.209100037249673,null,0,0,0.16490337541293043,0.35374934030362437,0.41859416577583464,0.47791871666187563,0.53297425520127828,0.58405519603863831,0.63281236414543918,null,0.16490337541293043,0.16490337541293043,0.16490337541293043]
["2013-01-23T13:00:00","2013-01-23T13:00:00",null,11.956121800373115,12.259694002029015,12.563266203684915,12.866838405340815,13.170410606996715,13.473982808652615,13.777555010308514,14.081127211964414,14.384699413620314,null,0,0,0.11814402096588622,0.30952405476185063,0.37679780105197569,0.43843560985984031,0.49570977304244657,0.54890419043565453,0.59969071662841889,null,0.11814402096588622,0.11814402096588622,0.11814402096588622]
["2013-01-23T14:00:00","2013-01-23T14:00:00",null,11.891588422675985,12.195160624331885,12.498732825987785,12.802305027643685,13.105877229299585,13.409449430955485,13.713021632611385,14.016593834267285,14.320166035923185,null,0,0,5.7326367239395624E-2,0.25113532185327486,0.32071181125648801,0.38455772989882064,0.44393485482853928,0.49914811549897514,0.55186936649908291,null,5.7326367239395624E-2,5.7326367239395624E-2,5.7326367239395624E-2]
["2013-01-23T15:00:00","2013-01-23T15:00:00",null,12.227596218438407,12.531168420094307,12.834740621750207,13.138312823406107,13.441885025062007,13.745457226717907,14.049029428373807,14.352601630029707,14.656173831685607,null,1.9967621788832234E-2,2.2827649764905096E-2,8.2887867275546839E-2,0.27930449445584543,0.35136247872065124,0.41758474413722091,0.47923306775382091,0.53662289383251816,0.59143659177100272,null,8.2887867275546839E-2,8.2887867275546839E-2,8.2887867275546839E-2]
["2013-01-23T16:00:00","2013-01-23T16:00:00",null,12.234189145753893,12.537761347409793,12.841333549065693,13.144905750721593,13.448477952377493,13.752050154033393,14.055622355689293,14.359194557345193,14.662766759001093,null,3.8736555381810395E-2,4.4467126142691688E-2,0.10726119392457956,0.30628549367129754,0.38083548760643154,0.44944461460597374,0.51336413690945515,0.57294104320514927,0.62984718808201068,null,0.10726119392457956,0.10726119392457956,0.10726119392457956]
["2013-01-23T17:00:00","2013-01-23T17:00:00",null,12.083253204651852,12.386825406307752,12.690397607963652,12.993969809619552,13.297542011275452,13.601114212931352,13.904686414587252,14.208258616243151,14.511830817899051,null,5.3310080289299323E-2,6.1869134600046796E-2,0.12735499341823853,0.32894490649643365,0.40594485086695359,0.47689878021452609,0.54305795677868218,0.60477988405643102,0.663736416636727,null,0.12735499341823853,0.12735499341823853,0.12735499341823853]
["2013-01-23T18:00:00","2013-01-23T18:00:00",null,11.793450257772493,12.097022459428393,12.400594661084293,12.704166862740193,13.007739064396093,13.311311266051993,13.614883467707893,13.918455669363793,14.222027871019693,null,7.7136636884082815E-2,8.8282334143778535E-2,0.15622865820609178,0.36016337363231721,0.43940297226351188,0.5124808929756679,0.58067994243452303,0.64434710932835082,0.70517527786357681,null,0.15622865820609178,0.15622865820609178,0.15622865820609178]
["2013-01-23T19:00:00","2013-01-23T19:00:00",null,11.639892207717267,11.943464409373167,12.247036611029067,12.550608812684967,12.854181014340867,13.157753215996767,13.461325417652667,13.764897619308567,14.068469820964467,null,0.10265607768529178,0.11633584385025794,0.18667954430427933,0.39290648803485728,0.47432265207431329,0.54948250491611061,0.61966885322598697,0.68523920050095144,0.74787591613869409,null,0.18667954430427933,0.18667954430427933,0.18667954430427933]
["2013-01-23T20:00:00","2013-01-23T20:00:00",null,11.532124923359984,11.835697125015884,12.139269326671783,12.442841528327683,12.746413729983583,13.049985931639483,13.353558133295383,13.657130334951283,13.960702536607183,null,0.12842787389615423,0.1446206793489197,0.21735124138591366,0.42584938380337301,0.50943159844235475,0.5866523537963223,0.65880497133974869,0.72625746937837876,0.79069221730990258,null,0.21735124138591366,0.21735124138591366,0.21735124138591366]
["2013-01-23T21:00:00","2013-01-23T21:00:00",null,11.398094369769726,11.701666571425626,12.005238773081526,12.308810974737426,12.612383176393326,12.915955378049226,13.219527579705126,13.523099781361026,13.826671983016926,null,0.15527218059804401,0.17392545129493098,0.24900081567995527,0.45972809754935373,0.545434303552919,0.62467390218411445,0.69876124453488431,0.76805383410223771,0.83424455509260032,null,0.24900081567995527,0.24900081567995527,0.24900081567995527]
["2013-01-23T22:00:00","2013-01-23T22:00:00",null,11.314866234506695,11.618438436162595,11.922010637818495,12.225582839474395,12.529155041130295,12.832727242786195,13.136299444442095,13.439871646097995,13.743443847753895,null,0.18263171292797634,0.20375596367772036,0.28117613041077499,0.49414306654084816,0.58196274910026136,0.6632317058174203,0.73924325816679803,0.81037593926287477,0.87833314812081176,null,0.28117613041077499,0.28117613041077499,0.28117613041077499]
["2013-01-23T23:00:00","2013-01-23T23:00:00",null,11.314096069293985,11.617668270949885,11.921240472605785,12.224812674261685,12.528384875917585,12.831957077573485,13.135529279229385,13.439101480885284,13.742673682541184,null,0.20991764159675971,0.2335128723993608,0.31328835628918134,0.52848443187119365,0.61841759098645477,0.70171590578957721,0.77965166813756281,0.85262444076236288,0.92233762267913877,null,0.31328835628918134,0.31328835628918134,0.31328835628918134]
["2013-01-24","2013-01-24",null,11.296287357763678,11.599859559419578,11.903431761075478,12.207003962731378,12.510576164387277,12.814148366043177,13.117720567699077,13.421292769354977,13.724864971010877,null,0.23810784381680142,0.26415302505478844,0.34626279648390379,0.56366698190038411,0.65571361757149316,0.74100974603437242,0.8208592035722303,0.8956615529170181,0.96712019308389729,null,0.34626279648390379,0.34626279648390379,0.34626279648390379]
["2013-01-24T01:00:00","2013-01-24T01:00:00",null,11.238897384127458,11.542469585783358,11.846041787439258,12.149613989095158,12.453186190751058,12.756758392406958,13.060330594062858,13.363902795718758,13.667474997374658,null,0.26900035188188254,0.2974429095115777,0.38182387962757447,0.60138360083484499,0.6954911390181242,0.78274302190581801,0.86445360058987031,0.94104346741970368,1,null,0.38182387962757447,0.38182387962757447,0.38182387962757447]
["2013-01-24T02:00:00","2013-01-24T02:00:00",null,11.124874637736948,11.428446839392848,11.732019041048748,12.035591242704648,12.339163444360548,12.642735646016448,12.946307847672347,13.249880049328247,13.553452250984147,null,0.3018275847543071,0.3326359743495037,0.41926711353491075,0.64095082610676479,0.7370877223760075,0.82626381526230908,0.90981448547508481,0.98816032536375698,1,null,0.41926711353491075,0.41926711353491075,0.41926711353491075]
["2013-01-24T03:00:00","2013-01-24T03:00:00",null,10.881909341734229,11.185481543390129,11.489053745046029,11.792625946701929,12.096198148357828,12.399770350013728,12.703342551669628,13.006914753325528,13.310486954981428,null,0.33604277237982583,0.36923802355799501,0.45811933181281234,0.68193755055798544,0.78011431972192724,0.87121462260683658,0.95660538434833575,1,1,null,0.45811933181281234,0.45811933181281234,0.45811933181281234]
["2013-01-24T04:00:00","2013-01-24T04:00:00",null,10.895671845865632,11.199244047521532,11.50281624917743,11.80638845083333,12.10996065248923,12.41353285414513,12.71710505580103,13.02067725745693,13.32424945911283,null,0.37317056202509524,0.40866855631635252,0.49972642997943117,0.72561606604550999,0.82575910444300182,0.91872052847410568,1,1,1,null,0.49972642997943117,0.49972642997943117,0.49972642997943117]
["2013-01-24T05:00:00","2013-01-24T05:00:00",null,10.888835370210934,11.192407571866834,11.495979773522734,11.799551975178634,12.103124176834534,12.406696378490434,12.710268580146334,13.013840781802234,13.317412983458134,null,0.40715442385843159,0.44503927973266144,0.53835783727388598,0.76639249432201939,0.86857540561421032,0.96347155445265753,1,1,1,null,0.53835783727388598,0.53835783727388598,0.53835783727388598]
["2013-01-24T06:00:00","2013-01-24T06:00:00",null,10.856652751711948,11.160224953367848,11.463797155023748,11.767369356679648,12.070941558335548,12.374513759991448,12.678085961647348,12.981658163303248,13.285230364959148,null,0.43919304607568899,0.47951733757656922,0.57514915303961744,0.80538140511348333,0.90965676334405099,1,1,1,1,null,0.57514915303961744,0.57514915303961744,0.57514915303961744]
["2013-01-24T07:00:00","2013-01-24T07:00:00",null,10.789666251902126,11.093238453558026,11.396810655213926,11.700382856869826,12.003955058525726,12.307527260181626,12.611099461837526,12.914671663493426,13.218243865149326,null,0.47111600539685522,0.51391127695059247,0.61187737995293545,0.844328256670005,0.9506960618389495,1,1,1,1,null,0.61187737995293545,0.61187737995293545,0.61187737995293545]
["2013-01-24T08:00:00","2013-01-24T08:00:00",null,10.765323006783809,11.068895208439711,11.372467410095611,11.676039611751511,11.979611813407411,12.283184015063311,12.586756216719211,12.890328418375111,13.193900620031011,null,0.50064158832631334,0.54597092878532094,0.64633440817937216,0.8810669983920586,0.9895903393517933,1,1,1,1,null,0.64633440817937216,0.64633440817937216,0.64633440817937216]
["2013-01-24T09:00:00","2013-01-24T09:00:00",null,11.20785909599693,11.51143129765283,11.81500349930873,12.11857570096463,12.42214790262053,12.72572010427643,13.02929230593233,13.33286450758823,13.63643670924413,null,0.52865303879785053,0.57652696297086414,0.67929833356535907,0.91632315208239801,1,1,1,1,1,null,0.67929833356535907,0.67929833356535907,0.67929833356535907]
["2013-01-24T10:00:00","2013-01-24T10:00:00",null,11.640349041060608,11.943921242716508,12.247493444372408,12.551065646028308,12.854637847684208,13.158210049340108,13.461782250996007,13.765354452651907,14.068926654307807,null,0.4945745436858941,0.54506665523406261,0.6503195206901502,0.88971017117269058,0.9756371881597028,0.97778220914175751,0.97983259684519208,0.98178835127000663,0.98367050203367223,null,0.6503195206901502,0.6503195206901502,0.6503195206901502]
["2013-01-24T11:00:00","2013-01-24T11:00:00",null,11.860549329491965,12.164121531147865,12.467693732803765,12.771265934459665,13.074838136115565,13.378410337771465,13.681982539427365,13.985554741083265,14.289126942739165,null,0.45054903951009601,0.50384860499065953,0.61176171705684435,0.85369695125339073,0.94204237424958226,0.94650065315346055,0.95075915069136319,0.95482838167202566,0.95873989052165476,null,0.61176171705684435,0.61176171705684435,0.61176171705684435]
["2013-01-24T12:00:00","2013-01-24T12:00:00",null,12.071602178782515,12.375174380438414,12.678746582094314,12.982318783750214,13.285890985406114,13.589463187062014,13.893035388717914,14.196607590373814,14.500179792029714,null,0.40220194894398192,0.458393086826825,0.56906107878172707,0.81362501516216401,0.90448347744615476,0.91133913274174128,0.91788985858399641,0.92414616978165576,0.9301606403783973,null,0.56906107878172707,0.56906107878172707,0.56906107878172707]
["2013-01-24T13:00:00","2013-01-24T13:00:00",null,12.388797350215862,12.692369551871762,12.995941753527662,13.299513955183562,13.603086156839462,13.906658358495362,14.210230560151262,14.513802761807161,14.817374963463061,null,0.34138429521749131,0.40048803512008507,0.51393193658117553,0.7611456047629741,0.85453813595223527,0.86381219725700109,0.8726866958298154,0.88116163167067829,0.88930009363200335,null,0.51393193658117553,0.51393193658117553,0.51393193658117553]
["2013-01-24T14:00:00","2013-01-24T14:00:00",null,12.616054857973877,12.919627059629777,13.223199261285677,13.526771462941577,13.830343664597477,14.133915866253377,14.437488067909277,14.741060269565176,15.044632471221076,null,0.27768558389745673,0.33972295543727227,0.45596379602202225,0.70584822562265359,0.80179585533465625,0.81350935226607246,0.82472865318691713,0.83544324328845476,0.84573724104057002,null,0.45596379602202225,0.45596379602202225,0.45596379602202225]
["2013-01-24T15:00:00","2013-01-24T15:00:00",null,12.806574125772451,13.110146327428351,13.413718529084251,13.717290730740151,14.020862932396051,14.324435134051951,14.628007335707851,14.931579537363751,15.235151739019651,null,0.20961271214342836,0.27463628936414353,0.39373715792496633,0.64634492298810819,0.74490022526653032,0.75911624667701028,0.77273292398956306,0.78573974239545319,0.79824184998203651,null,0.39373715792496633,0.39373715792496633,0.39373715792496633]
["2013-01-24T16:00:00","2013-01-24T16:00:00",null,12.858472791405838,13.162044993061738,13.465617194717638,13.769189396373537,14.072761598029437,14.376333799685337,14.679906001341237,14.983478202997137,15.287050404653037,null,0.13956305634711433,0.20760438367493578,0.32959682463803813,0.5849594695898972,0.68615398886094547,0.70290407917669584,0.71893916249842793,0.73428026844361272,0.74901151548213529,null,0.32959682463803813,0.32959682463803813,0.32959682463803813]
["2013-01-24T17:00:00","2013-01-24T17:00:00",null,12.754537783493262,13.058109985149162,13.361682186805062,13.665254388460962,13.968826590116862,14.272398791772762,14.575970993428662,14.879543195084562,15.183115396740462,null,7.0491277763207572E-2,0.14156087000687087,0.26643436856351721,0.52455189340409347,0.6283856296677679,0.64766978888878868,0.66612327821969997,0.68378815689544403,0.70074854338590575,null,0.26643436856351721,0.26643436856351721,0.26643436856351721]
["2013-01-24T18:00:00","2013-01-24T18:00:00",null,12.218371854315317,12.521944055971217,12.825516257627116,13.129088459283016,13.432660660938916,13.736232862594816,14.039805064250716,14.343377265906616,14.646949467562516,null,1.6644942228394584E-2,9.0490443978246238E-2,0.21802418914498978,0.47866526808210091,0.58491741035495459,0.60651482749779906,0.6271764266631783,0.6469547818947704,0.66594452647119551,null,0.21802418914498978,0.21802418914498978,0.21802418914498978]
["2013-01-24T19:00:00","2013-01-24T19:00:00",null,11.614713776296671,11.918285977952571,12.221858179608471,12.525430381264371,12.829002582920271,13.132574784576171,13.436146986232071,13.739719187887971,14.043291389543871,null,0,4.6075891879232361E-2,0.17622782442113083,0.43936091302857017,0.54798940207566083,0.57184750309665111,0.59467515286155614,0.61651441060531842,0.63748093922402915,null,0.17622782442113083,0.17622782442113083,0.17622782442113083]
["2013-01-24T20:00:00","2013-01-24T20:00:00",null,11.31026010360409,11.61383230525999,11.91740450691589,12.22097670857179,12.52454891022769,12.82812111188359,13.13169331353949,13.43526551519539,13.73883771685129,null,0,8.6326579718960864E-3,0.14128711499285831,0.4068070651832702,0.51770675291724222,0.54372038972902281,0.56860894200609791,0.59241446898341033,0.61526314836578666,null,0.14128711499285831,0.14128711499285831,0.14128711499285831]
["2013-01-24T21:00:00","2013-01-24T21:00:00",null,11.060932244739744,11.364504446395642,11.668076648051542,11.971648849707442,12.275221051363342,12.578793253019242,12.882365454675142,13.185937656331042,13.489509857986942,null,0,0,0.1078395084050356,0.37575683498715562,0.48893823621674459,0.51711792362805098,0.54406737841729624,0.5698391746281587,0.59457000477420063,null,0.1078395084050356,0.1078395084050356,0.1078395084050356]
["2013-01-24T22:00:00","2013-01-24T22:00:00",null,10.925650139532522,11.229222341188422,11.532794542844321,11.836366744500221,12.139938946156121,12.443511147812021,12.747083349467921,13.050655551123821,13.354227752779721,null,0,0,8.0469461266367726E-2,0.35064747172663357,0.46598440874701275,0.49620396905301817,0.52510917826707793,0.5527420956241349,0.57923941363775122,null,8.0469461266367726E-2,8.0469461266367726E-2,8.0469461266367726E-2]
["2013-01-24T23:00:00","2013-01-24T23:00:00",null,10.567045730871492,10.870617932527392,11.174190134183291,11.477762335839191,11.781334537495091,12.084906739150991,12.388478940806891,12.692051142462791,12.995623344118691,null,3.9745977020424353E-3,6.2773408151305127E-3,8.8933882298495137E-2,0.36117279527093116,0.47846548671612482,0.51054616816832477,0.54121786524995885,0.57054366681344137,0.59863923575486311,null,8.8933882298495137E-2,8.8933882298495137E-2,8.8933882298495137E-2]
["2013-01-25","2013-01-25",null,10.441359441441362,10.744931643097262,11.048503844753162,11.352076046409062,11.655648248064962,11.959220449720862,12.262792651376762,12.566364853032661,12.869937054688561,null,4.9850708215299432E-2,5.4298472310442152E-2,0.13898437187977025,0.41314749485081409,0.5322697630159956,0.5660853879095632,0.59839739515394497,0.62928990321902623,0.65887857500089775,null,0.13898437187977025,0.13898437187977025,0.13898437187977025]
["2013-01-25T01:00:00","2013-01-25T01:00:00",null,10.278133685196673,10.581705886852573,10.885278088508473,11.188850290164373,11.492422491820273,11.795994693476173,12.099566895132073,12.403139096787973,12.706711298443873,null,7.8629739724532619E-2,8.511737671437436E-2,0.17172748628231033,0.44772018597334196,0.56856688277115564,0.60402281782747091,0.63789101676471582,0.67026611286151128,0.70126376901394816,null,0.17172748628231033,0.17172748628231033,0.17172748628231033]
["2013-01-25T02:00:00","2013-01-25T02:00:00",null,10.437618859942283,10.741191061598183,11.044763263254083,11.348335464909983,11.651907666565883,11.955479868221783,12.259052069877683,12.562624271533583,12.866196473189483,null,0.10162562642920671,0.11045806576707877,0.19928679997821833,0.47738246141636237,0.60022697187393281,0.63756505769391369,0.67323128892493966,0.70732029884563175,0.73994775035208071,null,0.19928679997821833,0.19928679997821833,0.19928679997821833]
["2013-01-25T03:00:00","2013-01-25T03:00:00",null,10.447698467863603,10.751270669519503,11.054842871175403,11.358415072831303,11.661987274487203,11.965559476143103,12.269131677799002,12.572703879454902,12.876276081110802,null,0.14403185005972824,0.15512497327574615,0.24608821366020478,0.52620271837557675,0.65096092402301942,0.69011807175425255,0.72751924642664623,0.76324856651008599,0.79745323932686929,null,0.24608821366020478,0.24608821366020478,0.24608821366020478]
["2013-01-25T04:00:00","2013-01-25T04:00:00",null,10.546201534143165,10.849773735799065,11.153345937454963,11.456918139110863,11.760490340766763,12.064062542422663,12.367634744078563,12.671206945734463,12.974779147390363,null,0.19715266379178745,0.21052750050342231,0.30364627667867117,0.58580065428874217,0.7124935847435282,0.75349082400348466,0.79263745692598164,0.83003863159837576,0.86583104053422899,null,0.30364627667867117,0.30364627667867117,0.30364627667867117]
["2013-01-25T05:00:00","2013-01-25T05:00:00",null,10.563473104813813,10.867045306469713,11.170617508125613,11.474189709781513,11.777761911437413,12.081334113093313,12.384906314749212,12.688478516405112,12.992050718061012,null,0.2492640558852327,0.26494163570995566,0.36023697729346582,0.644452257415707,0.77310094229530757,0.81595930270145844,0.85687242349152992,0.89595596756161389,0.93334662742527263,null,0.36023697729346582,0.36023697729346582,0.36023697729346582]
["2013-01-25T06:00:00","2013-01-25T06:00:00",null,10.594094400507483,10.897666602163383,11.201238803819285,11.504811005475185,11.808383207131085,12.111955408786985,12.415527610442885,12.719099812098785,13.022672013754685,null,0.2969171690747997,0.31493955124755296,0.41244300266553113,0.69875072972614916,0.82938671345677095,0.87413773943532302,0.91683837771043997,0.95763583560442056,0.9966562908220914,null,0.41244300266553113,0.41244300266553113,0.41244300266553113]
["2013-01-25T07:00:00","2013-01-25T07:00:00",null,10.583939823964521,10.887512025620421,11.191084227276322,11.494656428932222,11.798228630588122,12.101800832244022,12.405373033899922,12.708945235555822,13.012517437211722,null,0.3354854875168411,0.35583164242015358,0.45553268886386422,0.74393286286285909,0.87654563063576652,0.92316829256924859,0.96765644832941111,1,1,null,0.45553268886386422,0.45553268886386422,0.45553268886386422]
["2013-01-25T08:00:00","2013-01-25T08:00:00",null,10.354940708487639,10.658512910143539,10.962085111799439,11.265657313455339,11.569229515111239,11.872801716767139,12.176373918423039,12.479946120078939,12.783518321734839,null,0.37492653508393414,0.39761749233527699,0.49953716342219118,0.79004029916829843,0.92464036579222708,0.97315569329811036,1,1,1,null,0.49953716342219118,0.49953716342219118,0.49953716342219118]
["2013-01-25T09:00:00","2013-01-25T09:00:00",null,10.1999106871901,10.503482888845999,10.807055090501898,11.110627292157798,11.414199493813697,11.717771695469597,12.021343897125497,12.324916098781397,12.628488300437297,null,0.41514567849745876,0.44019195290556751,0.54434076344442084,0.83695737574637608,0.97355525603006154,1,1,1,1,null,0.54434076344442084,0.54434076344442084,0.54434076344442084]
["2013-01-25T10:00:00","2013-01-25T10:00:00",null,10.271254562793473,10.574826764449373,10.878398966105273,11.181971167761173,11.485543369417073,11.789115571072973,12.092687772728873,12.396259974384773,12.699832176040672,null,0.45540688114592565,0.4827979579020647,0.58916539308412164,0.88388496713318931,1,1,1,1,1,null,0.58916539308412164,0.58916539308412164,0.58916539308412164]
["2013-01-25T11:00:00","2013-01-25T11:00:00",null,10.262703570360259,10.566275772016159,10.86984797367206,11.17342017532796,11.47699237698386,11.78056457863976,12.08413678029566,12.38770898195156,12.69128118360746,null,0.49600455767393054,0.5257299219693643,0.6343054669858893,0.93111748797333382,1,1,1,1,1,null,0.6343054669858893,0.6343054669858893,0.6343054669858893]
["2013-01-25T12:00:00","2013-01-25T12:00:00",null,10.202840018225896,10.506412219881796,10.809984421537695,11.113556623193595,11.417128824849495,11.720701026505395,12.024273228161295,12.327845429817195,12.631417631473095,null,0.48404922014159657,0.51614041640253172,0.62695561567973146,0.92588111322302391,0.99676143890944691,0.9986541044818481,1,1,1,null,0.62695561567973146,0.62695561567973146,0.62695561567973146]
["2013-01-25T13:00:00","2013-01-25T13:00:00",null,10.268069557539217,10.571641759195117,10.875213960851017,11.178786162506917,11.482358364162817,11.785930565818717,12.089502767474617,12.393074969130517,12.696647170786417,null,0.45968640830129942,0.4942275549976205,0.60735601219664392,0.90846858995693325,0.9814203329642619,0.98527926777021324,0.98848628443455966,0.99026328711086964,0.99194565650855948,null,0.60735601219664392,0.60735601219664392,0.60735601219664392]
["2013-01-25T14:00:00","2013-01-25T14:00:00",null,10.287439845637824,10.591012047293724,10.894584248949624,11.198156450605524,11.501728652261423,11.805300853917323,12.108873055573223,12.412445257229123,12.716017458885023,null,0.43439829329227281,0.47141042004145095,0.58687316477976914,0.89020436718326201,0.96524855712896751,0.97108427597720459,0.9761839582139521,0.97974847837530765,0.98313424678815853,null,0.58687316477976914,0.58687316477976914,0.58687316477976914]
["2013-01-25T15:00:00","2013-01-25T15:00:00",null,10.352716184155467,10.656288385811367,10.959860587467267,11.263432789123167,11.567004990779067,11.870577192434967,12.174149394090866,12.477721595746766,12.781293797402666,null,0.40940459292784193,0.44886667011240605,0.56664267277254787,0.87216095539303762,0.94928707746838437,0.95708906555017159,0.9640603837418491,0.96940190657951464,0.97448055919879095,null,0.56664267277254787,0.56664267277254787,0.56664267277254787]
["2013-01-25T16:00:00","2013-01-25T16:00:00",null,10.358930788399329,10.662502990055229,10.966075191711129,11.269647393367029,11.573219595022929,11.876791796678829,12.180363998334728,12.483936199990628,12.787508401646528,null,0.3840639038751375,0.42597593149508761,0.54607570688578866,0.85379158453201076,0.93299963873699887,0.94277841086107173,0.95162136500767924,0.95875040533039035,0.9655324569648277,null,0.54607570688578866,0.54607570688578866,0.54607570688578866]
["2013-01-25T17:00:00","2013-01-25T17:00:00",null,10.369759950375997,10.673332152031897,10.976904353687798,11.280476555343698,11.584048756999598,11.887620958655498,12.191193160311398,12.494765361967298,12.798337563623198,null,0.35817644476818389,0.40255945244099106,0.52499351537098682,0.83492801766041258,0.91622851880377754,0.92798407497013602,0.93871969468914462,0.94764676730563691,0.95613221795523529,null,0.52499351537098682,0.52499351537098682,0.52499351537098682]
["2013-01-25T18:00:00","2013-01-25T18:00:00",null,10.349155358038594,10.652727559694494,10.956299761350394,11.259871963006294,11.563444164662194,11.867016366318094,12.170588567973994,12.474160769629894,12.777732971285793,null,0.3333299517260509,0.380162909834244,0.50489971587732785,0.81702129838375048,0.90039321684802121,0.91411504224792972,0.92672229792186833,0.93741585840593511,0.94759419326195893,null,0.50489971587732785,0.50489971587732785,0.50489971587732785]
["2013-01-25T19:00:00","2013-01-25T19:00:00",null,10.203232080745755,10.506804282401655,10.810376484057553,11.113948685713453,11.417520887369353,11.721093089025253,12.024665290681153,12.328237492337053,12.631809693992953,null,0.30878838813724918,0.35809232629829935,0.48516341988067796,0.7994931122215686,0.88494696281548069,0.90065608706641032,0.91513497869527904,0.92762657147312688,0.93949779053557614,null,0.48516341988067796,0.48516341988067796,0.48516341988067796]
["2013-01-25T20:00:00","2013-01-25T20:00:00",null,10.180172114207377,10.483744315863277,10.787316517519177,11.090888719175076,11.394460920830976,11.698033122486876,12.001605324142776,12.305177525798676,12.608749727454576,null,0.28543499793556598,0.33717837172326653,0.46655220841873324,0.78306898097662081,0.87058373408270295,0.88824861275844713,0.90458862553351038,0.91883619137019701,0.93238977983033622,null,0.46655220841873324,0.46655220841873324,0.46655220841873324]
["2013-01-25T21:00:00","2013-01-25T21:00:00",null,10.140163525540636,10.443735727196536,10.747307928852436,11.050880130508336,11.354452332164236,11.658024533820136,11.961596735476036,12.265168937131936,12.568741138787836,null,0.26418456948099517,0.3183148048516683,0.44994932542528082,0.76860060415648745,0.85812368573106201,0.87770225959667847,0.89586133428299397,0.91183332875231271,0.9270377421839352,null,0.44994932542528082,0.44994932542528082,0.44994932542528082]
["2013-01-25T22:00:00","2013-01-25T22:00:00",null,10.107455687063087,10.411027888718987,10.714600090374887,11.018172292030787,11.321744493686687,11.625316695342587,11.928888896998487,12.232461098654387,12.536033300310287,null,0.24459548080664317,0.3010810333340822,0.43492366374216274,0.75567790422048176,0.84717776983734194,0.868638494466624,0.88857457182924948,0.90623945050499377,0.92305262967315715,null,0.43492366374216274,0.43492366374216274,0.43492366374216274]
["2013-01-25T23:00:00","2013-01-25T23:00:00",null,10.038756657050364,10.342328858706264,10.645901060362164,10.949473262018063,11.253045463673963,11.556617665329863,11.860189866985763,12.163762068641663,12.467334270297563,null,0.22871811961594457,0.28745384121279388,0.42343097779419347,0.7461935467410048,0.83958607793026618,0.8628553496620649,0.88449482603985141,0.90378950006960779,0.92214835612189883,null,0.42343097779419347,0.42343097779419347,0.42343097779419347]
["2013-01-26","2013-01-26",null,10.021302686967779,10.324874888623679,10.628447090279579,10.932019291935479,11.235591493591379,11.539163695247279,11.842735896903179,12.146308098559079,12.449880300214978,null,0.21378709121144654,0.27475195226023497,0.412832050588747,0.73758191838657949,0.83285660033950648,0.85791338955635077,0.88123523533182724,0.90213867509812451,0.92202217841707212,null,0.412832050588747,0.412832050588747,0.412832050588747]
["2013-01-26T01:00:00","2013-01-26T01:00:00",null,9.9245953938805478,10.228167595536448,10.531739797192348,10.835311998848248,11.138884200504148,11.442456402160047,11.746028603815947,12.049600805471847,12.353173007127747,null,0.20029659160372049,0.26346956248697695,0.40363159294513024,0.73034772997651287,0.82748353307563427,0.85429629535131746,0.87928999571574828,0.90177065679237989,0.92316829256924837,null,0.40363159294513024,0.40363159294513024,0.40363159294513024]
["2013-01-26T02:00:00","2013-01-26T02:00:00",null,9.9684320431457429,10.272004244801643,10.575576446457543,10.879148648113443,11.182720849769343,11.486293051425243,11.789865253081143,12.093437454737042,12.397009656392942,null,0.18818353194035306,0.25351203861439975,0.39571394196725207,0.72434377418850693,0.82329863919888058,0.85183583010719599,0.8784593258256389,0.90249617859513365,0.92536588759498084,null,0.39571394196725207,0.39571394196725207,0.39571394196725207]
["2013-01-26T03:00:00","2013-01-26T03:00:00",null,9.9071154350226003,10.2106876366785,10.5142598383344,10.8178320399903,11.1214042416462,11.4249764433021,11.728548644958,12.0321208466139,12.3356930482698,null,0.17570245397124096,0.24321804086228455,0.38747033191857144,0.71804540375590531,0.81884036029500229,0.84911249464468541,0.8773868153346116,0.90299037460570508,0.92735318644600206,null,0.38747033191857144,0.38747033191857144,0.38747033191857144]
["2013-01-26T04:00:00","2013-01-26T04:00:00",null,9.9710235036614474,10.274595705317347,10.578167906973247,10.881740108629145,11.185312310285045,11.488884511940945,11.792456713596845,12.096028915252745,12.399601116908645,null,0.1634316721768401,0.23311330966740945,0.37940547361839538,0.71190475545433707,0.8145187739046863,0.84651533688700165,0.87641945293093992,0.90357920389489654,0.92942460376690783,null,0.37940547361839538,0.37940547361839538,0.37940547361839538]
["2013-01-26T05:00:00","2013-01-26T05:00:00",null,9.9978840116983108,10.301456213354211,10.605028415010111,10.908600616666011,11.21217281832191,11.51574501997781,11.81931722163371,12.12288942328961,12.42646162494551,null,0.14974139120313837,0.22162062371944019,0.36998420499133183,0.70443924125208801,0.80891438084863176,0.8426669168897859,0.87423237271394305,0.902969344988234,0.93031836250943056,null,0.36998420499133183,0.36998420499133183,0.36998420499133183]
["2013-01-26T06:00:00","2013-01-26T06:00:00",null,10.034381154707262,10.337953356363162,10.641525558019062,10.945097759674962,11.248669961330862,11.552242162986762,11.855814364642661,12.159386566298561,12.462958767954461,null,0.13409535580462212,0.20822475739033419,0.35871233002680936,0.69517569475605789,0.80154349992500284,0.83709406825993804,0.87036292309925622,0.90071917591882378,0.92961387032414788,null,0.35871233002680936,0.35871233002680936,0.35871233002680936]
["2013-01-26T07:00:00","2013-01-26T07:00:00",null,10.050764651655573,10.354336853311473,10.657909054967373,10.961481256623273,11.265053458279173,11.568625659935073,11.872197861590973,12.175770063246873,12.479342264902773,null,0.11758710608978978,0.19398770636238324,0.34662029998091304,0.68510250798738948,0.7933945231549423,0.83075363859239415,0.86574692206434456,0.89774348504665968,0.92819437114484704,null,0.34662029998091304,0.34662029998091304,0.34662029998091304]
["2013-01-26T08:00:00","2013-01-26T08:00:00",null,10.101784081738465,10.405356283394365,10.708928485050265,11.012500686706165,11.316072888362065,11.619645090017965,11.923217291673865,12.226789493329765,12.530361694985665,null,0.10204621877862916,0.18067595850316176,0.33542202867753951,0.67589153553503711,0.78606570146625554,0.82521233438875297,0.86189850206712881,0.89550383078598494,0.92748987895956436,null,0.33542202867753951,0.33542202867753951,0.33542202867753951]
["2013-01-26T09:00:00","2013-01-26T09:00:00",null,10.193157598031908,10.496729799687808,10.800302001343708,11.103874202999608,11.407446404655508,11.711018606311407,12.014590807967307,12.318163009623207,12.621735211279107,null,8.5348702506556698E-2,0.16622861130049957,0.32308815803072527,0.66556599335671518,0.7776433396690704,0.81858800488534889,0.85697757157888577,0.89221269565175398,0.92574442070946106,null,0.32308815803072527,0.32308815803072527,0.32308815803072527]
["2013-01-26T10:00:00","2013-01-26T10:00:00",null,10.300250139196251,10.603822340852151,10.907394542508051,11.210966744163951,11.514538945819851,11.818111147475751,12.121683349131651,12.425255550787551,12.728827752443451,null,6.6737491044611963E-2,0.14989911333417177,0.3089141958551877,0.65342138926714111,0.76743346038683968,0.81020770232310602,0.85033221245801061,0.88721816150236199,0.9223271078704034,null,0.3089141958551877,0.3089141958551877,0.3089141958551877]
["2013-01-26T11:00:00","2013-01-26T11:00:00",null,10.416216732899953,10.719788934555853,11.023361136211753,11.326933337867652,11.630505539523552,11.934077741179452,12.237649942835352,12.541222144491252,12.844794346147152,null,4.5739417999694651E-2,0.13122481301981367,0.29243749056656204,0.63901610129942121,0.75499444165266982,0.79964031954386616,0.84154183235508073,0.88012066560585767,0.91683837771044008,null,0.29243749056656204,0.29243749056656204,0.29243749056656204]
["2013-01-26T12:00:00","2013-01-26T12:00:00",null,10.51099890916527,10.81457111082117,11.11814331247707,11.42171551413297,11.72528771578887,12.02885991744477,12.33243211910067,12.63600432075657,12.939576522412469,null,2.3384934627889844E-2,0.11120461718730362,0.27462540456852003,0.62330697704849158,0.74126210144402582,0.78779013009888776,0.8314896752038835,0.87177190746982147,0.91011941492841597,null,0.27462540456852003,0.27462540456852003,0.27462540456852003]
["2013-01-26T13:00:00","2013-01-26T13:00:00",null,10.541356333101884,10.844928534757784,11.148500736413686,11.452072938069586,11.755645139725486,12.059217341381386,12.362789543037286,12.666361744693186,12.969933946349085,null,0,8.9785951792963836E-2,0.25544639343485492,0.60625195727941006,0.7262259249521722,0.77466764879690642,0.82018625581315441,0.86220343152046008,0.90220176395053775,null,0.25544639343485492,0.25544639343485492,0.25544639343485492]
["2013-01-26T14:00:00","2013-01-26T14:00:00",null,10.642186776799914,10.945758978455814,11.249331180111714,11.552903381767614,11.856475583423514,12.160047785079414,12.463619986735313,12.767192188391213,13.070764390047113,null,0,6.6874183558174247E-2,0.23479530907821117,0.5877458939048209,0.70975973447228213,0.76013618312435971,0.80749488166933103,0.85125751562674001,0.89292770264577204,null,0.23479530907821117,0.23479530907821117,0.23479530907821117]
["2013-01-26T15:00:00","2013-01-26T15:00:00",null,10.660827932586606,10.964400134242506,11.267972335898406,11.571544537554306,11.875116739210206,12.178688940866106,12.482261142522006,12.785833344177906,13.089405545833806,null,0,4.2963508493506261E-2,0.21316634750916014,0.56828298293529567,0.69234721120619147,0.7446794142830836,0.79389923397424933,0.83942835579923281,0.88279142702469027,null,0.21316634750916014,0.21316634750916014,0.21316634750916014]
["2013-01-26T16:00:00","2013-01-26T16:00:00",null,10.632254890383727,10.935827092039627,11.239399293695527,11.542971495351427,11.846543697007327,12.150115898663227,12.453688100319127,12.757260301975027,13.060832503630927,null,0,2.0503877034345835E-2,0.19295688511940998,0.55021854152760019,0.6763016130757239,0.73055802615122378,0.78160742256237736,0.82888200263746414,0.87390641364314037,null,0.19295688511940998,0.19295688511940998,0.19295688511940998]
["2013-01-26T17:00:00","2013-01-26T17:00:00",null,10.639337849690161,10.942910051346061,11.246482253001961,11.550054454657861,11.853626656313761,12.157198857969661,12.460771059625561,12.764343261281461,13.067915462937361,null,0,0,0.17238991923265071,0.53179659662289558,0.65991954106571826,0.71610016413982602,0.76898965207970293,0.81802020521362862,0.8647059559995236,null,0.17238991923265071,0.17238991923265071,0.17238991923265071]
["2013-01-26T18:00:00","2013-01-26T18:00:00",null,10.600321129768201,10.903893331424101,11.207465533079999,11.511037734735899,11.814609936391799,12.118182138047699,12.421754339703599,12.725326541359498,13.028898743015398,null,0,0,0.15372613372702815,0.51523577286438549,0.64535653096696488,0.70342981961347384,0.75811733984713181,0.80886180680495412,0.85718786775359679,null,0.15372613372702815,0.15372613372702815,0.15372613372702815]
["2013-01-26T19:00:00","2013-01-26T19:00:00",null,10.572242668650713,10.875814870306613,11.179387071962511,11.482959273618411,11.786531475274311,12.090103676930211,12.393675878586111,12.69724808024201,13.00082028189791,null,0,0,0.1363661845046153,0.49994724096287835,0.63203426829900788,0.69197919290044685,0.7484332010016792,0.80087055216592695,0.85080537885111063,null,0.1363661845046153,0.1363661845046153,0.1363661845046153]
["2013-01-26T20:00:00","2013-01-26T20:00:00",null,10.575463725910176,10.879035927566076,11.182608129221975,11.486180330877875,11.789752532533775,12.093324734189675,12.396896935845575,12.700469137501475,13.004041339157375,null,0,0,0.11888005757737569,0.48453253135654445,0.61858582792622407,0.68040238848259305,0.73863339926013538,0.79276363463080868,0.84430722705253336,null,0.11888005757737569,0.11888005757737569,0.11888005757737569]
["2013-01-26T21:00:00","2013-01-26T21:00:00",null,10.666656329458633,10.970228531114532,11.273800732770432,11.577372934426332,11.880945136082232,12.184517337738132,12.488089539394032,12.791661741049932,13.095233942705832,null,0,0,9.7040799833613411E-2,0.46486983902104351,0.60098403810289325,0.66475635308407677,0.72484848500781363,0.7807557230547969,0.83399219968294702,null,9.7040799833613411E-2,9.7040799833613411E-2,9.7040799833613411E-2]
["2013-01-26T22:00:00","2013-01-26T22:00:00",null,10.59008249764797,10.89365469930387,11.19722690095977,11.50079910261567,11.804371304271569,12.107943505927469,12.411515707583369,12.715087909239269,13.018660110895169,null,3.1439278119330373E-2,3.3773565658625139E-2,0.13302247532670658,0.50294396145251352,0.64103494457664889,0.70668941032149801,0.76857957453901593,0.82619021160116035,0.88105648358332256,null,0.13302247532670658,0.13302247532670658,0.13302247532670658]
["2013-01-26T23:00:00","2013-01-26T23:00:00",null,10.426667103382975,10.730239305038875,11.033811506694775,11.337383708350675,11.640955910006575,11.944528111662475,12.248100313318375,12.551672514974275,12.855244716630175,null,8.5842898517128147E-2,9.0406325508362056E-2,0.19176871173229146,0.56368801151785519,0.70367166021439176,0.77112415825302194,0.83471772148570089,0.8939581539018574,0.95037010276814726,null,0.19176871173229146,0.19176871173229146,0.19176871173229146]
["2013-01-27","2013-01-27",null,10.38972298198151,10.69329518363741,10.99686738529331,11.30043958694921,11.60401178860511,11.90758399026101,12.21115619191691,12.51472839357281,12.81830059522871,null,0.15224391568220216,0.15899442289043297,0.26242822643526809,0.63630328064564634,0.77813753567964183,0.84734600677711081,0.91261142459874423,0.97343959313397055,1,null,0.26242822643526809,0.26242822643526809,0.26242822643526809]
["2013-01-27T01:00:00","2013-01-27T01:00:00",null,10.420552289508063,10.724124491163963,11.027696692819863,11.331268894475762,11.634841096131662,11.938413297787562,12.241985499443462,12.545557701099362,12.849129902755262,null,0.22435447399068634,0.23322897256350067,0.33867110457682814,0.71444933916834308,0.85808162649611974,0.92900401141748523,0.99588870978439525,1,1,null,0.33867110457682814,0.33867110457682814,0.33867110457682814]
["2013-01-27T02:00:00","2013-01-27T02:00:00",null,10.418397456031718,10.721969657687618,11.025541859343518,11.329114060999418,11.632686262655318,11.936258464311218,12.239830665967117,12.543402867623017,12.846975069278917,null,0.29668584328261732,0.3076843332200152,0.41512427889309944,0.79280569386575106,0.9382360134873089,1,1,1,1,null,0.41512427889309944,0.41512427889309944,0.41512427889309944]
["2013-01-27T03:00:00","2013-01-27T03:00:00",null,10.42567163895742,10.72924384061332,11.03281604226922,11.33638824392512,11.639960445581019,11.943532647236919,12.247104848892819,12.550677050548719,12.854249252204619,null,0.36851250175524131,0.38163498305722277,0.4910937720075349,0.8706783673613232,1,1,1,1,1,null,0.4910937720075349,0.4910937720075349,0.4910937720075349]
["2013-01-27T04:00:00","2013-01-27T04:00:00",null,10.496206743572216,10.799778945228116,11.103351146884018,11.406923348539918,11.710495550195818,12.014067751851718,12.317639953507618,12.621212155163517,12.924784356819417,null,0.44031813061039415,0.45556460327695919,0.56702120588702809,0.94849846681321759,1,1,1,1,1,null,0.56702120588702809,0.56702120588702809,0.56702120588702809]
["2013-01-27T05:00:00","2013-01-27T05:00:00",null,10.580846869840775,10.884419071496675,11.187991273152575,11.491563474808475,11.795135676464374,12.098707878120274,12.402280079776174,12.705852281432074,13.009424483087974,null,0.50785474711890888,0.52531984442867752,0.6388794087858588,1,1,1,1,1,1,null,0.6388794087858588,0.6388794087858588,0.6388794087858588]
["2013-01-27T06:00:00","2013-01-27T06:00:00",null,10.699196170506985,11.002768372162885,11.306340573818785,11.609912775474685,11.913484977130585,12.217057178786485,12.520629380442385,12.824201582098285,13.127773783754185,null,0.57292038357456654,0.592646164762481,0.70835075010171689,1,1,1,1,1,1,null,0.70835075010171689,0.70835075010171689,0.70835075010171689]
["2013-01-27T07:00:00","2013-01-27T07:00:00",null,10.918586506680422,11.22215870833632,11.52573090999222,11.82930311164812,12.132875313304019,12.436447514959919,12.740019716615819,13.043591918271719,13.347164119927619,null,0.63063616872406636,0.65278035592116002,0.77077716956474851,1,1,1,1,1,1,null,0.77077716956474851,0.77077716956474851,0.77077716956474851]
["2013-01-27T08:00:00","2013-01-27T08:00:00",null,10.963884819320233,11.267457020976131,11.571029222632031,11.874601424287931,12.178173625943831,12.481745827599731,12.785318029255631,13.088890230911531,13.392462432567431,null,0.66081366979512934,0.68533420376645993,0.80558118647945876,1,1,1,1,1,1,null,0.80558118647945876,0.80558118647945876,0.80558118647945876]
["2013-01-27T09:00:00","2013-01-27T09:00:00",null,11.293873046528685,11.597445248184584,11.901017449840484,12.204589651496384,12.508161853152284,12.811734054808184,13.115306256464084,13.418878458119984,13.722450659775884,null,0.641497966147902,0.66847896536335405,0.79104972080691205,0.98767664416192136,0.98977960590903369,0.9917879343775261,0.99370162956739838,0.99552069147865063,0.99726614972875383,null,0.79104972080691205,0.79104972080691205,0.79104972080691205]
["2013-01-27T10:00:00","2013-01-27T10:00:00",null,11.724122140194375,12.027694341850275,12.331266543506175,12.634838745162075,12.938410946817974,13.241983148473874,13.545555350129774,13.849127551785674,14.152699753441574,null,0.61714566911634039,0.64666073723706285,0.77162886907232908,0.97054802073169089,0.97482754788706449,0.97891780848519827,0.98280828771735618,0.98653053000974511,0.99009505017110055,null,0.77162886907232908,0.77162886907232908,0.77162886907232908]
["2013-01-27T11:00:00","2013-01-27T11:00:00",null,11.81259360520934,12.11616580686524,12.41973800852114,12.72331021017704,13.02688241183294,13.33045461348884,13.63402681514474,13.93759901680064,14.24117121845654,null,0.5890080409399765,0.62112026681838273,0.74856989351524161,0.94984436233136926,0.95637405855615321,0.96260934013634158,0.96855020707193407,0.97423871859787314,0.97968538952289419,null,0.74856989351524161,0.74856989351524161,0.74856989351524161]
["2013-01-27T12:00:00","2013-01-27T12:00:00",null,11.872690703317442,12.176262904973342,12.479835106629242,12.783407308285142,13.086979509941042,13.390551711596942,13.694123913252842,13.997696114908742,14.301268316564641,null,0.55813656249236643,0.59289852017213429,0.7228822157742637,0.92656457579083495,0.9353865003199715,0.94380886211715675,0.95185269079986157,0.95953901598555746,0.96690989690918638,null,0.7228822157742637,0.7228822157742637,0.7228822157742637]
["2013-01-27T13:00:00","2013-01-27T13:00:00",null,12.085878145737757,12.389450347393657,12.693022549049557,12.996594750705457,13.300166952361357,13.603739154017257,13.907311355673157,14.210883557329057,14.514455758984957,null,0.52447865972983243,0.56191137882843312,0.69445017295330402,0.90056145378779018,0.9117071510474859,0.9223481374878747,0.93251595753516303,0.94223164080682242,0.9515477613465303,null,0.69445017295330402,0.69445017295330402,0.69445017295330402]
["2013-01-27T14:00:00","2013-01-27T14:00:00",null,12.236745248726709,12.540317450382609,12.843889652038509,13.147461853694409,13.451034055350309,13.754606257006209,14.058178458662109,14.361750660318009,14.665322861973909,null,0.48766631434662988,0.52782236890774115,0.66294780598156033,0.87154058167763904,0.8850521109028362,0.89795378122137082,0.91027713705944946,0.92206423765201451,0.9333676570427436,null,0.66294780598156033,0.66294780598156033,0.66294780598156033]
["2013-01-27T15:00:00","2013-01-27T15:00:00",null,12.304931836502682,12.608504038158582,12.912076239814482,13.215648441470382,13.519220643126282,13.822792844782182,14.126365046438082,14.429937248093982,14.733509449749882,null,0.45110632437308079,0.4939646847792315,0.63166624999326337,0.84271949093346366,0.85857582250669107,0.87372766189463602,0.88819603871476926,0.90204404181950448,0.91531373044378361,null,0.63166624999326337,0.63166624999326337,0.63166624999326337]
["2013-01-27T16:00:00","2013-01-27T16:00:00",null,12.333921449277538,12.637493650933438,12.941065852589338,13.244638054245238,13.548210255901138,13.851782457557038,14.155354659212938,14.458926860868837,14.762499062524737,null,0.41337919062988437,0.45896088649854561,0.59925960947026125,0.81278383046331859,0.83101650881078304,0.84842903207687381,0.86506345949653285,0.88098287992217383,0.89625038220620967,null,0.59925960947026125,0.59925960947026125,0.59925960947026125]
["2013-01-27T17:00:00","2013-01-27T17:00:00",null,12.299359893050502,12.602932094706402,12.906504296362302,13.210076498018202,13.513648699674102,13.817220901330002,14.120793102985902,14.424365304641801,14.727937506297701,null,0.37136201492257864,0.41970910548869267,0.56265756026176994,0.77869482054262662,0.79933539009053478,0.81905065646971353,0.83789319372384063,0.85591557589659406,0.87321243626659328,null,0.56265756026176994,0.56265756026176994,0.56265756026176994]
["2013-01-27T18:00:00","2013-01-27T18:00:00",null,12.270898009398504,12.574470211054404,12.878042412710304,13.181614614366204,13.485186816022104,13.788759017678004,14.092331219333904,14.395903420989804,14.699475622645704,null,0.32937638364147959,0.38047835409631087,0.52604499624454304,0.74458478100446346,0.76761221213534425,0.7896091920101399,0.81063880948126399,0.83075363859239415,0.85004831262215019,null,0.52604499624454304,0.52604499624454304,0.52604499624454304]
["2013-01-27T19:00:00","2013-01-27T19:00:00",null,12.25871108727479,12.56228328893069,12.86585549058659,13.16942769224249,13.47299989389839,13.77657209555429,14.08014429721019,14.383716498866089,14.687288700521989,null,0.28078745247444759,0.33463378800926058,0.48280810272391211,0.70383989715416073,0.72924367505927856,0.75352236842969111,0.77672855130907659,0.798925312549848,0.82021780023936075,null,0.48280810272391211,0.48280810272391211,0.48280810272391211]
["2013-01-27T20:00:00","2013-01-27T20:00:00",null,12.21405535341264,12.51762755506854,12.82119975672444,13.124771958380339,13.428344160036239,13.731916361692139,14.035488563348039,14.339060765003939,14.642632966659839,null,0.23548965644164649,0.29204881263023447,0.44279925548509869,0.66629151515946883,0.69404009541261702,0.7205689578524398,0.74592016171387998,0.77016731065808597,0.79343658238988435,null,0.44279925548509869,0.44279925548509869,0.44279925548509869]
["2013-01-27T21:00:00","2013-01-27T21:00:00",null,12.229481186676516,12.533053388332416,12.836625589988316,13.140197791644216,13.443769993300116,13.747342194956016,14.050914396611915,14.354486598267815,14.658058799923715,null,0.19480786144375711,0.25401674943370672,0.40728023157637028,0.63318038245118413,0.66322119100868482,0.69193713366550447,0.71939129927405709,0.74564677668675539,0.77084025841716164,null,0.40728023157637028,0.40728023157637028,0.40728023157637028]
["2013-01-27T22:00:00","2013-01-27T22:00:00",null,12.217830071473349,12.521402273129249,12.824974474785149,13.128546676441049,13.432118878096949,13.735691079752849,14.039263281408749,14.342835483064649,14.646407684720549,null,0.15448356994287685,0.21633167492545252,0.37210819635591541,0.60039520881370179,0.63272824567555508,0.6636312685493716,0.69316736628756548,0.72143117216875607,0.7485383490890346,null,0.37210819635591541,0.37210819635591541,0.37210819635591541]
["2013-01-27T23:00:00","2013-01-27T23:00:00",null,12.121558499762429,12.425130701418329,12.728702903074229,13.032275104730129,13.335847306386029,13.639419508041929,13.942991709697829,14.246563911353729,14.550136113009629,null,0.11819696499645239,0.18260016850176963,0.34081612555888291,0.57142691074722851,0.60596805744354976,0.6389950716819498,0.67055001269737158,0.70075905819464124,0.72971684145237858,null,0.34081612555888291,0.34081612555888291,0.34081612555888291]
["2013-01-28","2013-01-28",null,12.117708323724511,12.421280525380411,12.724852727036311,13.02842492869221,13.33199713034811,13.63556933200401,13.93914153365991,14.24271373531581,14.54628593697171,null,8.209962660726805E-2,0.14905792863532685,0.30970280651035498,0.54263736442925981,0.579386620960049,0.61452711175429708,0.64810089604694676,0.68024466635155978,0.71106357075549165,null,0.30970280651035498,0.30970280651035498,0.30970280651035498]
["2013-01-28T01:00:00","2013-01-28T01:00:00",null,12.10697224356575,12.41054444522165,12.714116646877549,13.017688848533449,13.321261050189349,13.624833251845249,13.928405453501149,14.231977655157049,14.535549856812949,null,4.6349276906357255E-2,0.11585216264842207,0.27891544653262945,0.51416326237335797,0.55311011392987952,0.59036408127997564,0.62594619404111762,0.66002468915307411,0.69269419989446479,null,0.27891544653262945,0.27891544653262945,0.27891544653262945]
["2013-01-28T02:00:00","2013-01-28T02:00:00",null,12.111640285953637,12.415212487609537,12.718784689265437,13.022356890921337,13.325929092577237,13.629501294233137,13.933073495889037,14.236645697544937,14.540217899200837,null,1.0451719883148594E-2,8.2509704147954971E-2,0.24799139404134163,0.48555246780389377,0.52670742919488334,0.56607487310082738,0.60367582913919726,0.63968904905849722,0.67420916613734683,null,0.24799139404134163,0.24799139404134163,0.24799139404134163]
["2013-01-28T03:00:00","2013-01-28T03:00:00",null,12.174355158119877,12.477927359775776,12.781499561431676,13.085071763087576,13.388643964743476,13.692216166399376,13.995788368055276,14.299360569711176,14.602932771367076,null,0,4.9661441658059288E-2,0.21755102275188964,0.45740432481879428,0.50074636642678072,0.54220625727110161,0.58181554177796391,0.61974245688713614,0.65610266549470908,null,0.21755102275188964,0.21755102275188964,0.21755102275188964]
["2013-01-28T04:00:00","2013-01-28T04:00:00",null,12.192434960827843,12.496007162483743,12.799579364139642,13.103151565795542,13.406723767451442,13.710295969107342,14.013868170763242,14.317440372419142,14.621012574075042,null,0,1.5993024086789771E-2,0.18630101118979939,0.42846757117852768,0.47400720781224659,0.51758057521241541,0.55919818818777001,0.59904931329555011,0.63726012824058198,null,0.18630101118979939,0.18630101118979939,0.18630101118979939]
["2013-01-28T05:00:00","2013-01-28T05:00:00",null,12.283546648309068,12.587118849964968,12.890691051620868,13.194263253276768,13.497835454932668,13.801407656588568,14.104979858244468,14.408552059900368,14.712124261556268,null,0,1.7780541571835312E-2,0.19058053834517313,0.43512344510813844,0.4829342804287387,0.52867369842843326,0.57236272872469363,0.61420115268349496,0.6543256628183991,null,0.19058053834517313,0.19058053834517313,0.19058053834517313]
["2013-01-28T06:00:00","2013-01-28T06:00:00",null,12.407308644536462,12.710880846192362,13.014453047848262,13.318025249504162,13.621597451160062,13.925169652815962,14.228741854471862,14.532314056127762,14.835886257783661,null,0,0,0.17394611092551404,0.42095999774133641,0.47112615021870258,0.51911573728780736,0.56496030337485803,0.60885962984582942,0.65097143883175479,null,0.17394611092551404,0.17394611092551404,0.17394611092551404]
["2013-01-28T07:00:00","2013-01-28T07:00:00",null,12.550350342282954,12.853922543938854,13.157494745594754,13.461066947250654,13.764639148906554,14.068211350562454,14.371783552218353,14.675355753874253,14.978927955530153,null,4.395190051464915E-3,7.2762476450089026E-3,0.18397723845924019,0.43361982745895306,0.48629901922411856,0.53668598268493151,0.58483329188507016,0.63094072819050961,0.67516601373228291,null,0.18397723845924019,0.18397723845924019,0.18397723845924019]
["2013-01-28T08:00:00","2013-01-28T08:00:00",null,12.597217950879624,12.900790152535524,13.204362354191424,13.507934555847324,13.811506757503224,14.115078959159124,14.418651160815024,14.722223362470924,15.025795564126824,null,9.8628905939571535E-3,1.5593461354838443E-2,0.19500727282284472,0.44724701958024138,0.50240770620699959,0.55517101644204947,0.60558952432906954,0.65387352604277038,0.70019125852292041,null,0.19500727282284472,0.19500727282284472,0.19500727282284472]
["2013-01-28T09:00:00","2013-01-28T09:00:00",null,12.73625260611102,13.039824807766919,13.343397009422819,13.646969211078719,13.950541412734619,14.254113614390519,14.557685816046419,14.861258017702319,15.164830219358219,null,1.0020612724990583E-2,1.8695329931829232E-2,0.20091659533223055,0.45583761831719555,0.51356391827543091,0.56878769375460225,0.62156151879838817,0.67210620439023483,0.72058998746991065,null,0.20091659533223055,0.20091659533223055,0.20091659533223055]
["2013-01-28T10:00:00","2013-01-28T10:00:00",null,12.896833835827369,13.200406037483269,13.503978239139169,13.807550440795069,14.111122642450969,14.414694844106869,14.718267045762769,15.021839247418669,15.325411449074569,null,6.9082293392642314E-3,1.8558637418266927E-2,0.20362941598600554,0.46127377443348111,0.52159723214940024,0.57932353210763532,0.63448421873439387,0.68732113263059302,0.73801302554473691,null,0.20362941598600554,0.20362941598600554,0.20362941598600554]
["2013-01-28T11:00:00","2013-01-28T11:00:00",null,13.047633309605533,13.351205511261433,13.654777712917333,13.958349914573233,14.261922116229133,14.565494317885033,14.869066519540933,15.172638721196833,15.476210922852733,null,9.9890682987838902E-4,1.5656550207251815E-2,0.2036083863685344,0.46400762470472723,0.52695978460453685,0.58720963865930687,0.64478873129524461,0.69994941792200294,0.75288096509682156,null,0.2036083863685344,0.2036083863685344,0.2036083863685344]
["2013-01-28T12:00:00","2013-01-28T12:00:00",null,13.147934694589356,13.451506896245256,13.755079097901156,14.058651299557056,14.362223501212956,14.665795702868856,14.969367904524756,15.272940106180656,15.576512307836555,null,0,1.3069907258303563E-2,0.20390280101313013,0.46704640442930467,0.53262726651300474,0.59541118947304528,0.65540868811816222,0.71289314747547972,0.76806434891097308,null,0.20390280101313013,0.20390280101313013,0.20390280101313013]
["2013-01-28T13:00:00","2013-01-28T13:00:00",null,13.165487794752405,13.469059996408305,13.772632198064205,14.076204399720105,14.379776601376005,14.683348803031905,14.986921004687805,15.290493206343704,15.594065407999604,null,4.6265158436472791E-3,2.0714173209057135E-2,0.21442812455742769,0.48033712267105505,0.54855720174738121,0.61387519361269216,0.6763016130757239,0.73612035997233616,0.79354173047723986,null,0.21442812455742769,0.21442812455742769,0.21442812455742769]
["2013-01-28T14:00:00","2013-01-28T14:00:00",null,13.015674317212159,13.319246518868059,13.622818720523959,13.926390922179859,14.229963123835759,14.533535325491659,14.837107527147559,15.140679728803459,15.444251930459359,null,0,1.1934307914862868E-2,0.2084451983868929,0.47702495791935301,0.54781065032715626,0.61557859262785319,0.68034981443891529,0.74242924521367337,0.80201666631810287,null,0.2084451983868929,0.2084451983868929,0.2084451983868929]
["2013-01-28T15:00:00","2013-01-28T15:00:00",null,13.409594065587072,13.713166267242972,14.016738468898872,14.320310670554772,14.623882872210672,14.927455073866572,15.231027275522472,15.534599477178372,15.838171678834271,null,9.7051684629237238E-3,2.4804433807190752E-2,0.22433307438632707,0.49580440632106676,0.56936600823505834,0.63979419714585251,0.7071205174796561,0.77164989868980016,0.8336031517597311,null,0.22433307438632707,0.22433307438632707,0.22433307438632707]
["2013-01-28T16:00:00","2013-01-28T16:00:00",null,13.256233439502406,13.559805641158306,13.863377842814206,14.166950044470106,14.470522246126006,14.774094447781906,15.077666649437806,15.381238851093705,15.684811052749605,null,2.367934927248562E-2,4.1912027619950123E-2,0.24443738868872161,0.51877926340826974,0.59508523040224304,0.66815263630566324,0.73800251073600165,0.80496081276406062,0.8692588681820218,null,0.24443738868872161,0.24443738868872161,0.24443738868872161]
["2013-01-28T17:00:00","2013-01-28T17:00:00",null,13.139748750649183,13.443320952305083,13.746893153960983,14.050465355616883,14.354037557272783,14.657609758928682,14.961181960584582,15.264754162240482,15.568326363896382,null,4.2132838603396922E-2,6.3435841101645532E-2,0.26889483380763884,0.54603364765084639,0.62503140568112359,0.70066442491602099,0.77298527939921646,0.84231992820151236,0.90889969711509055,null,0.26889483380763884,0.26889483380763884,0.26889483380763884]
["2013-01-28T18:00:00","2013-01-28T18:00:00",null,12.999504904676531,13.303077106332431,13.606649307988331,13.910221509644231,14.213793711300131,14.517365912956031,14.820938114611931,15.12451031626783,15.42808251792373,null,6.3078337604636422E-2,8.7430634636198018E-2,0.295802229361942,0.57571695271133794,0.65738547216044785,0.73556307510935126,0.81033388002793272,0.88202384598699446,0.95085378396998288,null,0.295802229361942,0.295802229361942,0.295802229361942]
["2013-01-28T19:00:00","2013-01-28T19:00:00",null,13.050722345274504,13.354294546930404,13.657866748586304,13.961438950242204,14.265011151898104,14.568583353554004,14.872155555209904,15.175727756865804,15.479299958521704,null,8.499119900954763E-2,0.11235073133947995,0.32360338365876795,0.60627298689688114,0.69057020852988149,0.77128188038405532,0.84847109131181608,0.922484830001437,0.99355442224510016,null,0.32360338365876795,0.32360338365876795,0.32360338365876795]
["2013-01-28T20:00:00","2013-01-28T20:00:00",null,12.974786103119232,13.278358304775132,13.581930506431032,13.885502708086932,14.189074909742832,14.492647111398732,14.796219313054632,15.099791514710532,15.403363716366432,null,0.10678839751836765,0.1371867095728774,0.35133093429444495,0.63676593223001088,0.72371288566437286,0.8069691412325527,0.88658727297822837,0.96293529920714405,1,null,0.35133093429444495,0.35133093429444495,0.35133093429444495]
["2013-01-28T21:00:00","2013-01-28T21:00:00",null,12.999248911944935,13.302821113600835,13.606393315256735,13.909965516912635,14.213537718568535,14.517109920224435,14.820682121880335,15.124254323536235,15.427826525192135,null,0.12772338171087158,0.16116047348995877,0.37821730023127698,0.66643872248176683,0.75604592252622604,0.84185727661714738,0.92392535879820903,1,1,null,0.37821730023127698,0.37821730023127698,0.37821730023127698]
["2013-01-28T22:00:00","2013-01-28T22:00:00",null,12.832941196751673,13.136513398407573,13.440085600063473,13.743657801719372,14.047230003375272,14.350802205031172,14.654374406687072,14.957946608342972,15.261518809998872,null,0.15499879557091939,0.19138003379596394,0.41124431446967724,0.7021470129477354,0.79431982632367171,0.88259164565871451,0.96701504499654212,1,1,null,0.41124431446967724,0.41124431446967724,0.41124431446967724]
["2013-01-28T23:00:00","2013-01-28T23:00:00",null,12.718942909731961,13.022515111387861,13.326087313043761,13.629659514699661,13.933231716355561,14.236803918011461,14.540376119667361,14.843948321323261,15.147520522979161,null,0.18650116254266313,0.2257529435525161,0.44834055968873998,0.7418614455419531,0.83652626858821755,0.92718494950623298,1,1,1,null,0.44834055968873998,0.44834055968873998,0.44834055968873998]
["2013-01-29","2013-01-29",null,12.687981269034005,12.991553470689905,13.295125672345804,13.598697874001704,13.902270075657604,14.205842277313504,14.509414478969404,14.812986680625304,15.116558882281204,null,0.21917067328405426,0.26127196746124454,0.48656188944250783,0.78267993305340477,0.87981573615252628,0.97285076384477875,1,1,1,null,0.48656188944250783,0.48656188944250783,0.48656188944250783]
["2013-01-29T01:00:00","2013-01-29T01:00:00",null,12.633211260621326,12.936783462277226,13.240355663933126,13.543927865589026,13.847500067244926,14.151072268900826,14.454644470556726,14.758216672212626,15.061788873868526,null,0.24950589648615062,0.29441464459573596,0.52237532799583197,0.82104847012947046,0.92062370885524236,1,1,1,1,null,0.52237532799583197,0.52237532799583197,0.52237532799583197]
["2013-01-29T02:00:00","2013-01-29T02:00:00",null,12.651577280390793,12.955149482046693,13.258721683702593,13.562293885358493,13.865866087014393,14.169438288670293,14.473010490326192,14.776582691982092,15.080154893637992,null,0.27434187471954807,0.32206859157026402,0.55271055119792833,0.85394930666304392,0.95598501063293739,1,1,1,1,null,0.55271055119792833,0.55271055119792833,0.55271055119792833]
["2013-01-29T03:00:00","2013-01-29T03:00:00",null,12.633316427905243,12.936888629561142,13.240460831217042,13.544033032872942,13.847605234528842,14.151177436184742,14.454749637840642,14.758321839496542,15.061894041152442,null,0.29642297306422827,0.34694662903860368,0.58026986489383636,0.88406371888169344,0.9885388584782373,1,1,1,1,null,0.58026986489383636,0.58026986489383636,0.58026986489383636]
["2013-01-29T04:00:00","2013-01-29T04:00:00",null,12.663897491517016,12.967469693172916,13.271041894828816,13.574614096484716,13.878186298140616,14.181758499796516,14.485330701452416,14.788902903108315,15.092475104764215,null,0.31137503108619741,0.36471665580170348,0.60074219750197555,0.90710166482130983,1,1,1,1,1,null,0.60074219750197555,0.60074219750197555,0.60074219750197555]
["2013-01-29T05:00:00","2013-01-29T05:00:00",null,12.833579705332962,13.137151906988862,13.440724108644762,13.744296310300662,14.047868511956562,14.351440713612462,14.655012915268362,14.958585116924262,15.262157318580162,null,0.31452947370686601,0.37080473005959386,0.60963772569226105,0.91867846923916363,1,1,1,1,1,null,0.60963772569226105,0.60963772569226105,0.60963772569226105]
["2013-01-29T06:00:00","2013-01-29T06:00:00",null,12.938382472799276,13.241954674455176,13.545526876111076,13.849099077766976,14.152671279422876,14.456243481078776,14.759815682734676,15.063387884390576,15.366960086046475,null,0.31688479086363192,0.37610419366231712,0.61774464322737932,0.92947717781058581,1,1,1,1,1,null,0.61774464322737932,0.61774464322737932,0.61774464322737932]
["2013-01-29T07:00:00","2013-01-29T07:00:00",null,12.905620346116017,13.209192547771917,13.512764749427816,13.816336951083716,14.119909152739616,14.423481354395516,14.727053556051416,15.030625757707316,15.334197959363216,null,0.3174420757266167,0.37964768420620154,0.62413764693860097,0.93859351698431803,1,1,1,1,1,null,0.62413764693860097,0.62413764693860097,0.62413764693860097]
["2013-01-29T08:00:00","2013-01-29T08:00:00",null,12.975526237433385,13.279098439089285,13.582670640745185,13.886242842401085,14.189815044056985,14.493387245712885,14.796959447368785,15.100531649024685,15.404103850680585,null,0.31513933261352861,0.3803732060089553,0.62776525595236987,0.94498652069553968,1,1,1,1,1,null,0.62776525595236987,0.62776525595236987,0.62776525595236987]
["2013-01-29T09:00:00","2013-01-29T09:00:00",null,13.069508689373496,13.373080891029396,13.676653092685296,13.980225294341196,14.283797495997096,14.587369697652996,14.890941899308896,15.194514100964795,15.498086302620695,null,0.31226878982872019,0.38053092813998873,0.63080403567694732,0.95079069511756986,1,1,1,1,1,null,0.63080403567694732,0.63080403567694732,0.63080403567694732]
["2013-01-29T10:00:00","2013-01-29T10:00:00",null,13.058075904325278,13.361648105981178,13.665220307637078,13.968792509292978,14.272364710948878,14.575936912604778,14.879509114260678,15.183081315916578,15.486653517572478,null,0.30998707633310324,0.38126696475147809,0.63442112988198063,0.95716266921132043,1,1,1,1,1,null,0.63442112988198063,0.63442112988198063,0.63442112988198063]
["2013-01-29T11:00:00","2013-01-29T11:00:00",null,13.149305796809081,13.452877998464981,13.756450200120881,14.060022401776781,14.363594603432681,14.667166805088581,14.970739006744481,15.27431120840038,15.57788341005628,null,0.30429856480716422,0.37865929218505873,0.63474708895278309,0.9602960822145179,1,1,1,1,1,null,0.63474708895278309,0.63474708895278309,0.63474708895278309]
["2013-01-29T12:00:00","2013-01-29T12:00:00",null,13.20995012300326,13.51352232465916,13.81709452631506,14.12066672797096,14.42423892962686,14.72781113128276,15.03138333293866,15.33495553459456,15.63852773625046,null,0.29646503229917054,0.37393814306279138,0.63299111589394419,0.96138962232301639,1,1,1,1,1,null,0.63299111589394419,0.63299111589394419,0.63299111589394419]
["2013-01-29T13:00:00","2013-01-29T13:00:00",null,13.36532888311838,13.66890108477428,13.97247328643018,14.27604548808608,14.57961768974198,14.88318989139788,15.18676209305378,15.49033429470968,15.79390649636558,null,0.28562426449280615,0.36623078825962446,0.62828048158041239,0.95954953079429306,1,1,1,1,1,null,0.62828048158041239,0.62828048158041239,0.62828048158041239]
["2013-01-29T14:00:00","2013-01-29T14:00:00",null,13.44980940782542,13.75338160948132,14.05695381113722,14.36052601279312,14.66409821444902,14.967670416104919,15.271242617760819,15.574814819416719,15.878387021072619,null,0.2720286167977245,0.3558106128026825,0.62089908584804787,0.95509125189041477,0.99832814541104564,1,1,1,1,null,0.62089908584804787,0.62089908584804787,0.62089908584804787]
["2013-01-29T15:00:00","2013-01-29T15:00:00",null,13.042602734908133,13.346174936564033,13.649747138219933,13.953319339875833,14.256891541531733,14.560463743187633,14.864035944843533,15.167608146499433,15.471180348155332,null,0.27331142346346304,0.36003756591437841,0.62793349289213884,0.96481744997080965,1,1,1,1,1,null,0.62793349289213884,0.62793349289213884,0.62793349289213884]
["2013-01-29T16:00:00","2013-01-29T16:00:00",null,11.811096831708642,12.114669033364542,12.418241235020442,12.721813436676342,13.025385638332242,13.328957839988142,13.632530041644042,13.936102243299942,14.239674444955842,null,0.29036644323254462,0.37993158404206173,0.65052981686486155,0.98998990208374504,1,1,1,1,1,null,0.65052981686486155,0.65052981686486155,0.65052981686486155]
["2013-01-29T17:00:00","2013-01-29T17:00:00",null,11.79768756145841,12.10125976311431,12.40483196477021,12.70840416642611,13.01197636808201,13.31554856973791,13.61912077139381,13.92269297304971,14.22626517470561,null,0.30772639245495748,0.40012001681434078,0.67341004067344445,1,1,1,1,1,1,null,0.67341004067344445,0.67341004067344445,0.67341004067344445]
["2013-01-29T18:00:00","2013-01-29T18:00:00",null,11.562978144573906,11.866550346229806,12.170122547885706,12.473694749541606,12.777266951197506,13.080839152853406,13.384411354509306,13.687983556165205,13.991555757821105,null,0.33870301898992311,0.43364122706331243,0.70934965693159535,1,1,1,1,1,1,null,0.70934965693159535,0.70934965693159535,0.70934965693159535]
["2013-01-29T19:00:00","2013-01-29T19:00:00",null,10.903844330621721,11.207416532277621,11.510988733933521,11.814560935589421,12.118133137245321,12.421705338901221,12.725277540557121,13.028849742213021,13.332421943868921,null,0.37353858033084003,0.47106343135317758,0.74923232646558202,1,1,1,1,1,1,null,0.74923232646558202,0.74923232646558202,0.74923232646558202]
["2013-01-29T20:00:00","2013-01-29T20:00:00",null,10.927391055063676,11.230963256719575,11.534535458375474,11.838107660031374,12.141679861687274,12.445252063343174,12.748824264999074,13.052396466654974,13.355968668310874,null,0.41058225150622496,0.51063065662509732,0.79118641332047435,1,1,1,1,1,1,null,0.79118641332047435,0.79118641332047435,0.79118641332047435]
["2013-01-29T21:00:00","2013-01-29T21:00:00",null,10.896093327571913,11.199665529227813,11.503237730883713,11.806809932539613,12.110382134195513,12.413954335851413,12.717526537507313,13.021098739163213,13.324670940819113,null,0.45259942721353069,0.55503469391537563,0.83786164929763407,1,1,1,1,1,1,null,0.83786164929763407,0.83786164929763407,0.83786164929763407]
["2013-01-29T22:00:00","2013-01-29T22:00:00",null,10.444881386639757,10.748453588295657,11.052025789951557,11.355597991607457,11.659170193263357,11.962742394919257,12.266314596575157,12.569886798231057,12.873458999886957,null,0.49600455767393059,0.60090028961989705,0.88606153254145026,1,1,1,1,1,1,null,0.88606153254145026,0.88606153254145026,0.88606153254145026]
["2013-01-29T23:00:00","2013-01-29T23:00:00",null,10.338986935637092,10.642559137292992,10.946131338948891,11.249703540604791,11.553275742260691,11.856847943916591,12.160420145572491,12.463992347228391,12.767564548884291,null,0.54089227616604474,0.648216928929926,0.93568091496456729,1,1,1,1,1,1,null,0.93568091496456729,0.93568091496456729,0.93568091496456729]
["2013-01-30","2013-01-30",null,10.146389648701938,10.449961850357838,10.753534052013737,11.057106253669637,11.360678455325537,11.664250656981437,11.967822858637337,12.271395060293237,12.574967261949137,null,0.58861899301676068,0.69834102217235006,0.98807620689387277,1,1,1,1,1,1,null,0.98807620689387277,0.98807620689387277,0.98807620689387277]
["2013-01-30T01:00:00","2013-01-30T01:00:00",null,10.055482444105566,10.359054645761466,10.662626847417364,10.966199049073264,11.269771250729164,11.573343452385064,11.876915654040964,12.180487855696864,12.484060057352764,null,0.63743924997597501,0.74954814071453701,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-30T02:00:00","2013-01-30T02:00:00",null,9.9618278101135829,10.265400011769483,10.568972213425383,10.872544415081283,11.176116616737183,11.479688818393083,11.783261020048982,12.086833221704882,12.390405423360782,null,0.64824847335613278,0.76273371086893171,1,1,1,1,1,1,1,null,1,1,1]
["2013-01-30T03:00:00","2013-01-30T03:00:00",null,9.8522863376974446,10.155858539353344,10.459430741009244,10.763002942665144,11.066575144321044,11.370147345976944,11.673719547632844,11.977291749288744,12.280863950944644,null,0.63531525861139149,0.75213478366348518,0.99159866782028594,0.99367008514119171,0.99563635437474174,0.99748696071220067,0.99924293377103957,1,1,null,0.99159866782028594,0.99159866782028594,0.99159866782028594]
["2013-01-30T04:00:00","2013-01-30T04:00:00",null,9.9151424457587147,10.218714647414615,10.522286849070515,10.825859050726415,11.129431252382314,11.433003454038214,11.736575655694114,12.040147857350014,12.343720059005914,null,0.62651436369972613,0.7455314837775523,0.98706678525525871,0.99109395700097902,0.99491083257198798,0.99850689715955021,1,1,1,null,0.98706678525525871,0.98706678525525871,0.98706678525525871]
["2013-01-30T05:00:00","2013-01-30T05:00:00",null,9.7615009799854633,10.065073181641363,10.368645383297263,10.672217584953161,10.975789786609061,11.279361988264961,11.582934189920861,11.886506391576761,12.190078593232661,null,0.61862825714805458,0.73985348706034881,0.98346020585896099,0.98944313202949574,0.99511061393796363,1,1,1,1,null,0.98346020585896099,0.98346020585896099,0.98346020585896099]
["2013-01-30T06:00:00","2013-01-30T06:00:00",null,9.7043313131927533,10.007903514848653,10.311475716504553,10.615047918160453,10.918620119816353,11.222192321472253,11.525764523128153,11.829336724784053,12.132908926439953,null,0.61015332130719158,0.73360769067142495,0.97931737121714957,0.98728759623870554,0.99482671410210344,1,1,1,1,null,0.97931737121714957,0.97931737121714957,0.97931737121714957]
["2013-01-30T07:00:00","2013-01-30T07:00:00",null,9.5739853647854147,9.8775575664413147,10.181129768097215,10.484701969753115,10.788274171409014,11.091846373064914,11.395418574720814,11.698990776376714,12.002562978032614,null,0.60121573388196392,0.72695181674181419,0.97480651826959352,0.9847955865683774,0.99423788481291198,1,1,1,1,null,0.97480651826959352,0.97480651826959352,0.97480651826959352]
["2013-01-30T08:00:00","2013-01-30T08:00:00",null,9.5817738712569991,9.885346072912899,10.188918274568799,10.492490476224699,10.796062677880599,11.099634879536499,11.403207081192399,11.706779282848299,12.010351484504199,null,0.59181549487237151,0.71984380603657427,0.9698540433551438,0.98187246973989117,0.99323897798303362,1,1,1,1,null,0.9698540433551438,0.9698540433551438,0.9698540433551438]
["2013-01-30T09:00:00","2013-01-30T09:00:00",null,9.5805087630333787,9.8840809646892787,10.187653166345179,10.491225368001079,10.794797569656978,11.098369771312878,11.401941972968778,11.705514174624678,12.009086376280578,null,0.58247834471519244,0.71279888418374771,0.96496465729310743,0.9790124417638183,0.99229264519683302,1,1,1,1,null,0.96496465729310743,0.96496465729310743,0.96496465729310743]
["2013-01-30T10:00:00","2013-01-30T10:00:00",null,9.7135696606165567,10.017141862272457,10.320714063928355,10.624286265584255,10.927858467240155,11.231430668896055,11.535002870551955,11.838575072207854,12.142147273863754,null,0.56953461516171566,0.70222098659577237,0.95661589915707124,0.97276664537489443,0.98803414765893038,0.99761313841702748,0.99939014109333746,1,1,null,0.95661589915707124,0.95661589915707124,0.95661589915707124]
["2013-01-30T11:00:00","2013-01-30T11:00:00",null,9.7946247638031796,10.09819696545908,10.401769167114979,10.705341368770879,11.008913570426779,11.312485772082679,11.616057973738579,11.919630175394479,12.223202377050379,null,0.55595999708410515,0.69102271529239889,0.94764676730563691,0.96590047527057243,0.98315527640562961,0.99460590311865671,0.99817042328001226,1,1,null,0.94764676730563691,0.94764676730563691,0.94764676730563691]
["2013-01-30T12:00:00","2013-01-30T12:00:00",null,9.960871935345784,10.264444137001684,10.568016338657584,10.871588540313484,11.175160741969384,11.478732943625284,11.782305145281184,12.085877346937083,12.389449548592983,null,0.54098690944466488,0.67842597442719565,0.93727916589237281,0.95764635041315627,0.97689896520797026,0.99024225749339845,0.99559429513979958,0.99912727087494835,1,null,0.93727916589237281,0.93727916589237281,0.93727916589237281]
["2013-01-30T13:00:00","2013-01-30T13:00:00",null,9.9112449432393905,10.21481714489529,10.51838934655119,10.82196154820709,11.12553374986299,11.42910595151889,11.73267815317479,12.03625035483069,12.33982255648659,null,0.52479410399189941,0.66465157498360938,0.92577596513566796,0.94829868544724161,0.9695806583280191,0.98484816061205516,0.99201926016970854,0.99728717934622502,0.99981073344275984,null,0.92577596513566796,0.92577596513566796,0.92577596513566796]
["2013-01-30T14:00:00","2013-01-30T14:00:00",null,9.9168208883333318,10.220393089989232,10.523965291645132,10.827537493301032,11.131109694956931,11.434681896612831,11.738254098268731,12.041826299924631,12.345398501580531,null,0.50835945793821602,0.65063533493910519,0.91404143858678077,0.93871969468914462,0.96204154046462109,0.97924376755600062,0.98824444383364174,0.99524730645152604,0.99942168551954402,null,0.91404143858678077,0.91404143858678077,0.91404143858678077]
["2013-01-30T15:00:00","2013-01-30T15:00:00",null,9.9601747160018235,10.263746917657723,10.567319119313623,10.870891320969523,11.174463522625423,11.478035724281323,11.781607925937223,12.085180127593123,12.388752329249023,null,0.48963258358018008,0.63438995544266186,0.90013034662963221,0.92701671256646412,0.95243100528031743,0.97161001641398259,0.98248232864655372,0.99127270874948359,0.99713997202392712,null,0.90013034662963221,0.90013034662963221,0.90013034662963221]
["2013-01-30T16:00:00","2013-01-30T16:00:00",null,10.023721465691622,10.327293667347522,10.63086586900342,10.93443807065932,11.23801027231522,11.54158247397112,11.84515467562702,12.14872687728292,12.45229907893882,null,0.46753045561802875,0.61485344081198767,0.88301223800813733,0.91218031744058614,0.93976066075396525,0.96099005959106498,0.97379709663097946,0.98443808307136826,0.9920613194046507,null,0.88301223800813733,0.88301223800813733,0.88301223800813733]
["2013-01-30T17:00:00","2013-01-30T17:00:00",null,9.9557046273115191,10.259276828967419,10.562849030623319,10.866421232279219,11.169993433935119,11.473565635591019,11.777137837246919,12.080710038902819,12.384282240558719,null,0.44520751667243064,0.59511714481533784,0.86571537763813788,0.89718620018367479,0.92694310890531517,0.95023341025458508,0.96499620171931411,0.97749830930589732,0.98688803350675425,null,0.86571537763813788,0.86571537763813788,0.86571537763813788]
["2013-01-30T19:00:00","2013-01-30T19:00:00",null,9.6674667857481467,9.9710389874040466,10.274611189059948,10.578183390715848,10.881755592371748,11.185327794027648,11.488899995683548,11.792472197339448,12.096044398995348,null,0.43094943602700858,0.58327747017909504,0.85615741649751198,0.8897732600251036,0.92154901202397188,0.94675300856311406,0.96333486193909534,0.97755088334957507,0.98858091771317969,null,0.85615741649751198,0.85615741649751198,0.85615741649751198]
["2013-01-30T20:00:00","2013-01-30T20:00:00",null,9.6307110747575475,9.9342832764134474,10.237855478069347,10.541427679725247,10.844999881381147,11.148572083037047,11.452144284692947,11.755716486348847,12.059288688004747,null,0.41731172909698466,0.57200559521457262,0.8471146809849287,0.88282297145089716,0.91657550749205108,0.94365113998612327,0.96200999603841453,0.97790838684658421,0.99052615732925864,null,0.8471146809849287,0.8471146809849287,0.8471146809849287]
["2013-01-30T21:00:00","2013-01-30T21:00:00",null,9.4817219498911047,9.7852941515470047,10.088866353202905,10.392438554858805,10.696010756514704,10.999582958170604,11.303155159826504,11.606727361482404,11.910299563138304,null,0.40148694194996387,0.5585676696505244,0.83591640968155523,0.87372766189463602,0.90947801159554675,0.93842528004454895,0.95856113877315019,0.97615241378774531,0.99036843519822526,null,0.83591640968155523,0.83591640968155523,0.83591640968155523]
["2013-01-30T22:00:00","2013-01-30T22:00:00",null,9.3713630743019429,9.6749352759578429,9.9785074776137428,10.282079679269643,10.585651880925543,10.889224082581443,11.192796284237343,11.496368485893242,11.799940687549142,null,0.3880595311946512,0.54747454643450655,0.82702088149126973,0.8668930362165207,0.90458862553351038,0.93537598551123602,0.95724678768120497,0.97648888766728326,0.99227161557936194,null,0.82702088149126973,0.82702088149126973,0.82702088149126973]
["2013-01-30T23:00:00","2013-01-30T23:00:00",null,9.3304421332735661,9.634014334929466,9.9375865365853659,10.241158738241266,10.544730939897166,10.848303141553066,11.151875343208966,11.455447544864866,11.759019746520766,null,0.37690331912621994,0.53858953305295665,0.82027037428303895,0.86215085747678222,0.9017391123661731,0.9343139898289442,0.95786716139660311,0.9787075123104868,0.99600437268048647,null,0.82027037428303895,0.82027037428303895,0.82027037428303895]
["2013-01-31","2013-01-31",null,9.1777144578070331,9.481286659462933,9.784858861118833,10.088431062774733,10.392003264430633,10.695575466086533,10.999147667742433,11.302719869398333,11.606292071054233,null,0.36665138060904701,0.53060879322266508,0.81443465543480209,0.85832346709703766,0.89980438755882974,0.93416678250664631,0.95940232347199517,0.98184092531368428,1,null,0.81443465543480209,0.81443465543480209,0.81443465543480209]
["2013-01-31T01:00:00","2013-01-31T01:00:00",null,9.1983211581762436,9.5018933598321436,9.8054655614880435,10.109037763143943,10.412609964799843,10.716182166455743,11.019754368111643,11.323326569767543,11.626898771423443,null,0.35933307372909584,0.5254670517509753,0.81134330166654689,0.85715632332739033,0.90045630570043456,0.93652209966341216,0.96337692117403761,0.98734017028238319,1,null,0.81134330166654689,0.81134330166654689,0.81134330166654689]
["2013-01-31T02:00:00","2013-01-31T02:00:00",null,8.9878702424160082,9.2914424440719081,9.595014645727808,9.898586847383708,10.202159049039608,10.505731250695508,10.809303452351408,11.112875654007308,11.416447855663208,null,0.35229866668500487,0.52065126935008788,0.80860945139530072,0.85637822748095871,0.90151830138272637,0.93931903878707168,0.96780365565170923,0.99331258164418246,1,null,0.80860945139530072,0.80860945139530072,0.80860945139530072]
["2013-01-31T03:00:00","2013-01-31T03:00:00",null,9.080236020224012,9.3838082218799119,9.6873804235358119,9.9909526251917118,10.294524826847612,10.598097028503512,10.901669230159412,11.205241431815312,11.508813633471211,null,0.34789296182480439,0.51835904104573538,0.80830452194196944,0.85793441917382185,0.90481995132569282,0.9442715137015214,0.97432283706775769,1,1,null,0.80830452194196944,0.80830452194196944,0.80830452194196944]
["2013-01-31T04:00:00","2013-01-31T04:00:00",null,8.9620899778614813,9.2656621795173812,9.5692343811732812,9.8728065828291811,10.176378784485081,10.479950986140981,10.783523187796881,11.087095389452781,11.390667591108681,null,0.34243577609104769,0.51507842072024002,0.80706377451117317,0.85860736693289785,0.90729093137854988,0.9484458927695395,0.98009546706358119,1,1,null,0.80706377451117317,0.80706377451117317,0.80706377451117317]
["2013-01-31T05:00:00","2013-01-31T05:00:00",null,9.1163559650900936,9.4199281667459935,9.7235003684018935,10.027072570057795,10.330644771713695,10.634216973369595,10.937789175025495,11.241361376681395,11.544933578337295,null,0.33582196139637921,0.51064117143383281,0.80466639811946505,0.85812368573106201,0.9086157972792307,0.95146364287664575,0.98472198290722845,1,1,null,0.80466639811946505,0.80466639811946505,0.80466639811946505]
["2013-01-31T06:00:00","2013-01-31T06:00:00",null,9.0735555441467159,9.3771277458026159,9.6806999474585158,9.9842721491144175,10.287844350770317,10.591416552426217,10.894988754082117,11.198560955738017,11.502133157393917,null,0.3276940142437898,0.50475287854191808,0.80087055216592717,0.85629410901107428,0.90864734170543737,0.95324064555295573,0.98813929574628612,1,1,null,0.80087055216592717,0.80087055216592717,0.80087055216592717]
["2013-01-31T07:00:00","2013-01-31T07:00:00",null,9.0801040643811994,9.3836762660370994,9.6872484676929993,9.9908206693488992,10.294392871004799,10.597965072660699,10.901537274316599,11.205109475972499,11.508681677628399,null,0.31920856359419125,0.49851759696172981,0.79674874714158683,0.85414908802901968,0.90836344186957718,0.95471271877593444,0.99126219394074799,1,1,null,0.79674874714158683,0.79674874714158683,0.79674874714158683]
["2013-01-31T08:00:00","2013-01-31T08:00:00",null,9.0708698580164651,9.374442059672365,9.6780142613282649,9.9815864629841649,10.285158664640065,10.588730866295965,10.892303067951865,11.195875269607765,11.499447471263665,null,0.30712704835703053,0.48880191369007053,0.7892516885131311,0.84873396153020519,0.90491458460431284,0.95310395303939344,0.99139888645431029,1,1,null,0.7892516885131311,0.7892516885131311,0.7892516885131311]
["2013-01-31T09:00:00","2013-01-31T09:00:00",null,9.4485381217151971,9.7521103233710971,10.055682525026997,10.359254726682897,10.662826928338797,10.966399129994697,11.269971331650597,11.573543533306497,11.877115734962397,null,0.29320544159114642,0.47720407965474565,0.77985144950353869,0.84139462503278295,0.89952048772296955,0.94954994768677348,0.98957982454305804,0.99983176306023103,1,null,0.77985144950353869,0.77985144950353869,0.77985144950353869]
["2013-01-31T10:00:00","2013-01-31T10:00:00",null,9.732421855577762,10.035994057233662,10.339566258889562,10.643138460545462,10.946710662201362,11.250282863857262,11.553855065513162,11.857427267169061,12.160999468824961,null,0.27501482247862419,0.46141083693393153,0.76631889066087044,0.82998605755469823,0.89012024871337714,0.94204237424958226,0.98387028339964788,0.9958361357407175,0.99762365322576296,null,0.76631889066087044,0.76631889066087044,0.76631889066087044]
["2013-01-31T11:00:00","2013-01-31T11:00:00",null,10.213230664489101,10.516802866145001,10.820375067800899,11.123947269456799,11.427519471112699,11.731091672768599,12.034663874424499,12.338236076080399,12.641808277736299,null,0.24614115769077094,0.43512381509502651,0.74248181925735135,0.80846224407300282,0.8707835154486786,0.92477705830578949,0.96858175149814074,0.98241923979414036,0.9859942747642314,null,0.74248181925735135,0.74248181925735135,0.74248181925735135]
["2013-01-31T12:00:00","2013-01-31T12:00:00",null,10.575393120554743,10.878965322210643,11.182537523866543,11.486109725522443,11.789681927178343,12.093254128834243,12.396826330490143,12.700398532146043,13.003970733801943,null,0.20991764159675985,0.40161311965479041,0.71153673714859234,0.77994608278215871,0.84457009727092258,0.90075072034503034,0.94663734566702284,0.9624516180053081,0.96791931854780033,null,0.71153673714859234,0.71153673714859234,0.71153673714859234]
["2013-01-31T13:00:00","2013-01-31T13:00:00",null,10.714037353465725,11.017609555121625,11.321181756777525,11.624753958433425,11.928326160089325,12.231898361745225,12.535470563401125,12.839042765057025,13.142614966712925,null,0.17045556441219567,0.36491643716767902,0.67745824203663585,0.74834908253179488,0.81532841417732471,0.8737486915121071,0.92175930819868312,0.93960293862293187,0.94700536397276747,null,0.67745824203663585,0.67745824203663585,0.67745824203663585]
["2013-01-31T14:00:00","2013-01-31T14:00:00",null,10.865150494947402,11.168722696603302,11.472294898259202,11.775867099915102,12.079439301571002,12.383011503226902,12.686583704882802,12.990155906538702,13.293728108194601,null,0.12727124493524256,0.32456060124059205,0.63978368233711724,0.71321910654628229,0.78261684420099131,0.8433293498401262,0.8935270467436992,0.9134526092975892,0.92284233349844602,null,0.63978368233711724,0.63978368233711724,0.63978368233711724]
["2013-01-31T15:00:00","2013-01-31T15:00:00",null,10.977137776927206,11.280709978583106,11.584282180239006,11.887854381894906,12.191426583550806,12.494998785206706,12.798570986862606,13.102143188518506,13.405715390174405,null,8.2341467208186137E-2,0.28248033668087291,0.6004057236224376,0.67640676116307974,0.74824393444443915,0.81126969800539772,0.86367550474343868,0.88570402904444112,0.89710208171379024,null,0.6004057236224376,0.6004057236224376,0.6004057236224376]
["2013-01-31T16:00:00","2013-01-31T16:00:00",null,10.967879246833423,11.271451448489323,11.575023650145223,11.878595851801123,12.182168053457023,12.485740255112923,12.789312456768823,13.092884658424722,13.396456860080622,null,3.7895370682965571E-2,0.24088375332298964,0.56150093130085821,0.64005706736424195,0.71432316146351615,0.77965166813756281,0.83426558471007173,0.85838655594945101,0.87179293708729255,null,0.56150093130085821,0.56150093130085821,0.56150093130085821]
["2013-01-31T17:00:00","2013-01-31T17:00:00",null,10.837648112095684,11.141220313751584,11.444792515407483,11.748364717063383,12.051936918719283,12.355509120375183,12.659081322031083,12.962653523686983,13.266225725342883,null,0,0.20189484253152576,0.5251617523107559,0.60624144247067457,0.6828943981529213,0.75049410351384938,0.80727407068588408,0.83345594443743354,0.84882859480882511,null,0.5251617523107559,0.5251617523107559,0.5251617523107559]
["2013-02-01T01:00:00","2013-02-01T01:00:00",null,9.0999556870013549,9.4035278886572549,9.7071000903131548,10.010672291969055,10.314244493624955,10.617816695280855,10.921388896936755,11.224961098592654,11.528533300248554,null,0,0.19846701488373256,0.52374225313145506,0.60671460886377482,0.68514456722233152,0.75442664198094955,0.81279434527205408,0.84046932186405343,0.85726147141474585,null,0.52374225313145506,0.52374225313145506,0.52374225313145506]
["2013-02-01T02:00:00","2013-02-01T02:00:00",null,9.0260308603864949,9.3296030620423949,9.6331752636982948,9.9367474653541947,10.240319667010095,10.543891868665995,10.847464070321895,11.151036271977794,11.454608473633694,null,0,0.19544926477662627,0.52274334630157671,0.60760836760629755,0.68782584344989983,0.75879028760620781,0.81874572701638215,0.8479138064488313,0.86612545517882467,null,0.52274334630157671,0.52274334630157671,0.52274334630157671]
["2013-02-01T03:00:00","2013-02-01T03:00:00",null,8.879910638306157,9.1834828399620569,9.4870550416179569,9.790627243273855,10.094199444929755,10.397771646585655,10.701343848241555,11.004916049897455,11.308488251553355,null,0,0.19298879953250478,0.52231223914341862,0.60908044082927626,0.69108543415792401,0.76374276252065754,0.82528593804990169,0.85594712032280063,0.87558878304083043,null,0.52231223914341862,0.52231223914341862,0.52231223914341862]
["2013-02-01T04:00:00","2013-02-01T04:00:00",null,8.7969573860975316,9.1005295877534316,9.4041017894093315,9.7076739910652314,10.011246192721131,10.314818394377031,10.618390596032931,10.921962797688831,11.225534999344731,null,0,0.19143260783964161,0.52277489072778338,0.61143575798604211,0.69521775399099983,0.76954693694268772,0.83266733378226621,0.86481110408687933,0.8858617511754745,null,0.52277489072778338,0.52277489072778338,0.52277489072778338]
["2013-02-01T05:00:00","2013-02-01T05:00:00",null,8.7446817973433131,9.048253998999213,9.3518262006551129,9.6553984023110129,9.9589706039669128,10.262542805622813,10.566115007278713,10.869687208934613,11.173259410590513,null,0,0.18898265740425566,0.52238584280456757,0.61298143487016976,0.69857197797764414,0.77460455994449307,0.83933372252061256,0.87299162528314656,0.89548280116851375,null,0.52238584280456757,0.52238584280456757,0.52238584280456757]
["2013-02-01T06:00:00","2013-02-01T06:00:00",null,8.7075147356575702,9.0110869373134701,9.31465913896937,9.61823134062527,9.9218035422811699,10.22537574393707,10.52894794559297,10.83252014724887,11.13609234890477,null,0,0.18466107101393966,0.5201882477788351,0.61278165350419411,0.7002438325665985,0.77803238759228632,0.84442288994862458,0.87964749921275731,0.9036212631298387,null,0.5201882477788351,0.5201882477788351,0.5201882477788351]
["2013-02-01T07:00:00","2013-02-01T07:00:00",null,8.6895451507873851,8.993117352443285,9.296689554099185,9.6002617557550849,9.9038339574109848,10.207406159066885,10.510978360722785,10.814550562378685,11.118122764034585,null,0,0.18138045068844433,0.51901058920045218,0.61355974935062574,0.70287253475048905,0.78239603321754458,0.85041633092789493,0.88718661707615531,0.91262193940747982,null,0.51901058920045218,0.51901058920045218,0.51901058920045218]
["2013-02-01T08:00:00","2013-02-01T08:00:00",null,8.688929588282198,8.9925017899380979,9.2960739915939978,9.5996461932498978,9.9032183949057977,10.206790596561698,10.510362798217598,10.813934999873497,11.117507201529397,null,0,0.17817343402409791,0.51789601947448261,0.61441144885820631,0.70556432578679296,0.7868227676952162,0.85647286075957862,0.89478882379196667,0.92167518972879869,null,0.51789601947448261,0.51789601947448261,0.51789601947448261]
["2013-02-01T09:00:00","2013-02-01T09:00:00",null,8.8712412606535764,9.1748134623094764,9.4783856639653763,9.7819578656212745,10.085530067277174,10.389102268933074,10.692674470588974,10.996246672244874,11.299818873900774,null,0,0.17217999304482756,0.51404759947726686,0.61257135732948298,0.70561689983047071,0.78865234441520393,0.85998480687725631,0.89988850602871429,0.92827848961473158,null,0.51404759947726686,0.51404759947726686,0.51404759947726686]
["2013-02-01T10:00:00","2013-02-01T10:00:00",null,9.047303753533134,9.3508759551890339,9.6544481568449338,9.9580203585008356,10.261592560156735,10.565164761812635,10.868736963468535,11.172309165124435,11.475881366780335,null,0,0.16391535337867583,0.50797004002811197,0.60853367077502718,0.70350342327462279,0.78835792977060815,0.86140430605655716,0.90292728575329173,0.93285243141470109,null,0.50797004002811197,0.50797004002811197,0.50797004002811197]
["2013-02-01T11:00:00","2013-02-01T11:00:00",null,9.4616369923500407,9.7652091940059407,10.068781395661841,10.372353597317741,10.67592579897364,10.97949800062954,11.28307020228544,11.58664240394134,11.89021460559724,null,0,0.15160251234933272,0.49786530883323687,0.60051087170979334,0.69744689344293909,0.78415200627638337,0.85895435562117117,0.90213867509812462,0.9336410420698682,null,0.49786530883323687,0.49786530883323687,0.49786530883323687]
["2013-02-01T12:00:00","2013-02-01T12:00:00",null,9.8118474559413329,10.115419657597233,10.418991859253131,10.722564060909031,11.026136262564931,11.329708464220831,11.633280665876731,11.936852867532631,12.240425069188531,null,0,0.13525198476553382,0.48376495031884825,0.58853450455998824,0.68747885476162629,0.77608714797620737,0.85268752961477623,0.89757524810689071,0.93070741043264638,null,0.48376495031884825,0.48376495031884825,0.48376495031884825]
["2013-02-01T13:00:00","2013-02-01T13:00:00",null,10.088654127485768,10.392226329141668,10.695798530797568,10.999370732453468,11.302942934109367,11.606515135765267,11.910087337421167,12.213659539077067,12.517231740732967,null,0,0.11182499090270169,0.46273533284772428,0.56977608577574568,0.67085494215070274,0.76150310825998291,0.84002769989715953,0.88674499510926186,0.92162261568512083,null,0.46273533284772428,0.46273533284772428,0.46273533284772428]
["2013-02-01T14:00:00","2013-02-01T14:00:00",null,10.334205693849075,10.637777895504975,10.941350097160875,11.244922298816775,11.548494500472675,11.852066702128575,12.155638903784475,12.459211105440374,12.762783307096274,null,0,9.2845761135012278E-2,0.44624811275036308,0.55564418283515038,0.65895217866204658,0.75171382132717468,0.83224674143284361,0.88087773183481821,0.91757441432192943,null,0.44624811275036308,0.44624811275036308,0.44624811275036308]
["2013-02-01T15:00:00","2013-02-01T15:00:00",null,10.487119946572875,10.790692148228775,11.094264349884675,11.397836551540575,11.701408753196475,12.004980954852375,12.308553156508275,12.612125358164175,12.915697559820075,null,0,7.4886467814672383E-2,0.43085443276150032,0.54267942366420241,0.64827964779545111,0.74322837067757619,0.82584322291288637,0.8764509973571466,0.91502983060792342,null,0.43085443276150032,0.43085443276150032,0.43085443276150032]
["2013-02-01T16:00:00","2013-02-01T16:00:00",null,10.596186025779653,10.899758227435553,11.203330429091453,11.506902630747353,11.810474832403253,12.114047034059153,12.417619235715053,12.721191437370953,13.024763639026853,null,0,5.5150171818022509E-2,0.41370477971379871,0.52797972105188673,0.6359037179136946,0.73306055063028774,0.81776784980397477,0.8703839527167273,0.91086596634864092,null,0.41370477971379871,0.41370477971379871,0.41370477971379871]
["2013-02-01T17:00:00","2013-02-01T17:00:00",null,10.61538915959396,10.91896136124986,11.22253356290576,11.52610576456166,11.82967796621756,12.133250167873459,12.436822369529359,12.740394571185259,13.043966772841159,null,0,2.9010357301415383E-2,0.39008851929372645,0.50673980740605151,0.6169244881460052,0.71622634184465295,0.80297351391303906,0.85753485644187055,0.89987799121997858,null,0.39008851929372645,0.39008851929372645,0.39008851929372645]
["2013-02-01T18:00:00","2013-02-01T18:00:00",null,10.430856989683303,10.734429191339203,11.038001392995104,11.341573594651004,11.645145796306904,11.948717997962804,12.252290199618704,12.555862401274604,12.859434602930504,null,0,2.5656133314769583E-3,0.36605166652423171,0.48497415332343818,0.59731436985418207,0.69866661125626439,0.78735902294072946,0.84377097180701988,0.88788059445270229,null,0.36605166652423171,0.36605166652423171,0.36605166652423171]
["2013-02-01T19:00:00","2013-02-01T19:00:00",null,10.213373335445308,10.516945537101208,10.820517738757108,11.124089940413008,11.427662142068908,11.731234343724807,12.034806545380707,12.338378747036607,12.641950948692507,null,0,0,0.34576860047333263,0.46690971191574265,0.58134237538486344,0.68469243044670247,0.77527750770356874,0.83348748886364021,0.87930051052448366,null,0.34576860047333263,0.34576860047333263,0.34576860047333263]
["2013-02-01T20:00:00","2013-02-01T20:00:00",null,10.169215646640222,10.472787848296122,10.776360049952022,11.079932251607922,11.383504453263821,11.687076654919721,11.990648856575621,12.294221058231521,12.597793259887421,null,0,0,0.32775673310931491,0.45106389515125073,0.56754694632380609,0.67284224100172407,0.76527792459604926,0.82523336400622405,0.87271824025602185,null,0.32775673310931491,0.32775673310931491,0.32775673310931491]
["2013-02-01T21:00:00","2013-02-01T21:00:00",null,10.024842614052641,10.328414815708541,10.631987017364441,10.935559219020341,11.239131420676241,11.542703622332141,11.846275823988041,12.149848025643941,12.453420227299841,null,0,0,0.31335144514159496,0.43884568740052771,0.55740015589398872,0.66465120499672126,0.75894800973724097,0.82066993701499014,0.86983718266247789,null,0.31335144514159496,0.31335144514159496,0.31335144514159496]
["2013-02-01T22:00:00","2013-02-01T22:00:00",null,10.075779790209898,10.379351991865798,10.6829241935217,10.9864963951776,11.2900685968335,11.5936407984894,11.8972130001453,12.2007852018012,12.504357403457099,null,0,0,0.31103818721977133,0.43868796526949427,0.55928230665765433,0.66845756575899473,0.76458394721950218,0.82805133274735465,0.87886940336632569,null,0.31103818721977133,0.31103818721977133,0.31103818721977133]
["2013-02-01T23:00:00","2013-02-01T23:00:00",null,10.067003161229859,10.370575362885759,10.674147564541659,10.977719766197559,11.281291967853459,11.584864169509359,11.888436371165259,12.192008572821159,12.495580774477059,null,0,8.8324393378720785E-4,0.31407696694434872,0.44377713269750629,0.5663061988930097,0.67731103471433796,0.77518287442494871,0.84030108492428435,0.89268586204485412,null,0.31407696694434872,0.31407696694434872,0.31407696694434872]
["2013-02-02","2013-02-02",null,10.048597442882695,10.352169644538595,10.655741846194495,10.959314047850395,11.262886249506295,11.566458451162195,11.870030652818095,12.173602854473994,12.477175056129894,null,0,2.9756908721640454E-3,0.31831443486478023,0.4500334438951657,0.57447620528054133,0.68728958820438635,0.78688585654762921,0.85363386240097694,0.90757483121440985,null,0.31831443486478023,0.31831443486478023,0.31831443486478023]
["2013-02-02T01:00:00","2013-02-02T01:00:00",null,10.127219742580591,10.430791944236491,10.734364145892391,11.037936347548291,11.341508549204191,11.645080750860091,11.948652952515991,12.252225154171891,12.55579735582779,null,3.0072352983707314E-3,8.1384619613249862E-3,0.32551707884864017,0.45916029787763352,0.5854221211742614,0.69997044753947413,0.80119651123672908,0.86951122359167554,0.92493478043682276,null,0.32551707884864017,0.32551707884864017,0.32551707884864017]
["2013-02-02T02:00:00","2013-02-02T02:00:00",null,10.005045578651071,10.308617780306971,10.612189981962871,10.915762183618771,11.219334385274671,11.522906586930571,11.826478788586471,12.130050990242371,12.43362319189827,null,1.4226536219215383E-2,2.1450209820546476E-2,0.34081612555888285,0.47632046573407072,0.60435929170700853,0.72057947266117561,0.82339327247750049,0.89322211729036782,0.95007568812355148,null,0.34081612555888285,0.34081612555888285,0.34081612555888285]
["2013-02-02T03:00:00","2013-02-02T03:00:00",null,10.389685381990592,10.693257583646492,10.996829785302392,11.300401986958292,11.603974188614192,11.907546390270092,12.211118591925992,12.514690793581892,12.818262995237792,null,7.6463689125006853E-2,8.6284520484021757E-2,0.40811090146647966,0.54593901437222669,0.67617543537089697,0.7944880632634409,0.89927864712205141,0.97100015750731994,1,null,0.40811090146647966,0.40811090146647966,0.40811090146647966]
["2013-02-02T04:00:00","2013-02-02T04:00:00",null,10.491514710979754,10.795086912635654,11.098659114291554,11.402231315947454,11.705803517603353,12.009375719259253,12.312947920915153,12.616520122571053,12.920092324226953,null,0.13373785230761306,0.14628201912913852,0.47067401344307352,0.61093104716673541,0.74347021127849378,0.86398043419677018,0.97085295018502193,1,1,null,0.47067401344307352,0.47067401344307352,0.47067401344307352]
["2013-02-02T05:00:00","2013-02-02T05:00:00",null,9.9779289248278218,10.281501126483722,10.585073328139622,10.888645529795522,11.192217731451422,11.495789933107321,11.799362134763221,12.102934336419121,12.406506538075021,null,0.20989661197928861,0.22472249229643101,0.55127002240115619,0.69355641421078162,0.82801978832114775,0.9503490731506764,1,1,1,null,0.55127002240115619,0.55127002240115619,0.55127002240115619]
["2013-02-02T06:00:00","2013-02-02T06:00:00",null,10.047826610414869,10.351398812070769,10.654971013726669,10.958543215382569,11.262115417038469,11.565687618694369,11.869259820350269,12.172832022006169,12.476404223662069,null,0.28611846050337753,0.30320502469866578,0.63189757578544559,0.77620281087229892,0.91257988017253733,1,1,1,1,null,0.63189757578544559,0.63189757578544559,0.63189757578544559]
["2013-02-02T07:00:00","2013-02-02T07:00:00",null,10.041816550436387,10.345388752092287,10.648960953748187,10.952533155404087,11.256105357059987,11.559677558715887,11.863249760371787,12.166821962027687,12.470394163683586,null,0.36270832733321112,0.3820555754066452,0.71288263266674412,0.85920671103082535,0.99748696071220044,1,1,1,1,null,0.71288263266674412,0.71288263266674412,0.71288263266674412]
["2013-02-02T08:00:00","2013-02-02T08:00:00",null,9.9949980100238527,10.298570211679753,10.602142413335653,10.905714614991552,11.209286816647452,11.512859018303352,11.816431219959252,12.120003421615152,12.423575623271052,null,0.43837289099431526,0.46002288218083742,0.79302650484919768,0.94140097091671349,1,1,1,1,1,null,0.79302650484919768,0.79302650484919768,0.79302650484919768]
["2013-02-02T09:00:00","2013-02-02T09:00:00",null,10.40460883135718,10.70818103301308,11.01175323466898,11.31532543632488,11.61889763798078,11.92246983963668,12.22604204129258,12.52961424294848,12.83318644460438,null,0.51067271586003959,0.5346254501596498,0.86981615304500692,1,1,1,1,1,1,null,0.86981615304500692,0.86981615304500692,0.86981615304500692]
["2013-02-02T10:00:00","2013-02-02T10:00:00",null,10.921347328246801,11.224919529902701,11.528491731558601,11.832063933214501,12.135636134870401,12.439208336526301,12.742780538182201,13.046352739838101,13.349924941494001,null,0.50976844230878127,0.53642348245343086,0.87416928386152959,1,1,1,1,1,1,null,0.87416928386152959,0.87416928386152959,0.87416928386152959]
["2013-02-02T11:00:00","2013-02-02T11:00:00",null,11.057967402842074,11.361539604497974,11.665111806153874,11.968684007809774,12.272256209465674,12.575828411121574,12.879400612777474,13.182972814433374,13.486545016089273,null,0.48468010866573036,0.51407951389036166,0.85443298786487976,0.98273468405620723,0.98509000121297308,0.98732965547364782,0.98946416164696682,0.99149351973293032,0.99343875934900927,null,0.85443298786487976,0.85443298786487976,0.85443298786487976]
["2013-02-02T12:00:00","2013-02-02T12:00:00",null,11.062841450729872,11.366413652385772,11.669985854041672,11.973558055697572,12.277130257353472,12.580702459009371,12.884274660665271,13.187846862321171,13.491419063977071,null,0.46266209917346351,0.49473226581692759,0.83760929388798055,0.96830836647101615,0.97293488231466341,0.97735110198359942,0.9815465106690886,0.98555265279733784,0.98938004317708239,null,0.83760929388798055,0.83760929388798055,0.83760929388798055]
["2013-02-02T13:00:00","2013-02-02T13:00:00",null,10.959832321612833,11.263404523268733,11.566976724924633,11.870548926580533,12.174121128236433,12.477693329892332,12.781265531548232,13.084837733204132,13.388409934860032,null,0.4421582221391176,0.4768781205839433,0.82226818794279555,0.95534360730006818,0.96223080702186126,0.96880256248158747,0.97504835887051133,0.98101025542357501,0.98669876694951408,null,0.82226818794279555,0.82226818794279555,0.82226818794279555]
["2013-02-02T14:00:00","2013-02-02T14:00:00",null,10.99265152320875,11.29622372486465,11.599795926520549,11.903368128176449,12.206940329832349,12.510512531488249,12.814084733144149,13.117656934800049,13.421229136455949,null,0.42017175707305748,0.45757293174545149,0.8055075828183097,0.94100140818476163,0.95018083621090721,0.9589291570788947,0.96725688559745993,0.97519556619280923,0.9827767432911495,null,0.8055075828183097,0.8055075828183097,0.8055075828183097]
["2013-02-02T15:00:00","2013-02-02T15:00:00",null,10.955356397768746,11.258928599424646,11.562500801080546,11.866073002736446,12.169645204392346,12.473217406048246,12.776789607704146,13.080361809360046,13.383934011015945,null,0.39647137818310074,0.43661691793547641,0.78713821195728284,0.92509250256785636,0.93661673294203218,0.94758367845322333,0.95803539833637208,0.96799292220894928,0.97749830930589743,null,0.78713821195728284,0.78713821195728284,0.78713821195728284]
["2013-02-02T16:00:00","2013-02-02T16:00:00",null,11.03125440781877,11.334826609474669,11.638398811130569,11.941971012786469,12.245543214442369,12.549115416098269,12.852687617754169,13.156259819410069,13.459832021065969,null,0.37251864388349049,0.41538751909837673,0.76849545606913139,0.90888918230635529,0.92274770021982588,0.93593327037422069,0.94848795200448177,0.96046431915428687,0.9718834014411073,null,0.76849545606913139,0.76849545606913139,0.76849545606913139]
["2013-02-02T17:00:00","2013-02-02T17:00:00",null,10.972574988049587,11.276147189705485,11.579719391361385,11.883291593017285,12.186863794673185,12.490435996329085,12.794008197984985,13.097580399640885,13.401152601296785,null,0.34804016914710217,0.39366392425070562,0.74937953378787969,0.89225475488669626,0.90846858995693269,0.92388329956326665,0.93857248736684684,0.95258872741135092,0.96594253450551482,null,0.74937953378787969,0.74937953378787969,0.74937953378787969]
["2013-02-02T18:00:00","2013-02-02T18:00:00",null,10.767277902295422,11.070850103951322,11.374422305607222,11.677994507263122,11.981566708919022,12.285138910574922,12.588711112230822,12.892283313886722,13.195855515542622,null,0.32634811872563779,0.37469520929175176,0.73299746177787406,0.87831211850334101,0.89684972630413673,0.91448306055367423,0.93126469529563127,0.94728926380862766,0.96255676609266383,null,0.73299746177787406,0.73299746177787406,0.73299746177787406]
["2013-02-02T19:00:00","2013-02-02T19:00:00",null,10.490797306149098,10.794369507804998,11.097941709460898,11.401513911116798,11.705086112772698,12.008658314428597,12.312230516084497,12.615802717740397,12.919374919396297,null,0.30748455185403956,0.35854446307392851,0.71941232889152795,0.86716642124364529,0.8880067721575291,0.90782718662406348,0.92669075349566177,0.94469210605094389,0.96184175909864567,null,0.71941232889152795,0.71941232889152795,0.71941232889152795]
["2013-02-02T20:00:00","2013-02-02T20:00:00",null,10.479074352766741,10.782646554422641,11.086218756078541,11.389790957734441,11.693363159390341,11.996935361046241,12.300507562702141,12.60407976435804,12.90765196601394,null,0.29283742328540169,0.34650500707171,0.70983333813343097,0.85991120321610748,0.88295966396445935,0.90487252536937057,0.92573390590072557,0.94562792402840889,0.96458612417862732,null,0.70983333813343097,0.70983333813343097,0.70983333813343097]
["2013-02-02T21:00:00","2013-02-02T21:00:00",null,10.297593925355605,10.601166127011505,10.904738328667406,11.208310530323306,11.511882731979206,11.815454933635106,12.119027135291006,12.422599336946906,12.726171538602806,null,0.28024068242019839,0.33649490915545499,0.70227319065256189,0.85466431365706208,0.87989985462241083,0.9038946481569633,0.92673281273060393,0.94850898162195285,0.96925469925721686,null,0.70227319065256189,0.70227319065256189,0.70227319065256189]
["2013-02-02T22:00:00","2013-02-02T22:00:00",null,10.066925747615807,10.370497949271707,10.674070150927607,10.977642352583507,11.281214554239407,11.584786755895307,11.888358957551207,12.191931159207106,12.495503360863006,null,0.27236509067726244,0.33113235670031838,0.69927647016292671,0.85390724742810165,0.88126677975803391,0.90725938695234309,0.932011246715856,0.95559596270972169,0.97806610897761781,null,0.69927647016292671,0.69927647016292671,0.69927647016292671]
["2013-02-02T23:00:00","2013-02-02T23:00:00",null,10.093166482145492,10.396738683801392,10.700310885457291,11.003883087113191,11.307455288769091,11.611027490424991,11.914599692080891,12.218171893736791,12.521744095392691,null,0.27036727701750568,0.33146883057985638,0.70181053906819713,0.85851273365427783,0.88783853521776013,0.91569226355826383,0.94221061118935112,0.96747769658090677,0.99154609377660829,null,0.70181053906819713,0.70181053906819713,0.70181053906819713]
["2013-02-03","2013-02-03",null,9.8549770159509027,10.158549217606803,10.462121419262703,10.765693620918602,11.069265822574502,11.372838024230402,11.676410225886302,11.979982427542202,12.283554629198102,null,0.26847461144510454,0.33191045254675,0.70446027086955876,0.86323388277654511,0.89452595357357756,0.92424080306027578,0.95252563855893746,0.97946457853944746,1,null,0.70446027086955876,0.70446027086955876,0.70446027086955876]
["2013-02-03T01:00:00","2013-02-03T01:00:00",null,9.8249911540583508,10.128563355714251,10.432135557370151,10.735707759026051,11.03927996068195,11.34285216233785,11.64642436399375,11.94999656564965,12.25356876730555,null,0.26748621942396172,0.33321428882995968,0.70793015775229418,0.86874364255397962,0.90195992334961994,0.9335043495563059,0.9635136136875998,0.99209286383085737,1,null,0.70793015775229418,0.70793015775229418,0.70793015775229418]
["2013-02-03T02:00:00","2013-02-03T02:00:00",null,9.5725086680088864,9.8760808696647864,10.179653071320686,10.483225272976586,10.786797474632486,11.090369676288386,11.393941877944286,11.697514079600186,12.001086281256086,null,0.26912652958670941,0.33712579767958872,0.71398668758397787,0.87681901566289122,0.91193847683966833,0.94528093534013535,0.97699359848659029,1,1,null,0.71398668758397787,0.71398668758397787,0.71398668758397787]
["2013-02-03T03:00:00","2013-02-03T03:00:00",null,9.5367667717447482,9.8403389734006481,10.143911175056548,10.447483376712448,10.751055578368348,11.054627780024248,11.358199981680148,11.661772183336048,11.965344384991948,null,0.27278568302668499,0.34300357576276785,0.72195691260553385,0.88675550991799734,0.92373609224096886,0.95883452380027479,0.99220852672694848,1,1,null,0.72195691260553385,0.72195691260553385,0.72195691260553385]
["2013-02-03T04:00:00","2013-02-03T04:00:00",null,9.5576247986385923,9.8611970002944922,10.164769201950392,10.468341403606292,10.771913605262192,11.075485806918092,11.379058008573992,11.682630210229892,11.986202411885792,null,0.2751935742271287,0.34767215084135739,0.72873896423997131,0.89553537521219162,0.93439810829882874,0.97128405734318024,1,1,1,null,0.72873896423997131,0.72873896423997131,0.72873896423997131]
["2013-02-03T05:00:00","2013-02-03T05:00:00",null,9.622694759980293,9.9262669616361929,10.229839163292093,10.533411364947993,10.836983566603893,11.140555768259793,11.444127969915693,11.747700171571593,12.051272373227492,null,0.27247023876461812,0.34730413253561271,0.73057905576869464,0.8994679136792918,0.94029691599947907,0.97904398619002497,1,1,1,null,0.73057905576869464,0.73057905576869464,0.73057905576869464]
["2013-02-03T06:00:00","2013-02-03T06:00:00",null,9.5209894169551532,9.8245616186110531,10.128133820266953,10.431706021922853,10.735278223578753,11.038850425234653,11.342422626890553,11.645994828546453,11.949567030202353,null,0.26707614188327483,0.34434947128091981,0.72992713762708983,0.90097153132847718,0.94384040654336343,0.98452220154125281,1,1,1,null,0.72992713762708983,0.72992713762708983,0.72992713762708983]
["2013-02-03T07:00:00","2013-02-03T07:00:00",null,9.5109485758458838,9.8145207775017838,10.118092979157684,10.421665180813584,10.725237382469484,11.028809584125383,11.332381785781283,11.635953987437183,11.939526189093083,null,0.2620710929251473,0.34176282833197158,0.72962220817375856,0.90282213766593611,0.94772037096678585,0.99031586115454751,1,1,1,null,0.72962220817375856,0.72962220817375856,0.72962220817375856]
["2013-02-03T08:00:00","2013-02-03T08:00:00",null,9.593733644905706,9.8973058465616059,10.200878048217506,10.504450249873406,10.808022451529306,11.111594653185206,11.415166854841106,11.718739056497006,12.022311258152905,null,0.25640361101667936,0.33852426724141849,0.72866536057882236,0.90402082586179022,0.95094841724860335,0.99546811743497288,1,1,1,null,0.72866536057882236,0.72866536057882236,0.72866536057882236]
["2013-02-03T09:00:00","2013-02-03T09:00:00",null,9.9850556707849076,10.288627872440808,10.592200074096706,10.895772275752606,11.199344477408506,11.502916679064406,11.806488880720305,12.110061082376205,12.413633284032105,null,0.2485069896562723,0.33303553708145511,0.72543731429700486,0.90293780056202733,0.95188423522606835,0.99832814541104575,1,1,1,null,0.72543731429700486,0.72543731429700486,0.72543731429700486]
["2013-02-03T10:00:00","2013-02-03T10:00:00",null,10.560470510879824,10.864042712535726,11.167614914191626,11.471187115847526,11.774759317503426,12.078331519159326,12.381903720815226,12.685475922471126,12.989048124127025,null,0.22915974158283822,0.31628544676570486,0.71113717441664059,0.89097194822095782,0.94211597791073121,0.99065233503408545,0.99432200328279652,0.99621466885519772,0.99802321595771437,null,0.71113717441664059,0.71113717441664059,0.71113717441664059]
["2013-02-03T11:00:00","2013-02-03T11:00:00",null,10.855921368537942,11.159493570193842,11.463065771849742,11.766637973505642,12.070210175161542,12.373782376817442,12.677354578473341,12.980926780129241,13.284498981785141,null,0.20605870679080851,0.29581311415756567,0.69315685147882955,0.87535745724864822,0.92875165600783194,0.97942251930450519,0.98512154563917975,0.9889594508276599,0.99261860426763548,null,0.69315685147882955,0.69315685147882955,0.69315685147882955]
["2013-02-03T12:00:00","2013-02-03T12:00:00",null,10.990436419778449,11.294008621434349,11.597580823090249,11.901153024746149,12.204725226402049,12.508297428057949,12.811869629713849,13.115441831369749,13.419014033025649,null,0.17651209424387929,0.26904241111682481,0.66901485062197918,0.85370746606212611,0.90946749678681127,0.96238852915289474,0.9702430912783595,0.97612086936153875,0.98173577722632877,null,0.66901485062197918,0.66901485062197918,0.66901485062197918]
["2013-02-03T13:00:00","2013-02-03T13:00:00",null,11.030459874321147,11.334032075977047,11.637604277632947,11.941176479288847,12.244748680944747,12.548320882600647,12.851893084256547,13.155465285912447,13.459037487568347,null,0.14170807732916907,0.23714048141312971,0.63986780080700134,0.82717860362230322,0.88542012920858093,0.94069647873143036,0.95080120992630535,0.95883452380027479,0.96649981936849938,null,0.63986780080700134,0.63986780080700134,0.63986780080700134]
["2013-02-03T14:00:00","2013-02-03T14:00:00",null,11.105900063159456,11.409472264815356,11.713044466471256,12.016616668127156,12.320188869783056,12.623761071438956,12.927333273094856,13.230905474750756,13.534477676406656,null,0.10666221981354093,0.20498619629978113,0.6104473659648989,0.80035532653788455,0.86106783217701932,0.91869949885663471,0.93104388431218432,0.94121170435947288,0.95092738763113205,null,0.6104473659648989,0.6104473659648989,0.6104473659648989]
["2013-02-03T15:00:00","2013-02-03T15:00:00",null,11.052200116913747,11.355772318569647,11.659344520225547,11.962916721881447,12.266488923537347,12.570061125193247,12.873633326849147,13.177205528505047,13.480777730160947,null,7.4255579290538859E-2,0.17540803932664523,0.58356100002806688,0.77601354431505853,0.8391549707721081,0.89908938056481158,0.91363136104609366,0.92590214284049466,0.93761563977191054,null,0.58356100002806688,0.58356100002806688,0.58356100002806688]
["2013-02-03T16:00:00","2013-02-03T16:00:00",null,10.921879171707984,11.225451373363883,11.529023575019783,11.832595776675683,12.136167978331583,12.439740179987483,12.743312381643383,13.046884583299283,13.350456784955183,null,4.4477640951427283E-2,0.14842704011119315,0.55921921780524086,0.75418480138003186,0.81971308942005394,0.88191869789963884,0.89862672898044671,0.91295841328701788,0.92663817945198379,null,0.55921921780524086,0.55921921780524086,0.55921921780524086]
["2013-02-03T17:00:00","2013-02-03T17:00:00",null,10.801788372258695,11.105360573914597,11.408932775570497,11.712504977226397,12.016077178882297,12.319649380538197,12.623221582194097,12.926793783849996,13.230365985505896,null,1.6970901299197098E-2,0.12368569515641577,0.5370960602256184,0.73454313866200205,0.80242674385878998,0.86687200659904962,0.88571454385317661,0.90207558624571116,0.91770059202675613,null,0.5370960602256184,0.5370960602256184,0.5370960602256184]
["2013-02-03T18:00:00","2013-02-03T18:00:00",null,10.665202626364197,10.968774828020097,11.272347029675997,11.575919231331897,11.879491432987797,12.183063634643696,12.486635836299596,12.790208037955496,13.093780239611396,null,0,0.10207776320483586,0.51805374160551565,0.71792974085981409,0.78812660397842571,0.85475894693568222,0.87569393112818605,0.89404227237174183,0.91155994372518789,null,0.51805374160551565,0.51805374160551565,0.51805374160551565]
["2013-02-03T19:00:00","2013-02-03T19:00:00",null,10.614284236446759,10.917856438102659,11.221428639758559,11.525000841414458,11.828573043070358,12.132145244726258,12.435717446382158,12.739289648038058,13.042861849693958,null,0,8.2835663218757405E-2,0.50132468090723648,0.70357702693577195,0.77603457393252939,0.84481193787184061,0.86778679495904343,0.88808037581867816,0.90744865350958315,null,0.50132468090723648,0.50132468090723648,0.50132468090723648]
["2013-02-03T20:00:00","2013-02-03T20:00:00",null,10.50474975664708,10.808321958302979,11.111894159958879,11.415466361614779,11.719038563270679,12.022610764926579,12.326182966582479,12.629755168238379,12.933327369894279,null,0,6.5391595526460053E-2,0.48637262288526734,0.69098028607056872,0.7656669725192653,0.83656832782316004,0.86156202818759076,0.88376930423709776,0.90496715864799049,null,0.48637262288526734,0.48637262288526734,0.48637262288526734]
["2013-02-03T21:00:00","2013-02-03T21:00:00",null,10.534708832279245,10.838281033935145,11.141853235591045,11.445425437246945,11.748997638902845,12.052569840558744,12.356142042214644,12.659714243870544,12.963286445526444,null,0,4.9903282258977229E-2,0.4733027156269638,0.68021312192535321,0.75707637378231118,0.83004914640711158,0.85700911600509244,0.88108802800952946,0.90407339990546776,null,0.4733027156269638,0.4733027156269638,0.4733027156269638]
["2013-02-03T22:00:00","2013-02-03T22:00:00",null,10.453015757277141,10.756587958933041,11.060160160588941,11.363732362244841,11.667304563900741,11.970876765556641,12.274448967212541,12.578021168868441,12.881593370524341,null,0,3.8011033579056608E-2,0.46374475448633795,0.67286327061919537,0.75181896941453019,0.82677904089035181,0.85563167606073387,0.88150862035895194,0.90620790607878687,null,0.46374475448633795,0.46374475448633795,0.46374475448633795]
["2013-02-03T23:00:00","2013-02-03T23:00:00",null,10.324233962025572,10.627806163681472,10.931378365337373,11.234950566993273,11.538522768649173,11.842094970305073,12.145667171960973,12.449239373616873,12.752811575272773,null,0,2.6802247466947517E-2,0.45481768186984584,0.6660917337934934,0.7470978202922629,0.82399261657542788,0.85468534327453327,0.88231826063159025,0.90868940094037953,null,0.45481768186984584,0.45481768186984584,0.45481768186984584]
["2013-02-04","2013-02-04",null,10.350556851565555,10.654129053221455,10.957701254877355,11.261273456533255,11.564845658189155,11.868417859845055,12.171990061500955,12.475562263156855,12.779134464812755,null,0,1.1261360155786885E-2,0.44159005248050887,0.6550511846211533,0.73812868844082857,0.81698975395754359,0.84955411661157898,0.87896403664494593,0.90702806116016077,null,0.44159005248050887,0.44159005248050887,0.44159005248050887]
["2013-02-04T01:00:00","2013-02-04T01:00:00",null,10.295350711322097,10.598922912977997,10.902495114633897,11.206067316289797,11.509639517945697,11.813211719601597,12.116783921257497,12.420356122913397,12.723928324569297,null,0,0,0.42696395352934213,0.64264371031319012,0.72782417587997783,0.80868305505644966,0.84314008328288614,0.87434803561003427,0.90412597394914562,null,0.42696395352934213,0.42696395352934213,0.42696395352934213]
["2013-02-04T02:00:00","2013-02-04T02:00:00",null,10.399189072545635,10.702761274201535,11.006333475857435,11.309905677513335,11.613477879169235,11.917050080825135,12.220622282481035,12.524194484136935,12.827766685792835,null,0,0,0.41419897572436987,0.63202375349027251,0.7192440919517592,0.8020376959355745,0.83833481569073431,0.87128822626798574,0.90273801919605146,null,0.41419897572436987,0.41419897572436987,0.41419897572436987]
["2013-02-04T03:00:00","2013-02-04T03:00:00",null,10.471794113441678,10.775366315097578,11.07893851675348,11.38251071840938,11.68608292006528,11.98965512172118,12.29322732337708,12.59679952503298,12.90037172668888,null,0,0,0.39966751005182316,0.61962679399104492,0.70887649053849511,0.79359430452091817,0.83172100099606583,0.86641986982342056,0.89953100253170504,null,0.39966751005182316,0.39966751005182316,0.39966751005182316]
["2013-02-04T04:00:00","2013-02-04T04:00:00",null,10.563425699811404,10.866997901467304,11.170570103123206,11.474142304779106,11.777714506435006,12.081286708090905,12.384858909746805,12.688431111402705,12.992003313058605,null,0,0,0.38340110093790875,0.60550540585918511,0.69679497530133438,0.78344751409110081,0.8234143020949718,0.85986914398116543,0.89465213127840426,null,0.38340110093790875,0.38340110093790875,0.38340110093790875]
["2013-02-04T05:00:00","2013-02-04T05:00:00",null,10.74405335761762,11.047625559273518,11.351197760929418,11.654769962585318,11.958342164241218,12.261914365897118,12.565486567553018,12.869058769208918,13.172630970864818,null,0,0,0.36337039029666313,0.58764074581746528,0.68099121777178473,0.7695995109863657,0.8114274201364311,0.84964874989019912,0.8861246213938635,null,0.36337039029666313,0.36337039029666313,0.36337039029666313]
["2013-02-04T06:00:00","2013-02-04T06:00:00",null,10.801056454729107,11.104628656385007,11.408200858040907,11.711773059696807,12.015345261352707,12.318917463008606,12.622489664664506,12.926061866320406,13.229634067976306,null,0,0,0.34058479976670025,0.56708429473944155,0.66254824324960904,0.75316486493268231,0.79690646927261999,0.83694686093764026,0.87515767588267235,null,0.34058479976670025,0.34058479976670025,0.34058479976670025]
["2013-02-04T07:00:00","2013-02-04T07:00:00",null,10.778255936191142,11.081828137847042,11.385400339502942,11.688972541158842,11.992544742814742,12.296116944470642,12.599689146126542,12.903261347782442,13.206833549438342,null,0,0,0.31876657164040911,0.54746366163888283,0.64502005708742716,0.73762397762152165,0.78325824753386053,0.82509667149266186,0.86503191507032617,null,0.31876657164040911,0.31876657164040911,0.31876657164040911]
["2013-02-04T08:00:00","2013-02-04T08:00:00",null,10.843859827939623,11.147432029595523,11.451004231251423,11.754576432907323,12.058148634563223,12.361720836219122,12.665293037875022,12.968865239530922,13.272437441186822,null,0,0,0.29746356914216049,0.52834773935763113,0.62797555212708112,0.72255625670346135,0.77006216257073024,0.81368810401457714,0.85533726141613797,null,0.29746356914216049,0.29746356914216049,0.29746356914216049]
["2013-02-04T09:00:00","2013-02-04T09:00:00",null,11.098923856309746,11.402496057965646,11.706068259621546,12.009640461277446,12.313212662933346,12.616784864589246,12.920357066245145,13.223929267901045,13.527501469556945,null,0,0,0.2740260604705928,0.50709731090306032,0.60880705580215155,0.70536454442081753,0.7547631158604875,0.80018708959811558,0.84355016082357293,null,0.2740260604705928,0.2740260604705928,0.2740260604705928]
["2013-02-04T10:00:00","2013-02-04T10:00:00",null,11.336914414694455,11.640486616350355,11.944058818006255,12.247631019662155,12.551203221318055,12.854775422973955,13.158347624629855,13.461919826285754,13.765492027941654,null,0,0,0.24622490617376688,0.48154632567564465,0.58540109155679054,0.6839984530701555,0.73534226412590453,0.78262735900972702,0.82776743291149435,null,0.24622490617376688,0.24622490617376688,0.24622490617376688]
["2013-02-04T11:00:00","2013-02-04T11:00:00",null,11.502355037592183,11.805927239248083,12.109499440903983,12.413071642559883,12.716643844215783,13.020216045871683,13.323788247527583,13.627360449183483,13.930932650839383,null,0,0,0.21425988761765841,0.45190507985009537,0.55796795556570933,0.65866827882618662,0.71203093315916355,0.76122972323285831,0.80820988866334909,null,0.21425988761765841,0.21425988761765841,0.21425988761765841]
["2013-02-04T12:00:00","2013-02-04T12:00:00",null,11.710059376640007,12.013631578295907,12.317203779951807,12.620775981607707,12.924348183263607,13.227920384919507,13.531492586575407,13.835064788231307,14.138636989887207,null,0,0,0.17681665371032212,0.41688025195193834,0.52525638558937593,0.62815430387558568,0.68361991995567506,0.73482703849786213,0.78373141392696077,null,0.17681665371032212,0.17681665371032212,0.17681665371032212]
["2013-02-04T13:00:00","2013-02-04T13:00:00",null,11.709292805993133,12.012865007649033,12.316437209304933,12.620009410960833,12.923581612616733,13.227153814272633,13.530726015928533,13.834298217584433,14.137870419240333,null,0,0,0.13688141013265764,0.37930032553103976,0.48990559862041649,0.59493802307994537,0.65244351205473372,0.70559587021299974,0.75637188159702851,null,0.13688141013265764,0.13688141013265764,0.13688141013265764]
["2013-02-04T14:00:00","2013-02-04T14:00:00",null,11.941761762346028,12.245333964001928,12.548906165657828,12.852478367313728,13.156050568969627,13.459622770625527,13.763194972281427,14.066767173937327,14.370339375593227,null,0,0,8.5411421372081658E-2,0.33035389086699868,0.44337756996555466,0.55071273753817163,0.61042633634742793,0.66569217106154199,0.71848702572279866,null,8.5411421372081658E-2,8.5411421372081658E-2,8.5411421372081658E-2]
["2013-02-04T15:00:00","2013-02-04T15:00:00",null,12.167308321149424,12.470880522805324,12.774452724461224,13.078024926117124,13.381597127773023,13.685169329428923,13.988741531084823,14.292313732740723,14.595885934396623,null,0,0,4.4456241347067681E-2,0.29196432417346185,0.40742743889866817,0.5170968940105799,0.57905014708051095,0.63645048796794412,0.69129573033263536,null,4.4456241347067681E-2,4.4456241347067681E-2,4.4456241347067681E-2]
["2013-02-04T16:00:00","2013-02-04T16:00:00",null,12.217490362016289,12.521062563672189,12.824634765328089,13.128206966983988,13.431779168639888,13.735351370295788,14.038923571951688,14.342495773607588,14.646067975263488,null,0,0,7.8647069473119294E-3,0.25796994753138991,0.37591455711818889,0.4879603590043376,0.55217429595241452,0.61175120224810897,0.66867837674244146,null,7.8647069473119294E-3,7.8647069473119294E-3,7.8647069473119294E-3]
["2013-02-04T17:00:00","2013-02-04T17:00:00",null,12.193785612523422,12.497357814179322,12.800930015835222,13.104502217491122,13.408074419147022,13.711646620802922,14.015218822458822,14.318791024114722,14.622363225770622,null,0,0,0,0.22483778520563405,0.34525337484529012,0.45964397907946913,0.52611859990569187,0.58785104199217653,0.64683911899867919,null,-2.7843583518656616E-2,-2.7843583518656616E-2,-2.7843583518656616E-2]
["2013-02-04T18:00:00","2013-02-04T18:00:00",null,11.927405538787699,12.230977740443599,12.534549942099499,12.838122143755399,13.141694345411299,13.445266547067199,13.748838748723099,14.052410950378999,14.355983152034899,null,0,0,0,0.19636368314973215,0.31918716398983193,0.43586999652836345,0.50454221238031871,0.56837761621391569,0.62937402168891066,null,-3.099765615243677E-2,-3.099765615243677E-2,-3.099765615243677E-2]
["2013-02-04T19:00:00","2013-02-04T19:00:00",null,11.703807838461062,12.007380040116962,12.310952241772862,12.614524443428762,12.918096645084661,13.221668846740561,13.525241048396461,13.828813250052361,14.132385451708261,null,3.686491942688036E-2,3.9619799315597608E-2,4.2237986690752544E-2,0.2410936795108129,0.36628299231641415,0.48522650873309148,0.55606477518457254,0.62197159633907517,0.68494478585635576,null,4.2237986690752544E-2,4.2237986690752544E-2,4.2237986690752544E-2]
["2013-02-04T20:00:00","2013-02-04T20:00:00",null,11.617198357915949,11.920770559571849,12.224342761227749,12.527914962883649,12.831487164539549,13.135059366195449,13.438631567851349,13.742203769507249,14.045775971163149,null,8.2530733765426106E-2,8.7956375072976101E-2,9.3119146162137054E-2,0.29439324499137665,0.42188530091006599,0.54302641235247573,0.61595712574233363,0.68387227536532869,0.74876967488121715,null,9.3119146162137054E-2,9.3119146162137054E-2,9.3119146162137054E-2]
["2013-02-04T21:00:00","2013-02-04T21:00:00",null,11.530050024862323,11.833622226518223,12.137194428174123,12.440766629830023,12.744338831485923,13.047911033141823,13.351483234797723,13.655055436453623,13.958627638109522,null,0.12950038438718153,0.13760730192229986,0.14531465672546681,0.34900716156388567,0.4788019605956631,0.60214066706380531,0.67717434220077555,0.74708730548352742,0.81390891499802376,null,0.14531465672546681,0.14531465672546681,0.14531465672546681]
["2013-02-04T22:00:00","2013-02-04T22:00:00",null,11.493207710404484,11.796779912060384,12.100352113716283,12.403924315372183,12.707496517028083,13.011068718683983,13.314640920339883,13.618213121995783,13.921785323651683,null,0.18127530260108882,0.19194783346768426,0.20208410908876603,0.40808987184900852,0.54009278071525402,0.66552393412177302,0.74256593772723556,0.81439259619985971,0.88304378243434389,null,0.20208410908876603,0.20208410908876603,0.20208410908876603]
["2013-02-04T23:00:00","2013-02-04T23:00:00",null,11.34948800753585,11.65306020919175,11.95663241084765,12.26020461250355,12.56377681415945,12.86734901581535,13.17092121747125,13.47449341912715,13.77806562078305,null,0.23643598922784706,0.24961104457350625,0.26213418177756059,0.47040062841594893,0.60455907307298462,0.7320406141829382,0.81103837221321529,0.88473666664076944,0.95516485555156361,null,0.26213418177756059,0.26213418177756059,0.26213418177756059]
["2013-02-05","2013-02-05",null,11.290247728179949,11.593819929835849,11.897392131491749,12.200964333147649,12.504536534803549,12.808108736459449,13.111680938115349,13.415253139771249,13.718825341427149,null,0.29115505388771168,0.30676954486002128,0.3216164547946348,0.53209101126749114,0.66835241767163922,0.79784228725008521,0.87874322566149898,0.95426058200030539,1,null,0.3216164547946348,0.3216164547946348,0.3216164547946348]
["2013-02-05T01:00:00","2013-02-05T01:00:00",null,11.213219551970036,11.516791753625935,11.820363955281834,12.123936156937734,12.427508358593634,12.731080560249534,13.034652761905434,13.338224963561334,13.641797165217234,null,0.3385768412850963,0.35665179750152742,0.37382248016670011,0.58651566128276,0.72488002943402052,0.85637822748095882,0.93919286108224487,1,1,null,0.37382248016670011,0.37382248016670011,0.37382248016670011]
["2013-02-05T02:00:00","2013-02-05T02:00:00",null,11.352965955797778,11.656538157453678,11.960110359109578,12.263682560765478,12.567254762421378,12.870826964077278,13.174399165733178,13.477971367389078,13.781543569044977,null,0.38017342464297954,0.40066678686858992,0.4201402126468507,0.63502047397990746,0.77546677426080934,0.90895227115876875,0.993659570332456,1,1,null,0.4201402126468507,0.4201402126468507,0.4201402126468507]
["2013-02-05T03:00:00","2013-02-05T03:00:00",null,11.369058369134702,11.672630570790602,11.976202772446502,12.279774974102402,12.583347175758302,12.886919377414202,13.190491579070102,13.494063780726002,13.797635982381902,null,0.41338970543861991,0.43632250329088063,0.45810918699096509,0.67519755815848981,0.81773630537776854,0.95321961593548477,1,1,1,null,0.45810918699096509,0.45810918699096509,0.45810918699096509]
["2013-02-05T04:00:00","2013-02-05T04:00:00",null,11.387876459900298,11.691448661556198,11.995020863212098,12.298593064867998,12.602165266523897,12.905737468179797,13.209309669835697,13.512881871491597,13.816454073147497,null,0.44485001317542139,0.47024327627180362,0.49436424751118285,0.71367124332191112,0.85832346709703788,0.99581510612324642,1,1,1,null,0.49436424751118285,0.49436424751118285,0.49436424751118285]
["2013-02-05T05:00:00","2013-02-05T05:00:00",null,11.488602573904874,11.792174775560774,12.095746977216674,12.399319178872574,12.702891380528474,13.006463582184374,13.310035783840274,13.613607985496174,13.917180187152074,null,0.47175740872972455,0.49970577034884833,0.52625566240614241,0.74787591613869431,0.89472573493955354,1,1,1,1,null,0.52625566240614241,0.52625566240614241,0.52625566240614241]
["2013-02-05T06:00:00","2013-02-05T06:00:00",null,11.650729814549223,11.954302016205123,12.257874217861023,12.561446419516923,12.865018621172823,13.168590822828723,13.472163024484622,13.775735226140522,14.079307427796422,null,0.49471123619945639,0.52527778519373514,0.55431968692135736,0.77831628742814629,0.92742679010715134,1,1,1,1,null,0.55431968692135736,0.55431968692135736,0.55431968692135736]
["2013-02-05T07:00:00","2013-02-05T07:00:00",null,11.634871219942346,11.938443421598246,12.242015623254145,12.545587824910045,12.849160026565945,13.152732228221845,13.456304429877745,13.759876631533645,14.063448833189545,null,0.51507842072024002,0.5483367607508226,0.57993376100118643,0.80635928232589016,0.95779355773545438,1,1,1,1,null,0.57993376100118643,0.57993376100118643,0.57993376100118643]
["2013-02-05T08:00:00","2013-02-05T08:00:00",null,11.689228697558022,11.992800899213922,12.296373100869822,12.599945302525722,12.903517504181622,13.207089705837522,13.510661907493422,13.814234109149321,14.117806310805221,null,0.53627627513113296,0.57218434696307718,0.60631541611871154,0.83513831383512338,0.9888648175490401,1,1,1,1,null,0.60631541611871154,0.60631541611871154,0.60631541611871154]
["2013-02-05T09:00:00","2013-02-05T09:00:00",null,11.679710850611883,11.983283052267783,12.286855253923683,12.590427455579583,12.893999657235483,13.197571858891383,13.501144060547283,13.804716262203183,14.108288463859083,null,0.55788420708271291,0.59644201071601866,0.63308611915945234,0.86430639326757241,1,1,1,1,1,null,0.63308611915945234,0.63308611915945234,0.63308611915945234]
["2013-02-05T10:00:00","2013-02-05T10:00:00",null,11.645567659227487,11.949139860883387,12.252712062539286,12.556284264195186,12.859856465851086,13.163428667506986,13.467000869162886,13.770573070818786,14.074145272474686,null,0.57779925482786731,0.61904884949747696,0.65826908608112333,0.89192879581589379,1,1,1,1,1,null,0.65826908608112333,0.65826908608112333,0.65826908608112333]
["2013-02-05T11:00:00","2013-02-05T11:00:00",null,11.764528179172679,12.068100380828579,12.371672582484479,12.675244784140379,12.978816985796279,13.282389187452178,13.585961389108078,13.889533590763978,14.193105792419878,null,0.59577957776567836,0.63975250789779858,0.68155938743039313,0.91769007721802065,1,1,1,1,1,null,0.68155938743039313,0.68155938743039313,0.68155938743039313]
["2013-02-05T12:00:00","2013-02-05T12:00:00",null,11.919445468801896,12.223017670457796,12.526589872113696,12.830162073769596,13.133734275425496,13.437306477081396,13.740878678737296,14.044450880393196,14.348023082049096,null,0.61023743977707612,0.65698627941538468,0.70143237594060526,0.94007610501603212,1,1,1,1,1,null,0.70143237594060526,0.70143237594060526,0.70143237594060526]
["2013-02-05T13:00:00","2013-02-05T13:00:00",null,11.986421092960169,12.289993294616069,12.593565496271969,12.897137697927869,13.200709899583769,13.504282101239669,13.807854302895569,14.111426504551469,14.414998706207369,null,0.62498971643306955,0.67449343596009537,0.7215577198604709,0.96269345860622602,1,1,1,1,1,null,0.7215577198604709,0.7215577198604709,0.7215577198604709]
["2013-02-05T14:00:00","2013-02-05T14:00:00",null,12.041524653101641,12.345096854757541,12.648669056413441,12.952241258069341,13.255813459725241,13.559385661381141,13.862957863037041,14.166530064692941,14.470102266348841,null,0.63747079440218168,0.68977145305286691,0.73949598356333968,0.9831657912143652,1,1,1,1,1,null,0.73949598356333968,0.73949598356333968,0.73949598356333968]
["2013-02-05T15:00:00","2013-02-05T15:00:00",null,12.111750301950279,12.415322503606179,12.718894705262079,13.022466906917979,13.326039108573879,13.629611310229778,13.933183511885678,14.236755713541578,14.540327915197478,null,0.60367619912608539,0.65882637094410801,0.71127423691709124,0.95753068751706505,0.97683587635555691,0.97919119351232276,0.98145187739046869,0.98361792798999437,0.98568934531090013,null,0.71127423691709124,0.71127423691709124,0.71127423691709124]
["2013-02-05T16:00:00","2013-02-05T16:00:00",null,12.210704441263678,12.514276642919578,12.817848844575478,13.121421046231378,13.424993247887278,13.728565449543177,14.032137651199077,14.335709852854977,14.639282054510877,null,0.54916743064093199,0.60716711562629189,0.6623383170617857,0.91118141061070779,0.93296809431079231,0.93768924343305959,0.94221061118935134,0.94654271238840271,0.95069606183894984,null,0.6623383170617857,0.6623383170617857,0.6623383170617857]
["2013-02-05T17:00:00","2013-02-05T17:00:00",null,12.056267183227801,12.359839384883701,12.663411586539601,12.966983788195501,13.270555989851401,13.574128191507301,13.877700393163201,14.181272594819101,14.484844796475,null,0.49796031209874503,0.55876745101650005,0.61660941387082657,0.86799709113375467,0.89221269565175398,0.89925761750458044,0.90600812471281134,0.91246421727644622,0.91864692481295684,null,0.61660941387082657,0.61660941387082657,0.61660941387082657]
["2013-02-05T18:00:00","2013-02-05T18:00:00",null,11.846004031131985,12.149576232787885,12.453148434443785,12.756720636099685,13.060292837755584,13.363865039411484,13.667437241067384,13.971009442723284,14.274581644379184,null,0.45241016065629047,0.51593012022782048,0.57635872603109528,0.83019635372940925,0.85675676059543893,0.86604133670894012,0.87492635009049002,0.8834328303575596,0.89157129231888466,null,0.57635872603109528,0.57635872603109528,0.57635872603109528]
["2013-02-05T19:00:00","2013-02-05T19:00:00",null,11.721292683358184,12.024864885014084,12.328437086669984,12.632009288325884,12.935581489981784,13.239153691637684,13.542725893293584,13.846298094949484,14.149870296605384,null,0.40919429675313068,0.47539553255222899,0.5383792368782454,0.79464578539447417,0.82351945018232742,0.83501213613029668,0.8460106260676945,0.85653594961199198,0.86660913638066051,null,0.5383792368782454,0.5383792368782454,0.5383792368782454]
["2013-02-05T20:00:00","2013-02-05T20:00:00",null,11.763806763868214,12.067378965524114,12.370951167180014,12.674523368835914,12.978095570491814,13.281667772147713,13.585239973803613,13.888812175459513,14.192384377115413,null,0.36730329875065171,0.43614375154237606,0.5016404951561918,0.76029390525539309,0.79144928353886335,0.80511853489509388,0.81819895696213307,0.83071157935745166,0.84268794650725698,null,0.5016404951561918,0.5016404951561918,0.5016404951561918]
["2013-02-05T21:00:00","2013-02-05T21:00:00",null,11.681342953840156,11.984915155496056,12.288487357151956,12.592059558807856,12.895631760463756,13.199203962119656,13.502776163775556,13.806348365431456,14.109920567087356,null,0.32575928943644628,0.39724947402953226,0.46526977173988282,0.72632055823079222,0.75975765000987949,0.7756139815831069,0.79077633577978734,0.80527625702612715,0.81915580455706927,null,0.46526977173988282,0.46526977173988282,0.46526977173988282]
["2013-02-05T22:00:00","2013-02-05T22:00:00",null,11.582811001582856,11.886383203238756,12.189955404894656,12.493527606550556,12.797099808206456,13.100672009862356,13.404244211518256,13.707816413174156,14.011388614830055,null,0.288652529408648,0.36270832733321112,0.43315754586147648,0.69653210508294505,0.73216679188776479,0.75012608520810464,0.76729676787327739,0.78372089911822507,0.79943002336915492,null,0.43315754586147648,0.43315754586147648,0.43315754586147648]
["2013-02-05T23:00:00","2013-02-05T23:00:00",null,11.472501766779864,11.776073968435764,12.079646170091664,12.383218371747564,12.686790573403464,12.990362775059364,13.293934976715263,13.597507178371163,13.901079380027063,null,0.25322813877853961,0.32981800560837321,0.40268563014581782,0.66835241767163889,0.7061741846934555,0.72621541014343671,0.74537339165963057,0.76369018847697945,0.78121837463916155,null,0.40268563014581782,0.40268563014581782,0.40268563014581782]
["2013-02-06","2013-02-06",null,11.270406749660623,11.573978951316523,11.877551152972423,12.181123354628323,12.484695556284223,12.788267757940122,13.091839959596022,13.395412161251922,13.698984362907822,null,0.22036936147990838,0.29947226759754131,0.37472675371795849,0.64266473993066098,0.68264204274326779,0.70474417070541906,0.72585790664642746,0.74604633941870646,0.76536204306593403,null,0.37472675371795849,0.37472675371795849,0.37472675371795849]
["2013-02-06T01:00:00","2013-02-06T01:00:00",null,11.029705469876493,11.333277671532393,11.636849873188293,11.940422074844193,12.243994276500093,12.547566478155993,12.851138679811893,13.154710881467793,13.458283083123693,null,0.1887092723771312,0.2703462474000346,0.34800862472089544,0.61822832442921494,0.66038219265008302,0.68454522312440447,0.70762522829896302,0.7296958118349075,0.75079903296718065,null,0.34800862472089544,0.34800862472089544,0.34800862472089544]
["2013-02-06T02:00:00","2013-02-06T02:00:00",null,11.033068006103711,11.336640207759611,11.640212409415511,11.943784611071411,12.247356812727311,12.550929014383211,12.854501216039111,13.158073417695011,13.461645619350911,null,0.1602141407037582,0.24430106616204753,0.32428721621346757,0.59670451094751953,0.64096134091550006,0.66711167024084272,0.69209485579653796,0.7159739864349991,0.73881215100863995,null,0.32428721621346757,0.32428721621346757,0.32428721621346757]
["2013-02-06T03:00:00","2013-02-06T03:00:00",null,11.096144088709977,11.399716290365877,11.703288492021777,12.006860693677677,12.310432895333577,12.614005096989477,12.917577298645377,13.221149500301276,13.524721701957176,null,0.1322132050409566,0.21871853650842518,0.30100742967293331,0.5756118046239822,0.62194005191286839,0.65006716528049668,0.67694301640859311,0.70260966453209983,0.7271722577383728,null,0.30100742967293331,0.30100742967293331,0.30100742967293331]
["2013-02-06T04:00:00","2013-02-06T04:00:00",null,11.057297504185359,11.360869705841258,11.664441907497158,11.968014109153058,12.271586310808958,12.575158512464858,12.878730714120758,13.182302915776658,13.485875117432558,null,0.10260350364161401,0.19159032997067524,0.27622402548321368,0.55305753988620177,0.60149926373093587,0.63164522037579207,0.66044528150249637,0.68794150634599083,0.7142495578023671,null,0.27622402548321368,0.27622402548321368,0.27622402548321368]
["2013-02-06T05:00:00","2013-02-06T05:00:00",null,11.387626100507481,11.691198302163382,11.994770503819282,12.298342705475182,12.601914907131082,12.905487108786982,13.209059310442882,13.512631512098782,13.816203713754682,null,6.7725883065754861E-2,0.15925729310882208,0.2463093946305398,0.52543513733788039,0.57606394139961137,0.60829183017410893,0.63907919015183434,0.66847859537646559,0.69659519393535851,null,0.2463093946305398,0.2463093946305398,0.2463093946305398]
["2013-02-06T06:00:00","2013-02-06T06:00:00",null,11.539795881936636,11.843368083592535,12.146940285248435,12.450512486904335,12.754084688560235,13.057656890216135,13.361229091872035,13.664801293527935,13.968373495183835,null,2.9210138667391264E-2,0.12334922127687786,0.21287230285145264,0.49435336271555913,0.5472218210379648,0.58158421598578147,0.61441144885820587,0.64575609369891607,0.67574432821273911,null,0.21287230285145264,0.21287230285145264,0.21287230285145264]
["2013-02-06T07:00:00","2013-02-06T07:00:00",null,11.575927651624628,11.879499853280528,12.183072054936428,12.486644256592328,12.790216458248228,13.093788659904128,13.397360861560028,13.700933063215928,14.004505264871828,null,0,8.5958561413219392E-2,0.17799468227559351,0.46185208891393698,0.51699174592322406,0.55352019147056652,0.58841884166389657,0.62174027054689252,0.65361065582438105,null,0.17799468227559351,0.17799468227559351,0.17799468227559351]
["2013-02-06T08:00:00","2013-02-06T08:00:00",null,11.679342096004998,11.982914297660898,12.286486499316798,12.590058700972698,12.893630902628598,13.197203104284497,13.500775305940397,13.804347507596297,14.107919709252197,null,0,4.7158917178995619E-2,0.14170807732916907,0.42796286035922065,0.48538423086412469,0.52408924181972849,0.56106982414269979,0.59637855187671696,0.63015211753534228,null,0.14170807732916907,0.14170807732916907,0.14170807732916907]
["2013-02-06T09:00:00","2013-02-06T09:00:00",null,11.867999354374577,12.171571556030477,12.475143757686377,12.778715959342277,13.082288160998177,13.385860362654077,13.689432564309977,13.993004765965877,14.296576967621776,null,0,6.5296962247840609E-3,0.10360241047149238,0.39225456989325214,0.45196816870250867,0.49286025987510934,0.53193328913645754,0.56923983053023142,0.60492709137872902,null,0.10360241047149238,0.10360241047149238,0.10360241047149238]
["2013-02-06T10:00:00","2013-02-06T10:00:00",null,12.019103442017604,12.322675643673504,12.626247845329404,12.929820046985304,13.233392248641204,13.536964450297104,13.840536651953004,14.144108853608904,14.447681055264804,null,0,0,5.9303521268569685E-2,0.35047923478686432,0.41260072479656457,0.45578504427351774,0.49705566856059841,0.53646517170148467,0.57416076101847457,null,5.9303521268569685E-2,5.9303521268569685E-2,5.9303521268569685E-2]
["2013-02-06T11:00:00","2013-02-06T11:00:00",null,12.257601493150869,12.561173694806769,12.864745896462669,13.168318098118569,13.471890299774469,13.775462501430368,14.079034703086268,14.382606904742168,14.686179106398068,null,0,0,4.2532401335348302E-2,0.33626321337638448,0.40082413901273511,0.44634274602898305,0.48985302457673846,0.53139703389094384,0.57114301091136832,null,4.2532401335348302E-2,4.2532401335348302E-2,4.2532401335348302E-2]
["2013-02-06T12:00:00","2013-02-06T12:00:00",null,12.444124593112017,12.747696794767917,13.051268996423817,13.354841198079717,13.658413399735617,13.961985601391516,14.265557803047416,14.569130004703316,14.872702206359216,null,1.1461141521762577E-2,1.4342199115306565E-2,5.9618965530636545E-2,0.3559679649468277,0.42304192987097761,0.47095791327893366,0.51676042013104162,0.56050202447097941,0.60235096323851633,null,5.9618965530636545E-2,5.9618965530636545E-2,5.9618965530636545E-2]
["2013-02-06T13:00:00","2013-02-06T13:00:00",null,12.328401125225822,12.631973326881722,12.935545528537622,13.239117730193522,13.542689931849422,13.846262133505322,14.149834335161222,14.453406536817122,14.756978738473022,null,2.1134765558479617E-2,2.6886365936832027E-2,7.4896982623408132E-2,0.37385365460601866,0.44341962920049677,0.4937119593826898,0.54179617973041472,0.58772486428734938,0.63166624999326315,null,7.4896982623408132E-2,7.4896982623408132E-2,7.4896982623408132E-2]
["2013-02-06T14:00:00","2013-02-06T14:00:00",null,12.295351609071005,12.598923810726905,12.902496012382805,13.206068214038705,13.509640415694605,13.813212617350505,14.116784819006405,14.420357020662305,14.723929222318205,null,3.726448215883172E-2,4.5939199365670369E-2,9.6725725558434839E-2,0.39833212934240697,0.47043217284215555,0.52314290903352778,0.57355090211181192,0.62169821131195024,0.66776358838244754,null,9.6725725558434839E-2,9.6725725558434839E-2,9.6725725558434839E-2]
["2013-02-06T15:00:00","2013-02-06T15:00:00",null,12.365870796188338,12.669442997844238,12.973015199500137,13.276587401156037,13.580159602811937,13.883731804467837,14.187304006123737,14.490876207779637,14.794448409435537,null,6.0912287005110657E-2,7.2562695084113352E-2,0.12617770482674401,0.43047589964701999,0.50516258609571685,0.56033378753121055,0.61310761257499613,0.66351560565328027,0.71174703332330336,null,0.12617770482674401,0.12617770482674401,0.12617770482674401]
["2013-02-06T16:00:00","2013-02-06T16:00:00",null,12.456862484222352,12.760434685878252,13.064006887534152,13.367579089190052,13.671151290845952,13.974723492501852,14.278295694157752,14.581867895813652,14.885440097469552,null,8.9249696547450241E-2,0.10379167702873249,0.16016156666008038,0.46708846366424683,0.54428818940074308,0.60186728203668038,0.65693333538481857,0.70954943829757067,0.75989434252344179,null,0.16016156666008038,0.16016156666008038,0.16016156666008038]
["2013-02-06T17:00:00","2013-02-06T17:00:00",null,12.427444791108961,12.731016992764861,13.034589194420761,13.338161396076661,13.641733597732561,13.945305799388461,14.248878001044361,14.55245020270026,14.85602240435616,null,0.1112571912309815,0.12880640701063448,0.18804683942679079,0.49771810151093893,0.57753601462259008,0.63761763173759123,0.69508106147743753,0.74999990750327772,0.8025424067548812,null,0.18804683942679079,0.18804683942679079,0.18804683942679079]
["2013-02-06T18:00:00","2013-02-06T18:00:00",null,12.146764907219515,12.450337108875415,12.753909310531315,13.057481512187215,13.361053713843114,13.664625915499014,13.968198117154914,14.271770318810814,14.575342520466714,null,0.14292779514249424,0.16334755370695564,0.22533235120309364,0.53762180066239673,0.61993172344437608,0.68240020214234975,0.74214534537781307,0.79924075681191453,0.85387570300189486,null,0.22533235120309364,0.22533235120309364,0.22533235120309364]
["2013-02-06T19:00:00","2013-02-06T19:00:00",null,12.056206328050878,12.359778529706778,12.663350731362678,12.966922933018578,13.270495134674478,13.574067336330378,13.877639537986278,14.181211739642178,14.484783941298078,null,0.18004506997902808,0.20327228247588455,0.26792784139085529,0.58276187456416439,0.66750071816405854,0.73229296959259149,0.79426725227999384,0.85348665507867882,0.91015095935462265,null,0.26792784139085529,0.26792784139085529,0.26792784139085529]
["2013-02-06T20:00:00","2013-02-06T20:00:00",null,12.01148136983281,12.315053571488709,12.618625773144609,12.922197974800509,13.225770176456409,13.529342378112309,13.832914579768209,14.136486781424109,14.440058983080009,null,0.21904449557922753,0.2450371027735368,0.3123318786811336,0.62967895114224204,0.71682568594257989,0.78389965086672975,0.84807152857986456,0.90938337831692639,0.96805601106136252,null,0.3123318786811336,0.3123318786811336,0.3123318786811336]
["2013-02-06T21:00:00","2013-02-06T21:00:00",null,11.967775117968369,12.271347319624269,12.574919521280169,12.878491722936069,13.182063924591969,13.485636126247869,13.789208327903768,14.092780529559668,14.396352731215568,null,0.25982092385573696,0.28854738132129232,0.35844982979530854,0.67827839711800963,0.76779096388384893,0.8371256126861446,0.90345302619006962,0.9668362932480371,1,null,0.35844982979530854,0.35844982979530854,0.35844982979530854]
["2013-02-06T22:00:00","2013-02-06T22:00:00",null,11.886096975670831,12.189669177326731,12.493241378982631,12.796813580638531,13.100385782294431,13.403957983950331,13.707530185606231,14.011102387262131,14.314674588918031,null,0.30417238710233746,0.33555909117798999,0.40800612336601222,0.73025309669789262,0.82206840657682001,0.89360065040484815,0.9620310256558855,1,1,null,0.40800612336601222,0.40800612336601222,0.40800612336601222]
["2013-02-06T23:00:00","2013-02-06T23:00:00",null,11.801740258705163,12.105312460361063,12.408884662016963,12.712456863672863,13.016029065328762,13.319601266984662,13.623173468640562,13.926745670296462,14.230317871952362,null,0.35207785570155792,0.38606171753489427,0.46096921496703802,0.78557150545568433,0.87962646959528634,0.9532932195966336,1,1,1,null,0.46096921496703802,0.46096921496703802,0.46096921496703802]
["2013-02-07","2013-02-07",null,11.718017086547665,12.021589288203565,12.325161489859465,12.628733691515365,12.932305893171264,13.235878094827164,13.539450296483064,13.843022498138964,14.146594699794864,null,0.39765955157021915,0.43416696750009043,0.5114718413239423,0.83835584530820551,0.93458737485606891,1,1,1,1,null,0.5114718413239423,0.5114718413239423,0.5114718413239423]
["2013-02-07T01:00:00","2013-02-07T01:00:00",null,11.607553713123187,11.911125914779086,12.214698116434986,12.518270318090886,12.821842519746786,13.125414721402686,13.428986923058586,13.732559124714486,14.036131326370386,null,0.43901429432718447,0.47802423473611955,0.55770545533420846,0.88685014319661748,0.98523720853527108,1,1,1,1,null,0.55770545533420846,0.55770545533420846,0.55770545533420846]
["2013-02-07T02:00:00","2013-02-07T02:00:00",null,11.591725170171838,11.895297371827738,12.198869573483638,12.502441775139538,12.806013976795438,13.109586178451337,13.413158380107237,13.716730581763137,14.020302783419037,null,0.47660473555681859,0.51810668563608187,0.60014322339093673,0.93153808032275598,1,1,1,1,1,null,0.60014322339093673,0.60014322339093673,0.60014322339093673]
["2013-02-07T03:00:00","2013-02-07T03:00:00",null,11.521788100169758,11.825360301825659,12.128932503481559,12.432504705137459,12.736076906793359,13.039649108449259,13.343221310105159,13.646793511761059,13.950365713416959,null,0.50589899269409433,0.54990346725242134,0.63431635178151324,0.96797189259147831,1,1,1,1,1,null,0.63431635178151324,0.63431635178151324,0.63431635178151324]
["2013-02-07T04:00:00","2013-02-07T04:00:00",null,11.552304332011129,11.855876533667029,12.159448735322929,12.463020936978829,12.766593138634729,13.070165340290629,13.373737541946529,13.677309743602429,13.980881945258329,null,0.53321646578908444,0.57975500925268186,0.66656527017348188,1,1,1,1,1,1,null,0.66656527017348188,0.66656527017348188,0.66656527017348188]
["2013-02-07T05:00:00","2013-02-07T05:00:00",null,11.636027988996958,11.939600190652857,12.243172392308757,12.546744593964657,12.850316795620557,13.153888997276457,13.457461198932357,13.761033400588257,14.064605602244157,null,0.55675912254800775,0.60590533857802453,0.69518657955168162,1,1,1,1,1,1,null,0.69518657955168162,0.69518657955168162,0.69518657955168162]
["2013-02-07T06:00:00","2013-02-07T06:00:00",null,11.724556603081837,12.028128804737737,12.331701006393637,12.635273208049536,12.938845409705436,13.242417611361336,13.545989813017236,13.849562014673136,14.153134216329036,null,0.57581195597684609,0.62763944823443119,0.71948630253956536,1,1,1,1,1,1,null,0.71948630253956536,0.71948630253956536,0.71948630253956536]
["2013-02-07T07:00:00","2013-02-07T07:00:00",null,11.657872652479828,11.961444854135728,12.265017055791628,12.568589257447528,12.872161459103427,13.175733660759327,13.479305862415227,13.782878064071127,14.086450265727027,null,0.55731640741099253,0.61177260185246818,0.7061114658279305,0.98900151006260217,0.99127270874948359,0.99342824454027379,0.99549966186117944,0.99746593109472959,0.99935859666713067,null,0.7061114658279305,0.7061114658279305,0.7061114658279305]
["2013-02-07T08:00:00","2013-02-07T08:00:00",null,12.160719818671071,12.464292020326971,12.767864221982871,13.071436423638771,13.37500862529467,13.67858082695057,13.98215302860647,14.28572523026237,14.58929743191827,null,0.5060777444425989,0.56357271860865199,0.66080315498639386,0.94645859391851839,0.95136900959802584,0.95603758467661537,0.96051689319796463,0.96479642035333846,0.96889719576020761,null,0.66080315498639386,0.66080315498639386,0.66080315498639386]
["2013-02-07T09:00:00","2013-02-07T09:00:00",null,12.064683714839477,12.368255916495377,12.671828118151277,12.975400319807177,13.278972521463077,13.582544723118977,13.886116924774877,14.189689126430777,14.493261328086676,null,0.45890831245486779,0.51936846268434933,0.6194273826119574,0.90777461258038583,0.91525064159137037,0.92237968191408137,0.92920379278346099,0.93573348900824505,0.94197928539716891,null,0.6194273826119574,0.6194273826119574,0.6194273826119574]
["2013-02-07T10:00:00","2013-02-07T10:00:00",null,12.126545367536957,12.430117569192857,12.733689770848757,13.037261972504657,13.340834174160557,13.644406375816457,13.947978577472357,14.251550779128257,14.555122980784157,null,0.39843764741665078,0.46176834043094073,0.56455059582105938,0.85549498354717157,0.86545250741974877,0.87495789451669681,0.88404268926422225,0.89274895089726758,0.90107667941583269,null,0.56455059582105938,0.56455059582105938,0.56455059582105938]
["2013-02-07T11:00:00","2013-02-07T11:00:00",null,12.167507264107334,12.471079465763234,12.774651667419134,13.078223869075034,13.381796070730934,13.685368272386834,13.988940474042733,14.292512675698633,14.596084877354533,null,0.32748371806907839,0.39355877616335005,0.49894870411988806,0.79238510151632846,0.80472948697187818,0.81650607275570763,0.82776743291149446,0.83855562667418104,0.84888116885250298,null,0.49894870411988806,0.49894870411988806,0.49894870411988806]
["2013-02-07T12:00:00","2013-02-07T12:00:00",null,12.471591764135662,12.775163965791561,13.078736167447461,13.382308369103361,13.685880570759261,13.989452772415161,14.293024974071061,14.596597175726961,14.900169377382861,null,0.27191295390163323,0.34089009920692004,0.44904542186091084,0.74512103624997728,0.75998897580206193,0.77417345278633498,0.78774807086394549,0.80075488926983562,0.81320442281274108,null,0.44904542186091084,0.44904542186091084,0.44904542186091084]
["2013-02-07T13:00:00","2013-02-07T13:00:00",null,12.476350916162035,12.779923117817935,13.083495319473835,13.387067521129735,13.690639722785635,13.994211924441535,14.297784126097435,14.601356327753335,14.904928529409235,null,0.21125302230617607,0.283132254822478,0.39406348698265714,0.69277831836434967,0.71016981201296914,0.7267726950064215,0.7426605710058557,0.75788601405494938,0.77245953896243835,null,0.39406348698265714,0.39406348698265714,0.39406348698265714]
["2013-02-07T14:00:00","2013-02-07T14:00:00",null,12.417842527891629,12.721414729547529,13.024986931203429,13.328559132859329,13.632131334515229,13.935703536171129,14.239275737827029,14.542847939482929,14.846420141138829,null,0.15289583382380698,0.22763509431618179,0.34130017674760704,0.64261216588698333,0.66249566920593106,0.68147489897362046,0.69964448846867155,0.71704649692602662,0.73371246877189233,null,0.34130017674760704,0.34130017674760704,0.34130017674760704]
["2013-02-07T15:00:00","2013-02-07T15:00:00",null,11.850973154464576,12.154545356120476,12.458117557776376,12.761689759432276,13.065261961088176,13.368834162744076,13.672406364399976,13.975978566055876,14.279550767711775,null,9.6105351843036618E-2,0.17379927359010436,0.29027180995392465,0.59426507532086925,0.61670367716255858,0.63811182774816277,0.65861570478250864,0.67824685269180285,0.69703681590225208,null,0.29027180995392465,0.29027180995392465,0.29027180995392465]
["2013-02-07T16:00:00","2013-02-07T16:00:00",null,11.978134050505714,12.281706252161614,12.585278453817514,12.888850655473414,13.192422857129314,13.495995058785214,13.799567260441114,14.103139462097014,14.406711663752914,null,4.0324291500880217E-2,0.12092030045896307,0.24015823152023619,0.54678019907107123,0.57172132539182441,0.59552685236913672,0.61832295770783507,0.64014118583412616,0.66103411079168783,null,0.24015823152023619,0.24015823152023619,0.24015823152023619]
["2013-02-07T17:00:00","2013-02-07T17:00:00",null,11.972735256798554,12.276307458454454,12.579879660110354,12.883451861766254,13.187024063422154,13.490596265078054,13.794168466733954,14.097740668389854,14.401312870045754,null,0,7.1311432844581565E-2,0.193230640133423,0.50240770620699959,0.52978826815440316,0.55592808267101024,0.58094281265291214,0.60489554695252234,0.627828344804783,null,0.193230640133423,0.193230640133423,0.193230640133423]
["2013-02-07T18:00:00","2013-02-07T18:00:00",null,11.634932171718026,11.938504373373926,12.242076575029825,12.545648776685725,12.849220978341625,13.152793179997525,13.456365381653425,13.759937583309325,14.063509784965225,null,0,2.9756908721640551E-2,0.15423121453322355,0.46583720142471496,0.49554153610267776,0.52388946045375284,0.55101766699150267,0.57698924456834078,0.6018462524192093,null,0.15423121453322355,0.15423121453322355,0.15423121453322355]
["2013-02-07T19:00:00","2013-02-07T19:00:00",null,11.335103910256674,11.638676111912574,11.942248313568474,12.245820515224374,12.549392716880273,12.852964918536173,13.156537120192073,13.460109321847973,13.763681523503873,null,3.5960645875622033E-3,3.5844982979530947E-2,0.1626851207566154,0.47654127671751706,0.50839063237753457,0.53877842962330869,0.56785187577713747,0.5956740596914345,0.62230807021861301,null,0.1626851207566154,0.1626851207566154,0.1626851207566154]
["2013-02-07T20:00:00","2013-02-07T20:00:00",null,11.158792993460482,11.462365195116382,11.765937396772282,12.069509598428182,12.373081800084082,12.676654001739982,12.980226203395882,13.283798405051781,13.587370606707681,null,5.6117534221694382E-2,9.0942580753875818E-2,0.22023266896634622,0.53641259765780713,0.57047006315229265,0.60297133695391469,0.6340425967675003,0.6637784758716696,0.69224206311883585,null,0.22023266896634622,0.22023266896634622,0.22023266896634622]
["2013-02-07T21:00:00","2013-02-07T21:00:00",null,10.935035919525365,11.238608121181263,11.542180322837163,11.845752524493063,12.149324726148963,12.452896927804863,12.756469129460763,13.060041331116663,13.363613532772563,null,0.11708239527048284,0.15444151070793471,0.28612897531211323,0.60458010269045559,0.6407931039757313,0.67535528028952352,0.70838229452792367,0.73997929477828739,0.77023039951049921,null,0.28612897531211323,0.28612897531211323,0.28612897531211323]
["2013-02-07T22:00:00","2013-02-07T22:00:00",null,10.886592829652308,11.190165031308208,11.493737232964108,11.797309434620008,12.100881636275908,12.404453837931808,12.708026039587708,13.011598241243608,13.315170442899507,null,0.18018176249259038,0.22001185798289935,0.35405463974384377,0.67472439176538967,0.71305086960651332,0.74963188919753343,0.78457259862580586,0.81799917559615742,0.84998522376973695,null,0.35405463974384377,0.35405463974384377,0.35405463974384377]
["2013-02-07T23:00:00","2013-02-07T23:00:00",null,10.862818351117282,11.16639055277318,11.46996275442908,11.77353495608498,12.07710715774088,12.38067935939678,12.68425156105268,12.98782376270858,13.291395964364479,null,0.24451136233675869,0.28680192307118918,0.42316847756269277,0.7460358246099712,0.78645474938947157,0.82502306783151291,0.86185644283218654,0.89709156690505476,0.93080204371126651,null,0.42316847756269277,0.42316847756269277,0.42316847756269277]
["2013-02-08","2013-02-08",null,10.579408244217486,10.882980445873386,11.186552647529286,11.490124849185186,11.793697050841086,12.097269252496986,12.400841454152886,12.704413655808786,13.007985857464686,null,0.30517129393221587,0.34988026067582562,0.48852852866294616,0.81356192630975033,0.85604175360142087,0.89656582646827676,0.93524980780640932,0.97225141974685192,1,null,0.48852852866294616,0.48852852866294616,0.48852852866294616]
["2013-02-08T01:00:00","2013-02-08T01:00:00",null,10.455790756266262,10.759362957922162,11.062935159578062,11.366507361233962,11.670079562889862,11.973651764545762,12.277223966201662,12.580796167857562,12.884368369513462,null,0.35911226274564889,0.40619757626349567,0.54708549851129096,0.87424288752267865,0.9187310432828415,0.96115829653083407,1,1,1,null,0.54708549851129096,0.54708549851129096,0.54708549851129096]
["2013-02-08T02:00:00","2013-02-08T02:00:00",null,10.262303689376322,10.565875891032222,10.869448092688122,11.173020294344022,11.476592495999922,11.780164697655822,12.083736899311722,12.387309100967622,12.690881302623522,null,0.40513558058120375,0.4545551816383453,0.59765121372060859,0.92690104967037312,0.9733659894728216,1,1,1,1,null,0.59765121372060859,0.59765121372060859,0.59765121372060859]
["2013-02-08T03:00:00","2013-02-08T03:00:00",null,10.174407193913924,10.477979395569823,10.781551597225722,11.085123798881622,11.388696000537522,11.692268202193421,11.995840403849321,12.299412605505221,12.602984807161121,null,0.45082242453722066,0.50257631313365692,0.64786994024165268,0.97919119351232298,1,1,1,1,1,null,0.64786994024165268,0.64786994024165268,0.64786994024165268]
["2013-02-08T04:00:00","2013-02-08T04:00:00",null,10.072472312261223,10.376044513917122,10.679616715573022,10.983188917228922,11.286761118884822,11.590333320540722,11.893905522196622,12.197477723852522,12.501049925508422,null,0.4941644661452072,0.54833676075082272,0.69590158654569989,1,1,1,1,1,1,null,0.69590158654569989,0.69590158654569989,0.69590158654569989]
["2013-02-08T05:00:00","2013-02-08T05:00:00",null,10.091012394657456,10.394584596313356,10.698156797969258,11.001728999625158,11.305301201281058,11.608873402936958,11.912445604592858,12.216017806248757,12.519590007904657,null,0.53700179693388683,0.59360301235741708,0.74347058126538235,1,1,1,1,1,1,null,0.74347058126538235,0.74347058126538235,0.74347058126538235]
["2013-02-08T06:00:00","2013-02-08T06:00:00",null,9.9618641070287879,10.265436308684688,10.569008510340588,10.872580711996488,11.176152913652388,11.479725115308288,11.783297316964187,12.086869518620087,12.390441720275987,null,0.57906103187613478,0.63814374216125769,0.79035611341725331,1,1,1,1,1,1,null,0.79035611341725331,0.79035611341725331,0.79035611341725331]
["2013-02-08T07:00:00","2013-02-08T07:00:00",null,9.9097099329910421,10.213282134646942,10.516854336302842,10.820426537958742,11.123998739614642,11.427570941270542,11.731143142926442,12.034715344582342,12.338287546238242,null,0.61827075365104545,0.67987701803270328,0.83447625087167143,1,1,1,1,1,1,null,0.83447625087167143,0.83447625087167143,0.83447625087167143]
["2013-02-08T08:00:00","2013-02-08T08:00:00",null,9.9918337819971779,10.295405983653078,10.598978185308978,10.902550386964878,11.206122588620778,11.509694790276678,11.813266991932577,12.116839193588477,12.420411395244377,null,0.6568390720930869,0.72096889057127955,0.87795498499322033,1,1,1,1,1,1,null,0.87795498499322033,0.87795498499322033,0.87795498499322033]
["2013-02-08T09:00:00","2013-02-08T09:00:00",null,10.164658119428568,10.468230321084468,10.771802522740369,11.075374724396269,11.378946926052169,11.682519127708069,11.986091329363969,12.289663531019869,12.593235732675769,null,0.69388274326847177,0.76054663065193495,0.91991958665684825,1,1,1,1,1,1,null,0.91991958665684825,0.91991958665684825,0.91991958665684825]
["2013-02-08T10:00:00","2013-02-08T10:00:00",null,10.256718921516025,10.560291123171925,10.863863324827825,11.167435526483725,11.471007728139625,11.774579929795525,12.078152131451425,12.381724333107325,12.685296534763225,null,0.69659556392224675,0.76580403501971595,0.92757436741633736,1,1,1,1,1,1,null,0.92757436741633736,0.92757436741633736,0.92757436741633736]
["2013-02-08T11:00:00","2013-02-08T11:00:00",null,10.494922889745206,10.798495091401106,11.102067293057006,11.405639494712906,11.709211696368806,12.012783898024706,12.316356099680606,12.619928301336506,12.923500502992406,null,0.66488290077579182,0.73670955924841586,0.90096138650662994,0.97573182143832293,0.97795044608152648,0.98006392263737441,0.98207225110586682,0.9839754314870035,0.98580500820699135,null,0.90096138650662994,0.90096138650662994,0.90096138650662994]
["2013-02-08T12:00:00","2013-02-08T12:00:00",null,10.642084858494163,10.945657060150063,11.249229261805963,11.552801463461863,11.856373665117763,12.159945866773663,12.463518068429563,12.767090270085463,13.070662471741363,null,0.62539979397375656,0.70001287676130453,0.86689340620340904,0.94416636561416578,0.94875082222287077,0.95311446784812903,0.95726781729867605,0.96121087057451182,0.96498568691057862,null,0.86689340620340904,0.86689340620340904,0.86689340620340904]
["2013-02-08T13:00:00","2013-02-08T13:00:00",null,10.788065828232083,11.091638029887983,11.395210231543883,11.698782433199783,12.002354634855683,12.305926836511583,12.609499038167483,12.913071239823383,13.216643441479283,null,0.57897691340625035,0.65653414263975562,0.82620109639678407,0.90611327280016696,0.91320025388793569,0.91995076109616647,0.92636479442485931,0.93247389830022087,0.93830961714845784,null,0.82620109639678407,0.82620109639678407,0.82620109639678407]
["2013-02-08T14:00:00","2013-02-08T14:00:00",null,10.853222945493894,11.156795147149793,11.460367348805693,11.763939550461593,12.067511752117493,12.371083953773393,12.674656155429293,12.978228357085193,13.281800558741093,null,0.52944164945301775,0.6099955991761582,0.78251206610052393,0.86512654834894631,0.87477914276819213,0.8839690856030733,0.89270689166232531,0.90102410537215494,0.90897330077623983,null,0.78251206610052393,0.78251206610052393,0.78251206610052393]
["2013-02-08T15:00:00","2013-02-08T15:00:00",null,10.821353317311019,11.124925518966919,11.428497720622818,11.732069922278718,12.035642123934618,12.339214325590518,12.642786527246418,12.946358728902318,13.249930930558218,null,0.47794011626623506,0.56155387533142409,0.73698294427554045,0.82235230641268009,0.83462308820708087,0.8462945259035547,0.85739816392830814,0.86797606151628359,0.87808079271115869,null,0.73698294427554045,0.73698294427554045,0.73698294427554045]
["2013-02-08T16:00:00","2013-02-08T16:00:00",null,10.890681600446586,11.194253802102486,11.497826003758385,11.801398205414285,12.104970407070185,12.408542608726085,12.712114810381985,13.015687012037885,13.319259213693785,null,0.42669093848910589,0.5133539920876079,0.69166411862526822,0.77976733103365403,0.79463527058573857,0.80877768833506947,0.82223664351658887,0.83505419536523895,0.84730394754216876,null,0.69166411862526822,0.69166411862526822,0.69166411862526822]
["2013-02-08T17:00:00","2013-02-08T17:00:00",null,10.759745705378188,11.063317907034088,11.366890108689988,11.670462310345888,11.974034512001788,12.277606713657688,12.581178915313588,12.884751116969488,13.188323318625388,null,0.38157189420480936,0.47114754982306206,0.65221255624943963,0.7429339560329804,0.76028339044665749,0.77678112535275434,0.79247973479494838,0.80743179281691757,0.82172141788854647,null,0.65221255624943963,0.65221255624943963,0.65221255624943963]
["2013-02-08T18:00:00","2013-02-08T18:00:00",null,10.526987069804662,10.830559271460562,11.134131473116462,11.437703674772361,11.741275876428261,12.044848078084161,12.348420279740061,12.651992481395961,12.955564683051861,null,0.3442338083848287,0.43656434389179866,0.62023702288459559,0.71342940272099342,0.73311312467396528,0.75183999903200127,0.76965208503004323,0.78661247152050484,0.80282630659074161,null,0.62023702288459559,0.62023702288459559,0.62023702288459559]
["2013-02-08T19:00:00","2013-02-08T19:00:00",null,10.429438774785973,10.733010976441875,11.036583178097775,11.340155379753675,11.643727581409575,11.947299783065475,12.250871984721375,12.554444186377275,12.858016388033175,null,0.31365674458181442,0.40863701189014601,0.59481221536200668,0.69037042716390595,0.71229380337755255,0.73314466910017206,0.75298611318417752,0.77187070967324689,0.78991412146347151,null,0.59481221536200668,0.59481221536200668,0.59481221536200668]
["2013-02-08T20:00:00","2013-02-08T20:00:00",null,10.246109356423712,10.549681558079612,10.853253759735512,11.156825961391412,11.460398163047312,11.763970364703212,12.067542566359112,12.371114768015012,12.674686969670912,null,0.2853508794656815,0.38295984895790358,0.57162706210009251,0.66953007625002203,0.69368259191560777,0.71663641938533973,0.73848619193783749,0.75927396880804365,0.77913644250952041,null,0.57162706210009251,0.57162706210009251,0.57162706210009251]
["2013-02-08T21:00:00","2013-02-08T21:00:00",null,10.248194095142614,10.551766296798514,10.855338498454415,11.158910700110315,11.462482901766215,11.766055103422115,12.069627305078015,12.373199506733915,12.676771708389815,null,0.25681368855736625,0.35705136023347883,0.5482105830459959,0.64845839954395579,0.67484005466148067,0.69990735868706055,0.72376545970805073,0.74645641695939358,0.76813795257212258,null,0.5482105830459959,0.5482105830459959,0.5482105830459959]
["2013-02-08T22:00:00","2013-02-08T22:00:00",null,10.227920006029795,10.531492207685694,10.835064409341594,11.138636610997494,11.442208812653394,11.745781014309294,12.049353215965194,12.352925417621094,12.656497619276994,null,0.23302919119752502,0.33576938735270134,0.52929444213071986,0.63178191288935448,0.66027704456272729,0.68735267705679948,0.71311395845892644,0.73761346281278595,0.76101942705814707,null,0.52929444213071986,0.52929444213071986,0.52929444213071986]
["2013-02-08T23:00:00","2013-02-08T23:00:00",null,10.142547826974186,10.446120028630085,10.749692230285984,11.053264431941884,11.356836633597784,11.660408835253683,11.963981036909583,12.267553238565483,12.571125440221383,null,0.21000176006664426,0.31524448070088434,0.51113536744440424,0.61585197765497801,0.64646058588419886,0.67553403203802775,0.70319849382129151,0.72950654527766767,0.75462642334692542,null,0.51113536744440424,0.51113536744440424,0.51113536744440424]
["2013-02-09T00:00:00.065","2013-02-09",null,10.092909246321385,10.396481447977285,10.700053649633187,11.003625851289087,11.307198052944987,11.610770254600887,11.914342456256787,12.217914657912686,12.521486859568586,null,0.18958200150218285,0.29726415776307336,0.49545778761968129,0.60235096323851645,0.63500995917117187,0.66603915974981531,0.6955437130618024,0.72361825238575295,0.75040998504396506,null,0.49545778761968129,0.49545778761968129,0.49545778761968129]
["2013-02-09T01:00:00.070","2013-02-09T01:00:00",null,10.127655364000709,10.431227565656609,10.734799767312509,11.038371968968409,11.341944170624309,11.645516372280209,11.949088573936109,12.252660775592009,12.556232977247909,null,0.17103387889265148,0.28109238192777902,0.48152566604506164,0.59054283302848032,0.62519964262089256,0.65813202358067269,0.68943460918644084,0.71922306233428801,0.7476551051552478,null,0.48152566604506164,0.48152566604506164,0.48152566604506164]
["2013-02-09T02:00:00.075","2013-02-09T02:00:00",null,10.242450514665002,10.546022716320902,10.849594917976802,11.153167119632702,11.456739321288602,11.760311522944502,12.063883724600402,12.367455926256302,12.671028127912201,null,0.15387371103621431,0.26624547199316551,0.46885532151870946,0.57993339101429831,0.61654595503152498,0.65132894232876404,0.68439801580210669,0.71585832353890821,0.74587810247893782,null,0.46885532151870946,0.46885532151870946,0.46885532151870946]
["2013-02-09T03:00:00.080","2013-02-09T03:00:00",null,10.271259465469704,10.574831667125604,10.878403868781504,11.181976070437404,11.485548272093304,11.789120473749204,12.092692675405104,12.396264877061004,12.699837078716904,null,0.13880599011815398,0.25341740533577989,0.45814073141717176,0.57122712938125297,0.60973235897088085,0.64631337856190096,0.68109636585914024,0.71417595414121826,0.74575192477411112,null,0.45814073141717176,0.45814073141717176,0.45814073141717176]
["2013-02-09T04:00:00.085","2013-02-09T04:00:00",null,10.322940132160825,10.626512333816725,10.930084535472627,11.233656737128527,11.537228938784427,11.840801140440327,12.144373342096227,12.447945543752127,12.751517745408027,null,0.19925562553889992,0.31618029867834946,0.52308019016800267,0.63823800545298959,0.67868847465869642,0.71713061539591105,0.75366957575198912,0.78843153343175709,0.82159524018371977,null,0.52308019016800267,0.52308019016800267,0.52308019016800267]
["2013-02-09T05:00:00.090","2013-02-09T05:00:00",null,10.462521152258528,10.766093353914428,11.069665555570328,11.373237757226228,11.676809958882128,11.980382160538028,12.283954362193928,12.587526563849828,12.891098765505728,null,0.26209212254261843,0.38140365726504055,0.59055371782410404,0.70783552447367448,0.75030483695660921,0.79066067288369613,0.82902920995976193,0.86551559627216212,0.90034064280434356,null,0.59055371782410404,0.59055371782410404,0.59055371782410404]
["2013-02-09T06:00:00.095","2013-02-09T06:00:00",null,10.476358241753212,10.779930443409112,11.083502645065012,11.387074846720912,11.690647048376812,11.994219250032712,12.297791451688612,12.601363653344512,12.904935855000412,null,0.32424515697852541,0.44595406809265564,0.65737532733860049,0.77680215497022564,0.82130082553912387,0.86359138627355414,0.90378950006960768,0.94202134463211118,0.97851824575324697,null,0.65737532733860049,0.65737532733860049,0.65737532733860049]
["2013-02-09T07:00:00.100","2013-02-09T07:00:00",null,10.441229673111053,10.744801874766953,11.048374076422853,11.351946278078753,11.655518479734653,11.959090681390553,12.262662883046453,12.566235084702353,12.869807286358252,null,0.37572566054783696,0.4997898888187331,0.71344028751661703,0.83497007689535463,0.88146656112400956,0.92564978743084103,0.96764593352067574,1,1,null,0.71344028751661703,0.71344028751661703,0.71344028751661703]
["2013-02-09T08:00:00.105","2013-02-09T08:00:00",null,10.384990741778786,10.688562943434686,10.992135145090586,11.295707346746486,11.599279548402386,11.902851750058286,12.206423951714186,12.509996153370086,12.813568355025986,null,0.43894069066603569,0.56539178051990435,0.78129234828719862,0.90495664383925534,0.95348248615387365,0.9995794076505774,1,1,1,null,0.78129234828719862,0.78129234828719862,0.78129234828719862]
["2013-02-09T09:00:00.110","2013-02-09T09:00:00",null,10.254364428502328,10.557936630158228,10.861508831814128,11.165081033470027,11.468653235125927,11.772225436781827,12.075797638437727,12.379369840093627,12.682942041749527,null,0.50153534706883629,0.63041535774061974,0.84860815381226651,0.97444901477258461,1,1,1,1,1,null,0.84860815381226651,0.84860815381226651,0.84860815381226651]
["2013-02-09T10:00:00.115","2013-02-09T10:00:00",null,10.396353083219546,10.699925284875446,11.003497486531348,11.307069688187248,11.610641889843148,11.914214091499048,12.217786293154948,12.521358494810848,12.824930696466748,null,0.56415103308910797,0.69543893496133513,0.91589241491112772,1,1,1,1,1,1,null,0.91589241491112772,0.91589241491112772,0.91589241491112772]
["2013-02-09T11:00:00.120","2013-02-09T11:00:00",null,10.410671336996005,10.714243538651905,11.017815740307807,11.321387941963707,11.624960143619607,11.928532345275507,12.232104546931406,12.535676748587306,12.839248950243206,null,0.62603068249789029,0.75973699037929676,0.98248269863344184,1,1,1,1,1,1,null,0.98248269863344184,0.98248269863344184,0.98248269863344184]
["2013-02-09T12:00:00.125","2013-02-09T12:00:00",null,10.536578084743004,10.840150286398904,11.143722488054804,11.447294689710704,11.750866891366604,12.054439093022504,12.358011294678404,12.661583496334304,12.965155697990204,null,0.68858327966574862,0.82466593432139212,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-09T13:00:00.130","2013-02-09T13:00:00",null,10.577861033379957,10.881433235035857,11.185005436691757,11.488577638347657,11.792149840003557,12.095722041659457,12.399294243315357,12.702866444971256,13.006438646627156,null,0.74922218164373466,0.88772324230855748,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-09T14:00:00.135","2013-02-09T14:00:00",null,10.619721347260334,10.923293548916234,11.226865750572133,11.530437952228032,11.834010153883932,12.137582355539832,12.441154557195732,12.744726758851632,13.048298960507532,null,0.77906320883525959,0.91993010146558385,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-09T15:00:00.140","2013-02-09T15:00:00",null,10.7690806040016,11.0726528056575,11.376225007313399,11.679797208969299,11.983369410625199,12.286941612281099,12.590513813936999,12.894086015592899,13.197658217248799,null,0.76358541037651229,0.90689173863348693,0.98927489508972677,0.99146197530672364,0.99354390743636489,0.99553120628738612,0.99741335705105172,0.99920087453609729,1,null,0.98927489508972677,0.98927489508972677,0.98927489508972677]
["2013-02-09T16:00:00.145","2013-02-09T16:00:00",null,10.666019960176218,10.969592161832118,11.273164363488018,11.576736565143918,11.880308766799818,12.183880968455718,12.487453170111618,12.791025371767518,13.094597573423417,null,0.74962174437568596,0.8953569934505754,0.98003237821116773,0.9843855090276904,0.98852834366950182,0.99247139694533759,0.9962146688551976,0.99977918901655316,1,null,0.98003237821116773,0.98003237821116773,0.98003237821116773]
["2013-02-09T17:00:00.150","2013-02-09T17:00:00",null,10.648198012690862,10.951770214346762,11.255342416002662,11.558914617658562,11.862486819314462,12.166059020970362,12.469631222626262,12.773203424282162,13.076775625938062,null,0.73657286673485356,0.88471600701018671,0.97166259045766035,0.97817125706497321,0.98435396460148372,0.99023174268466285,0.99582562093198179,1,1,null,0.97166259045766035,0.97166259045766035,0.97166259045766035]
["2013-02-09T18:00:00.155","2013-02-09T18:00:00",null,10.598510477593711,10.902082679249611,11.205654880905511,11.509227082561411,11.812799284217311,12.116371485873211,12.419943687529111,12.723515889185011,13.027088090840911,null,0.72600548395561371,0.87649342657897722,0.9656586346696544,0.97427026302407971,0.98244026941161144,0.99021071306719177,0.99760262360829177,1,1,null,0.9656586346696544,0.9656586346696544,0.9656586346696544]
["2013-02-09T19:00:00.160","2013-02-09T19:00:00",null,10.588991268948391,10.892563470604291,11.196135672260191,11.499707873916091,11.80328007557199,12.10685227722789,12.41042447888379,12.71399668053969,13.01756888219559,null,0.7159217823782098,0.86874401254086808,0.96011733046601322,0.97082140575881537,0.98096819618863274,0.99062079060787867,0.99980021863402424,1,1,null,0.96011733046601322,0.96011733046601322,0.96011733046601322]
["2013-02-09T20:00:00.165","2013-02-09T20:00:00",null,10.679957858331989,10.983530059987888,11.287102261643788,11.590674463299688,11.894246664955588,12.197818866611488,12.501391068267388,12.804963269923288,13.108535471579188,null,0.70484968877966303,0.86000620648161608,0.95359814904996476,0.96639467128114376,0.97853927537071794,0.99008453536236496,1,1,1,null,0.95359814904996476,0.95359814904996476,0.95359814904996476]
["2013-02-09T21:00:00.170","2013-02-09T21:00:00",null,10.814222279526414,11.117794481182314,11.421366682838213,11.724938884494113,12.028511086150013,12.332083287805913,12.635655489461813,12.939227691117713,13.242799892773613,null,0.6941140690606542,0.85157332987569534,0.94734183785230541,0.96220977740439007,0.97632065072751439,0.98972703186535582,1,1,1,null,0.94734183785230541,0.94734183785230541,0.94734183785230541]
["2013-02-09T22:00:00.175","2013-02-09T22:00:00",null,10.750650557472143,11.054222759128043,11.357794960783943,11.661367162439843,11.964939364095743,12.268511565751643,12.572083767407543,12.875655969063443,13.179228170719343,null,0.6861753884653049,0.84586378873228518,0.94374577326474318,0.96061152647658465,0.97662558018084566,0.99184050842120375,1,1,1,null,0.94374577326474318,0.94374577326474318,0.94374577326474318]
["2013-02-09T23:00:00.180","2013-02-09T23:00:00",null,10.919747505399236,11.223319707055136,11.526891908711036,11.830464110366936,12.134036312022836,12.437608513678736,12.741180715334636,13.044752916990536,13.348325118646436,null,0.67505072082308026,0.83696826054199969,0.93697423643904121,0.9558483181193751,0.97376555220477279,0.99079954235638312,1,1,1,null,0.93697423643904121,0.93697423643904121,0.93697423643904121]
["2013-02-10T00:00:00.185","2013-02-10",null,11.275274887863679,11.578847089519579,11.882419291175479,12.185991492831379,12.489563694487279,12.793135896143179,13.096708097799079,13.400280299454979,13.703852501110878,null,0.66042462187191353,0.82460284546897877,0.9267538423480749,0.94765728211437228,0.96751975581584893,0.9863938374961827,0.99736078300737396,0.99903263759632832,1,null,0.9267538423480749,0.9267538423480749,0.9267538423480749]
["2013-02-10T01:00:00.190","2013-02-10T01:00:00",null,11.500543303193039,11.804115504848939,12.107687706504839,12.411259908160739,12.714832109816639,13.018404311472539,13.321976513128439,13.625548714784339,13.929120916440239,null,0.64191855849732438,0.8084100400162133,0.91276914672977749,0.93575451862571613,0.95761480598694948,0.97838155323968445,0.99116756066212797,0.99457435869245003,0.99719254606760499,null,0.91276914672977749,0.91276914672977749,0.91276914672977749]
["2013-02-10T02:00:00.195","2013-02-10T02:00:00",null,11.710018184924394,12.013590386580294,12.317162588236194,12.620734789892094,12.924306991547994,13.227879193203893,13.531451394859793,13.835023596515693,14.138595798171593,null,0.6203526857806867,0.78919948445634158,0.8957982454305804,0.92090760869110255,0.9447972541382994,0.96749872619837773,0.98213533995828017,0.98730862585617674,0.99160918262902153,null,0.8957982454305804,0.8957982454305804,0.8957982454305804]
["2013-02-10T03:00:00.200","2013-02-10T03:00:00",null,11.44154025147737,11.745112453133268,12.048684654789168,12.352256856445068,12.655829058100968,12.959401259756868,13.262973461412768,13.566545663068668,13.870117864724568,null,0.60452789863366585,0.77563538118746655,0.88436864833502449,0.91151788449024573,0.93735276955352154,0.96190484795105879,0.97829743476980002,0.98516360487412213,0.99107292738350783,null,0.88436864833502449,0.88436864833502449,0.88436864833502449]
["2013-02-10T04:00:00.205","2013-02-10T04:00:00",null,11.267529464610028,11.571101666265928,11.874673867921828,12.178246069577728,12.481818271233628,12.785390472889528,13.088962674545428,13.392534876201328,13.696107077857228,null,0.59023827356203706,0.7635959251852481,0.87446369850612504,0.90364229274730978,0.93140138780919346,0.95779355773545405,0.97594211761303418,0.98448014230631065,0.99199823055223724,null,0.87446369850612504,0.87446369850612504,0.87446369850612504]
["2013-02-10T05:00:00.210","2013-02-10T05:00:00",null,10.929229956399645,11.232802158055545,11.536374359711445,11.839946561367345,12.143518763023245,12.447090964679145,12.750663166335045,13.054235367990945,13.357807569646845,null,0.5786194099092411,0.75422723060186236,0.86721899528732282,0.89841643280573547,0.92808922305749142,0.95631096970373985,0.97619447302268769,0.98639383749618292,0.99548914705244385,null,0.86721899528732282,0.86721899528732282,0.86721899528732282]
["2013-02-10T06:00:00.215","2013-02-10T06:00:00",null,10.510369744970154,10.813941946626054,11.117514148281954,11.421086349937854,11.724658551593754,12.028230753249654,12.331802954905553,12.635375156561453,12.938947358217353,null,0.56683230931667605,0.74477441754859208,0.85997429206852061,0.89326417652531009,0.92492426562808727,0.95502816303800131,0.97669918384199472,0.98860194733065099,0.999327052240924,null,0.85997429206852061,0.85997429206852061,0.85997429206852061]
["2013-02-10T07:00:00.220","2013-02-10T07:00:00",null,10.399622800033681,10.703195001689581,11.006767203345481,11.310339405001381,11.613911606657281,11.917483808313181,12.221056009969081,12.524628211624981,12.82820041328088,null,0.55354159107492573,0.73388107569854988,0.8513626637140953,0.8867975691529395,0.92049753115041566,0.95253615336767317,0.97604726570038991,0.98969548743914948,1,null,0.8513626637140953,0.8513626637140953,0.8513626637140953]
["2013-02-10T08:00:00.225","2013-02-10T08:00:00",null,10.339731443020904,10.643303644676804,10.946875846332704,11.250448047988604,11.554020249644504,11.857592451300404,12.161164652956304,12.464736854612203,12.768309056268103,null,0.53969358797019062,0.72247250822046516,0.84224632454036308,0.87985779538746856,0.91561865989711488,0.94961303653918694,0.97498527001809809,0.99039997962443216,1,null,0.84224632454036308,0.84224632454036308,0.84224632454036308]
["2013-02-10T09:00:00.230","2013-02-10T09:00:00",null,10.316412119006085,10.619984320661985,10.923556522317885,11.227128723973784,11.530700925629684,11.834273127285584,12.137845328941484,12.441417530597384,12.744989732253284,null,0.52339563443006953,0.70867707915940781,0.83082724225354276,0.87067836736132298,0.90856322323555283,0.94456592834611719,0.97185185701490062,0.98908562853248694,1,null,0.83082724225354276,0.83082724225354276,0.83082724225354276]
["2013-02-10T10:00:00.235","2013-02-10T10:00:00",null,10.332664192940205,10.636236394596105,10.939808596252007,11.243380797907907,11.546952999563807,11.850525201219707,12.154097402875607,12.457669604531507,12.761241806187407,null,0.50627752580857455,0.69408252463444775,0.81861954931155534,0.86073135829748137,0.90076123515376583,0.93879329835029368,0.96801395182642047,0.98707730006399463,0.999737129781611,null,0.81861954931155534,0.81861954931155534,0.81861954931155534]
["2013-02-10T11:00:00.240","2013-02-10T11:00:00",null,10.453468336351976,10.757040538007876,11.060612739663776,11.364184941319676,11.667757142975576,11.971329344631476,12.274901546287376,12.578473747943276,12.882045949599176,null,0.48665689270801588,0.67702750486536623,0.80399345036038861,0.84840800245940273,0.89061444472394846,0.93071792524138208,0.96190484795105891,0.98285034695229867,0.99728717934622502,null,0.80399345036038861,0.80399345036038861,0.80399345036038861]
["2013-02-10T12:00:00.245","2013-02-10T12:00:00",null,10.63498297720381,10.938555178859712,11.242127380515612,11.545699582171512,11.849271783827412,12.152843985483312,12.456416187139212,12.759988388795112,13.063560590451011,null,0.46164216272611386,0.65469405111103252,0.78419406551132531,0.83101650881078315,0.87549414976221029,0.91776368087916971,0.9510115061010167,0.9739232743358065,0.99023174268466296,null,0.78419406551132531,0.78419406551132531,0.78419406551132531]
["2013-02-10T13:00:00.250","2013-02-10T13:00:00",null,10.726442318001673,11.030014519657573,11.333586721313473,11.637158922969373,11.940731124625273,12.244303326281173,12.547875527937073,12.851447729592973,13.155019931248873,null,0.43213760941412688,0.62797592211396946,0.76010463869815281,0.80941909166793879,0.85626256458486738,0.90078226477123713,0.93617511097513872,0.9611267521046275,0.97938046006956303,null,0.76010463869815281,0.76010463869815281,0.76010463869815281]
["2013-02-10T14:00:00.255","2013-02-10T14:00:00",null,10.800460251586344,11.104032453242244,11.407604654898144,11.711176856554044,12.014749058209944,12.318321259865844,12.621893461521744,12.925465663177643,13.229037864833543,null,0.39911059517572667,0.59780893585164208,0.73263995828086492,0.78452002458212799,0.83380293312570697,0.88063589123390029,0.91823684727226995,0.94528093534013558,0.96554297177356341,null,0.73263995828086492,0.73263995828086492,0.73263995828086492]
["2013-02-10T15:00:00.260","2013-02-10T15:00:00",null,10.94283631559639,11.24640851725229,11.54998071890819,11.853552920564089,12.157125122219989,12.460697323875889,12.764269525531789,13.067841727187689,13.371413928843589,null,0.36628336230330211,0.56779967172034818,0.70530145556840373,0.75971559077493722,0.81140639051895991,0.86052106212277024,0.90029858356940118,0.92942460376690805,0.95167393905135711,null,0.70530145556840373,0.70530145556840373,0.70530145556840373]
["2013-02-10T16:00:00.265","2013-02-10T16:00:00",null,10.953143799731965,11.256716001387865,11.560288203043765,11.863860404699665,12.167432606355565,12.471004808011465,12.774577009667365,13.078149211323264,13.381721412979164,null,0.32955513538998404,0.5339945616355164,0.67426174018102469,0.73129406276271314,0.78548738698579956,0.83696789055511134,0.87900609587988809,0.91028765186818517,0.93459788966480439,null,0.67426174018102469,0.67426174018102469,0.67426174018102469]
["2013-02-10T17:00:00.270","2013-02-10T17:00:00",null,10.866794158508485,11.170366360164385,11.473938561820285,11.777510763476185,12.081082965132085,12.384655166787985,12.688227368443885,12.991799570099785,13.295371771755685,null,0.29339470814838631,0.50075725122240489,0.64380033927410163,0.70346136403968051,0.76014669793309519,0.8140035482766439,0.85830243747956647,0.89173952925865385,0.91810015475870765,null,0.64380033927410163,0.64380033927410163,0.64380033927410163]
["2013-02-10T18:00:00.275","2013-02-10T18:00:00",null,10.775948443397462,11.079520645053364,11.383092846709264,11.686665048365164,11.990237250021064,12.293809451676964,12.597381653332864,12.900953854988764,13.204526056644664,null,0.26154535248836902,0.47174689392098934,0.61747125820025439,0.67966635187110369,0.73877009177369768,0.79491917042159888,0.84140513984151832,0.87692416375024695,0.9052615732925865,null,0.61747125820025439,0.61747125820025439,0.61747125820025439]
["2013-02-10T19:00:00.280","2013-02-10T19:00:00",null,10.53932345128889,10.84289565294479,11.14646785460069,11.45004005625659,11.75361225791249,12.05718445956839,12.36075666122429,12.66432886288019,12.96790106453609,null,0.23411221649728778,0.44708966743609646,0.59543221909051647,0.66010880762295843,0.72156786468231826,0.7799460827821586,0.82855604356666157,0.8660939107526181,0.896366045102301,null,0.59543221909051647,0.59543221909051647,0.59543221909051647]
["2013-02-10T20:00:00.285","2013-02-10T20:00:00",null,10.486148742397141,10.789720944053041,11.093293145708941,11.396865347364841,11.700437549020741,12.004009750676641,12.307581952332541,12.611154153988441,12.914726355644341,null,0.20930778269009703,0.42498753947394513,0.57589570445984228,0.64300121381019903,0.70675249917391136,0.76731779749074869,0.81799917559615731,0.85751382682439947,0.88966811193774797,null,0.57589570445984228,0.57589570445984228,0.57589570445984228]
["2013-02-10T21:00:00.290","2013-02-10T21:00:00",null,10.443467798990248,10.747040000646148,11.050612202302048,11.354184403957948,11.657756605613848,11.961328807269748,12.264901008925648,12.568473210581548,12.872045412237448,null,0.18662734024748981,0.40496734364143511,0.55839906272386708,0.62788091884846087,0.69389288809031902,0.75659269258047546,0.80931394358058306,0.85076331961616869,0.88476821106697612,null,0.55839906272386708,0.55839906272386708,0.55839906272386708]
["2013-02-10T22:00:00.295","2013-02-10T22:00:00",null,10.226247699555113,10.529819901211013,10.833392102866913,11.136964304522813,11.440536506178713,11.744108707834613,12.047680909490513,12.351253111146413,12.654825312802313,null,0.16769016971474265,0.38863784567510734,0.54453003000166078,0.61633565885681374,0.68455573793313995,0.74933747455293764,0.80404602440406647,0.8473880660120533,0.8831804749479063,null,0.54453003000166078,0.54453003000166078,0.54453003000166078]
["2013-02-10T23:00:00.300","2013-02-10T23:00:00",null,10.150237606451416,10.453809808107316,10.757382009763216,11.060954211419116,11.364526413075016,11.668098614730916,11.971670816386816,12.275243018042715,12.578815219698615,null,0.15272759688403792,0.37618831213220194,0.53444632842425688,0.60849161154008446,0.6788356819809942,0.74562574706928431,0.80224799211028541,0.84739858082078889,0.88491541838927401,null,0.53444632842425688,0.53444632842425688,0.53444632842425688]
["2013-02-11T00:00:00.305","2013-02-11",null,10.147396577693645,10.450968779349544,10.754540981005444,11.058113182661344,11.361685384317244,11.665257585973144,11.968829787629044,12.272401989284944,12.575974190940844,null,0.14153984038939996,0.36740844683800766,0.52792714700820842,0.60411745110609072,0.67648036482422835,0.74519463991112622,0.80364646167211518,0.85052147901525077,0.88968914155521917,null,0.52792714700820842,0.52792714700820842,0.52792714700820842]
["2013-02-11T01:00:00.310","2013-02-11T01:00:00",null,10.043308711745954,10.346880913401854,10.650453115057754,10.954025316713654,11.257597518369554,11.561169720025454,11.864741921681354,12.168314123337254,12.471886324993154,null,0.13215011618854308,0.36039506941138783,0.52315342384226327,0.60145720449599349,0.67581793187388794,0.74642487253318701,0.80667472658795703,0.85525314294625365,0.89605060084023413,null,0.52315342384226327,0.52315342384226327,0.52315342384226327]
["2013-02-11T02:00:00.315","2013-02-11T02:00:00",null,10.07249942835757,10.37607163001347,10.67964383166937,10.98321603332527,11.28678823498117,11.59036043663707,11.89393263829297,12.19750483994887,12.50107704160477,null,0.12327561761572875,0.35382331395166156,0.51875823379079833,0.59911240214796313,0.67541836914193654,0.74786540132995905,0.80985019882609677,0.86008995496461216,0.90246463416892697,null,0.51875823379079833,0.51875823379079833,0.51875823379079833]
["2013-02-11T03:00:00.320","2013-02-11T03:00:00",null,9.9704296970361668,10.274001898692067,10.577574100347967,10.881146302003867,11.184718503659766,11.488290705315666,11.791862906971566,12.095435108627466,12.399007310283366,null,0.11390692303234301,0.34672581805515723,0.51380575887634861,0.5961892853194769,0.67440894750332259,0.74866452679386175,0.8123632381138961,0.86424330441515917,0.90816366050360153,null,0.51380575887634861,0.51380575887634861,0.51380575887634861]
["2013-02-11T04:00:00.325","2013-02-11T04:00:00",null,9.9703647639427544,10.273936965598654,10.577509167254554,10.881081368910454,11.184653570566354,11.488225772222254,11.791797973878154,12.095370175534054,12.398942377189954,null,9.8050591459115516E-2,0.33314068516881112,0.5023656469720571,0.58676801669241341,0.66690137406613137,0.74296550045918719,0.80838864041185365,0.86189850206712881,0.90737504984843442,null,0.5023656469720571,0.5023656469720571,0.5023656469720571]
["2013-02-11T05:00:00.330","2013-02-11T05:00:00",null,9.9857210849915532,10.289293286647453,10.592865488303353,10.896437689959253,11.200009891615153,11.503582093271053,11.807154294926953,12.110726496582853,12.414298698238753,null,7.7452081146149571E-2,0.31495006605628889,0.48643571173768069,0.57298310244009165,0.65514581789977311,0.73312363948270121,0.80036584134661981,0.85561064644326279,0.90272750438731597,null,0.48643571173768069,0.48643571173768069,0.48643571173768069]
["2013-02-11T06:00:00.335","2013-02-11T06:00:00",null,10.053002271738684,10.356574473394584,10.660146675050484,10.963718876706384,11.267291078362284,11.570863280018184,11.874435481674084,12.178007683329984,12.481579884985884,null,5.3278535863092537E-2,0.29327904525229559,0.46710949328171775,0.55588602343606786,0.64015170064286175,0.72011682107681096,0.78925168851313077,0.84629452590355481,0.89511478286276913,null,0.46710949328171775,0.46710949328171775,0.46710949328171775]
["2013-02-11T07:00:00.340","2013-02-11T07:00:00",null,10.003495539108222,10.307067740764122,10.610639942420022,10.914212144075922,11.217784345731822,11.521356547387722,11.824928749043622,12.128500950699522,12.432073152355422,null,3.177575199886825E-2,0.27420518220598611,0.45032785853976082,0.54125992448490112,0.6275759893951296,0.70947583463642228,0.78045079360146541,0.83923908924199275,0.88972068598142584,null,0.45032785853976082,0.45032785853976082,0.45032785853976082]
["2013-02-11T08:00:00.345","2013-02-11T08:00:00",null,10.129405574923078,10.432977776578978,10.736549978234876,11.040122179890776,11.343694381546676,11.647266583202576,11.950838784858476,12.254410986514376,12.557983188170276,null,5.0050489581275004E-2,0.29507707754607665,0.47363918950650175,0.56688451337346568,0.65538765850069103,0.73936943587162507,0.81231066407021824,0.8729705956656757,0.92522919508141865,null,0.47363918950650175,0.47363918950650175,0.47363918950650175]
["2013-02-11T09:00:00.350","2013-02-11T09:00:00",null,10.367404289385124,10.670976491041024,10.974548692696924,11.278120894352824,11.581693096008724,11.885265297664624,12.188837499320524,12.492409700976424,12.795981902632324,null,8.4549577042653923E-2,0.33245722260099952,0.51374267002393526,0.60955360722237628,0.70049618797625202,0.78680173807774523,0.86194056130207086,0.92469293983590517,0.97893883810266935,null,0.51374267002393526,0.51374267002393526,0.51374267002393526]
["2013-02-11T10:00:00.355","2013-02-11T10:00:00",null,9.9706771291576093,10.274249330813509,10.577821532469409,10.881393734125309,11.184965935781209,11.488538137437109,11.792110339093009,12.095682540748909,12.399254742404809,null,0.13952099711217203,0.38981550425349021,0.57335112074583616,0.67128604930886082,0.76422644372249326,0.85243517420512327,0.92938254453196556,0.99384883688969639,1,null,0.57335112074583616,0.57335112074583616,0.57335112074583616]
["2013-02-11T11:00:00.360","2013-02-11T11:00:00",null,9.9698941294294023,10.273466331085302,10.577038532741202,10.880610734397102,11.184182936053002,11.487755137708902,11.791327339364802,12.094899541020702,12.398471742676602,null,0.19447138756421903,0.44714224147977422,0.63292802704153039,0.73298694696913858,0.82793566985126343,0.91803706590629452,0.99679298333565347,1,1,null,0.63292802704153039,0.63292802704153039,0.63292802704153039]
["2013-02-11T12:00:00.365","2013-02-11T12:00:00",null,10.11791390763357,10.42148610928947,10.725058310945368,11.028630512601268,11.332202714257168,11.635774915913068,11.939347117568968,12.242919319224868,12.546491520880767,null,0.24164081955195016,0.496887801607718,0.68510250798738903,0.7874641710280853,0.88458945931847144,0.9767517578856727,1,1,1,null,0.68510250798738903,0.68510250798738903,0.68510250798738903]
["2013-02-11T13:00:00.370","2013-02-11T13:00:00",null,10.207927145026297,10.511499346682196,10.815071548338096,11.118643749993996,11.422215951649896,11.725788153305796,12.029360354961696,12.332932556617596,12.636504758273496,null,0.28777980028359618,0.54561342528831225,0.73626756729463372,0.84094248825715368,0.94024434195580109,1,1,1,1,null,0.73626756729463372,0.73626756729463372,0.73626756729463372]
["2013-02-11T14:00:00.375","2013-02-11T14:00:00",null,10.303131987155453,10.606704188811353,10.910276390467253,11.213848592123153,11.517420793779053,11.820992995434953,12.124565197090853,12.428137398746752,12.731709600402652,null,0.33324583325616625,0.59367661601856614,0.78678070846027359,0.89377940215335272,0.9952788508777326,1,1,1,1,null,0.78678070846027359,0.78678070846027359,0.78678070846027359]
["2013-02-11T15:00:00.380","2013-02-11T15:00:00",null,10.35897529699659,10.66254749865249,10.96611970030839,11.26969190196429,11.57326410362019,11.87683630527609,12.18040850693199,12.48398070858789,12.787552910243789,null,0.38110924262044443,0.64409512390558588,0.83961762235647264,0.94890854435390426,1,1,1,1,1,null,0.83961762235647264,0.83961762235647264,0.83961762235647264]
["2013-02-11T16:00:00.385","2013-02-11T16:00:00",null,10.377905106188134,10.681477307844034,10.985049509499934,11.288621711155834,11.592193912811734,11.895766114467634,12.199338316123534,12.502910517779434,12.806482719435333,null,0.4279947747723154,0.69355678419766953,0.89151871827520668,1,1,1,1,1,1,null,0.89151871827520668,0.89151871827520668,0.89151871827520668]
["2013-02-11T17:00:00.390","2013-02-11T17:00:00",null,10.427428382453195,10.731000584109095,11.034572785764995,11.338144987420895,11.641717189076795,11.945289390732695,12.248861592388595,12.552433794044495,12.856005995700395,null,0.47256704900236268,0.74067364214172282,0.94103295261096809,1,1,1,1,1,1,null,0.94103295261096809,0.94103295261096809,0.94103295261096809]
["2013-02-11T18:00:00.395","2013-02-11T18:00:00",null,10.373211839833376,10.676784041489276,10.980356243145176,11.283928444801075,11.587500646456975,11.891072848112875,12.194645049768775,12.498217251424675,12.801789453080575,null,0.45447106316846048,0.72505915116941322,0.92775274917795325,0.98892790640145323,0.99103086814856567,0.99301816699958678,0.99491083257198798,0.99670886486576904,0.99842277868966567,null,0.92775274917795325,0.92775274917795325,0.92775274917795325]
["2013-02-11T19:00:00.400","2013-02-11T19:00:00",null,10.364128498328794,10.667700699984694,10.971272901640594,11.274845103296494,11.578417304952394,11.881989506608294,12.185561708264194,12.489133909920094,12.792706111575994,null,0.43629095886467378,0.70935002691848359,0.91436739765758279,0.97775066471555083,0.98193555859230452,0.98589964148561127,0.98967445782167807,0.9932600076005047,0.99668783524829796,null,0.91436739765758279,0.91436739765758279,0.91436739765758279]
["2013-02-11T20:00:00.405","2013-02-11T20:00:00",null,10.263669835392232,10.567242037048132,10.870814238704032,11.174386440359932,11.477958642015832,11.781530843671732,12.085103045327632,12.388675246983532,12.692247448639431,null,0.4186365949976652,0.69414561348686099,0.90146572733904817,0.9670255598052776,0.97328187100293695,0.97920170832105824,0.98483764580331956,0.99020019825845618,0.99531039530393939,null,0.90146572733904817,0.90146572733904817,0.90146572733904817]
["2013-02-11T21:00:00.410","2013-02-11T21:00:00",null,10.241122831046026,10.544695032701926,10.848267234357827,11.151839436013727,11.455411637669627,11.758983839325527,12.062556040981427,12.366128242637327,12.669700444293227,null,0.40204422681294838,0.67996113650258783,0.88956296385039202,0.95727833210741164,0.96557451619976997,0.97342907832523473,0.98090510733621938,0.98802363285019479,0.99479516967589687,null,0.88956296385039202,0.88956296385039202,0.88956296385039202]
["2013-02-11T22:00:00.415","2013-02-11T22:00:00",null,10.150388973693742,10.453961175349642,10.757533377005544,11.061105578661444,11.364677780317344,11.668249981973243,11.971822183629143,12.275394385285043,12.578966586940943,null,0.39025712622038339,0.67047677902311087,0.88224465697044085,0.95201041293089506,0.96224132183059685,0.97193597548478494,0.9811574627458729,0.98993732804006707,0.99828608617610348,null,0.88224465697044085,0.88224465697044085,0.88224465697044085]
["2013-02-11T23:00:00.420","2013-02-11T23:00:00",null,10.026818591874235,10.330390793530135,10.633962995186035,10.937535196841935,11.241107398497835,11.544679600153735,11.848251801809635,12.151824003465535,12.455396205121435,null,0.36509518891618353,0.6475544959795857,0.86143585048276361,0.93319942010297463,0.94531247976634203,0.95679465090557569,0.96771953718182468,0.97810816821255986,0.98799208842398833,null,0.86143585048276361,0.86143585048276361,0.86143585048276361]
["2013-02-12T00:00:00.425","2013-02-12",null,9.9825756045905951,10.286147806246495,10.589720007902397,10.893292209558297,11.196864411214197,11.500436612870097,11.804008814525996,12.107581016181896,12.411153217837796,null,0.35899659984955756,0.64373762040857674,0.85978502551128033,0.93358846802619044,0.94762573768816571,0.96093748554738712,0.97358680045626833,0.98562625645848667,0.99707688317151388,null,0.85978502551128033,0.85978502551128033,0.85978502551128033]
["2013-02-12T01:00:00.430","2013-02-12T01:00:00",null,9.8617435991277631,10.165315800783663,10.468888002439563,10.772460204095463,11.076032405751363,11.379604607407263,11.683176809063163,11.986749010719063,12.290321212374963,null,0.35229866668500459,0.63915316379987175,0.85719838256233205,0.93289449064964336,0.94870876298792861,0.96370288024483997,0.97795044608152659,0.9915145493504014,1,null,0.85719838256233205,0.85719838256233205,0.85719838256233205]
["2013-02-12T02:00:00.435","2013-02-12T02:00:00",null,10.004682195028568,10.308254396684468,10.611826598340368,10.915398799996268,11.218971001652168,11.522543203308068,11.826115404963968,12.129687606619868,12.433259808275768,null,0.34877620575859131,0.63783881270792653,0.85796596360002808,0.93562834092088953,0.9533037344053692,0.97006433952985494,0.98598375995549592,1,1,null,0.85796596360002808,0.85796596360002808,0.85796596360002808]
["2013-02-12T03:00:00.440","2013-02-12T03:00:00",null,10.110782586162832,10.414354787818732,10.717926989474632,11.021499191130532,11.325071392786432,11.628643594442332,11.932215796098232,12.235787997754132,12.539360199410032,null,0.34693611422986798,0.63813322735252231,0.86027922152185177,0.9398447792238499,0.95932871981084622,0.97779272395049299,0.99533142492141058,1,1,null,0.86027922152185177,0.86027922152185177,0.86027922152185177]
["2013-02-12T04:00:00.445","2013-02-12T04:00:00",null,10.092344603013554,10.395916804669454,10.699489006325354,11.003061207981254,11.306633409637154,11.610205611293054,11.913777812948954,12.217350014604854,12.520922216260754,null,0.34615801838343641,0.63946860806193873,0.8636019010822894,0.94504960954795314,0.96632106761999492,0.98646744115733165,1,1,1,null,0.8636019010822894,0.8636019010822894,0.8636019010822894]
["2013-02-12T05:00:00.450","2013-02-12T05:00:00",null,10.134943063710912,10.438515265366812,10.742087467022712,11.045659668678612,11.349231870334512,11.652804071990412,11.956376273646312,12.259948475302211,12.563520676958111,null,0.3430666646151812,0.63854330489320932,0.86472698561699457,0.94810941889000167,0.97121045368203129,0.99309177066073573,1,1,1,null,0.86472698561699457,0.86472698561699457,0.86472698561699457]
["2013-02-12T06:00:00.455","2013-02-12T06:00:00",null,10.14582829293415,10.44940049459005,10.75297269624595,11.056544897901849,11.360117099557749,11.663689301213649,11.967261502869549,12.270833704525449,12.574405906181349,null,0.33814573412693821,0.63579893981322766,0.86404352304918308,0.94938171074700461,0.97432283706775769,0.99794961229656542,1,1,1,null,0.86404352304918308,0.86404352304918308,0.86404352304918308]
["2013-02-12T07:00:00.460","2013-02-12T07:00:00",null,10.167230097894102,10.470802299550002,10.774374501205902,11.077946702861801,11.381518904517701,11.685091106173601,11.988663307829501,12.292235509485401,12.595807711141301,null,0.33035426085388675,0.6302260911833798,0.86055260654897647,0.94786757828908363,0.97468034056476682,1,1,1,1,null,0.86055260654897647,0.86055260654897647,0.86055260654897647]
["2013-02-12T08:00:00.465","2013-02-12T08:00:00",null,10.143095522369265,10.446667724025165,10.750239925681067,11.053812127336966,11.357384328992866,11.660956530648766,11.964528732304666,12.268100933960566,12.571673135616466,null,0.31834634927787497,0.6203947450156293,0.85278216289339615,0.94204237424958226,0.97069522805398878,0.99774983093058978,0.99941117071080854,1,1,null,0.85278216289339615,0.85278216289339615,0.85278216289339615]
["2013-02-12T09:00:00.470","2013-02-12T09:00:00",null,10.333543183905954,10.637115385561854,10.940687587217754,11.244259788873654,11.547831990529554,11.851404192185454,12.154976393841354,12.458548595497254,12.762120797153154,null,0.30997656152436764,0.6143487299926812,0.8489337428961804,0.94026537157327228,0.97088449461122894,0.99980021863402435,1,1,1,null,0.8489337428961804,0.8489337428961804,0.8489337428961804]
["2013-02-12T10:00:00.475","2013-02-12T10:00:00",null,10.331790732040398,10.635362933696298,10.938935135352198,11.242507337008098,11.546079538663998,11.849651740319898,12.153223941975797,12.456796143631697,12.760368345287597,null,0.30173295147568702,0.6084288926745598,0.84520098579505587,0.93860403179305352,0.97118942406456021,1,1,1,1,null,0.84520098579505587,0.84520098579505587,0.84520098579505587]
["2013-02-12T11:00:00.480","2013-02-12T11:00:00",null,10.311719508690393,10.615291710346293,10.918863912002193,11.222436113658093,11.526008315313993,11.829580516969893,12.133152718625793,12.436724920281693,12.740297121937592,null,0.29445670383067812,0.6034448733339034,0.84238301705392526,0.93783645075535749,0.97236708264294314,1,1,1,1,null,0.84238301705392526,0.84238301705392526,0.84238301705392526]
["2013-02-12T12:00:00.485","2013-02-12T12:00:00",null,10.357304079911572,10.660876281567472,10.964448483223372,11.268020684879271,11.571592886535171,11.875165088191071,12.178737289846971,12.482309491502871,12.785881693158771,null,0.28848429246887891,0.59972263104151446,0.84078476612611985,0.93825704310477998,0.97469085537350231,1,1,1,1,null,0.84078476612611985,0.84078476612611985,0.84078476612611985]
["2013-02-12T13:00:00.490","2013-02-12T13:00:00",null,10.332371125795483,10.635943327451383,10.939515529107283,11.243087730763182,11.546659932419082,11.850232134074982,12.153804335730882,12.457376537386782,12.760948739042682,null,0.27901044979813755,0.59257256110133227,0.83582177640293454,0.93537598551123602,0.97377606701350838,1,1,1,1,null,0.83582177640293454,0.83582177640293454,0.83582177640293454]
["2013-02-12T14:00:00.495","2013-02-12T14:00:00",null,10.333768964275668,10.637341165931568,10.94091336758747,11.24448556924337,11.54805777089927,11.85162997255517,12.15520217421107,12.45877437586697,12.762346577522869,null,0.26848512625383997,0.58436049547885838,0.82980730580619311,0.93144344704413584,0.97180979777995824,0.99989485191264438,1,1,1,null,0.82980730580619311,0.82980730580619311,0.82980730580619311]
["2013-02-12T15:00:00.500","2013-02-12T15:00:00",null,10.313586828399243,10.617159030055143,10.920731231711043,11.224303433366943,11.527875635022843,11.831447836678743,12.135020038334643,12.438592239990543,12.742164441646443,null,0.2585486319987339,0.57671622952810475,0.82433960526370087,0.92802613420507818,0.97033772455697953,1,1,1,1,null,0.82433960526370087,0.82433960526370087,0.82433960526370087]
["2013-02-12T16:00:00.505","2013-02-12T16:00:00",null,10.296840928637097,10.600413130292997,10.903985331948899,11.207557533604799,11.511129735260699,11.814701936916599,12.118274138572499,12.421846340228399,12.725418541884299,null,0.24953744091235727,0.56997623712860956,0.81975514865499588,0.92547103568233657,0.9697068360328458,1,1,1,1,null,0.81975514865499588,0.81975514865499588,0.81975514865499588]
["2013-02-12T17:00:00.510","2013-02-12T17:00:00",null,10.311510657073224,10.615082858729124,10.918655060385024,11.222227262040924,11.525799463696824,11.829371665352724,12.132943867008624,12.436516068664524,12.740088270320424,null,0.23974815397954904,0.56248969330888943,0.81443465543480154,0.9222009301655768,0.96837145532342939,1,1,1,1,null,0.81443465543480154,0.81443465543480154,0.81443465543480154]
["2013-02-12T18:00:00.515","2013-02-12T18:00:00",null,10.292370984729054,10.595943186384954,10.899515388040854,11.203087589696754,11.506659791352654,11.810231993008554,12.113804194664453,12.417376396320353,12.720948597976253,null,0.23093674425914809,0.55594948227536989,0.8100394653833366,0.91982458339133977,0.96791931854780022,1,1,1,1,null,0.8100394653833366,0.8100394653833366,0.8100394653833366]
["2013-02-12T19:00:00.520","2013-02-12T19:00:00",null,10.209416562414299,10.512988764070199,10.816560965726099,11.120133167381999,11.423705369037899,11.727277570693799,12.030849772349699,12.334421974005599,12.637994175661499,null,0.22290343038517874,0.55017685227954638,0.80641185636956769,0.91821581765479876,0.96823476280986709,1,1,1,1,null,0.80641185636956769,0.80641185636956769,0.80641185636956769]
["2013-02-12T20:00:00.525","2013-02-12T20:00:00",null,10.194399679520652,10.497971881176552,10.801544082832452,11.105116284488352,11.408688486144252,11.712260687800152,12.015832889456052,12.319405091111951,12.622977292767851,null,0.21558512350522757,0.54510871446900555,0.80345719511487479,0.91726948486859816,0.96919161040480328,1,1,1,1,null,0.80345719511487479,0.80345719511487479,0.80345719511487479]
["2013-02-12T21:00:00.530","2013-02-12T21:00:00",null,10.168640609159958,10.472212810815858,10.775785012471758,11.079357214127658,11.382929415783558,11.686501617439458,11.990073819095358,12.293646020751257,12.597218222407157,null,0.20961271214342836,0.54135492775040994,0.80179585533465603,0.91757441432192943,0.97136817581306467,1,1,1,1,null,0.80179585533465603,0.80179585533465603,0.80179585533465603]
["2013-02-12T22:00:00.535","2013-02-12T22:00:00",null,9.9612762697872093,10.264848471443109,10.568420673099009,10.871992874754909,11.175565076410809,11.479137278066709,11.782709479722609,12.086281681378509,12.389853883034409,null,0.20741511711769589,0.54130235370673219,0.80377263937694166,0.92146489355408734,0.97706720214773923,1,1,1,1,null,0.80377263937694166,0.80377263937694166,0.80377263937694166]
["2013-02-12T23:00:00.540","2013-02-12T23:00:00",null,9.6793784830435907,9.9829506846994907,10.286522886355391,10.590095088011289,10.893667289667189,11.197239491323089,11.500811692978989,11.804383894634888,12.107956096290788,null,0.20512288881334337,0.54097639463592972,0.80529728664359812,0.92472448426211151,0.98197761782724668,1,1,1,1,null,0.80529728664359812,0.80529728664359812,0.80529728664359812]
["2013-02-13T00:00:00.545","2013-02-13",null,9.6142469476771382,9.9178191493330381,10.221391350988938,10.524963552644838,10.828535754300738,11.132107955956638,11.435680157612538,11.739252359268438,12.042824560924338,null,0.20688937668091778,0.54484584425061655,0.81114352030057058,0.93243183906527849,0.99144094568925245,1,1,1,1,null,0.81114352030057058,0.81114352030057058,0.81114352030057058]
["2013-02-13T01:00:00.550","2013-02-13T01:00:00",null,9.3442572266893862,9.6478294283452861,9.951401630001186,10.254973831657086,10.558546033312986,10.862118234968886,11.165690436624786,11.469262638280686,11.772834839936586,null,0.20651084356643754,0.5461286509163551,0.81399303346790786,0.93674291064685888,0.99713997202392701,1,1,1,1,null,0.81399303346790786,0.81399303346790786,0.81399303346790786]
["2013-02-13T02:00:00.555","2013-02-13T02:00:00",null,9.5499869689367163,9.8535591705926162,10.157131372248516,10.460703573904416,10.764275775560316,11.067847977216216,11.371420178872116,11.674992380528016,11.978564582183916,null,0.20881358667952563,0.55042920768920001,0.82017574100441826,0.94470262085967927,1,1,1,1,1,null,0.82017574100441826,0.82017574100441826,0.82017574100441826]
["2013-02-13T03:00:00.560","2013-02-13T03:00:00",null,9.455774083288544,9.7593462849444439,10.062918486600344,10.366490688256244,10.670062889912144,10.973635091568044,11.277207293223944,11.580779494879843,11.884351696535743,null,0.21264097705927018,0.55623338211123019,0.82783052176390737,0.95410285986927168,1,1,1,1,1,null,0.82783052176390737,0.82783052176390737,0.82783052176390737]
["2013-02-13T04:00:00.565","2013-02-13T04:00:00",null,9.4510613913688459,9.7546335930247459,10.058205794680646,10.361777996336546,10.665350197992446,10.968922399648346,11.272494601304246,11.576066802960145,11.879639004616045,null,0.21682587093602385,0.56238454522153392,0.83582177640293454,0.96383957275840204,1,1,1,1,1,null,0.83582177640293454,0.83582177640293454,0.83582177640293454]
["2013-02-13T05:00:00.570","2013-02-13T05:00:00",null,9.4289250557702164,9.7324972574261164,10.036069459082016,10.339641660737916,10.643213862393816,10.946786064049716,11.250358265705616,11.553930467361516,11.857502669017416,null,0.21826639973279585,0.56587546172174052,0.8412474177104845,0.97108427597720426,1,1,1,1,1,null,0.8412474177104845,0.8412474177104845,0.8412474177104845]
["2013-02-13T06:00:00.575","2013-02-13T06:00:00",null,9.4341587467847177,9.7377309484406176,10.041303150096518,10.344875351752417,10.648447553408317,10.952019755064217,11.255591956720117,11.559164158376017,11.862736360031917,null,0.21945457311991437,0.56912453762102921,0.84644173322585214,0.97809765340382415,1,1,1,1,1,null,0.84644173322585214,0.84644173322585214,0.84644173322585214]
["2013-02-13T07:00:00.580","2013-02-13T07:00:00",null,9.4536045742808259,9.7571767759367258,10.060748977592626,10.364321179248526,10.667893380904426,10.971465582560326,11.275037784216225,11.578609985872125,11.882182187528025,null,0.21948611754612105,0.57124852898561274,0.85053199382398581,0.98403852033941663,1,1,1,1,1,null,0.85053199382398581,0.85053199382398581,0.85053199382398581]
["2013-02-13T08:00:00.585","2013-02-13T08:00:00",null,9.477199900095453,9.7807721017513529,10.084344303407253,10.387916505063153,10.691488706719053,10.995060908374953,11.298633110030853,11.602205311686753,11.905777513342652,null,0.21819279607164693,0.57208971368445771,0.8533709921825875,0.98877018427041952,1,1,1,1,1,null,0.8533709921825875,0.8533709921825875,0.8533709921825875]
["2013-02-13T09:00:00.590","2013-02-13T09:00:00",null,9.5075225412437483,9.8110947428996482,10.114666944555548,10.418239146211448,10.721811347867348,11.025383549523248,11.328955751179148,11.632527952835048,11.936100154490948,null,0.21505938306844946,0.57113286608952152,0.85446453229108599,0.99178793437752577,1,1,1,1,1,null,0.85446453229108599,0.85446453229108599,0.85446453229108599]
["2013-02-13T10:00:00.595","2013-02-13T10:00:00",null,9.509814072375093,9.813386274030993,10.116958475686893,10.420530677342793,10.724102878998693,11.027675080654593,11.331247282310493,11.634819483966393,11.938391685622292,null,0.20117983553750762,0.5593142210707498,0.84458061207965773,0.98373359088608525,0.99365957033245611,0.9952893656864682,0.99682452776186026,0.99828608617610337,0.99966352612046205,null,0.84458061207965773,0.84458061207965773,0.84458061207965773]
["2013-02-13T11:00:00.600","2013-02-13T11:00:00",null,9.9323112523066772,10.235883453962577,10.539455655618477,10.843027857274377,11.146600058930277,11.450172260586177,11.753744462242077,12.057316663897977,12.360888865553877,null,0.1892350128139092,0.54981934878253735,0.83738848290453327,0.97871802711922218,0.99069439426902761,0.99427994404785425,0.99765519765196964,1,1,null,0.83738848290453327,0.83738848290453327,0.83738848290453327]
["2013-02-13T12:00:00.605","2013-02-13T12:00:00",null,10.135555910625245,10.439128112281145,10.742700313937043,11.046272515592943,11.349844717248843,11.653416918904743,11.956989120560642,12.260561322216542,12.564133523872442,null,0.17403059938228654,0.5371069450212429,0.82703139630000466,0.97057956515789723,0.98465889405481499,0.99024225749339845,0.99551017666991504,0.99965301131172646,1,null,0.82703139630000466,0.82703139630000466,0.82703139630000466]
["2013-02-13T13:00:00.610","2013-02-13T13:00:00",null,10.279817039663982,10.583389241319882,10.886961442975782,11.190533644631682,11.494105846287582,11.797678047943482,12.101250249599381,12.404822451255281,12.708394652911181,null,0.15493570671850596,0.52057766568893948,0.81293103778561604,0.9587714349478611,0.97501681444430466,0.98266108039505828,0.98989526880512491,0.99589922459313085,0.99801270114897878,null,0.81293103778561604,0.81293103778561604,0.81293103778561604]
["2013-02-13T14:00:00.615","2013-02-13T14:00:00",null,10.659900889138735,10.963473090794635,11.267045292450534,11.570617494106434,11.874189695762334,12.177761897418234,12.481334099074134,12.784906300730034,13.088478502385934,null,0.1240747430796315,0.49252415598246008,0.7875377746892338,0.9358912111392782,0.95452345221869428,0.96442840204759372,0.97381812624845066,0.98188298454862666,0.98595221552928913,null,0.7875377746892338,0.7875377746892338,0.7875377746892338]
["2013-02-13T15:00:00.620","2013-02-13T15:00:00",null,10.662827904017284,10.966400105673184,11.269972307329084,11.573544508984984,11.877116710640884,12.180688912296784,12.484261113952684,12.787833315608584,13.091405517264484,null,9.3066572118459173E-2,0.46432343895368278,0.76199730427055368,0.91286378000839741,0.93388288267078612,0.94605903118656687,0.95761480598694959,0.96773005199056017,0.97376555220477279,null,0.76199730427055368,0.76199730427055368,0.76199730427055368]
["2013-02-13T16:00:00.625","2013-02-13T16:00:00",null,10.694108273364989,10.997680475020889,11.301252676676789,11.604824878332689,11.908397079988589,12.211969281644489,12.515541483300389,12.819113684956289,13.122685886612189,null,6.0565298316837039E-2,0.43467167831939796,0.73502681986383711,0.88844839412442245,0.91188590279599047,0.92635427961612371,0.94009713463350331,0.95229431276675514,0.96031711183198898,null,0.73502681986383711,0.73502681986383711,0.73502681986383711]
["2013-02-13T17:00:00.630","2013-02-13T17:00:00",null,10.616001055602446,10.919573257258346,11.223145458914246,11.526717660570146,11.830289862226046,12.133862063881946,12.437434265537846,12.741006467193746,13.044578668849645,null,3.1817811233810542E-2,0.40867907112508872,0.71164188523594718,0.86753443954938958,0.89331675056898796,0.91000375203232475,0.92587059841428787,0.94008661982476771,0.95002311407987383,null,0.71164188523594718,0.71164188523594718,0.71164188523594718]
["2013-02-13T18:00:00.635","2013-02-13T18:00:00",null,10.44082213170617,10.74439433336207,11.04796653501797,11.35153873667387,11.65511093832977,11.95868313998567,12.26225534164157,12.56582754329747,12.86939974495337,null,7.7073548031668798E-3,0.38722886130454226,0.69270471470320005,0.85097361579087938,0.87900609587988809,0.89783811832527949,0.9157343227932061,0.9318850690110293,0.94367216960359435,null,0.69270471470320005,0.69270471470320005,0.69270471470320005]
["2013-02-13T19:00:00.640","2013-02-13T19:00:00",null,10.181146596069869,10.484718797725769,10.788290999381669,11.091863201037569,11.395435402693469,11.699007604349369,12.002579806005269,12.306152007661169,12.609724209317068,null,0,0.37112017432166128,0.67900391892076273,0.83954401869532347,0.86973203457512238,0.89061444472394835,0.91044537399921843,0.92843621174576496,0.94197928539716891,null,0.67900391892076273,0.67900391892076273,0.67900391892076273]
["2013-02-13T20:00:00.645","2013-02-13T20:00:00",null,10.116191514982617,10.419763716638517,10.723335918294417,11.026908119950317,11.330480321606217,11.634052523262117,11.937624724918017,12.241196926573917,12.544769128229817,null,0,0.35820798919439112,0.66841550652405179,0.8311637161330806,0.86343366414252076,0.88628234352489677,0.90798490875509696,0.92776326398668896,0.94299922184451845,null,0.66841550652405179,0.66841550652405179,0.66841550652405179]
["2013-02-13T21:00:00.650","2013-02-13T21:00:00",null,10.001379608148333,10.304951809804233,10.608524011460133,10.912096213116033,11.215668414771933,11.519240616427833,11.822812818083733,12.126385019739633,12.429957221395533,null,0,0.34759854718020905,0.66009829281422228,0.82500203821404128,0.85932237392691602,0.88410577811663538,0.90763792006682342,0.92916173354851872,0.94605903118656698,null,0.66009829281422228,0.66009829281422228,0.66009829281422228]
["2013-02-13T22:00:00.655","2013-02-13T22:00:00",null,9.914835206029375,10.218407407685275,10.521979609341175,10.825551810997075,11.129124012652975,11.432696214308875,11.736268415964775,12.039840617620674,12.343412819276574,null,0,0.34158407658346757,0.65626038762574213,0.8232145207289957,0.85946958124921391,0.8860930769676566,0.91137067716794795,0.93454531562112642,0.95301983456950901,null,0.65626038762574213,0.65626038762574213,0.65626038762574213]
["2013-02-13T23:00:00.660","2013-02-13T23:00:00",null,9.8188167651461598,10.12238896680206,10.42596116845796,10.72953337011386,11.033105571769759,11.336677773425659,11.640249975081559,11.943822176737459,12.247394378393359,null,0,0.33699961997476252,0.65383146680782733,0.82281495799704429,0.86099422851587037,0.88942627133682972,0.9164283001697533,0.94124324878567944,0.96126344461818958,null,0.65383146680782733,0.65383146680782733,0.65383146680782733]
["2013-02-14T00:00:00.665","2013-02-14",null,9.7234681159473482,10.027040317603248,10.330612519259148,10.634184720915048,10.937756922570948,11.241329124226848,11.544901325882748,11.848473527538648,12.152045729194548,null,0,0.33382414773662278,0.65279050074300671,0.82378232040071597,0.86386477130067885,0.89408433160668366,0.92278975945476827,0.94922398861597101,0.97077934652387321,null,0.65279050074300671,0.65279050074300671,0.65279050074300671]
["2013-02-14T01:00:00.670","2013-02-14T01:00:00",null,9.6077666712239065,9.9113388728798064,10.214911074535706,10.518483276191606,10.822055477847506,11.125627679503406,11.429199881159306,11.732772082815206,12.036344284471106,null,0,0.33325634806490245,0.65430463320092769,0.82726272209218699,0.86919577932960879,0.9011607978857169,0.93151705070528468,0.95952850117682176,0.98256644711643826,null,0.65430463320092769,0.65430463320092769,0.65430463320092769]
["2013-02-14T02:00:00.675","2013-02-14T02:00:00",null,9.6508971445191918,9.9544693461750917,10.258041547830992,10.561613749486892,10.865185951142792,11.168758152798691,11.472330354454591,11.775902556110491,12.079474757766391,null,0,0.33415010680742524,0.65722775002941392,0.83209953411054549,0.87584113845048395,0.9095095560217531,0.94148508938659747,0.97103170193352661,0.99552069147865063,null,0.65722775002941392,0.65722775002941392,0.65722775002941392]
["2013-02-14T03:00:00.680","2013-02-14T03:00:00",null,9.5064440319988499,9.8100162336547498,10.11358843531065,10.41716063696655,10.72073283862245,11.02430504027835,11.327877241934249,11.631449443590149,11.935021645246049,null,0,0.33536982462075043,0.66048734073743809,0.83729384962591313,0.88285451587710384,0.91823684727226951,0.95183166118239049,0.98292395061344728,1,null,0.66048734073743809,0.66048734073743809,0.66048734073743809]
["2013-02-14T04:00:00.685","2013-02-14T04:00:00",null,9.5304868309031185,9.8340590325590185,10.137631234214918,10.441203435870818,10.744775637526718,11.048347839182618,11.351920040838518,11.655492242494418,11.959064444150318,null,0,0.33523313210718814,0.66243258035351704,0.84120535847554223,0.88861663106419186,0.92574442070946072,0.96099005959106498,0.99364905552372051,1,null,0.66243258035351704,0.66243258035351704,0.66243258035351704]
["2013-02-14T05:00:00.690","2013-02-14T05:00:00",null,9.4728349515357344,9.7764071531916343,10.079979354847534,10.383551556503434,10.687123758159334,10.990695959815234,11.294268161471134,11.597840363127034,11.901412564782934,null,0,0.33448658068696324,0.66378899068040453,0.84454906765345095,0.89384249100576618,0.93273676851860943,0.96966477679790364,1,1,null,0.66378899068040453,0.66378899068040453,0.66378899068040453]
["2013-02-14T06:00:00.695","2013-02-14T06:00:00",null,9.4405911575610357,9.7441633592169357,10.047735560872836,10.351307762528736,10.654879964184635,10.958452165840535,11.262024367496435,11.565596569152335,11.869168770808235,null,0,0.33255185587961983,0.66404134609005805,0.84685181076653904,0.89807995892619763,0.93880381315902872,0.97745625007095505,1,1,null,0.66404134609005805,0.66404134609005805,0.66404134609005805]
["2013-02-14T07:00:00.700","2013-02-14T07:00:00",null,9.4738108284995182,9.7773830301554181,10.080955231811318,10.384527433467218,10.688099635123118,10.991671836779018,11.295244038434918,11.598816240090818,11.902388441746718,null,0,0.33012293506170498,0.6638415647240824,0.84874447633894023,0.90195992334962005,0.94454489872864555,0.98497433831688186,1,1,null,0.6638415647240824,0.6638415647240824,0.6638415647240824]
["2013-02-14T08:00:00.705","2013-02-14T08:00:00",null,9.621178451487264,9.924750653143164,10.228322854799064,10.531895056454964,10.835467258110864,11.139039459766764,11.442611661422664,11.746183863078564,12.049756064734463,null,0,0.32719981823321875,0.66313707253879972,0.85012191628329881,0.90530363252752877,0.94974972905274879,0.99193514169982389,1,1,null,0.66313707253879972,0.66313707253879972,0.66313707253879972]
["2013-02-14T09:00:00.710","2013-02-14T09:00:00",null,10.058830724706961,10.362402926362861,10.665975128018761,10.969547329674661,11.273119531330561,11.576691732986461,11.880263934642361,12.183836136298261,12.487408337954161,null,0,0.32314110206129182,0.66123389215766304,0.85024809398812551,0.90735402023096334,0.95362969347617121,0.99753953475587842,1,1,null,0.66123389215766304,0.66123389215766304,0.66123389215766304]
["2013-02-14T10:00:00.715","2013-02-14T10:00:00",null,10.40392830166415,10.70750050332005,11.01107270497595,11.31464490663185,11.61821710828775,11.92178930994365,12.22536151159955,12.52893371325545,12.83250591491135,null,0,0.31212158250642286,0.65248557128967544,0.8436553089109281,0.90280110804846503,0.95102202090975185,0.99677195371818239,1,1,null,0.65248557128967544,0.65248557128967544,0.65248557128967544]
["2013-02-14T11:00:00.720","2013-02-14T11:00:00",null,10.754265007961799,11.057837209617698,11.361409411273598,11.664981612929498,11.968553814585398,12.272126016241298,12.575698217897198,12.879270419553098,13.182842621208998,null,0,0.28753795968267892,0.63046756179740859,0.82407673504531165,0.88553579210467226,0.93595429999169155,0.98379667973849894,0.98901202487133766,0.99091520525247445,null,0.63046756179740859,0.63046756179740859,0.63046756179740859]
["2013-02-14T12:00:00.725","2013-02-14T12:00:00",null,10.994177073823616,11.297749275479516,11.601321477135416,11.904893678791316,12.208465880447216,12.512038082103116,12.815610283759016,13.119182485414916,13.422754687070816,null,0,0.25854863199873451,0.60410693629735468,0.80021863402432147,0.86404352304918353,0.91672271481434864,0.96672063035194622,0.97398636318821952,0.97784529799417086,null,0.60410693629735468,0.60410693629735468,0.60410693629735468]
["2013-02-14T13:00:00.730","2013-02-14T13:00:00",null,11.161796014965477,11.465368216621377,11.768940418277277,12.072512619933176,12.376084821589076,12.679657023244976,12.983229224900876,13.286801426556776,13.590373628212676,null,0,0.22534286601182973,0.57360347615548934,0.77228078721393323,0.83855562667418126,0.89355859116990555,0.94577513135070668,0.95515434074282801,0.96103211882600725,null,0.57360347615548934,0.57360347615548934,0.57360347615548934]
["2013-02-14T14:00:00.735","2013-02-14T14:00:00",null,11.19647632043216,11.500048522088059,11.803620723743959,12.107192925399859,12.410765127055759,12.714337328711659,13.017909530367559,13.321481732023459,13.625053933679359,null,0,0.19059142314079733,0.54158588355570303,0.74286035237183079,0.81160617188493589,0.86896445353742602,0.92342064797890189,0.93494487835307782,0.94286252933095616,null,0.54158588355570303,0.54158588355570303,0.54158588355570303]
["2013-02-14T15:00:00.740","2013-02-14T15:00:00",null,11.224683111537718,11.528255313193618,11.831827514849518,12.135399716505418,12.438971918161318,12.742544119817218,13.046116321473118,13.349688523129018,13.653260724784918,null,0,0.154494084751613,0.50825393986397149,0.71214659605525421,0.78338442523868745,0.84311905366541462,0.8998464467937719,0.91353672776747363,0.92351528125752202,null,0.50825393986397149,0.50825393986397149,0.50825393986397149]
["2013-02-14T16:00:00.745","2013-02-14T16:00:00",null,11.200987221465132,11.504559423121032,11.808131624776932,12.111703826432832,12.415276028088732,12.718848229744632,13.022420431400532,13.325992633056432,13.629564834712331,null,0,0.11665128811232536,0.47323962677455006,0.67981355919340103,0.75360648689957588,0.81577003614421784,0.87481068719439881,0.89070907800256849,0.90280110804846492,null,0.47323962677455006,0.47323962677455006,0.47323962677455006]
["2013-02-14T17:00:00.750","2013-02-14T17:00:00",null,11.171148403927873,11.474720605583773,11.778292807239673,12.081865008895573,12.385437210551473,12.689009412207373,12.992581613863273,13.296153815519173,13.599726017175072,null,0,8.1668519449110605E-2,0.44105379723499477,0.65028797626394297,0.72660445806665264,0.79117589851173831,0.85250877786627177,0.87059424889143844,0.8847787258757116,null,0.44105379723499477,0.44105379723499477,0.44105379723499477]
["2013-02-14T18:00:00.755","2013-02-14T18:00:00",null,11.044058742595176,11.347630944251076,11.651203145906976,11.954775347562876,12.258347549218776,12.561919750874676,12.865491952530576,13.169064154186476,13.472636355842376,null,0,5.2489925207926058E-2,0.41455647922137856,0.62632472715559717,0.70505961496748615,0.7719337985256598,0.83545375809719025,0.85563167606073376,0.87181396670476363,null,0.41455647922137856,0.41455647922137856,0.41455647922137856]
["2013-02-14T19:00:00.760","2013-02-14T19:00:00",null,10.776479526158006,11.080051727813906,11.383623929469806,11.687196131125706,11.990768332781606,12.294340534437506,12.597912736093406,12.901484937749306,13.205057139405206,null,0,2.8936753640267182E-2,0.39358995060266794,0.60781866378100802,0.68888783913219176,0.75798064733356907,0.82360356865221185,0.84580032989298326,0.86389631572688541,null,0.39358995060266794,0.39358995060266794,0.39358995060266794]
["2013-02-14T20:00:00.765","2013-02-14T20:00:00",null,10.548963381045347,10.852535582701247,11.156107784357147,11.459679986013047,11.763252187668947,12.066824389324847,12.370396590980747,12.673968792636646,12.977540994292546,null,0,1.0178334856024578E-2,0.37737611553243133,0.59400220510247959,0.67735309394928023,0.74860143794144773,0.81628526177226068,0.84043777743784664,0.8604053992266788,null,0.37737611553243133,0.37737611553243133,0.37737611553243133]
["2013-02-14T21:00:00.770","2013-02-14T21:00:00",null,10.507061040308969,10.810633241964869,11.114205443620769,11.417777645276669,11.721349846932569,12.024922048588468,12.328494250244368,12.632066451900268,12.935638653556168,null,0,0,0.36649328849112467,0.58547469521793882,0.6710652383254142,0.74442705887342964,0.81412972598147049,0.84020645164566432,0.86200365015448421,null,0.36649328849112467,0.36649328849112467,0.36649328849112467]
["2013-02-14T22:00:00.775","2013-02-14T22:00:00",null,10.375931998524404,10.679504200180304,10.983076401836204,11.286648603492104,11.590220805148004,11.893793006803904,12.197365208459804,12.500937410115704,12.804509611771604,null,0,0,0.36190883188241962,0.58310886325243738,0.6708023681070252,0.74615148750606175,0.8177468201865038,0.8456215781444788,0.86914320528593081,null,0.36190883188241962,0.36190883188241962,0.36190883188241962]
["2013-02-14T23:00:00.780","2013-02-14T23:00:00",null,10.388994903522853,10.692567105178753,10.996139306834653,11.299711508490553,11.603283710146453,11.906855911802353,12.210428113458253,12.514000315114153,12.817572516770053,null,5.8567484657080324E-2,6.0954346240052901E-2,0.42512386200061836,0.64845839954395523,0.73818126248450644,0.81545459188215086,0.88887950128258075,0.91848920268192347,0.94367216960359424,null,0.42512386200061836,0.42512386200061836,0.42512386200061836]
["2013-02-15T00:00:00.785","2013-02-15",null,10.1545912435923,10.4581634452482,10.7617356469041,11.06530784856,11.3688800502159,11.6724522518718,11.9760244535277,12.2795966551836,12.583168856839499,null,0.12271833275274407,0.12751308553616036,0.49395379998360722,0.71944387331773429,0.811196094344249,0.89040414854923677,0.96565863466965451,0.99700327951036494,1,null,0.49395379998360722,0.49395379998360722,0.49395379998360722]
["2013-02-15T01:00:00.790","2013-02-15T01:00:00",null,10.227098446239832,10.530670647895732,10.834242849551634,11.137815051207534,11.441387252863434,11.744959454519334,12.048531656175234,12.352103857831134,12.655676059487034,null,0.18965560516333174,0.19674258625110055,0.56533883648933758,0.79287929752689923,0.8865662433607574,0.96761438909446851,1,1,1,null,0.56533883648933758,0.56533883648933758,0.56533883648933758]
["2013-02-15T02:00:00.795","2013-02-15T02:00:00",null,10.149194685375264,10.452766887031164,10.756339088687064,11.059911290342963,11.363483491998863,11.667055693654763,11.970627895310663,12.274200096966563,12.577772298622463,null,0.25147216571970071,0.26086188992055759,0.63162419075832044,0.86120452469058106,0.95683671014051819,1,1,1,1,null,0.63162419075832044,0.63162419075832044,0.63162419075832044]
["2013-02-15T03:00:00.800","2013-02-15T03:00:00",null,10.036606105351037,10.340178307006937,10.643750508662837,10.947322710318737,11.250894911974637,11.554467113630537,11.858039315286437,12.161611516942337,12.465183718598237,null,0.31195334556665333,0.32359323883692048,0.69647953103926685,0.92806819344001978,1,1,1,1,1,null,0.69647953103926685,0.69647953103926685,0.69647953103926685]
["2013-02-15T04:00:00.805","2013-02-15T04:00:00",null,9.9341429948914808,10.237715196547381,10.541287398203281,10.844859599859181,11.148431801515081,11.45200400317098,11.75557620482688,12.05914840648278,12.36272060813868,null,0.35517972427854871,0.36904875700075501,0.74402749614147823,0.97759294258451679,1,1,1,1,1,null,0.74402749614147823,0.74402749614147823,0.74402749614147823]
["2013-02-15T05:00:00.810","2013-02-15T05:00:00",null,9.9153855556058978,10.218957757261798,10.522529958917698,10.826102160573598,11.129674362229498,11.433246563885398,11.736818765541297,12.040390967197197,12.343963168853097,null,0.40072987572100327,0.41679650346894204,0.79384665993057102,1,1,1,1,1,1,null,0.79384665993057102,0.79384665993057102,0.79384665993057102]
["2013-02-15T06:00:00.815","2013-02-15T06:00:00",null,9.9955310750112059,10.299103276667106,10.602675478323004,10.906247679978904,11.209819881634804,11.513392083290704,11.816964284946604,12.120536486602504,12.424108688258404,null,0.45904500496843009,0.47741437582945695,0.85664109769934726,1,1,1,1,1,1,null,0.85664109769934726,0.85664109769934726,0.85664109769934726]
["2013-02-15T07:00:00.820","2013-02-15T07:00:00",null,9.8834950192321198,10.18706722088802,10.49063942254392,10.794211624199818,11.097783825855718,11.401356027511618,11.704928229167518,12.008500430823418,12.312072632479317,null,0.51801205235746173,0.53865262190537,0.92001384994857938,1,1,1,1,1,1,null,0.92001384994857938,0.92001384994857938,0.92001384994857938]
["2013-02-15T08:00:00.825","2013-02-15T08:00:00",null,9.8138415671838537,10.117413768839754,10.420985970495654,10.724558172151553,11.028130373807453,11.331702575463353,11.635274777119253,11.938846978775153,12.242419180431053,null,0.55198539938206259,0.57479201952949655,0.95819312046740501,1,1,1,1,1,1,null,0.95819312046740501,0.95819312046740501,0.95819312046740501]
["2013-02-15T09:00:00.830","2013-02-15T09:00:00",null,9.8887914233643208,10.192363625020221,10.495935826676121,10.799508028332021,11.103080229987921,11.40665243164382,11.71022463329972,12.01379683495562,12.31736903661152,null,0.60849198152697281,0.63356980036128807,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-15T10:00:00.835","2013-02-15T10:00:00",null,9.8417320869335576,10.145304288589458,10.448876490245357,10.752448691901257,11.056020893557157,11.359593095213057,11.663165296868957,11.966737498524857,12.270309700180757,null,0.66371575700614438,0.69111734857101892,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-15T11:00:00.840","2013-02-15T11:00:00",null,9.7799281851052111,10.083500386761111,10.387072588417011,10.690644790072911,10.994216991728811,11.297789193384711,11.601361395040611,11.904933596696511,12.208505798352411,null,0.71858202898830692,0.74832842290121171,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-15T12:00:00.845","2013-02-15T12:00:00",null,9.7237916524792496,10.02736385413515,10.330936055791048,10.634508257446948,10.938080459102848,11.241652660758747,11.545224862414647,11.848797064070547,12.152369265726447,null,0.77271226435898011,0.80483500504612193,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-15T13:00:00.850","2013-02-15T13:00:00",null,9.6842048015535038,9.9877770032094038,10.291349204865304,10.594921406521204,10.898493608177104,11.202065809833003,11.505638011488903,11.809210213144803,12.112782414800703,null,0.82522321918437669,0.8597853954981689,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-15T14:00:00.855","2013-02-15T14:00:00",null,9.7547912337128242,10.058363435368724,10.361935637024624,10.665507838680524,10.969080040336424,11.272652241992324,11.576224443648224,11.879796645304124,12.183368846960024,null,0.81119646433113701,0.84818756146284402,0.99068387946029202,0.99283941525108232,0.9948792881457813,0.99680349814438918,0.99862256005564143,1,1,null,0.99068387946029202,0.99068387946029202,0.99068387946029202]
["2013-02-15T15:00:00.860","2013-02-15T15:00:00",null,9.9316727278409687,10.235244929496869,10.538817131152767,10.842389332808667,11.145961534464567,11.449533736120467,11.753105937776366,12.056678139432266,12.360250341088166,null,0.79432019631056006,0.83375072906891745,0.97854979017945343,0.98288189137850512,0.98698266678537427,0.9908521164000611,0.99451126984003668,0.99764468284323415,0.99931653743218851,null,0.97854979017945343,0.97854979017945343,0.97854979017945343]
["2013-02-15T16:00:00.865","2013-02-15T16:00:00",null,9.7814015636658027,10.084973765321703,10.388545966977604,10.692118168633504,10.995690370289404,11.299262571945304,11.602834773601204,11.906406975257104,12.209979176913004,null,0.77801172796170337,0.81991324077291783,0.96702555980527749,0.97355525603006166,0.97971693394910098,0.98554213798860224,0.99106241257477234,0.99595179863680872,0.99929550781471743,null,0.96702555980527749,0.96702555980527749,0.96702555980527749]
["2013-02-15T17:00:00.870","2013-02-15T17:00:00",null,9.729812068872409,10.033384270528309,10.336956472184209,10.640528673840109,10.944100875496009,11.247673077151909,11.551245278807809,11.854817480463709,12.158389682119608,null,0.76065177873929046,0.80506633083830426,0.95453396702742987,0.96329280270415318,0.97155744237030484,0.97936994526082732,0.98677237061066303,0.99344927415774498,0.99848586754207913,null,0.95453396702742987,0.95453396702742987,0.95453396702742987]
["2013-02-15T18:00:00.875","2013-02-15T18:00:00",null,9.7244291868304344,10.028001388486334,10.331573590142234,10.635145791798134,10.938717993454034,11.242290195109934,11.545862396765834,11.849434598421734,12.153006800077634,null,0.74359675897020894,0.79051383554828647,0.94233678889417793,0.9533142492141049,0.96367133581863329,0.973471137560177,0.98274519886494283,0.99120961989707024,0.99793909748782994,null,0.94233678889417793,0.94233678889417793,0.94233678889417793]
["2013-02-15T19:00:00.880","2013-02-15T19:00:00",null,9.5507100865483121,9.854282288204212,10.157854489860112,10.461426691516012,10.764998893171912,11.068571094827812,11.372143296483712,11.675715498139612,11.979287699795512,null,0.72838183072985074,0.77778040216952093,0.93193764305470717,0.94512321320910209,0.95755171713453624,0.96931778810962999,0.98045297056059033,0.99068387946029213,0.99908521164000619,null,0.93193764305470717,0.93193764305470717,0.93193764305470717]
["2013-02-15T20:00:00.885","2013-02-15T20:00:00",null,9.4398353650566289,9.7434075667125288,10.046979768368429,10.350551970024329,10.654124171680229,10.957696373336129,11.261268574992028,11.564840776647928,11.868412978303828,null,0.71546964560258064,0.7673181674776367,0.92376763666717554,0.93911925742109614,0.95357711943249379,0.96726740040619541,0.98022164476840801,0.99218749710947751,1,null,0.92376763666717554,0.92376763666717554,0.92376763666717554]
["2013-02-15T21:00:00.890","2013-02-15T21:00:00",null,9.3473816991334093,9.6509539007893093,9.9545261024452092,10.258098304101109,10.561670505757009,10.865242707412909,11.168814909068809,11.472387110724709,11.775959312380609,null,0.70393490041966911,0.75820182830390448,0.91693301098906022,0.93442965272503553,0.95090635801366108,0.96649981936849938,0.98125209602449304,0.99493186218945917,1,null,0.91693301098906022,0.91693301098906022,0.91693301098906022]
["2013-02-15T22:00:00.895","2013-02-15T22:00:00",null,9.2783845703291199,9.5819567719850198,9.8855289736409198,10.18910117529682,10.49267337695272,10.79624557860862,11.099817780264519,11.403389981920419,11.706962183576319,null,0.6962696048514444,0.75284979065750346,0.91375753875092047,0.93329405338159488,0.95170548347756379,0.96910749193491874,0.98558419722354462,1,1,null,0.91375753875092047,0.91375753875092047,0.91375753875092047]
["2013-02-15T23:00:00.900","2013-02-15T23:00:00",null,9.178741946691666,9.4823141483475659,9.7858863500034659,10.089458551659366,10.393030753315266,10.696602954971166,11.000175156627066,11.303747358282966,11.607319559938865,null,0.68963476053930473,0.74849665984098079,0.91153891410771692,0.93309427201561923,0.95339836768398922,0.97258789362638975,0.99074696831270559,1,1,null,0.91153891410771692,0.91153891410771692,0.91153891410771692]
["2013-02-16T00:00:00.905","2013-02-16",null,9.0349407534787538,9.3385129551346537,9.6420851567905537,9.9456573584464536,10.249229560102354,10.552801761758253,10.856373963414153,11.159946165070053,11.463518366725953,null,0.68703760278162096,0.74806555268282271,0.91313716503552234,0.93660621813329692,0.95870834609544808,0.97959075624427405,0.9993480818583953,1,1,null,0.91313716503552234,0.91313716503552234,0.91313716503552234]
["2013-02-16T01:00:00.910","2013-02-16T01:00:00",null,8.9344029102889095,9.2379751119448095,9.5415473136007094,9.8451195152566093,10.148691716912509,10.452263918568409,10.755836120224309,11.059408321880209,11.362980523536109,null,0.68650134753610725,0.74966380361062812,0.91672271481434897,0.94206340386705356,0.96592150488804362,0.98846525481708836,1,1,1,null,0.91672271481434897,0.91672271481434897,0.91672271481434897]
["2013-02-16T02:00:00.915","2013-02-16T02:00:00",null,8.9923305564251432,9.2959027580810432,9.5994749597369431,9.9030471613928412,10.206619363048741,10.510191564704641,10.813763766360541,11.117335968016441,11.420908169672341,null,0.68650134753610725,0.75175625054900497,0.92077091617754037,0.94795169675896829,0.97354474122132606,0.99771828650438288,1,1,1,null,0.92077091617754037,0.92077091617754037,0.92077091617754037]
["2013-02-16T03:00:00.920","2013-02-16T03:00:00",null,8.9133494976388121,9.2169216992947121,9.520493900950612,9.8240661026065119,10.127638304262412,10.431210505918312,10.734782707574212,11.038354909230112,11.341927110886012,null,0.68716378048644766,0.75451113043772222,0.92548155049107217,0.95449190779248783,0.98180938088747782,1,1,1,1,null,0.92548155049107217,0.92548155049107217,0.92548155049107217]
["2013-02-16T04:00:00.925","2013-02-16T04:00:00",null,8.9082547508866305,9.2118269525425305,9.5153991541984304,9.8189713558543303,10.12254355751023,10.42611575916613,10.72968796082203,11.03326016247793,11.33683236413383,null,0.68816268731632602,0.75758145458850634,0.93050762906667084,0.96133704827933864,0.99037895000696086,1,1,1,1,null,0.93050762906667084,0.93050762906667084,0.93050762906667084]
["2013-02-16T05:00:00.930","2013-02-16T05:00:00",null,8.8966810605445463,9.2002532622004463,9.5038254638563462,9.8073976655122443,10.110969867168144,10.414542068824044,10.718114270479944,11.021686472135844,11.325258673791744,null,0.68574428130714671,0.7573606436050595,0.93233720578665857,0.96510134980666984,0.99595179863680872,1,1,1,1,null,0.93233720578665857,0.93233720578665857,0.93233720578665857]
["2013-02-16T06:00:00.935","2013-02-16T06:00:00",null,8.8162665438695083,9.1198387455254082,9.4234109471813081,9.7269831488372063,10.030555350493106,10.334127552149006,10.637699753804906,10.941271955460806,11.244844157116706,null,0.68397779343957232,0.75778123595448199,0.93480818583951564,0.96949653985813478,1,1,1,1,1,null,0.93480818583951564,0.93480818583951564,0.93480818583951564]
["2013-02-16T07:00:00.940","2013-02-16T07:00:00",null,8.8852518580080506,9.1888240596639505,9.4923962613198505,9.7959684629757504,10.09954066463165,10.40311286628755,10.70668506794345,11.01025726959935,11.31382947125525,null,0.68221130557199794,0.75819131349516888,0.93725813627490162,0.97384967067465744,1,1,1,1,1,null,0.93725813627490162,0.93725813627490162,0.93725813627490162]
["2013-02-16T08:00:00.945","2013-02-16T08:00:00",null,9.0371008511389235,9.3406730527948234,9.6442452544507233,9.9478174561066233,10.251389657762523,10.554961859418423,10.858534061074323,11.162106262730223,11.465678464386123,null,0.67950899972695855,0.75766557305839077,0.93876175392408701,0.9772669835137151,1,1,1,1,1,null,0.93876175392408701,0.93876175392408701,0.93876175392408701]
["2013-02-16T09:00:00.950","2013-02-16T09:00:00",null,9.271488136879233,9.5750603385351329,9.8786325401910329,10.182204741846933,10.485776943502833,10.789349145158733,11.092921346814633,11.396493548470533,11.700065750126432,null,0.67501917639687359,0.75535231513656709,0.93848836889696241,0.97891780848519838,1,1,1,1,1,null,0.93848836889696241,0.93848836889696241,0.93848836889696241]
["2013-02-16T10:00:00.955","2013-02-16T10:00:00",null,9.4801423939879434,9.7837145956438434,10.087286797299743,10.390858998955643,10.694431200611543,10.998003402267443,11.301575603923343,11.605147805579243,11.908720007235143,null,0.66646012208612615,0.74904342989522987,0.93430347502020872,0.97673072826820151,0.99970558535540421,1,1,1,1,null,0.93430347502020872,0.93430347502020872,0.93430347502020872]
["2013-02-16T11:00:00.960","2013-02-16T11:00:00",null,9.6322623053919685,9.9358345070478684,10.239406708703768,10.542978910359668,10.846551112015568,11.150123313671468,11.453695515327368,11.757267716983268,12.060839918639168,null,0.65311682980069796,0.73806596957530313,0.92554463934348552,0.97007485433859075,0.99502649546807909,0.99719254606760499,0.99896954874391497,1,1,null,0.92554463934348552,0.92554463934348552,0.92554463934348552]
["2013-02-16T12:00:00.965","2013-02-16T12:00:00",null,9.8173935964358616,10.120965798091762,10.424537999747661,10.728110201403561,11.031682403059461,11.335254604715361,11.638826806371261,11.942399008027161,12.245971209683061,null,0.63726049822747044,0.72460701439378372,0.91434636804011205,0.9610005743998008,0.98797105880651703,0.99204028978717962,0.99562583956600625,0.99837020464598791,1,null,0.91434636804011205,0.91434636804011205,0.91434636804011205]
["2013-02-16T13:00:00.970","2013-02-16T13:00:00",null,9.944750888805574,10.248323090461474,10.551895292117374,10.855467493773274,11.159039695429174,11.462611897085074,11.766184098740974,12.069756300396874,12.373328502052773,null,0.61830229807725212,0.70810927948768698,0.90017240586457448,0.9490136924412601,0.9780555941688821,0.98408057957435924,0.98952725049938028,0.99403810344693633,0.99735026819863837,null,0.90017240586457448,0.90017240586457448,0.90017240586457448]
["2013-02-16T14:00:00.975","2013-02-16T14:00:00",null,10.064429565927252,10.368001767583152,10.67157396923905,10.97514617089495,11.27871837255085,11.58229057420675,11.88586277586265,12.18943497751855,12.49300717917445,null,0.60344487333390306,0.69587004211949277,0.89040414854923733,0.94157972266521772,0.97282973422730779,0.98094716657116177,0.98837062153846844,0.99477414005842568,0.9998738222951733,null,0.89040414854923733,0.89040414854923733,0.89040414854923733]
["2013-02-16T15:00:00.980","2013-02-16T15:00:00",null,10.176716844671891,10.48028904632779,10.78386124798369,11.08743344963959,11.39100565129549,11.69457785295139,11.99815005460729,12.30172225626319,12.60529445791909,null,0.58963892946411012,0.68471383005106146,0.88175046095986975,0.9352918670413517,0.96878153286411639,0.97902295657255389,0.98846525481708847,0.99678246852691799,1,null,0.88175046095986975,0.88175046095986975,0.88175046095986975]
["2013-02-16T16:00:00.985","2013-02-16T16:00:00",null,10.283549247348549,10.587121449004449,10.890693650660349,11.194265852316249,11.497838053972149,11.801410255628049,12.104982457283949,12.408554658939849,12.712126860595749,null,0.57406649772674279,0.67181215973252684,0.87138285954660566,0.92731112721106013,0.96307199172070623,0.97545843641119834,0.986940607550432,0.99720306087634047,1,null,0.87138285954660566,0.87138285954660566,0.87138285954660566]
["2013-02-16T17:00:00.990","2013-02-16T17:00:00",null,10.276229801428888,10.57980200308479,10.88337420474069,11.18694640639659,11.49051860805249,11.79409080970839,12.09766301136429,12.40123521302019,12.70480741467609,null,0.55886208429512019,0.65927850771973695,0.86137276163035059,0.9196773760690421,0.95769892445683402,0.97223039012938084,0.98574191935457789,0.99793909748782983,1,null,0.86137276163035059,0.86137276163035059,0.86137276163035059]
["2013-02-16T18:00:00.995","2013-02-16T18:00:00",null,10.158498209088384,10.462070410744284,10.765642612400182,11.069214814056082,11.372787015711982,11.676359217367882,11.979931419023782,12.283503620679681,12.587075822335581,null,0.54601298802026343,0.64905811362877064,0.85363386240097694,0.91428327918769881,0.95452345221869428,0.97116839444708902,0.98667773733204289,1,1,null,0.85363386240097694,0.85363386240097694,0.85363386240097694]
["2013-02-16T19:00:01","2013-02-16T19:00:00",null,9.8740311368107339,10.177603338466634,10.481175540122534,10.784747741778434,11.088319943434334,11.391892145090234,11.695464346746133,11.999036548402033,12.302608750057933,null,0.53690716365526669,0.64253893221272218,0.84955411661157887,0.91251679132012442,0.95493352975938117,0.97363937449994609,0.9911044718097145,1,1,null,0.84955411661157887,0.84955411661157887,0.84955411661157887]
["2013-02-16T20:00:01.005","2013-02-16T20:00:00",null,9.8735992501002983,10.177171451756198,10.480743653412096,10.784315855067996,11.087888056723896,11.391460258379796,11.695032460035696,11.998604661691596,12.302176863347496,null,0.53163924447875011,0.63974199308906265,0.84909146502721411,0.91426224957022773,0.95876092013912573,0.97943303411324079,0.99876976737793921,1,1,null,0.84909146502721411,0.84909146502721411,0.84909146502721411]
["2013-02-16T21:00:01.010","2013-02-16T21:00:00",null,9.7720838035697888,10.075656005225689,10.379228206881587,10.682800408537487,10.986372610193387,11.289944811849287,11.593517013505187,11.897089215161087,12.200661416816986,null,0.52822193163969244,0.63877463068539098,0.85042684573663052,0.91777419568790541,0.96433376876897359,0.9869511223591676,1,1,1,null,0.85042684573663052,0.85042684573663052,0.85042684573663052]
["2013-02-16T22:00:01.015","2013-02-16T22:00:00",null,9.6245567844412214,9.9281289860971214,10.231701187753021,10.535273389408921,10.838845591064821,11.142417792720721,11.445989994376621,11.749562196032521,12.053134397688421,null,0.52850583147555263,0.64142436248675261,0.85528468737246022,0.92472448426211185,0.97325032657673016,0.99773931612185418,1,1,1,null,0.85528468737246022,0.85528468737246022,0.85528468737246022]
["2013-02-16T23:00:01.020","2013-02-16T23:00:00",null,9.6442923932767215,9.9478645949326214,10.251436796588521,10.555008998244423,10.858581199900323,11.162153401556223,11.465725603212123,11.769297804868023,12.072870006523923,null,0.5266762547555649,0.64185546964491069,0.85785030070393731,0.92929842606208135,0.97971693394910075,1,1,1,1,null,0.85785030070393731,0.85785030070393731,0.85785030070393731]
["2013-02-17T00:00:01.025","2013-02-17",null,9.533594017288463,9.8371662189443629,10.140738420600263,10.444310622256163,10.747882823912063,11.051455025567963,11.355027227223863,11.658599428879763,11.962171630535662,null,0.52624514759740681,0.64364298712995627,0.86171975031862413,0.93513414491031821,0.98740325913479654,1,1,1,1,null,0.86171975031862413,0.86171975031862413,0.86171975031862413]
["2013-02-17T01:00:01.030","2013-02-17T01:00:00",null,9.4391448518199024,9.7427170534758023,10.046289255131702,10.349861456787602,10.653433658443502,10.957005860099402,11.260578061755302,11.564150263411202,11.867722465067102,null,0.52735971732337639,0.64694463707292271,0.86708230277376075,0.94244193698153378,0.99654062792599996,1,1,1,1,null,0.86708230277376075,0.86708230277376075,0.86708230277376075]
["2013-02-17T02:00:01.035","2013-02-17T02:00:00",null,9.4094748029440005,9.7130470045999004,10.0166192062558,10.3201914079117,10.6237636095676,10.9273358112235,11.2309080128794,11.5344802145353,11.8380524161912,null,0.53019871568197807,0.65192865641357911,0.87408516539164505,0.95133746517181927,1,1,1,1,1,null,0.87408516539164505,0.87408516539164505,0.87408516539164505]
["2013-02-17T03:00:01.040","2013-02-17T03:00:00",null,9.3359824140919923,9.6395546157478922,9.9431268174037921,10.246699019059692,10.550271220715592,10.853843422371492,11.157415624027392,11.460987825683292,11.764560027339192,null,0.53331109906770446,0.6571965755900957,0.88138244265412502,0.96053792281543604,1,1,1,1,1,null,0.88138244265412502,0.88138244265412502,0.88138244265412502]
["2013-02-17T04:00:01.045","2013-02-17T04:00:00",null,9.2906721116864031,9.594244313342303,9.8978165149982029,10.201388716654103,10.504960918310003,10.808533119965903,11.112105321621803,11.415677523277703,11.719249724933603,null,0.53509861655275004,0.66118168810087374,0.88743897248580872,0.96855020707193429,1,1,1,1,1,null,0.88743897248580872,0.88743897248580872,0.88743897248580872]
["2013-02-17T05:00:01.050","2013-02-17T05:00:00",null,9.309229261493229,9.612801463149129,9.9163736648050289,10.219945866460929,10.523518068116829,10.827090269772729,11.130662471428629,11.434234673084529,11.737806874740428,null,0.53571899026814818,0.66404171607694662,0.89240196220899404,0.97548998083740524,1,1,1,1,1,null,0.89240196220899404,0.89240196220899404,0.89240196220899404]
["2013-02-17T06:00:01.055","2013-02-17T06:00:00",null,9.3182065763167596,9.6217787779726596,9.9253509796285595,10.228923181284459,10.532495382940359,10.836067584596259,11.139639786252159,11.443211987908059,11.746784189563959,null,0.5358136235467682,0.66638651842497698,0.89686024111287233,0.98193555859230475,1,1,1,1,1,null,0.89686024111287233,0.89686024111287233,0.89686024111287233]
["2013-02-17T07:00:01.060","2013-02-17T07:00:00",null,9.469375905231125,9.772948106887025,10.076520308542925,10.380092510198825,10.683664711854725,10.987236913510625,11.290809115166525,11.594381316822425,11.897953518478324,null,0.53507758693527885,0.66789013607416237,0.90047733531790564,0.98752943683962369,1,1,1,1,1,null,0.90047733531790564,0.90047733531790564,0.90047733531790564]
["2013-02-17T08:00:01.065","2013-02-17T08:00:00",null,9.5668359913965997,9.8704081930524996,10.1739803947084,10.477552596364299,10.781124798020199,11.084696999676099,11.388269201331999,11.691841402987899,11.995413604643799,null,0.53270124016104181,0.66778498798680674,0.90250669340386913,0.99156712339407949,1,1,1,1,1,null,0.90250669340386913,0.90250669340386913,0.90250669340386913]
["2013-02-17T09:00:01.070","2013-02-17T09:00:00",null,9.9207329257741357,10.224305127430036,10.527877329085936,10.831449530741835,11.135021732397735,11.438593934053635,11.742166135709535,12.045738337365435,12.349310539021335,null,0.52828502049210579,0.6656820262396943,0.90259081187375367,0.99371214437613409,1,1,1,1,1,null,0.90259081187375367,0.90259081187375367,0.90259081187375367]
["2013-02-17T10:00:01.075","2013-02-17T10:00:00",null,11.249895190327155,11.553467391983055,11.857039593638955,12.160611795294855,12.464183996950755,12.767756198606655,13.071328400262555,13.374900601918455,13.678472803574355,null,0.46896046960606502,0.60981684742765341,0.85000625338720814,0.94425048408405043,0.95350351577134485,0.95633199932121105,0.95902379035751495,0.96159991849772763,0.96404986893311351,null,0.85000625338720814,0.85000625338720814,0.85000625338720814]
["2013-02-17T11:00:01.080","2013-02-17T11:00:00",null,11.464173591479398,11.767745793135298,12.071317994791197,12.374890196447097,12.678462398102997,12.982034599758897,13.285606801414797,13.589179003070697,13.892751204726597,null,0.41614458532733711,0.56037621675304095,0.80378315418567758,0.90107667941583292,0.91323179831414236,0.91882567656146141,0.92415668459039135,0.92925636682713897,0.93412472327170404,null,0.80378315418567758,0.80378315418567758,0.80378315418567758]
["2013-02-17T12:00:01.085","2013-02-17T12:00:00",null,11.180059790331798,11.483631991987698,11.787204193643598,12.090776395299498,12.394348596955398,12.697920798611298,13.001493000267198,13.305065201923098,13.608637403578998,null,0.38251822699100985,0.52970451967140664,0.77591891103643829,0.87587268287669084,0.89056187068027071,0.89857415493676895,0.9061973912700515,0.91349466853253158,0.92045547191547339,null,0.77591891103643829,0.77591891103643829,0.77591891103643829]
["2013-02-17T13:00:01.090","2013-02-17T13:00:00",null,11.067777834358633,11.371350036014533,11.674922237670433,11.978494439326333,12.282066640982233,12.585638842638133,12.889211044294033,13.192783245949933,13.496355447605833,null,0.35725114159945437,0.50719231416856836,0.75602489290875496,0.85846015961060018,0.87550466457094589,0.88576711789685447,0.89553537521219162,0.90487252536937079,0.91377856836839155,null,0.75602489290875496,0.75602489290875496,0.75602489290875496]
["2013-02-17T14:00:01.095","2013-02-17T14:00:00",null,11.251948854215479,11.555521055871379,11.859093257527279,12.162665459183179,12.466237660839079,12.769809862494979,13.073382064150879,13.376954265806779,13.680526467462679,null,0.33028065719273786,0.48298722445930464,0.7344379905746462,0.83936526694681957,0.85877560387266672,0.87128822626798563,0.88321201937411298,0.89459955723472673,0.90547186946729763,null,0.7344379905746462,0.7344379905746462,0.7344379905746462]
["2013-02-17T15:00:01.100","2013-02-17T15:00:00",null,11.160650888723064,11.464223090378963,11.767795292034863,12.071367493690763,12.374939695346663,12.678511897002563,12.982084098658463,13.285656300314363,13.589228501970263,null,0.30082867792442869,0.45638475835833281,0.71054834512744935,0.81804123483109981,0.83989100738359734,0.85472740250947554,0.86886982025880644,0.88237083467526811,0.89526199018506691,null,0.71054834512744935,0.71054834512744935,0.71054834512744935]
["2013-02-17T16:00:01.105","2013-02-17T16:00:00",null,11.21980609816586,11.52337829982176,11.826950501477659,12.130522703133559,12.434094904789459,12.737667106445359,13.041239308101259,13.344811509757159,13.648383711413059,null,0.27196552794531098,0.43033957712034576,0.68717392530829502,0.79720088391721589,0.82146906247889273,0.83860820071785902,0.85493769868418679,0.8705416748477609,0.88543064401731641,null,0.68717392530829502,0.68717392530829502,0.68717392530829502]
["2013-02-17T17:00:01.110","2013-02-17T17:00:00",null,11.094799379940408,11.398371581596308,11.701943783252208,12.005515984908108,12.309088186564008,12.612660388219908,12.916232589875808,13.219804791531708,13.523376993187608,null,0.24549975435790145,0.40664971303912456,0.66613379302843545,0.77866327611642006,0.80531831626106953,0.82472865318691724,0.8432136869440352,0.86088908042851497,0.87774431883162063,null,0.66613379302843545,0.66613379302843545,0.66613379302843545]
["2013-02-17T18:00:01.115","2013-02-17T18:00:00",null,10.899964364699448,11.203536566355348,11.507108768011248,11.810680969667148,12.114253171323048,12.417825372978948,12.721397574634848,13.024969776290748,13.328541977946648,null,0.22480661076631545,0.38863784567510684,0.65065599456968815,0.76559336885811646,0.79454063730711844,0.81612753964122753,0.83668399071925115,0.85632565343728106,0.87507355741278792,null,0.65065599456968815,0.65065599456968815,0.65065599456968815]
["2013-02-17T19:00:01.120","2013-02-17T19:00:00",null,10.785393648867618,11.088965850523518,11.392538052179418,11.696110253835318,11.999682455491218,12.303254657147118,12.606826858803018,12.910399060458918,13.213971262114818,null,0.2095180788648083,0.37591492710507685,0.6403514820088374,0.75758108460161822,0.78870491845888158,0.81236323811389632,0.83489647323420557,0.85640977190716561,0.87695570817645352,null,0.6403514820088374,0.6403514820088374,0.6403514820088374]
["2013-02-17T20:00:01.125","2013-02-17T20:00:00",null,10.73001940269395,11.03359160434985,11.33716380600575,11.64073600766165,11.944308209317549,12.247880410973449,12.551452612629349,12.855024814285249,13.158597015941149,null,0.19700545646948953,0.36590482918882183,0.63269670124934829,0.75216595810280373,0.78541378332465062,0.81109094625689337,0.83554839137581038,0.85889126676875827,0.88118266128814948,null,0.63269670124934829,0.63269670124934829,0.63269670124934829]
["2013-02-17T21:00:01.130","2013-02-17T21:00:00",null,10.690164827250218,10.993737028906118,11.297309230562018,11.600881432217918,11.904453633873818,12.208025835529718,12.511598037185617,12.815170238841517,13.118742440497417,null,0.18639601445530746,0.35774533761002575,0.62685046759237584,0.74851731947156375,0.78384707682305188,0.81151153860631586,0.83785113448889847,0.86299204217562742,0.88699735051891526,null,0.62685046759237584,0.62685046759237584,0.62685046759237584]
["2013-02-17T22:00:01.135","2013-02-17T22:00:00",null,10.720835532100637,11.024407733756536,11.327979935412436,11.631552137068336,11.935124338724236,12.238696540380136,12.542268742036036,12.845840943691936,13.149413145347836,null,0.17840475981628034,0.35204631127535113,0.62331749185722696,0.74704524624858504,0.78433075802488772,0.81384582614561063,0.84195190989576763,0.86877518698018652,0.89437874625127978,null,0.62331749185722696,0.62331749185722696,0.62331749185722696]
["2013-02-17T23:00:01.140","2013-02-17T23:00:00",null,10.555427195260151,10.858999396916051,11.162571598571949,11.466143800227849,11.769716001883749,12.073288203539649,12.376860405195549,12.680432606851449,12.984004808507349,null,0.1641677087883294,0.34000685527313262,0.61334945317591416,0.73904347680082239,0.77819010972331948,0.80947166571161688,0.83926011885946372,0.86768164687168803,0.89480985340943786,null,0.61334945317591416,0.61334945317591416,0.61334945317591416]
["2013-02-18T00:00:01.145","2013-02-18",null,10.590377454331618,10.893949655987518,11.197521857643418,11.501094059299318,11.804666260955218,12.108238462611117,12.411810664267017,12.715382865922917,13.018955067578817,null,0.15062463513692553,0.32859828779504785,0.60395972897505734,0.73156744778983784,0.77253314262358708,0.80553912724451671,0.83696789055511123,0.86694561026019867,0.8955669196383983,null,0.60395972897505734,0.60395972897505734,0.60395972897505734]
["2013-02-18T01:00:01.150","2013-02-18T01:00:00",null,10.555348503326725,10.858920704982625,11.162492906638525,11.466065108294424,11.769637309950324,12.073209511606224,12.376781713262124,12.680353914918024,12.983926116573924,null,0.13887959377930278,0.31894569337580192,0.59628391859809704,0.72577378817654314,0.76851648568660236,0.80320483970522194,0.83624236875235747,0.86774473572410138,0.89782760351654411,null,0.59628391859809704,0.59628391859809704,0.59628391859809704]
["2013-02-18T02:00:01.155","2013-02-18T02:00:00",null,10.589468731070271,10.893040932726171,11.196613134382071,11.500185336037971,11.803757537693871,12.107329739349771,12.410901941005671,12.714474142661571,13.018046344317471,null,0.12537857936284119,0.30757918513265942,0.58693625363218238,0.71833981840050076,0.76289106301307674,0.79930384566432844,0.83398168487421165,0.8670402435388187,0.89861621417171123,null,0.58693625363218238,0.58693625363218238,0.58693625363218238]
["2013-02-18T03:00:01.160","2013-02-18T03:00:00",null,10.709992596437496,11.013564798093396,11.317136999749296,11.620709201405196,11.924281403061096,12.227853604716996,12.531425806372896,12.834998008028796,13.138570209684696,null,0.11280286811510905,0.29708540601456856,0.57841925855637721,0.7116944592796256,0.75801219175977597,0.7961178586174531,0.83240446356387732,0.86698766949514094,0.90002519854227658,null,0.57841925855637721,0.57841925855637721,0.57841925855637721]
["2013-02-18T04:00:01.165","2013-02-18T04:00:00",null,10.802041492237267,11.105613693893167,11.409185895549065,11.712758097204965,12.016330298860865,12.319902500516765,12.623474702172665,12.927046903828565,13.230619105484465,null,9.9081042715200643E-2,0.28545602755303701,0.56878769375460247,0.70394504524151635,0.75205029520671229,0.79185936107955046,0.82976524657125128,0.86589412938664245,0.9004037316567568,null,0.56878769375460247,0.56878769375460247,0.56878769375460247]
["2013-02-18T05:00:01.170","2013-02-18T05:00:00",null,10.982139684561243,11.285711886217143,11.589284087873043,11.892856289528943,12.196428491184843,12.500000692840743,12.803572894496643,13.107145096152543,13.410717297808443,null,7.6474203933742352E-2,0.26515193188466679,0.55067067830322913,0.68789944711104878,0.73797096630979475,0.77965166813756304,0.81934507111430932,0.85717735294486153,0.89330623576025248,null,0.55067067830322913,0.55067067830322913,0.55067067830322913]
["2013-02-18T06:00:01.175","2013-02-18T06:00:00",null,11.09303429523349,11.39660649688939,11.70017869854529,12.00375090020119,12.30732310185709,12.61089530351299,12.91446750516889,13.21803970682479,13.52161190848069,null,6.8104416180234995E-2,0.25911643167045423,0.54684328792348458,0.68617501847841667,0.73824435133691935,0.78181771873708883,0.82333018362508736,0.86288689408827168,0.90066660187514591,null,0.54684328792348458,0.54684328792348458,0.54684328792348458]
["2013-02-18T07:00:01.180","2013-02-18T07:00:00",null,11.202871832902041,11.506444034557941,11.810016236213841,12.11358843786974,12.41716063952564,12.72073284118154,13.02430504283744,13.32787724449334,13.63144944614924,null,0.10459080249263512,0.2980527684182403,0.58810339740182982,0.72963272298249437,0.7838050175881095,0.82937619864803569,0.87279184391717102,0.91416761629160759,0.95368226751984952,null,0.58810339740182982,0.58810339740182982,0.58810339740182982]
["2013-02-18T08:00:01.185","2013-02-18T08:00:00",null,11.355371847693583,11.658944049349483,11.962516251005383,12.266088452661283,12.569660654317182,12.873232855973082,13.176805057628982,13.480377259284882,13.783949460940782,null,0.14261235088042731,0.33858735609383178,0.63101433185165834,0.77481485611920431,0.83114268651560963,0.87877477008770599,0.92414616978165576,0.96740409291975804,1,null,0.63101433185165834,0.63101433185165834,0.63101433185165834]
["2013-02-18T09:00:01.190","2013-02-18T09:00:00",null,11.535769882059311,11.839342083715211,12.142914285371111,12.446486487027011,12.750058688682911,13.053630890338811,13.357203091994711,13.660775293650611,13.964347495306511,null,0.17907770757535632,0.37756575207656012,0.6723795894173592,0.81846182718052218,0.8769557081764533,0.92664869426071972,0.97399687799695522,1,1,null,0.6723795894173592,0.6723795894173592,0.6723795894173592]
["2013-02-18T10:00:01.195","2013-02-18T10:00:00",null,11.822876779391342,12.126448981047242,12.430021182703141,12.733593384359041,13.037165586014941,13.340737787670841,13.644309989326741,13.947882190982641,14.251454392638541,null,0.20923417902894814,0.41034041090530687,0.70763574310769861,0.85608381283636303,0.91683837771043997,0.96868689958549659,1,1,1,null,0.70763574310769861,0.70763574310769861,0.70763574310769861]
["2013-02-18T11:00:01.200","2013-02-18T11:00:00",null,11.980985595482531,12.284557797138431,12.588129998794331,12.891702200450231,13.195274402106131,13.498846603762031,13.802418805417931,14.105991007073831,14.409563208729731,null,0.23584715993865557,0.43962415323384701,0.73945355434150917,0.89033054488808849,0.95338785287525352,1,1,1,1,null,0.73945355434150917,0.73945355434150917,0.73945355434150917]
["2013-02-18T12:00:01.205","2013-02-18T12:00:00",null,11.843565703892626,12.147137905548526,12.450710107204426,12.754282308860326,13.057854510516226,13.361426712172126,13.664998913828025,13.968571115483925,14.272143317139825,null,0.26199748926399824,0.46847678840422913,0.77089283246083951,0.92421977344280482,0.9896218837780002,1,1,1,1,null,0.77089283246083951,0.77089283246083951,0.77089283246083951]
["2013-02-18T13:00:01.210","2013-02-18T13:00:00",null,11.802513282899614,12.106085484555514,12.409657686211414,12.713229887867314,13.016802089523214,13.320374291179114,13.623946492835014,13.927518694490914,14.231090896146814,null,0.2867493490275112,0.49598352805645929,0.80101775948822462,0.95683671014051819,1,1,1,1,1,null,0.80101775948822462,0.80101775948822462,0.80101775948822462]
["2013-02-18T14:00:01.215","2013-02-18T14:00:00",null,11.519028663519766,11.822600865175666,12.126173066831566,12.429745268487466,12.733317470143366,13.036889671799265,13.340461873455165,13.644034075111065,13.947606276766965,null,0.31605412097352248,0.52804317989118776,0.83568508388937257,0.99399604421199428,1,1,1,1,1,null,0.83568508388937257,0.83568508388937257,0.83568508388937257]
["2013-02-18T15:00:01.220","2013-02-18T15:00:00",null,11.243429860445479,11.547002062101379,11.850574263757279,12.154146465413179,12.457718667069079,12.761290868724979,13.064863070380879,13.368435272036779,13.672007473692679,null,0.34676787729009906,0.56160644937510162,0.87194014440959033,1,1,1,1,1,1,null,0.87194014440959033,0.87194014440959033,0.87194014440959033]
["2013-02-18T16:00:01.225","2013-02-18T16:00:00",null,11.192240936807487,11.495813138463387,11.799385340119287,12.102957541775186,12.406529743431086,12.710101945086986,13.013674146742886,13.317246348398786,13.620818550054686,null,0.3765247860117395,0.59424441569028608,0.90731196099602085,1,1,1,1,1,1,null,0.90731196099602085,0.90731196099602085,0.90731196099602085]
["2013-02-18T17:00:01.230","2013-02-18T17:00:00",null,11.142443761447838,11.446015963103738,11.749588164759638,12.053160366415538,12.356732568071438,12.660304769727338,12.963876971383238,13.267449173039138,13.571021374695038,null,0.40850031937658354,0.62905894741373181,0.94480776894703489,1,1,1,1,1,1,null,0.94480776894703489,0.94480776894703489,0.94480776894703489]
["2013-02-18T18:00:01.235","2013-02-18T18:00:00",null,10.891911499082884,11.195483700738782,11.499055902394682,11.802628104050582,12.106200305706482,12.409772507362382,12.713344709018282,13.016916910674182,13.320489112330081,null,0.44533369437725723,0.66865771711185829,0.98702472602031632,1,1,1,1,1,1,null,0.98702472602031632,0.98702472602031632,0.98702472602031632]
["2013-02-18T19:00:01.240","2013-02-18T19:00:00",null,10.722146798496803,11.025719000152703,11.329291201808603,11.632863403464503,11.936435605120403,12.240007806776303,12.543580008432203,12.847152210088103,13.150724411744003,null,0.48618372631491558,0.71218902527708494,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-18T20:00:01.245","2013-02-18T20:00:00",null,10.60064222102053,10.904214422676432,11.207786624332332,11.511358825988232,11.814931027644132,12.118503229300032,12.422075430955932,12.725647632611832,13.029219834267732,null,0.52546705175097519,0.75411156770577059,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-18T21:00:01.250","2013-02-18T21:00:00",null,10.456697798036124,10.760269999692024,11.063842201347924,11.367414403003824,11.670986604659724,11.974558806315624,12.278131007971524,12.581703209627424,12.885275411283324,null,0.56805202713000125,0.79927267122500933,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-18T22:00:01.255","2013-02-18T22:00:00",null,10.306895799532491,10.610468001188391,10.914040202844291,11.217612404500191,11.521184606156091,11.82475680781199,12.12832900946789,12.43190121112379,12.73547341277969,null,0.61189877955729477,0.845611433322631,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-18T23:00:01.260","2013-02-18T23:00:00",null,10.088849532347641,10.392421734003541,10.695993935659439,10.999566137315339,11.303138338971239,11.606710540627139,11.910282742283039,12.213854943938939,12.517427145594839,null,0.65528288040022353,0.89152960307083029,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T00:00:01.265","2013-02-19",null,9.9394459215616138,10.243018123217514,10.546590324873414,10.850162526529314,11.153734728185213,11.457306929841113,11.760879131497013,12.064451333152913,12.368023534808813,null,0.70285187511990599,0.94155906303463432,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T01:00:01.270","2013-02-19T01:00:00",null,9.8666115858453178,10.170183787501218,10.473755989157118,10.777328190813018,11.080900392468918,11.384472594124817,11.688044795780717,11.991616997436617,12.295189199092517,null,0.7543849527328953,0.99544745780438959,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T02:00:01.275","2013-02-19T02:00:00",null,9.7556787322732355,10.059250933929135,10.362823135585035,10.666395337240935,10.969967538896835,11.273539740552735,11.577111942208635,11.880684143864535,12.184256345520435,null,0.80817871422403043,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T03:00:01.280","2013-02-19T03:00:00",null,9.7344980977254831,10.038070299381383,10.341642501037283,10.645214702693183,10.948786904349083,11.252359106004983,11.555931307660883,11.859503509316783,12.163075710972683,null,0.8631291046760774,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T04:00:01.285","2013-02-19T04:00:00",null,9.519312553006035,9.8228847546619349,10.126456956317835,10.430029157973735,10.733601359629635,11.037173561285535,11.340745762941435,11.644317964597334,11.947890166253234,null,0.9078170418022159,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T05:00:01.290","2013-02-19T05:00:00",null,9.5481325763118114,9.8517047779677114,10.155276979623611,10.458849181279511,10.762421382935411,11.065993584591311,11.369565786247211,11.673137987903111,11.976710189559011,null,0.96464958301792847,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T06:00:01.295","2013-02-19T06:00:00",null,9.5344361841163821,9.838008385772282,10.141580587428182,10.445152789084082,10.748724990739982,11.052297192395882,11.355869394051782,11.659441595707682,11.963013797363582,null,0.98523757852215887,1,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-19T07:00:01.300","2013-02-19T07:00:00",null,9.5678999484062786,9.8714721500621785,10.175044351718078,10.478616553373978,10.782188755029878,11.085760956685778,11.389333158341678,11.692905359997578,11.996477561653478,null,0.96871881399859094,0.9859942747642314,0.98834959192099725,0.99057873137293639,0.99268169312004884,0.99465847716233446,0.99654062792600007,0.99832814541104564,1,null,0.98834959192099725,0.98834959192099725,0.98834959192099725]
["2013-02-19T08:00:01.305","2013-02-19T08:00:00",null,9.7133495164570895,10.016921718112989,10.320493919768889,10.624066121424789,10.927638323080689,11.231210524736589,11.534782726392489,11.838354928048389,12.141927129704289,null,0.95193717925663401,0.97169413488386713,0.97639425438866323,0.98082098886633484,0.98500588274308853,0.9889594508276599,0.99270272273751992,0.99625672809013988,0.99961095207678419,null,0.97639425438866323,0.97639425438866323,0.97639425438866323]
["2013-02-19T09:00:01.310","2013-02-19T09:00:00",null,9.8302472698988979,10.133819471554798,10.437391673210698,10.740963874866598,11.044536076522498,11.348108278178398,11.651680479834297,11.955252681490197,12.258824883146097,null,0.93261096080067107,0.95490198533317461,0.96197845161220774,0.96865535515928958,0.97497475520936239,0.98093665176242606,0.98658310405342287,0.99195617131729497,0.99702430912783591,null,0.96197845161220774,0.96197845161220774,0.96197845161220774]
["2013-02-19T10:00:01.315","2013-02-19T10:00:00",null,9.9674227483747639,10.270994950030664,10.574567151686564,10.878139353342464,11.181711554998364,11.485283756654264,11.788855958310164,12.092428159966063,12.396000361621963,null,0.90974125180082377,0.93462943409101107,0.94416636561416567,0.95315652708307119,0.96166300735014087,0.9697068360328458,0.97731955755739275,0.98456426077619486,0.99140940126304578,null,0.94416636561416567,0.94416636561416567,0.94416636561416567]
["2013-02-19T11:00:01.320","2013-02-19T11:00:00",null,10.053449956455816,10.357022158111716,10.660594359767616,10.964166561423516,11.267738763079416,11.571310964735316,11.874883166391216,12.178455368047116,12.482027569703016,null,0.88229760100100696,0.90989860394496924,0.92200114879960093,0.93340971627768576,0.94419791004037235,0.95440778932260306,0.96408141335932018,0.97328187100293684,0.98198813263598228,null,0.92200114879960093,0.92200114879960093,0.92200114879960093]
["2013-02-19T12:00:01.325","2013-02-19T12:00:00",null,10.379750789558345,10.683322991214245,10.986895192870145,11.290467394526045,11.594039596181945,11.897611797837845,12.201183999493745,12.504756201149645,12.808328402805545,null,0.8456324629401023,0.87612503828634414,0.89096143341222189,0.904956643839255,0.91819478803732757,0.93073895485885305,0.94262068873003813,0.95392410812076722,0.96462818341356937,null,0.89096143341222189,0.89096143341222189,0.89096143341222189]
["2013-02-19T13:00:01.330","2013-02-19T13:00:00",null,10.505587190568804,10.809159392224704,11.112731593880603,11.416303795536503,11.719875997192403,12.023448198848303,12.327020400504203,12.630592602160103,12.934164803816003,null,0.80639119673898496,0.83981740372244851,0.85742970835451471,0.87405362096543826,0.88978377483383908,0.90468325881213041,0.91881516175272582,0.93226360212550952,0.94500755031301065,null,0.85742970835451471,0.85742970835451471,0.85742970835451471]
["2013-02-19T14:00:01.335","2013-02-19T14:00:00",null,10.581274914164096,10.884847115819994,11.188419317475894,11.491991519131794,11.795563720787694,12.099135922443594,12.402708124099494,12.706280325755394,13.009852527411294,null,0.76697117878936305,0.80330998779257723,0.82368768712209628,0.84291927229943919,0.86113092102943267,0.87838572216448985,0.8947467645570244,0.91032971110312721,0.92510301737659173,null,0.82368768712209628,0.82368768712209628,0.82368768712209628]
["2013-02-19T15:00:01.340","2013-02-19T15:00:00",null,10.6463334470084,10.949905648664302,11.253477850320202,11.557050051976102,11.860622253632002,12.164194455287902,12.467766656943802,12.771338858599702,13.074911060255602,null,0.72798226799789911,0.76721264940339284,0.79032419900415807,0.81214242713044926,0.83281454110456421,0.85239311497018055,0.87098329681465425,0.8886797199166051,0.90546135465856192,null,0.79032419900415807,0.79032419900415807,0.79032419900415807]
["2013-02-19T16:00:01.345","2013-02-19T16:00:00",null,10.65526571137562,10.95883791303152,11.26241011468742,11.56598231634332,11.869554517999219,12.173126719655119,12.476698921311019,12.780271122966919,13.083843324622819,null,0.68864636851816163,0.73076832232593492,0.75662423700668191,0.78103962289065687,0.80418271691762888,0.82609557832253999,0.84691489961895283,0.86673531408548721,0.88553579210467193,null,0.75662423700668191,0.75662423700668191,0.75662423700668191]
["2013-02-19T17:00:01.350","2013-02-19T17:00:00",null,10.644032000805915,10.947604202461815,11.251176404117714,11.554748605773614,11.858320807429514,12.161893009085414,12.465465210741314,12.769037412397214,13.072609614053114,null,0.64979415024025999,0.69480767645031283,0.7233869265935704,0.75038895542649364,0.77599251469758712,0.80022914883305751,0.8232670947726739,0.8452009857950562,0.86602030709146882,null,0.7233869265935704,0.7233869265935704,0.7233869265935704]
["2013-02-19T18:00:01.355","2013-02-19T18:00:00",null,10.48345660683032,10.78702880848622,11.09060101014212,11.394173211798019,11.697745413453919,12.001317615109819,12.304889816765719,12.608462018421619,12.912034220077519,null,0.61525300354393886,0.6630739836863867,0.6943134804397415,0.72382854856046408,0.75180845460579449,0.7783057726194107,0.80349925434981739,0.82748353307563427,0.85024809398812584,null,0.6943134804397415,0.6943134804397415,0.6943134804397415]
["2013-02-19T19:00:01.360","2013-02-19T19:00:00",null,10.319665311194239,10.623237512850139,10.926809714506039,11.230381916161939,11.533954117817839,11.837526319473739,12.141098521129638,12.444670722785538,12.748242924441438,null,0.58522270979517377,0.63576702540013219,0.66957213548496408,0.70152663923233705,0.73180928839075554,0.76048317181263314,0.78775858567268109,0.813709133632048,0.83835584530820517,null,0.66957213548496408,0.66957213548496408,0.66957213548496408]
["2013-02-19T20:00:01.365","2013-02-19T20:00:00",null,10.29366678085945,10.59723898251535,10.90081118417125,11.20438338582715,11.50795558748305,11.81152778913895,12.11509999079485,12.418672192450749,12.722244394106649,null,0.55651728194708949,0.60975338858835182,0.64609256757845412,0.6804549625262708,0.71300881037157071,0.74383822958423851,0.77316403114772103,0.80107033353190249,0.82756765154551859,null,0.64609256757845412,0.64609256757845412,0.64609256757845412]
["2013-02-19T21:00:01.370","2013-02-19T21:00:00",null,10.258119117483442,10.561691319139342,10.865263520795242,11.168835722451142,11.472407924107042,11.775980125762942,12.079552327418842,12.383124529074742,12.686696730730642,null,0.52962040120152187,0.58550623964414583,0.62434794311331188,0.66106565521789451,0.69585915732386905,0.72881256790112037,0.76015721274183079,0.78997721031588464,0.81830410504948847,null,0.62434794311331188,0.62434794311331188,0.62434794311331188]
["2013-02-19T22:00:01.375","2013-02-19T22:00:00",null,10.183324704546926,10.486896906202826,10.790469107858726,11.094041309514626,11.397613511170526,11.701185712826426,12.004757914482326,12.308330116138226,12.611902317794126,null,0.50662451449684776,0.56506545146221332,0.60631504613182308,0.64531447173202261,0.68226350962878735,0.71726730790947324,0.75054667755752713,0.7822172814690399,0.81230014926148253,null,0.60631504613182308,0.60631504613182308,0.60631504613182308]
["2013-02-19T23:00:01.380","2013-02-19T23:00:00",null,10.186403350182321,10.489975551838221,10.793547753494121,11.097119955150021,11.400692156805921,11.70426435846182,12.00783656011772,12.31140876177362,12.61498096342952,null,0.48713005910111579,0.54802094650186728,0.59158379909330072,0.63277030491049713,0.67179076012816763,0.70876082764240356,0.74390131843665197,0.77733841021573913,0.80911416221460719,null,0.59158379909330072,0.59158379909330072,0.59158379909330072]
["2013-02-20T00:00:01.385","2013-02-20",null,10.07761635253374,10.38118855418964,10.684760755845542,10.988332957501441,11.291905159157341,11.595477360813241,11.899049562469141,12.202621764125041,12.506193965780941,null,0.46966496179134731,0.53297425520127806,0.57880830647959292,0.62215034808757952,0.663210676199949,0.7021154685215284,0.73908553603576455,0.77426808606495501,0.80770517784404183,null,0.57880830647959292,0.57880830647959292,0.57880830647959292]
["2013-02-20T01:00:01.390","2013-02-20T01:00:00",null,10.022927917841006,10.326500119496906,10.630072321152806,10.933644522808706,11.237216724464606,11.540788926120506,11.844361127776406,12.147933329432306,12.451505531088205,null,0.45509143688385839,0.52074553264181944,0.56878769375460236,0.61422218230096581,0.65725929445562092,0.69803572273213033,0.73678279292267645,0.77364771234955687,0.8086935698651847,null,0.56878769375460236,0.56878769375460236,0.56878769375460236]
["2013-02-20T02:00:01.395","2013-02-20T02:00:00",null,10.023255627451949,10.326827829107849,10.630400030763749,10.933972232419649,11.237544434075549,11.541116635731449,11.844688837387348,12.148261039043248,12.451833240699148,null,0.4442401542687584,0.51213390428739414,0.5622790271472895,0.60971132935340977,0.65463059227173037,0.69718402322454975,0.73762397762152143,0.77609766278494285,0.81267868237596275,null,0.5622790271472895,0.5622790271472895,0.5622790271472895]
["2013-02-20T03:00:01.400","2013-02-20T03:00:00",null,9.9374245867998461,10.240996788455746,10.544568990111646,10.848141191767546,11.151713393423446,11.455285595079346,11.758857796735246,12.062429998391146,12.366002200047046,null,0.43434571924859455,0.50445809391043384,0.55670617851744164,0.60612577957458313,0.65291667844783374,0.6972471120769631,0.73936943587162474,0.77944137196285157,0.81753652401179244,null,0.55670617851744164,0.55670617851744164,0.55670617851744164]
["2013-02-20T04:00:01.405","2013-02-20T04:00:00",null,9.9962973699248447,10.299869571580745,10.603441773236645,10.907013974892543,11.210586176548443,11.514158378204343,11.817730579860243,12.121302781516142,12.424874983172042,null,0.42496650985647327,0.49727647954404497,0.55159598147195854,0.60297133695391458,0.65161284216462401,0.69769924885259227,0.74148291242747266,0.78313206982903383,0.82273083952716008,null,0.55159598147195854,0.55159598147195854,0.55159598147195854]
["2013-02-20T05:00:01.410","2013-02-20T05:00:00",null,9.9918661242505635,10.295438325906463,10.599010527562363,10.902582729218263,11.206154930874163,11.509727132530063,11.813299334185963,12.116871535841863,12.420443737497763,null,0.41583965587400545,0.49034722058730962,0.54672762502739336,0.60005873493416395,0.65054033167359671,0.69838271142040376,0.74382771477550302,0.78704357867866293,0.82814596602597457,null,0.54672762502739336,0.54672762502739336,0.54672762502739336]
["2013-02-20T06:00:01.415","2013-02-20T06:00:00",null,9.9619722396161876,10.265544441272088,10.569116642927987,10.872688844583887,11.176261046239787,11.479833247895687,11.783405449551587,12.086977651207487,12.390549852863387,null,0.40450469205706963,0.48127294064851961,0.53978785126192241,0.5951378044459209,0.64752258156649045,0.69716299360707856,0.74432191078607446,0.78915705523451085,0.83180511946595015,null,0.53978785126192241,0.53978785126192241,0.53978785126192241]
["2013-02-20T07:00:01.420","2013-02-20T07:00:00",null,9.942346433909627,10.245918635565527,10.549490837221427,10.853063038877327,11.156635240533227,11.460207442189127,11.763779643845027,12.067351845500927,12.370924047156826,null,0.39048845201256549,0.46960150295204578,0.53032452339991665,0.58776692352229198,0.64211796987641157,0.69363001787192968,0.74256593772723556,0.7890834515733619,0.83332976673260661,null,0.53032452339991665,0.53032452339991665,0.53032452339991665]
["2013-02-20T08:00:01.425","2013-02-20T08:00:00",null,9.9498855143374172,10.253457715993317,10.557029917649217,10.860602119305117,11.164174320961017,11.467746522616917,11.771318724272817,12.074890925928717,12.378463127584617,null,0.37609367885358114,0.45756204694982727,0.52050369204090174,0.58004905391038952,0.63637688430679473,0.68977108306597845,0.74048400559759431,0.78869440365014609,0.83454948454593181,null,0.52050369204090174,0.52050369204090174,0.52050369204090174]
["2013-02-20T09:00:01.430","2013-02-20T09:00:00",null,9.9324868152281418,10.236059016884042,10.539631218539942,10.843203420195842,11.146775621851742,11.450347823507641,11.753920025163541,12.057492226819441,12.361064428475341,null,0.36262420886332619,0.44642686449886709,0.51156610461567409,0.57318288380606752,0.63147698343602288,0.68673230334140101,0.73920119893185576,0.7890834515733619,0.83653678339695303,null,0.51156610461567409,0.51156610461567409,0.51156610461567409]
["2013-02-20T10:00:01.435","2013-02-20T10:00:00",null,10.082809705722989,10.386381907378889,10.68995410903479,10.99352631069069,11.29709851234659,11.60067071400249,11.90424291565839,12.20781511731429,12.51138731897019,null,0.34857642439261538,0.43469233794997991,0.50201865828378378,0.56569633998634739,0.62594619404111729,0.68305212028395434,0.73727698893324789,0.78883109616370839,0.83787216410636944,null,0.50201865828378378,0.50201865828378378,0.50201865828378378]
["2013-02-20T11:00:01.440","2013-02-20T11:00:00",null,10.002961896562137,10.306534098218037,10.610106299873937,10.913678501529837,11.217250703185737,11.520822904841637,11.824395106497537,12.127967308153437,12.431539509809337,null,0.33505438035868262,0.42348355183787084,0.49299695238867158,0.55873553660340536,0.62094114508298981,0.67989767766328579,0.73586800456268253,0.78909396638209739,0.83972277044382837,null,0.49299695238867158,0.49299695238867158,0.49299695238867158]
["2013-02-20T12:00:01.445","2013-02-20T12:00:00",null,10.001479709686794,10.305051911342694,10.608624112998594,10.912196314654494,11.215768516310394,11.519340717966294,11.822912919622194,12.126485121278094,12.430057322933994,null,0.32161645479463441,0.41235888419564626,0.48404885015470833,0.55185885169034776,0.61600969978601128,0.67681683870376608,0.73453262385326612,0.78943044026163534,0.84163646563370065,null,0.48404885015470833,0.48404885015470833,0.48404885015470833]
["2013-02-20T13:00:01.450","2013-02-20T13:00:00",null,10.019575986597374,10.323148188253274,10.626720389909174,10.930292591565074,11.233864793220974,11.537436994876874,11.841009196532774,12.144581398188674,12.448153599844574,null,0.30722168163565006,0.40030891338469221,0.47420698917822229,0.54409892284350303,0.61021604017271658,0.6728948150454015,0.73238760287121152,0.78896778867727058,0.8427720649771413,null,0.47420698917822229,0.47420698917822229,0.47420698917822229]
["2013-02-20T14:00:01.455","2013-02-20T14:00:00",null,9.940897850877441,10.244470052533341,10.548042254189241,10.851614455845141,11.155186657501041,11.458758859156941,11.762331060812841,12.065903262468741,12.36947546412464,null,0.29326853044355927,0.38870056454063179,0.46480675016862988,0.53678061596355187,0.60487451733505104,0.66942492816266608,0.73068420385605048,0.7889467590597995,0.84434928628747563,null,0.46480675016862988,0.46480675016862988,0.46480675016862988]
["2013-02-20T15:00:01.460","2013-02-20T15:00:00",null,9.946221694329914,10.249793895985814,10.553366097641714,10.856938299297614,11.160510500953514,11.464082702609414,11.767654904265314,12.071227105921214,12.374799307577113,null,0.27910508307675724,0.37689243433059566,0.45521724460179736,0.52928355733509613,0.59935424274888094,0.66577628953142609,0.72881256790112048,0.78876800731129493,0.84576878546677647,null,0.45521724460179736,0.45521724460179736,0.45521724460179736]
["2013-02-20T16:00:01.465","2013-02-20T16:00:00",null,9.8505360046923514,10.154108206348251,10.457680408004151,10.761252609660051,11.064824811315951,11.368397012971851,11.671969214627751,11.975541416283651,12.279113617939551,null,0.2663085608455783,0.36643019963871148,0.44695260493564565,0.52309033498985014,0.59511677482844949,0.66339994275718905,0.72819219418572234,0.78981948818485115,0.84839748765066703,null,0.44695260493564565,0.44695260493564565,0.44695260493564565]
["2013-02-20T17:00:01.470","2013-02-20T17:00:00",null,9.836096266115204,10.139668467771104,10.443240669427004,10.746812871082904,11.050385072738804,11.353957274394704,11.657529476050604,11.961101677706504,12.264673879362403,null,0.25427961965209539,0.3567145163670522,0.4394134870722477,0.5176121196386223,0.59157328428456513,0.66169654374202802,0.72822373861192902,0.79151237239127659,0.8516570783586912,null,0.4394134870722477,0.4394134870722477,0.4394134870722477]
["2013-02-20T18:00:01.475","2013-02-20T18:00:00",null,9.8187744114076647,10.122346613063565,10.425918814719465,10.729491016375365,11.033063218031264,11.336635419687164,11.640207621343064,11.943779822998964,12.247352024654864,null,0.24442724386687381,0.34914385407744758,0.43399836057343327,0.51422635122577132,0.59011172587032201,0.66204353243030156,0.73029515593283478,0.79522409987492992,0.85692499753520779,null,0.43399836057343327,0.43399836057343327,0.43399836057343327]
["2013-02-20T19:00:01.480","2013-02-20T19:00:00",null,9.7686634681419271,10.072235669797827,10.375807871453727,10.679380073109627,10.982952274765527,11.286524476421427,11.590096678077327,11.893668879733227,12.197241081389127,null,0.23935910605633293,0.3462838261013747,0.43323077953573724,0.51542503942162543,0.59316102040363494,0.66685931483118899,0.73677227811394097,0.80327844336637044,0.86648295867583369,null,0.43323077953573724,0.43323077953573724,0.43323077953573724]
["2013-02-20T20:00:01.485","2013-02-20T20:00:00",null,9.6692364710146652,9.9728086726705651,10.276380874326465,10.579953075982365,10.883525277638265,11.187097479294165,11.490669680950065,11.794241882605965,12.097814084261865,null,0.2359628228347464,0.34507462309678505,0.43407196423458222,0.51820094892781376,0.59776650662981112,0.67319974449873288,0.74475301794423254,0.81281537488952516,0.87749196342196711,null,0.43407196423458222,0.43407196423458222,0.43407196423458222]
["2013-02-20T21:00:01.490","2013-02-20T21:00:00",null,9.6527207293224091,9.956292930978309,10.259865132634209,10.563437334290107,10.867009535946007,11.170581737601907,11.474153939257807,11.777726140913707,12.081298342569607,null,0.2335023575906249,0.34478020845218932,0.43580690767594993,0.52184958755905375,0.60322369236356777,0.68037084405638615,0.75354339804716242,0.82314091706784709,0.88926854920579657,null,0.43580690767594993,0.43580690767594993,0.43580690767594993]
["2013-02-20T22:00:01.495","2013-02-20T22:00:00",null,9.5681191395649474,9.8716913412208473,10.175263542876747,10.478835744532647,10.782407946188547,11.085980147844447,11.389552349500347,11.693124551156247,11.996696752812147,null,0.23584715993865524,0.34915436888618312,0.44209476329981601,0.52993547547670095,0.6130024644876404,0.69175838191699979,0.76644506836569704,0.83748311618315363,0.90497767345672619,null,0.44209476329981601,0.44209476329981601,0.44209476329981601]
["2013-02-20T23:00:01.500","2013-02-20T23:00:00",null,9.5055453223103576,9.8091175239662576,10.112689725622158,10.416261927278057,10.719834128933957,11.023406330589857,11.326978532245757,11.630550733901657,11.934122935557557,null,0.24183008610919002,0.35706150505532575,0.45182096138021083,0.54136507257225686,0.6260513421284728,0.70632139201575317,0.78245912206995794,0.85486409502303762,0.92365197377108432,null,0.45182096138021083,0.45182096138021083,0.45182096138021083]
["2013-02-21T00:00:01.505","2013-02-21",null,9.5004575453781044,9.8040297470340043,10.107601948689904,10.411174150345802,10.714746352001702,11.018318553657602,11.321890755313502,11.625462956969402,11.929035158625302,null,0.24803382326317158,0.36517893739917962,0.46174694082658135,0.55299445103378841,0.63928948632654536,0.7210736686717466,0.79864141271398781,0.87241331080269058,0.94249451102521142,null,0.46174694082658135,0.46174694082658135,0.46174694082658135]
["2013-02-21T01:00:01.510","2013-02-21T01:00:00",null,9.4937751060787221,9.797347307734622,10.100919509390522,10.404491711046422,10.708063912702322,11.011636114358222,11.315208316014122,11.618780517670022,11.922352719325922,null,0.25475278604519569,0.37380108056234046,0.47216711628352331,0.56510751069715581,0.65300079691771817,0.7362885969121048,0.81528635494238244,0.8904146633579727,0.96177867024623209,null,0.47216711628352331,0.47216711628352331,0.47216711628352331]
["2013-02-21T02:00:01.515","2013-02-21T02:00:00",null,9.5436467483166894,9.8472189499725893,10.150791151628489,10.454363353284389,10.757935554940289,11.061507756596189,11.365079958252089,11.668652159907989,11.972224361563889,null,0.26242859642215594,0.38334852689423077,0.48347053567425247,0.57807226986810378,0.66753226259026488,0.75229213580763021,0.83268836339973751,0.90914153771600859,0.98176732165253544,null,0.48347053567425247,0.48347053567425247,0.48347053567425247]
["2013-02-21T03:00:01.520","2013-02-21T03:00:00",null,9.5102601225490435,9.8138323242049434,10.117404525860843,10.420976727516743,10.724548929172643,11.028121130828543,11.331693332484443,11.635265534140343,11.938837735796243,null,0.27208119084140187,0.39480966841599335,0.49664559101991163,0.592856090950304,0.68383021613038597,0.77002010333578774,0.85177274125478253,0.92950872223679215,1,null,0.49664559101991163,0.49664559101991163,0.49664559101991163]
["2013-02-21T04:00:01.525","2013-02-21T04:00:00",null,9.6072695553355061,9.910841756991406,10.214413958647306,10.517986160303206,10.821558361959106,11.125130563615006,11.428702765270906,11.732274966926806,12.035847168582706,null,0.28001987143675117,0.40459895534880158,0.50816982139408762,0.60602063148722762,0.69855094836017273,0.78620239397981762,0.86934298665190668,0.94839331872586152,1,null,0.50816982139408762,0.50816982139408762,0.50816982139408762]
["2013-02-21T05:00:01.530","2013-02-21T05:00:00",null,9.8162566677489984,10.119828869404898,10.423401071060798,10.726973272716698,11.030545474372598,11.334117676028498,11.637689877684398,11.941262079340298,12.244834280996198,null,0.27988317892318887,0.40652316534740945,0.51202875620003885,0.61169862820443111,0.70595337371000833,0.79523461468366541,0.87992088423988202,0.96044328953681557,1,null,0.51202875620003885,0.51202875620003885,0.51202875620003885]
["2013-02-21T06:00:01.535","2013-02-21T06:00:00",null,9.8930827744914964,10.196654976147396,10.500227177803296,10.803799379459196,11.107371581115096,11.410943782770996,11.714515984426896,12.018088186082796,12.321660387738696,null,0.27929434963399741,0.40798472376165257,0.51542503942162532,0.61691397333726983,0.71289314747547927,0.80380418380314844,0.89004664505222819,0.97204112357214045,1,null,0.51542503942162532,0.51542503942162532,0.51542503942162532]
["2013-02-21T07:00:01.540","2013-02-21T07:00:00",null,9.9571618696512445,10.260734071307144,10.564306272963044,10.867878474618944,11.171450676274844,11.475022877930744,11.778595079586644,12.082167281242544,12.385739482898444,null,0.27895787575445941,0.4096881227768136,0.51904213362665863,0.62233961464481979,0.72002218779819027,0.81255250467113604,0.90034064280434334,0.98378616492976323,1,null,0.51904213362665863,0.51904213362665863,0.51904213362665863]
["2013-02-21T08:00:01.545","2013-02-21T08:00:00",null,10.13483566558377,10.43840786723967,10.74198006889557,11.04555227055147,11.34912447220737,11.65269667386327,11.95626887551917,12.25984107717507,12.56341327883097,null,0.27640277723171786,0.40919392676624217,0.52049317723216615,0.62563074977905075,0.72504826637378894,0.81922940821821788,0.90858425285302391,0.99352287781889359,1,null,0.52049317723216615,0.52049317723216615,0.52049317723216615]
["2013-02-21T09:00:01.550","2013-02-21T09:00:00",null,10.081138744696526,10.384710946352426,10.688283148008326,10.991855349664226,11.295427551320126,11.598999752976026,11.902571954631926,12.206144156287825,12.509716357943725,null,0.27361635291679393,0.40849994938969508,0.52177598389790469,0.62878519239971931,0.72996919686203199,0.82582219329541529,0.91676477404929113,1,1,null,0.52177598389790469,0.52177598389790469,0.52177598389790469]
["2013-02-21T10:00:01.555","2013-02-21T10:00:00",null,10.260793479413415,10.564365681069315,10.867937882725215,11.171510084381115,11.475082286037015,11.778654487692915,12.082226689348815,12.385798891004715,12.689371092660615,null,0.26948403308371804,0.40659676900855835,0.52197576526388034,0.63098278742545177,0.73404894265143006,0.83168945656985893,0.92433543633889581,1,1,null,0.52197576526388034,0.52197576526388034,0.52197576526388034]
["2013-02-21T11:00:01.560","2013-02-21T11:00:00",null,10.403707715883041,10.707279917538941,11.010852119194841,11.31442432085074,11.61799652250664,11.92156872416254,12.22514092581844,12.52871312747434,12.83228532913024,null,0.26171358942813772,0.40113958327480165,0.51869514493838498,0.62977358442086218,0.73479549407165501,0.8342866143275427,0.92869908196415407,1,1,null,0.51869514493838498,0.51869514493838498,0.51869514493838498]
["2013-02-21T12:00:01.565","2013-02-21T12:00:00",null,10.78072598183255,11.084298183488448,11.387870385144348,11.691442586800248,11.995014788456148,12.298586990112048,12.602159191767948,12.905731393423848,13.209303595079747,null,0.24564696168019898,0.3875334207709844,0.50741275516512696,0.62068878967333663,0.72781366107124179,0.8292920801781507,0.92559721338716328,0.99869616371679026,1,null,0.50741275516512696,0.50741275516512696,0.50741275516512696]
["2013-02-21T13:00:01.570","2013-02-21T13:00:00",null,10.963580182602513,11.267152384258413,11.570724585914313,11.874296787570213,12.177868989226113,12.481441190882013,12.785013392537913,13.088585594193813,13.392157795849712,null,0.22125260541369515,0.36578879630584221,0.48818116998778405,0.60384406607896635,0.71324013616375281,0.81687409106145203,0.91522961197389918,0.99028431672834072,0.99345978896648046,null,0.48818116998778405,0.48818116998778405,0.48818116998778405]
["2013-02-21T14:00:01.575","2013-02-21T14:00:00",null,11.059587116933384,11.363159318589284,11.666731520245184,11.970303721901084,12.273875923556984,12.577448125212884,12.881020326868784,13.184592528524684,13.488164730180584,null,0.19057039352332525,0.33794558277407405,0.46302974749231973,0.58125825691497912,0.69308324781768049,0.79903046063720329,0.8995835765753829,0.97674124307693688,0.98192504378356893,null,0.46302974749231973,0.46302974749231973,0.46302974749231973]
["2013-02-21T15:00:01.580","2013-02-21T15:00:00",null,11.151993167612821,11.45556536926872,11.75913757092462,12.06270977258052,12.36628197423642,12.66985417589232,12.97342637754822,13.27699857920412,13.58057078086002,null,0.15905751174284594,0.30927169935219651,0.43705816991548158,0.55784177786088252,0.67210620439023427,0.78036667513158076,0.88312790090422832,0.96238852915289474,0.96959117313675469,null,0.43705816991548158,0.43705816991548158,0.43705816991548158]
["2013-02-21T16:00:01.585","2013-02-21T16:00:00",null,11.242128166050129,11.545700367706029,11.849272569361929,12.152844771017829,12.456416972673729,12.759989174329629,13.063561375985529,13.367133577641429,13.670705779297329,null,0.1268296229683484,0.27988280893630074,0.41036107053588966,0.53369977700403215,0.6504036391600343,0.76097736782320446,0.86595721823905558,0.94732080823483444,0.95654229549592229,null,0.41036107053588966,0.41036107053588966,0.41036107053588966]
["2013-02-21T17:00:01.590","2013-02-21T17:00:00",null,11.041864181029325,11.345436382685225,11.649008584341125,11.952580785997025,12.256152987652925,12.559725189308825,12.863297390964725,13.166869592620625,13.470441794276525,null,9.5674244684878201E-2,0.25165054748131677,0.38488368896962294,0.51085109762165593,0.63004696944798622,0.74298653007665794,0.85022706437065487,0.93374619015722393,0.94502857993048195,null,0.38488368896962294,0.38488368896962294,0.38488368896962294]
["2013-02-21T18:00:01.595","2013-02-21T18:00:00",null,10.904262895130987,11.207835096786887,11.511407298442787,11.814979500098687,12.118551701754587,12.422123903410487,12.725696105066387,13.029268306722287,13.332840508378187,null,7.0974958965043064E-2,0.22972717126767001,0.36558901493986667,0.49404843326222786,0.61562065186279513,0.73081038156087719,0.84019593683692873,0.92576545032693236,0.93900359452500493,null,0.36558901493986667,0.36558901493986667,0.36558901493986667]
["2013-02-21T19:00:01.600","2013-02-21T19:00:00",null,10.727740936482469,11.031313138138369,11.334885339794269,11.638457541450169,11.942029743106069,12.245601944761969,12.549174146417869,12.852746348073769,13.156318549729669,null,5.1154544498508703E-2,0.21259854783743951,0.35099446041490662,0.48186176993771151,0.60572621684263128,0.72308199714023913,0.83453896973719632,0.9220747524607501,0.93719504742248827,null,0.35099446041490662,0.35099446041490662,0.35099446041490662]
["2013-02-21T20:00:01.605","2013-02-21T20:00:00",null,10.573023691219875,10.876595892875775,11.180168094531675,11.483740296187575,11.787312497843475,12.090884699499375,12.394456901155275,12.698029102811175,13.001601304467075,null,3.4688354018618611E-2,0.1987400299239688,0.33960692255429298,0.47280851961639264,0.59889159116451596,0.71836084801797184,0.83181563427468574,0.92125459737937632,0.93819395425236662,null,0.33960692255429298,0.33960692255429298,0.33960692255429298]
["2013-02-21T21:00:01.610","2013-02-21T21:00:00",null,10.46479179612701,10.76836399778291,11.071936199438809,11.375508401094709,11.679080602750609,11.982652804406509,12.286225006062409,12.589797207718309,12.893369409374209,null,2.279610533869799E-2,0.18923464282702077,0.33235170452675522,0.46768780776217395,0.59578972258752516,0.71717267463085332,0.83245703760755507,0.92363094415361335,0.94222112599808683,null,0.33235170452675522,0.33235170452675522,0.33235170452675522]
["2013-02-21T22:00:01.615","2013-02-21T22:00:00",null,10.059153354517612,10.362725556173512,10.666297757829412,10.969869959485312,11.273442161141212,11.577014362797112,11.880586564453012,12.184158766108911,12.487730967764811,null,1.9094892663780168E-2,0.18770999556036427,0.33287744496353333,0.47014827300629547,0.60009027936037007,0.72320817484506594,0.84013284798451537,0.93287346103217239,0.95295674571709565,null,0.33287744496353333,0.33287744496353333,0.33287744496353333]
["2013-02-21T23:00:01.620","2013-02-21T23:00:00",null,9.7687109577986071,10.072283159454507,10.375855361110407,10.679427562766307,10.982999764422207,11.286571966078107,11.590144167734007,11.893716369389907,12.197288571045807,null,2.2690957251342372E-2,0.19328284419021213,0.3403219295483112,0.47934873064991224,0.6109520767842056,0.7356471935792358,0.85406496955913502,0.9482145669773574,0.96964374718043256,null,0.3403219295483112,0.3403219295483112,0.3403219295483112]
["2013-02-22T00:00:01.625","2013-02-22",null,9.7114922884099339,10.015064490065834,10.318636691721734,10.622208893377634,10.925781095033534,11.229353296689434,11.532925498345334,11.836497700001233,12.140069901657133,null,2.5750766593390914E-2,0.19835098200075302,0.34728273293125322,0.48809705151789984,0.62139328185861864,0.74767613477271877,0.86760804321053886,0.96319816942553327,0.98598375995549592,null,0.34728273293125322,0.34728273293125322,0.34728273293125322]
["2013-02-22T01:00:01.630","2013-02-22T01:00:00",null,9.5708677112479883,9.8744399129038882,10.178012114559788,10.481584316215686,10.785156517871586,11.088728719527486,11.392300921183386,11.695873122839286,11.999445324495186,null,2.9031386918886258E-2,0.20366096041221182,0.35450640653258431,0.49712927222174758,0.63211838676889187,0.76001000541953301,0.88146656112400956,0.978497216135776,1,null,0.35450640653258431,0.35450640653258431,0.35450640653258431]
["2013-02-22T02:00:01.635","2013-02-22T02:00:00",null,9.3887233372442225,9.6922955389001224,9.9958677405560223,10.299439942211922,10.603012143867822,10.906584345523722,11.210156547179622,11.513728748835522,11.817300950491422,null,3.4898650193329855E-2,0.21151552253767664,0.36423260461297913,0.5086114433609813,0.64525138287960881,0.77470970803184869,0.89764885176803944,0.99607797634163564,1,null,0.36423260461297913,0.36423260461297913,0.36423260461297913]
["2013-02-22T03:00:01.640","2013-02-22T03:00:00",null,9.1141368509598415,9.4177090526157414,9.7212812542716414,10.024853455927541,10.328425657583441,10.631997859239341,10.935570060895241,11.239142262551141,11.542714464207041,null,4.1007754068691379E-2,0.21965398449900161,0.37428476176417641,0.5204616328059597,0.65879445653101265,0.78985103261105793,0.91429379399643407,1,1,null,0.37428476176417641,0.37428476176417641,0.37428476176417641]
["2013-02-22T04:00:01.645","2013-02-22T04:00:00",null,8.9659966919791572,9.2695688936350571,9.573141095290957,9.876713296946857,10.180285498602757,10.483857700258657,10.787429901914557,11.091002103570457,11.394574305226357,null,4.7873924173013366E-2,0.22857054230675819,0.38511501476180526,0.53308991809736961,0.67311562602884811,0.80577045303669881,0.93171683207126033,1,1,null,0.38511501476180526,0.38511501476180526,0.38511501476180526]
["2013-02-22T05:00:01.650","2013-02-22T05:00:00",null,8.9346523757518046,9.2382245774077045,9.5417967790636045,9.8453689807195026,10.148941182375403,10.452513384031302,10.756085585687202,11.059657787343102,11.363229988999002,null,5.261610291275183E-2,0.23543671241108016,0.39396848371714849,0.54381502300764284,0.68559670399796024,0.8199128707860297,0.94742595632218995,1,1,null,0.39396848371714849,0.39396848371714849,0.39396848371714849]
["2013-02-22T06:00:01.655","2013-02-22T06:00:00",null,8.8960611265274618,9.1996333281833618,9.5032055298392617,9.8067777314951616,10.110349933151062,10.413922134806961,10.717494336462861,11.021066538118761,11.324638739774661,null,5.544458646261801E-2,0.2404627909866788,0.40104494999618173,0.55282621409401944,0.6964164421868535,0.83244652279881959,0.96156837407152085,1,1,null,0.40104494999618173,0.40104494999618173,0.40104494999618173]
["2013-02-22T07:00:01.660","2013-02-22T07:00:00",null,8.9283913807539594,9.2319635824098594,9.5355357840657593,9.8391079857216575,10.142680187377557,10.446252389033457,10.749824590689357,11.053396792345257,11.356968994001157,null,5.6296285970198534E-2,0.2435646595636696,0.40626029512902051,0.56002885807787939,0.70548020731690797,0.84326626098771285,0.97403893723189738,1,1,null,0.40626029512902051,0.40626029512902051,0.40626029512902051]
["2013-02-22T08:00:01.665","2013-02-22T08:00:00",null,8.8115621625883822,9.1151343642442821,9.4187065659001821,9.722278767556082,10.025850969211982,10.329423170867882,10.632995372523782,10.936567574179682,11.240139775835582,null,5.5928267664453864E-2,0.24552041398848412,0.41039261496209639,0.5662010508056543,0.71356609523455516,0.8531606960078767,0.98562625645848667,1,1,null,0.41039261496209639,0.41039261496209639,0.41039261496209639]
["2013-02-22T09:00:01.670","2013-02-22T09:00:00",null,8.9233062533602343,9.2268784550161342,9.5304506566720342,9.8340228583279341,10.137595059983834,10.441167261639734,10.744739463295634,11.048311664951534,11.351883866607434,null,8.4539062233918064E-2,0.27638137762735859,0.44335654034808325,0.60114176023392685,0.75035741100028663,0.89169747002371147,1,1,1,null,0.44335654034808325,0.44335654034808325,0.44335654034808325]
["2013-02-22T10:00:01.675","2013-02-22T10:00:00",null,8.9843579717469346,9.2879301734028346,9.5915023750587345,9.8950745767146344,10.198646778370534,10.502218980026434,10.805791181682334,11.109363383338234,11.412935584994134,null,0.13226577908463397,0.32631620431254249,0.49537329916290845,0.65510375866483106,0.80615950095991418,0.94922398861597113,1,1,1,null,0.49537329916290845,0.49537329916290845,0.49537329916290845]
["2013-02-22T11:00:01.680","2013-02-22T11:00:00",null,9.0757922285227259,9.3793644301786259,9.6829366318345258,9.9865088334904257,10.290081035146326,10.593653236802226,10.897225438458126,11.200797640114025,11.504369841769925,null,0.19134848936975685,0.38777526137190238,0.55906149567420749,0.7208738873057714,0.87389589883440455,1,1,1,1,null,0.55906149567420749,0.55906149567420749,0.55906149567420749]
["2013-02-22T12:00:01.685","2013-02-22T12:00:00",null,9.1377728004717351,9.4413450021276351,9.744917203783535,10.048489405439437,10.352061607095337,10.655633808751237,10.959206010407136,11.262778212063036,11.566350413718936,null,0.24957950014729918,0.44835107449747502,0.62183490382551265,0.78571871277798222,0.94068596392269432,1,1,1,1,null,0.62183490382551265,0.62183490382551265,0.62183490382551265]
["2013-02-22T13:00:01.690","2013-02-22T13:00:00",null,9.3227613243487628,9.6263335260046627,9.9299057276605627,10.233477929316464,10.537050130972364,10.840622332628264,11.144194534284164,11.447766735940064,11.751338937595964,null,0.23708790736945154,0.43824634330259993,0.6139698268913123,0.7799565975908942,0.93691114758662752,0.9981073344275988,0.9998738222951733,1,1,null,0.6139698268913123,0.6139698268913123,0.6139698268913123]
["2013-02-22T14:00:01.695","2013-02-22T14:00:00",null,9.6063699908236675,9.9099421924795674,10.213514394135467,10.517086595791367,10.820658797447267,11.124230999103167,11.427803200759067,11.731375402414967,12.034947604070867,null,0.22026421339255234,0.42387259976108665,0.60189882646288717,0.77005164776199475,0.92905658546116276,0.9921874971094774,0.99579407650577523,0.99765519765196964,0.99930602262345292,null,0.60189882646288717,0.60189882646288717,0.60189882646288717]
["2013-02-22T15:00:01.700","2013-02-22T15:00:00",null,9.7754589707244772,10.079031172380377,10.382603374036277,10.686175575692177,10.989747777348077,11.293319979003977,11.596892180659877,11.900464382315777,12.204036583971677,null,0.20182123887037659,0.40787957567429683,0.58821906029792104,0.75854844700528989,0.91961428721662808,0.98470095328975726,0.99014762421477842,0.99376471841981173,0.99708739798024937,null,0.58821906029792104,0.58821906029792104,0.58821906029792104]
["2013-02-22T16:00:01.705","2013-02-22T16:00:00",null,9.8061371401570128,10.109709341812913,10.413281543468813,10.716853745124713,11.020425946780612,11.323998148436512,11.627570350092412,11.931142551748312,12.234714753404212,null,0.18203236883004892,0.39059323011303293,0.57328803189342303,0.74583604324399544,0.90899433039371047,0.97606829531786088,0.98339711700654764,0.98880172869662641,0.9938172924634896,null,0.57328803189342303,0.57328803189342303,0.57328803189342303]
["2013-02-22T17:00:01.710","2013-02-22T17:00:00",null,9.7604311385914606,10.064003340247361,10.36757554190326,10.67114774355916,10.97471994521506,11.27829214687096,11.58186434852686,11.88543655018276,12.18900875183866,null,0.17911976681029823,0.39010954891119709,0.57509657899593969,0.74981064094603789,0.9150088009904519,0.98401749072194578,0.99317588913062027,1,1,null,0.57509657899593969,0.57509657899593969,0.57509657899593969]
["2013-02-22T18:00:01.715","2013-02-22T18:00:00",null,9.6812053803100113,9.9847775819659113,10.288349783621811,10.591921985277711,10.895494186933611,11.199066388589511,11.502638590245411,11.806210791901311,12.109782993557211,null,0.18065492888569029,0.39395796890841278,0.58113207921015231,0.75790704367242068,0.92503992852417805,0.99588870978439525,1,1,1,null,0.58113207921015231,0.58113207921015231,0.58113207921015231]
["2013-02-22T19:00:01.720","2013-02-22T19:00:00",null,9.5291775147540108,9.8327497164099107,10.136321918065811,10.439894119721711,10.74346632137761,11.04703852303351,11.35061072468941,11.65418292634531,11.95775512800121,null,0.18288406833762944,0.39852139589964669,0.58789310122711869,0.76672896820155723,0.93580709266939355,1,1,1,1,null,0.58789310122711869,0.58789310122711869,0.58789310122711869]
["2013-02-22T20:00:01.725","2013-02-22T20:00:00",null,9.5266447311858915,9.8302169328417914,10.133789134497691,10.437361336153591,10.740933537809491,11.044505739465391,11.348077941121291,11.651650142777191,11.955222344433091,null,0.18529195953807312,0.40326357463938517,0.59482236018385404,0.77571912967046275,0.94674249375437802,1,1,1,1,null,0.59482236018385404,0.59482236018385404,0.59482236018385404]
["2013-02-22T21:00:01.730","2013-02-22T21:00:00",null,9.4898530866844162,9.7934252883403161,10.096997489996216,10.400569691652116,10.704141893308016,11.007714094963916,11.311286296619816,11.614858498275716,11.918430699931616,null,0.18577564073990896,0.40614463223292918,0.59995358684680833,0.78297434769800056,0.95599552544167254,1,1,1,1,null,0.59995358684680833,0.59995358684680833,0.59995358684680833]
["2013-02-22T22:00:01.735","2013-02-22T22:00:00",null,9.4283115266761079,9.7318837283320079,10.035455929987908,10.339028131643808,10.642600333299708,10.946172534955608,11.249744736611508,11.553316938267407,11.856889139923307,null,0.18583872959232234,0.40862612709452184,0.60471679520401789,0.78988257703726483,0.96492259805816472,1,1,1,1,null,0.60471679520401789,0.60471679520401789,0.60471679520401789]
["2013-02-22T23:00:01.740","2013-02-22T23:00:00",null,9.3259056295907623,9.6294778312466622,9.9330500329025622,10.236622234558464,10.540194436214364,10.843766637870264,11.147338839526164,11.450911041182064,11.754483242837964,null,0.18781551363460799,0.41298977271978005,0.61132009508995078,0.79859935347904576,0.97563718815970235,1,1,1,1,null,0.61132009508995078,0.61132009508995078,0.61132009508995078]
["2013-02-23T00:00:01.745","2013-02-23",null,9.1949534228337431,9.498525624489643,9.8020978261455429,10.105670027801443,10.409242229457343,10.712814431113243,11.016386632769143,11.319958834425043,11.623531036080943,null,0.19751016728879617,0.42486099178222952,0.62523118704709935,0.81443465543480209,0.99328103721797534,1,1,1,1,null,0.62523118704709935,0.62523118704709935,0.62523118704709935]
["2013-02-23T01:00:01.750","2013-02-23T01:00:00",null,9.0748161201386228,9.3783883217945228,9.6819605234504227,9.9855327251063244,10.289104926762224,10.592677128418124,10.896249330074024,11.199821531729924,11.503393733385824,null,0.21035926356365292,0.43981304980419866,0.64214951430261857,0.83321410383651584,1,1,1,1,1,null,0.64214951430261857,0.64214951430261857,0.64214951430261857]
["2013-02-23T02:00:01.755","2013-02-23T02:00:00",null,8.9818940386480257,9.2854662403039256,9.5890384419598256,9.8926106436157255,10.196182845271625,10.499755046927525,10.803327248583425,11.106899450239325,11.410471651895225,null,0.22465940344401725,0.4561846070054687,0.66046631111996756,0.85336047737385268,1,1,1,1,1,null,0.66046631111996756,0.66046631111996756,0.66046631111996756]
["2013-02-23T03:00:01.760","2013-02-23T03:00:00",null,8.9456729549817542,9.2492451566376541,9.5528173582935541,9.856389559949454,10.159961761605356,10.463533963261256,10.767106164917156,11.070678366573055,11.374250568228955,null,0.24118868277632072,0.47473272961500007,0.68089658449316448,0.87555723861462409,1,1,1,1,1,null,0.68089658449316448,0.68089658449316448,0.68089658449316448]
["2013-02-23T04:00:01.765","2013-02-23T04:00:00",null,8.8909754111577541,9.1945476128136541,9.498119814469554,9.8016920161254539,10.105264217781354,10.408836419437254,10.712408621093154,11.015980822749054,11.319553024404954,null,0.25698192549713483,0.49257636003924876,0.7006539101072855,0.89712311133126177,1,1,1,1,1,null,0.7006539101072855,0.7006539101072855,0.7006539101072855]
["2013-02-23T05:00:01.770","2013-02-23T05:00:00",null,8.9367410647640497,9.2403132664199497,9.5438854680758496,9.8474576697317495,10.151029871387649,10.454602073043549,10.758174274699449,11.061746476355349,11.365318678011249,null,0.26989411062440499,0.50762305133983798,0.71769841506763155,0.91603925224653782,1,1,1,1,1,null,0.71769841506763155,0.71769841506763155,0.71769841506763155]
["2013-02-23T06:00:01.775","2013-02-23T06:00:00",null,8.8832266928952759,9.1867988945511758,9.4903710962070758,9.7939432978629757,10.097515499518876,10.401087701174776,10.704659902830675,11.008232104486575,11.311804306142475,null,0.28190202220041677,0.52180752832411115,0.73391225013786809,0.93416678250664675,1,1,1,1,1,null,0.73391225013786809,0.73391225013786809,0.73391225013786809]
["2013-02-23T07:00:01.780","2013-02-23T07:00:00",null,8.8053259439232257,9.1088981455791256,9.4124703472350255,9.7160425488909254,10.019614750546825,10.323186952202725,10.626759153858625,10.930331355514525,11.233903557170425,null,0.2945092778743556,0.53659134940631137,0.7507254293060317,0.95288314205594715,1,1,1,1,1,null,0.7507254293060317,0.7507254293060317,0.7507254293060317]
["2013-02-23T08:00:01.785","2013-02-23T08:00:00",null,9.0255081328116766,9.3290803344675766,9.6326525361234765,9.9362247377793764,10.239796939435276,10.543369141091176,10.846941342747076,11.150513544402976,11.454085746058876,null,0.30617020076209384,0.5504078080848398,0.76656073126178803,0.97061110958410468,1,1,1,1,1,null,0.76656073126178803,0.76656073126178803,0.76656073126178803]
["2013-02-23T09:00:01.790","2013-02-23T09:00:00",null,9.1615012966980522,9.4650734983539522,9.7686457000098521,10.072217901665752,10.375790103321652,10.679362304977552,10.982934506633452,11.286506708289352,11.590078909945252,null,0.31374086305169846,0.5602286394438547,0.77849503917665086,0.98452220154125325,1,1,1,1,1,null,0.77849503917665086,0.77849503917665086,0.77849503917665086]
["2013-02-23T10:00:01.795","2013-02-23T10:00:00",null,9.2757909844117084,9.5793631860676083,9.8829353877235082,10.186507589379408,10.490079791035308,10.793651992691208,11.097224194347108,11.400796396003008,11.704368597658908,null,0.31867230834867705,0.56747334266265692,0.78790579299497887,0.99597282825428024,1,1,1,1,1,null,0.78790579299497887,0.78790579299497887,0.78790579299497887]
["2013-02-23T11:00:01.800","2013-02-23T11:00:00",null,9.4911107589505797,9.7946829606064796,10.09825516226238,10.401827363918279,10.705399565574179,11.008971767230079,11.312543968885979,11.616116170541879,11.919688372197779,null,0.32301492435646417,0.57408715735732541,0.79665411386296647,1,1,1,1,1,1,null,0.79665411386296647,0.79665411386296647,0.79665411386296647]
["2013-02-23T12:00:01.805","2013-02-23T12:00:00",null,9.6079397217723574,9.9115119234282574,10.215084125084157,10.518656326740057,10.822228528395957,11.125800730051857,11.429372931707757,11.732945133363657,12.036517335019557,null,0.3247288381803608,0.5781353587205168,0.80288939544315474,1,1,1,1,1,1,null,0.80288939544315474,0.80288939544315474,0.80288939544315474]
["2013-02-23T13:00:01.810","2013-02-23T13:00:00",null,9.8422554289677127,10.145827630623613,10.449399832279513,10.752972033935412,11.056544235591312,11.360116437247212,11.663688638903112,11.967260840559012,12.270833042214912,null,0.32120637725394752,0.57704181861201831,0.80408808363900885,1,1,1,1,1,1,null,0.80408808363900885,0.80408808363900885,0.80408808363900885]
["2013-02-23T14:00:01.815","2013-02-23T14:00:00",null,9.9325175563578458,10.236089758013746,10.539661959669646,10.843234161325546,11.146806362981446,11.450378564637345,11.753950766293245,12.057522967949145,12.361095169605045,null,0.31661140583650693,0.57489679762996371,0.80424580577004223,1,1,1,1,1,1,null,0.80424580577004223,0.80424580577004223,0.80424580577004223]
["2013-02-23T15:00:01.820","2013-02-23T15:00:00",null,10.05855039685634,10.36212259851224,10.66569480016814,10.96926700182404,11.27283920347994,11.57641140513584,11.87998360679174,12.18355580844764,12.48712801010354,null,0.30904074354690231,0.56982865981942288,0.80154349992500284,0.99952683360689976,1,1,1,1,1,null,0.80154349992500284,0.80154349992500284,0.80154349992500284]
["2013-02-23T16:00:01.825","2013-02-23T16:00:00",null,10.207890619410854,10.511462821066754,10.815035022722654,11.118607224378554,11.422179426034454,11.725751627690354,12.029323829346254,12.332896031002154,12.636468232658054,null,0.29739033546789961,0.56075437988063292,0.79491917042159876,0.99520524721658377,0.99786549382668088,0.99993691114758665,1,1,1,null,0.79491917042159876,0.79491917042159876,0.79491917042159876]
["2013-02-23T17:00:01.830","2013-02-23T17:00:00",null,10.290839289745689,10.594411491401589,10.89798369305749,11.20155589471339,11.50512809636929,11.80870029802519,12.11227249968109,12.41584470133699,12.71941690299289,null,0.28504595001234984,0.55098612256529578,0.787590348732912,0.99018968344972069,0.9950264954680792,0.99916933010989062,1,1,1,null,0.787590348732912,0.787590348732912,0.787590348732912]
["2013-02-23T18:00:01.835","2013-02-23T18:00:00",null,10.107945545585032,10.411517747240932,10.715089948896832,11.018662150552732,11.322234352208632,11.625806553864532,11.929378755520432,12.232950957176332,12.536523158832232,null,0.2748676151563258,0.54337340104074894,0.78239603321754436,0.98728759623870554,0.99429045885658984,1,1,1,1,null,0.78239603321754436,0.78239603321754436,0.78239603321754436]
["2013-02-23T19:00:01.840","2013-02-23T19:00:00",null,9.8806975105744819,10.184269712230382,10.487841913886282,10.791414115542182,11.094986317198082,11.398558518853982,11.702130720509881,12.005702922165781,12.309275123821681,null,0.26916858882165118,0.54016638437640252,0.78152330409249271,0.98863349175685744,0.9977182865043831,1,1,1,1,null,0.78152330409249271,0.78152330409249271,0.78152330409249271]
["2013-02-23T20:00:01.845","2013-02-23T20:00:00",null,9.6983478887198906,10.001920090375791,10.30549229203169,10.60906449368759,10.91263669534349,11.21620889699939,11.51978109865529,11.82335330031119,12.12692550196709,null,0.26596157215730476,0.53943034776491317,0.78310052540282704,0.99239779328418865,1,1,1,1,1,null,0.78310052540282704,0.78310052540282704,0.78310052540282704]
["2013-02-23T21:00:01.850","2013-02-23T21:00:00",null,9.6308334815108445,9.9344056831667444,10.237977884822644,10.541550086478544,10.845122288134444,11.148694489790344,11.452266691446244,11.755838893102144,12.059411094758044,null,0.2664452533591406,0.54227986093225045,0.78816866321336787,0.99956889284184192,1,1,1,1,1,null,0.78816866321336787,0.78816866321336787,0.78816866321336787]
["2013-02-23T22:00:01.855","2013-02-23T22:00:00",null,9.5992796467439163,9.9028518483998162,10.206424050055716,10.509996251711616,10.813568453367516,11.117140655023416,11.420712856679316,11.724285058335216,12.027857259991116,null,0.26856924472372412,0.54672762502739314,0.79479299271677195,1,1,1,1,1,1,null,0.79479299271677195,0.79479299271677195,0.79479299271677195]
["2013-02-23T23:00:01.860","2013-02-23T23:00:00",null,9.5893518851203048,9.8929240867762047,10.196496288432105,10.500068490088005,10.803640691743905,11.107212893399804,11.410785095055704,11.714357296711604,12.017929498367504,null,0.27120846171635016,0.55166958513310727,0.80190100342201187,1,1,1,1,1,1,null,0.80190100342201187,0.80190100342201187,0.80190100342201187]
["2013-02-24T00:00:01.865","2013-02-24",null,9.5337964173967578,9.8373686190526577,10.140940820708558,10.444513022364458,10.748085224020357,11.051657425676257,11.355229627332157,11.658801828988057,11.962374030643957,null,0.27714932865194269,0.55982907671190341,0.81214242713044926,1,1,1,1,1,1,null,0.81214242713044926,0.81214242713044926,0.81214242713044926]
["2013-02-24T01:00:01.870","2013-02-24T01:00:00",null,9.3895922855334764,9.6931644871893763,9.9967366888452762,10.300308890501176,10.603881092157076,10.907453293812976,11.211025495468876,11.514597697124776,11.818169898780676,null,0.28336358061465983,0.56828298293529522,0.82269929510095352,1,1,1,1,1,1,null,0.82269929510095352,0.82269929510095352,0.82269929510095352]
["2013-02-24T02:00:01.875","2013-02-24T02:00:00",null,9.3368362656796133,9.6404084673355133,9.9439806689914132,10.247552870647313,10.551125072303213,10.854697273959113,11.158269475615013,11.461841677270913,11.765413878926813,null,0.29277433443298784,0.57984927254441343,0.83628442798729963,1,1,1,1,1,1,null,0.83628442798729963,0.83628442798729963,0.83628442798729963]
["2013-02-24T03:00:01.880","2013-02-24T03:00:00",null,9.271982867100764,9.575555068756664,9.8791272704125639,10.182699472068464,10.486271673724364,10.789843875380264,11.093416077036164,11.396988278692064,11.700560480347963,null,0.3019117032241912,0.59116320674387812,0.84963823508146341,1,1,1,1,1,1,null,0.84963823508146341,0.84963823508146341,0.84963823508146341]
["2013-02-24T04:00:01.885","2013-02-24T04:00:00",null,9.2706590975215164,9.5742312991774163,9.8778035008333163,10.181375702489218,10.484947904145118,10.788520105801018,11.092092307456918,11.395664509112818,11.699236710768718,null,0.31114370529401464,0.60257177422196284,0.86308667545424722,1,1,1,1,1,1,null,0.86308667545424722,0.86308667545424722,0.86308667545424722]
["2013-02-24T05:00:01.890","2013-02-24T05:00:00",null,9.3304336454074583,9.6340058470633583,9.9375780487192582,10.241150250375158,10.544722452031058,10.848294653686958,11.151866855342858,11.455439056998758,11.759011258654658,null,0.32085938856567392,0.61443247847567672,0.876966222985189,1,1,1,1,1,1,null,0.876966222985189,0.876966222985189,0.876966222985189]
["2013-02-24T06:00:01.895","2013-02-24T06:00:00",null,9.3654452561312596,9.6690174577871595,9.9725896594430594,10.276161861098959,10.579734062754859,10.883306264410759,11.186878466066659,11.490450667722559,11.794022869378459,null,0.32856674336884084,0.62434794311331165,0.8889425901349941,1,1,1,1,1,1,null,0.8889425901349941,0.8889425901349941,0.8889425901349941]
["2013-02-24T07:00:01.900","2013-02-24T07:00:00",null,9.2695510975470476,9.5731232992029476,9.8766955008588475,10.180267702514747,10.483839904170647,10.787412105826547,11.090984307482447,11.394556509138347,11.698128710794247,null,0.33381363292788629,0.63189757578544514,0.89864775859791779,1,1,1,1,1,1,null,0.89864775859791779,0.89864775859791779,0.89864775859791779]
["2013-02-24T08:00:01.905","2013-02-24T08:00:00",null,9.4962459714666529,9.7998181731225529,10.103390374778453,10.406962576434353,10.710534778090253,11.014106979746153,11.317679181402053,11.621251383057952,11.924823584713852,null,0.33786183429107769,0.63822749064425344,0.9071226944387808,1,1,1,1,1,1,null,0.9071226944387808,0.9071226944387808,0.9071226944387808]
["2013-02-24T09:00:01.910","2013-02-24T09:00:00",null,9.9972550868524301,10.30082728850833,10.60439949016423,10.90797169182013,11.21154389347603,11.51511609513193,11.81868829678783,12.12226049844373,12.42583270009963,null,0.33729403461935736,0.63997294889435674,0.91104471809714538,1,1,1,1,1,1,null,0.91104471809714538,0.91104471809714538,0.91104471809714538]
["2013-02-24T10:00:01.915","2013-02-24T10:00:00",null,11.269164509749515,11.572736711405415,11.876308913061315,12.179881114717215,12.483453316373115,12.787025518029015,13.090597719684915,13.394169921340815,13.697742122996715,null,0.29433052612585103,0.60014285340404794,0.87417979867026507,0.9659530493142503,0.96863432554181861,0.9711894240645601,0.9736183448824749,0.97595263242176966,0.97817125706497332,null,0.87417979867026507,0.87417979867026507,0.87417979867026507]
["2013-02-24T11:00:01.920","2013-02-24T11:00:00",null,11.53049200783428,11.83406420949018,12.137636411146079,12.441208612801979,12.744780814457879,13.048353016113779,13.351925217769679,13.655497419425579,13.959069621081479,null,0.24819154539420499,0.55718985971927715,0.83424455509260065,0.92888834852139424,0.93430347502020872,0.93947676091810517,0.94438717659761251,0.94910832571987991,0.95359814904996498,null,0.83424455509260065,0.83424455509260065,0.83424455509260065]
["2013-02-24T12:00:01.925","2013-02-24T12:00:00",null,11.526133570265729,11.829705771921629,12.133277973577529,12.436850175233429,12.740422376889329,13.043994578545229,13.347566780201129,13.651138981857029,13.954711183512929,null,0.21202060334387171,0.52394203449743015,0.80377263937694199,0.90106616460709721,0.90899433039371103,0.91656499268331559,0.92376763666717543,0.9306758660064397,0.93726865108363722,null,0.80377263937694199,0.80377263937694199,0.80377263937694199]
["2013-02-24T13:00:01.930","2013-02-24T13:00:00",null,11.451975667037583,11.755547868693483,12.059120070349383,12.362692272005283,12.666264473661183,12.969836675317083,13.273408876972983,13.576981078628883,13.880553280284783,null,0.17904616314914928,0.49382762227878058,0.77637104781206745,0.87625121599117084,0.88663984702190624,0.89655531165954117,0.90598709509534014,0.91502983060792342,0.92367300338855551,null,0.77637104781206745,0.77637104781206745,0.77637104781206745]
["2013-02-24T14:00:01.935","2013-02-24T14:00:00",null,11.420388927121007,11.723961128776907,12.027533330432806,12.331105532088706,12.634677733744606,12.938249935400506,13.241822137056406,13.545394338712306,13.848966540368206,null,0.15077184245922307,0.46830818147757158,0.75345927957727787,0.85581042780923833,0.86856489080547516,0.88073052451252032,0.89230732893037401,0.90340045214639186,0.9139993793518385,null,0.75345927957727787,0.75345927957727787,0.75345927957727787]
["2013-02-24T15:00:01.940","2013-02-24T15:00:00",null,11.342643839797567,11.646216041453467,11.949788243109367,12.253360444765267,12.556932646421167,12.860504848077067,13.164077049732967,13.467649251388867,13.771221453044767,null,0.12274987717895033,0.44304109608601611,0.7308103815608773,0.83565353946316601,0.85077383442490429,0.86520015201009526,0.87893249221873915,0.89207600313819158,0.90464119957718836,null,0.7308103815608773,0.7308103815608773,0.7308103815608773]
["2013-02-24T16:00:01.945","2013-02-24T16:00:00",null,11.420760199330623,11.724332400986523,12.027904602642423,12.331476804298322,12.635049005954222,12.938621207610122,13.242193409266022,13.545765610921922,13.849337812577822,null,9.4528130532701926E-2,0.41756371451974938,0.70794067256102999,0.81526532532491125,0.83274093744341549,0.84941742409801668,0.86529478528871528,0.88048868391160229,0.89502014958414911,null,0.70794067256102999,0.70794067256102999,0.70794067256102999]
["2013-02-24T17:00:01.950","2013-02-24T17:00:00",null,11.316078735638834,11.619650937294734,11.923223138950634,12.226795340606534,12.530367542262434,12.833939743918334,13.137511945574234,13.441084147230134,13.744656348886034,null,6.7620734978398767E-2,0.39339016923669234,0.68636428503565683,0.79615991785239515,0.81598033231892964,0.83489647323420557,0.8528978257894877,0.87013159730707368,0.88660830259569956,null,0.68636428503565683,0.68636428503565683,0.68636428503565683]
["2013-02-24T18:00:01.955","2013-02-24T18:00:00",null,11.090558191499341,11.39413039315524,11.69770259481114,12.00127479646704,12.30484699812294,12.60841919977884,12.91199140143474,13.21556360309064,13.51913580474654,null,4.4319918820393378E-2,0.3727811441149908,0.66831035843669684,0.78052439726261447,0.80264755484223704,0.82376129078324545,0.84384457546816882,0.86307616064551163,0.88145604631527419,null,0.66831035843669684,0.66831035843669684,0.66831035843669684]
["2013-02-24T19:00:01.960","2013-02-24T19:00:00",null,10.873623425007674,11.177195626663574,11.480767828319474,11.784340029975374,12.087912231631273,12.391484433287173,12.695056634943073,12.998628836598973,13.302201038254873,null,2.4478474736387888E-2,0.35558943183234692,0.65363168544185224,0.7682220710420069,0.7926059124997753,0.8158751842315739,0.83800885661993196,0.85918568141335372,0.87943720303804629,null,0.65363168544185224,0.65363168544185224,0.65363168544185224]
["2013-02-24T20:00:01.965","2013-02-24T20:00:00",null,10.725681351231257,11.029253552887157,11.332825754543057,11.636397956198957,11.939970157854857,12.243542359510757,12.547114561166657,12.850686762822557,13.154258964478457,null,8.3066989010935344E-3,0.34200429894600082,0.64249650299089212,0.75940014651287036,0.78599209780510682,0.81135381647528226,0.83547478771466155,0.85855479288921999,0.88061486161642921,null,0.64249650299089212,0.64249650299089212,0.64249650299089212]
["2013-02-24T21:00:01.970","2013-02-24T21:00:00",null,10.652913520577926,10.956485722233825,11.260057923889725,11.563630125545625,11.867202327201525,12.170774528857425,12.474346730513325,12.777918932169225,13.081491133825125,null,0,0.33194162698606799,0.63479966299646073,0.75394296077911371,0.78266941824466918,0.81006049500080812,0.83610567623879528,0.86101525813334145,0.88482078511065398,null,0.63479966299646073,0.63479966299646073,0.63479966299646073]
["2013-02-24T22:00:01.975","2013-02-24T22:00:00",null,10.590128511679849,10.893700713335749,11.197272914991649,11.500845116647548,11.804417318303448,12.107989519959348,12.411561721615248,12.715133923271148,13.018706124927048,null,0,0.32426581660910775,0.62942659573258852,0.75074645892350289,0.78154433370996401,0.8109016796996531,0.83880798208383467,0.86549456665469082,0.8909929778384289,null,0.62942659573258852,0.62942659573258852,0.62942659573258852]
["2013-02-24T23:00:01.980","2013-02-24T23:00:00",null,10.614376777445175,10.917948979101075,11.221521180756975,11.525093382412875,11.828665584068775,12.132237785724675,12.435809987380575,12.739382189036474,13.042954390692374,null,0,0.31427674831032387,0.62167718169447928,0.74511052144124168,0.77791672469619511,0.80917725106702099,0.8389026153624547,0.86731362856594307,0.89446286472116432,null,0.62167718169447928,0.62167718169447928,0.62167718169447928]
["2013-02-25T00:00:01.985","2013-02-25",null,10.512730746052192,10.816302947708092,11.119875149363992,11.423447351019892,11.727019552675792,12.030591754331692,12.334163955987592,12.637736157643491,12.941308359299391,null,0,0.30156434454902942,0.61118340257638837,0.73670918926152762,0.77150269136750227,0.80464536850199375,0.83616876509120852,0.86628317730985804,0.89506220881909138,null,0.61118340257638837,0.61118340257638837,0.61118340257638837]
["2013-02-25T01:00:01.990","2013-02-25T01:00:00",null,10.620773580872578,10.924345782528478,11.227917984184378,11.531490185840278,11.835062387496178,12.138634589152078,12.442206790807978,12.745778992463878,13.049351194119778,null,0,0.28938819603324861,0.60116278985139782,0.72871793462250045,0.76544616153581857,0.80041841539029779,0.83368727022961586,0.86546302222848426,0.89582978985678741,null,0.60116278985139782,0.60116278985139782,0.60116278985139782]
["2013-02-25T02:00:01.995","2013-02-25T02:00:00",null,10.637644875001065,10.941217076656965,11.244789278312865,11.548361479968765,11.851933681624665,12.155505883280565,12.459078084936465,12.762650286592365,13.066222488248265,null,0,0.27639189243609397,0.59033253685376896,0.71993806932830617,0.75861153585770325,0.79543439604964139,0.83046973875653385,0.8639173453443566,0.89589287870920076,null,0.59033253685376896,0.59033253685376896,0.59033253685376896]
["2013-02-25T03:00:02","2013-02-25T03:00:00",null,10.615841383396941,10.91941358505284,11.22298578670874,11.52655798836464,11.83013019002054,12.13370239167644,12.43727459333234,12.74084679498824,13.04441899664414,null,0,0.26445758452123108,0.58054324992096074,0.71217814048146144,0.75277581700946639,0.79142825392139227,0.82820905487838803,0.86330748643769406,0.89687075592160803,null,0.58054324992096074,0.58054324992096074,0.58054324992096074]
["2013-02-25T04:00:02.005","2013-02-25T04:00:00",null,10.590970027651863,10.894542229307763,11.198114430963663,11.501686632619563,11.805258834275463,12.108831035931363,12.412403237587263,12.715975439243163,13.019547640899063,null,0,0.2537955684633712,0.57199471041894878,0.70562741463920631,0.74812827154834793,0.78857874075405499,0.82708397034368286,0.86381219725700109,0.8989316584337782,null,0.57199471041894878,0.57199471041894878,0.57199471041894878]
["2013-02-25T05:00:02.010","2013-02-25T05:00:00",null,10.460444634014721,10.764016835670621,11.067589037326522,11.371161238982422,11.674733440638322,11.978305642294222,12.281877843950122,12.585450045606022,12.889022247261922,null,0,0.24271296005608886,0.56306763780245661,0.69872970010867763,0.74316528182516262,0.78544532775085751,0.82569601559058869,0.86408558228412569,0.90078226477123713,null,0.56306763780245661,0.56306763780245661,0.56306763780245661]
["2013-02-25T06:00:02.015","2013-02-25T06:00:00",null,10.488940109982931,10.792512311638831,11.096084513294731,11.39965671495063,11.70322891660653,12.00680111826243,12.31037331991833,12.61394552157423,12.91751772323013,null,0,0.23012673399962114,0.55265797715425025,0.69039145678137692,0.73679330773141205,0.78093447480330147,0.82295165051060704,0.86302358660183387,0.90132903482548632,null,0.55265797715425025,0.55265797715425025,0.55265797715425025]
["2013-02-25T07:00:02.020","2013-02-25T07:00:00",null,10.456116430797179,10.759688632453079,11.063260834108979,11.366833035764879,11.670405237420779,11.973977439076679,12.277549640732579,12.581121842388479,12.884694044044378,null,0,0.21928596619325672,0.54396223032994051,0.68372506804303057,0.73205112899167357,0.77802187278355084,0.82177399193222411,0.86350726780366971,0.90337942252892089,null,0.54396223032994051,0.54396223032994051,0.54396223032994051]
["2013-02-25T08:00:02.025","2013-02-25T08:00:00",null,10.481807423162412,10.785379624818312,11.088951826474212,11.392524028130111,11.696096229786011,11.999668431441911,12.303240633097811,12.606812834753711,12.910385036409611,null,0,0.20715187691241818,0.53400470645736331,0.67582844668262354,0.72611026205608109,0.77393161218541717,0.81945021920166494,0.8628553496620649,0.90432575531512149,null,0.53400470645736331,0.53400470645736331,0.53400470645736331]
["2013-02-25T09:00:02.030","2013-02-25T09:00:00",null,10.665953911876118,10.969526113532018,11.273098315187918,11.576670516843818,11.880242718499717,12.183814920155617,12.487387121811517,12.790959323467417,13.094531525123317,null,0,0.19257835200492926,0.5216287765756068,0.66553444893050839,0.71779304834625157,0.76749654923925326,0.81480267374054649,0.85991120321610759,0.90300088941444068,null,0.5216287765756068,0.5216287765756068,0.5216287765756068]
["2013-02-25T10:00:02.035","2013-02-25T10:00:00",null,10.745823873866222,11.049396075522122,11.352968277178022,11.656540478833922,11.960112680489821,12.263684882145721,12.567257083801621,12.870829285457521,13.174401487113421,null,0,0.17464008830206049,0.50580398942858595,0.65169696063450877,0.70585874043138874,0.75736027361817149,0.80638031194336135,0.85311863677293454,0.89776451466413076,null,0.50580398942858595,0.50580398942858595,0.50580398942858595]
["2013-02-25T11:00:02.040","2013-02-25T11:00:00",null,10.577409285574538,10.880981487230438,11.184553688886337,11.488125890542237,11.791698092198137,12.095270293854037,12.398842495509937,12.702414697165837,13.005986898821737,null,0,0.1577007314290701,0.49115686085994809,0.63921588266539664,0.69542805016571119,0.748874822968573,0.79975598243995727,0.84826079513710484,0.89458904242599102,null,0.49115686085994809,0.49115686085994809,0.49115686085994809]
["2013-02-25T12:00:02.045","2013-02-25T12:00:00",null,10.474866679639087,10.778438881294987,11.082011082950888,11.385583284606788,11.689155486262688,11.992727687918588,12.296299889574488,12.599872091230388,12.903444292886288,null,0,0.13890025340988524,0.4747116999975291,0.6250103760636524,0.68333602011981487,0.73879112139116909,0.79158597605242564,0.84190985066082535,0.88997304139107936,null,0.4747116999975291,0.4747116999975291,0.4747116999975291]
["2013-02-25T13:00:02.050","2013-02-25T13:00:00",null,10.519279604817228,10.82285180647313,11.12642400812903,11.42999620978493,11.73356841144083,12.03714061309673,12.34071281475263,12.64428501640853,12.94785721806443,null,0,0.11585179266153334,0.45407113044962089,0.60665152001136113,0.6671326998583138,0.7246487036418382,0.7793887979191737,0.83157379367376794,0.88141398708033192,null,0.45407113044962089,0.45407113044962089,0.45407113044962089]
["2013-02-25T14:00:02.055","2013-02-25T14:00:00",null,10.620332912881548,10.923905114537446,11.227477316193346,11.531049517849246,11.834621719505146,12.138193921161045,12.441766122816945,12.745338324472845,13.048910526128745,null,0,9.4717027103053714E-2,0.43527065243043606,0.59006966663537985,0.65264329342070937,0.71215711086399058,0.76878987071372717,0.82278341357083806,0.87433752080129867,null,0.43527065243043606,0.43527065243043606,0.43527065243043606]
["2013-02-25T15:00:02.060","2013-02-25T15:00:00",null,10.329752458387411,10.633324660043311,10.936896861699211,11.240469063355111,11.54404126501101,11.84761346666691,12.15118566832281,12.45475786997871,12.75833007163461,null,0,7.3960794659054335E-2,0.41690128156940925,0.57396097965249893,0.63866911261114745,0.70021228814039216,0.75876925798873662,0.81459237756583525,0.86789194304639916,null,0.41690128156940925,0.41690128156940925,0.41690128156940925]
["2013-02-25T16:00:02.065","2013-02-25T16:00:00",null,10.110556224484419,10.414128426140319,10.717700627796219,11.021272829452119,11.324845031108019,11.628417232763919,11.931989434419819,12.235561636075719,12.539133837731619,null,0,5.7168645108361824E-2,0.40243290474927595,0.56167968304936255,0.62846974813765233,0.69197919290044707,0.75240779870372165,0.80999740614839466,0.86498985583538401,null,0.40243290474927595,0.40243290474927595,0.40243290474927595]
["2013-02-25T17:00:02.070","2013-02-25T17:00:00",null,10.014033550800367,10.317605752456267,10.621177954112166,10.924750155768066,11.228322357423966,11.531894559079866,11.835466760735766,12.139038962391666,12.442611164047566,null,0,4.5350000089590142E-2,0.3928223695649723,0.55414056518596455,0.62289689950780447,0.68826746541679373,0.7504625590876427,0.80973453593000566,0.86631472173606483,null,0.3928223695649723,0.3928223695649723,0.3928223695649723]
["2013-02-25T18:00:02.075","2013-02-25T18:00:00",null,9.8499190071295875,10.153491208785487,10.457063410441387,10.760635612097287,11.064207813753187,11.367780015409087,11.671352217064987,11.974924418720887,12.278496620376787,null,2.6518347631087357E-2,7.4086972363881079E-2,0.4236412739689045,0.58693625363218238,0.65755370910021682,0.72468024806804499,0.78854719632784831,0.84940690928928109,0.90749071274452564,null,0.4236412739689045,0.4236412739689045,0.4236412739689045]
["2013-02-25T19:00:02.080","2013-02-25T19:00:00",null,9.6231983645252068,9.9267705661811068,10.230342767837007,10.533914969492907,10.837487171148807,11.141059372804706,11.444631574460606,11.748203776116506,12.051775977772406,null,8.7115190374131152E-2,0.13691295455886401,0.48857021791099986,0.65384198161656337,0.72633107303952782,0.79522409987493048,0.86077341753242365,0.92322086661292635,0.98280828771735629,null,0.48857021791099986,0.48857021791099986,0.48857021791099986]
["2013-02-25T20:00:02.085","2013-02-25T20:00:00",null,9.5137709752563246,9.8173431769122246,10.120915378568125,10.424487580224024,10.728059781879924,11.031631983535824,11.335204185191724,11.638776386847624,11.942348588503524,null,0.14985705409922959,0.20184189850095935,0.5555495495565298,0.72275603806943667,0.79707470621238896,0.86769216168042373,0.93488178950066458,0.99887491546529494,1,null,0.5555495495565298,0.5555495495565298,0.5555495495565298]
["2013-02-25T21:00:02.090","2013-02-25T21:00:00",null,9.4944498025352893,9.7980220041911892,10.101594205847089,10.405166407502989,10.708738609158889,11.012310810814789,11.315883012470689,11.619455214126589,11.923027415782489,null,0.21381863563765321,0.26795901583017318,0.62369602497170706,0.79281620867448621,0.86893290911121968,0.94125376359441548,1,1,1,null,0.62369602497170706,0.62369602497170706,0.62369602497170706]
["2013-02-25T22:00:02.095","2013-02-25T22:00:00",null,9.4330694247505278,9.7366416264064277,10.040213828062328,10.343786029718226,10.647358231374126,10.950930433030026,11.254502634685926,11.558074836341826,11.861647037997725,null,0.28126061886754788,0.33746190157223799,0.69513363552111529,0.86607288113514669,0.94391401020451227,1,1,1,1,null,0.69513363552111529,0.69513363552111529,0.69513363552111529]
["2013-02-25T23:00:02.100","2013-02-25T23:00:00",null,9.4045217776841774,9.7080939793400773,10.011666180995977,10.315238382651877,10.618810584307777,10.922382785963677,11.225954987619577,11.529527189275477,11.833099390931377,null,0.35038497149513248,0.40860509747705048,0.76816949699832893,0.94088574528867031,1,1,1,1,1,null,0.76816949699832893,0.76816949699832893,0.76816949699832893]
["2013-02-26T00:00:02.105","2013-02-26",null,9.3795181997009305,9.6830904013568304,9.9866626030127303,10.29023480466863,10.59380700632453,10.89737920798043,11.20095140963633,11.50452361129223,11.80809581294813,null,0.42097088253696019,0.48116779256116382,0.84258279841990125,1,1,1,1,1,1,null,0.84258279841990125,0.84258279841990125,0.84258279841990125]
["2013-02-26T01:00:02.110","2013-02-26T01:00:00",null,9.3181319107554295,9.6217041124113294,9.9252763140672293,10.228848515723129,10.532420717379029,10.835992919034929,11.139565120690829,11.443137322346729,11.746709524002629,null,0.49524749144497016,0.55731603742410385,0.92048701634168006,1,1,1,1,1,1,null,0.92048701634168006,0.92048701634168006,0.92048701634168006]
["2013-02-26T02:00:02.115","2013-02-26T02:00:00",null,9.2337269502859005,9.5372991519418004,9.8408713535977004,10.1444435552536,10.4480157569095,10.7515879585654,11.0551601602213,11.3587323618772,11.6623045635331,null,0.57051249237412294,0.63443164469071556,0.99933756704965948,1,1,1,1,1,1,null,0.99933756704965948,0.99933756704965948,0.99933756704965948]
["2013-02-26T03:00:02.120","2013-02-26T03:00:00",null,9.2512257208684296,9.5547979225243296,9.8583701241802295,10.161942325836129,10.465514527492029,10.769086729147929,11.072658930803829,11.376231132459729,11.679803334115629,null,0.64468395319477723,0.71048525627503545,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T04:00:02.125","2013-02-26T04:00:00",null,9.2674193614896083,9.5709915631455083,9.8745637648014082,10.178135966457308,10.481708168113208,10.785280369769108,11.088852571425008,11.392424773080908,11.695996974736808,null,0.71802474412532213,0.78573974239545263,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T05:00:02.130","2013-02-26T05:00:00",null,9.2450793076141675,9.5486515092700675,9.8522237109259674,10.155795912581867,10.459368114237767,10.762940315893667,11.066512517549567,11.370084719205467,11.673656920861367,null,0.7779591539180255,0.84754578814308601,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T06:00:02.135","2013-02-26T06:00:00",null,9.2098386401683676,9.5134108418242675,9.8169830434801675,10.120555245136067,10.424127446791967,10.727699648447867,11.031271850103767,11.334844051759667,11.638416253415567,null,0.78702291904807997,0.85841810037565713,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T07:00:02.140","2013-02-26T07:00:00",null,9.2894960833531339,9.5930682850090339,9.8966404866649338,10.200212688320834,10.503784889976734,10.807357091632634,11.110929293288534,11.414501494944433,11.718073696600333,null,0.7927745194264324,0.86611494037008852,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T08:00:02.145","2013-02-26T08:00:00",null,9.3303264056471455,9.6338986073030455,9.9374708089589454,10.241043010614845,10.544615212270745,10.848187413926645,11.151759615582545,11.455331817238445,11.758904018894345,null,0.79612874341307671,0.87148800763396073,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T09:00:02.150","2013-02-26T09:00:00",null,9.4118312688632084,9.7154034705191084,10.018975672175008,10.322547873830908,10.626120075486808,10.929692277142708,11.233264478798608,11.536836680454508,11.840408882110408,null,0.79865229750961164,0.87603040500772356,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T10:00:02.155","2013-02-26T10:00:00",null,9.6603641342939959,9.9639363359498958,10.267508537605796,10.571080739261696,10.874652940917596,11.178225142573496,11.481797344229395,11.785369545885295,12.088941747541195,null,0.79868384193581832,0.87811233713736481,1,1,1,1,1,1,1,null,1,1,1]
["2013-02-26T11:00:02.160","2013-02-26T11:00:00",null,9.8217728330011003,10.125345034657,10.4289172363129,10.7324894379688,11.0360616396247,11.3396338412806,11.6432060429365,11.9467782445924,12.2503504462483,null,0.79350004122918627,0.87510510183899404,0.99904315240506381,1,1,1,1,1,1,null,0.99904315240506381,0.99904315240506381,0.99904315240506381]
["2013-02-26T12:00:02.165","2013-02-26T12:00:00",null,10.011923650195072,10.315495851850972,10.619068053506872,10.922640255162772,11.226212456818672,11.529784658474572,11.833356860130472,12.136929061786372,12.440501263442272,null,0.78546672735521694,0.86929041260822826,0.99532091011267487,0.9982545417498967,1,1,1,1,1,null,0.99532091011267487,0.99532091011267487,0.99532091011267487]
["2013-02-26T13:00:02.170","2013-02-26T13:00:00",null,10.104060556484527,10.407632758140426,10.711204959796326,11.014777161452226,11.318349363108126,11.621921564764026,11.925493766419926,12.229065968075826,12.532638169731726,null,0.7724704237580623,0.85863891135910397,0.98687751869801854,0.99190359727361721,0.99562583956600625,0.99749747552093626,0.99927447819724624,1,1,null,0.98687751869801854,0.98687751869801854,0.98687751869801854]
["2013-02-26T14:00:02.175","2013-02-26T14:00:00",null,10.246481537271869,10.550053738927769,10.853625940583669,11.157198142239569,11.460770343895469,11.764342545551369,12.067914747207269,12.371486948863168,12.675059150519068,null,0.75556261131127855,0.84414950492149954,0.9746803405647666,0.98186195493115547,0.98763458492697909,0.99144094568925256,0.99506855470302147,0.99755004956461402,0.99921138934483289,null,0.9746803405647666,0.9746803405647666,0.9746803405647666]
["2013-02-26T15:00:02.180","2013-02-26T15:00:00",null,10.367738285517845,10.671310487173745,10.974882688829647,11.278454890485547,11.582027092141447,11.885599293797346,12.189171495453246,12.492743697109146,12.796315898765046,null,0.73425960881302998,0.82530696766737244,0.95817209084993427,0.9675618150507912,0.97542689198499166,0.98122055159828625,0.98673031137572076,0.99099932372235888,0.99437457732647438,null,0.95817209084993427,0.95817209084993427,0.95817209084993427]
["2013-02-26T16:00:02.185","2013-02-26T16:00:00",null,10.466029143134074,10.769601344789974,11.073173546445874,11.376745748101774,11.680317949757674,11.983890151413574,12.287462353069474,12.591034554725374,12.894606756381274,null,0.71129526653456254,0.80482412025049765,0.94004456058982533,0.95165290943388592,0.96163146292393431,0.96942293619698572,0.97683587635555691,0.98291343580471169,0.98801311804145941,null,0.94004456058982533,0.94004456058982533,0.94004456058982533]
["2013-02-26T17:00:02.190","2013-02-26T17:00:00",null,10.422509401099914,10.726081602755814,11.029653804411714,11.333226006067614,11.636798207723514,11.940370409379414,12.243942611035314,12.547514812691213,12.851087014347113,null,0.68694296950300093,0.78300589212420646,0.92062370885524236,0.93449274157744877,0.94662683085828736,0.95645817702603775,0.96580584199195241,0.97372349296983052,0.98057914826541703,null,0.92062370885524236,0.92062370885524236,0.92062370885524236]
["2013-02-26T18:00:02.195","2013-02-26T18:00:00",null,10.287596431596825,10.591168633252725,10.894740834908625,11.198313036564524,11.501885238220424,11.805457439876324,12.109029641532224,12.412601843188124,12.716174044844024,null,0.66585026317946361,0.7643841658535262,0.90433627012385687,0.92041341268053123,0.93463994889974666,0.94645859391851828,0.95768840964809854,0.96740409291975771,0.97596314723050537,null,0.90433627012385687,0.90433627012385687,0.90433627012385687]
["2013-02-26T19:00:02.200","2013-02-26T19:00:00",null,10.073801472318227,10.377373673974127,10.680945875630027,10.984518077285927,11.288090278941826,11.591662480597726,11.895234682253626,12.198806883909526,12.502379085565426,null,0.64858494723567084,0.74953725591891263,0.89176055887612471,0.90998272241485367,0.9262491315287682,0.93999198654614768,0.95305137899571568,0.96451252051747816,0.97472239979970909,null,0.89176055887612471,0.89176055887612471,0.89176055887612471]
["2013-02-26T20:00:02.205","2013-02-26T20:00:00",null,9.9621714984241851,10.265743700080085,10.569315901735985,10.872888103391885,11.176460305047785,11.480032506703685,11.783604708359585,12.087176910015485,12.390749111671385,null,0.63350671150887494,0.73683536696635377,0.88129832418424048,0.90163396427881748,0.91989818705248871,0.9355337076422694,0.95038061757688297,0.96354515811380648,0.97537431794131391,null,0.88129832418424048,0.88129832418424048,0.88129832418424048]
["2013-02-26T21:00:02.210","2013-02-26T21:00:00",null,9.9252636429239534,10.228835844579853,10.532408046235751,10.835980247891651,11.139552449547551,11.443124651203451,11.746696852859351,12.050269054515251,12.353841256171151,null,0.62044731905930695,0.72609974724734494,0.87274978468222852,0.8951463272889757,0.91536630448746148,0.93285243141470109,0.94945531440815356,0.96429170953403143,0.97769809067187308,null,0.87274978468222852,0.87274978468222852,0.87274978468222852]
["2013-02-26T22:00:02.215","2013-02-26T22:00:00",null,9.7481669050049007,10.051739106660801,10.355311308316701,10.6588835099726,10.9624557116285,11.2660279132844,11.5696001149403,11.8731723165962,12.1767445182521,null,0.6094698587393802,0.71742503004050628,0.86624111807491566,0.89067753357636181,0.91282172077345547,0.93213742442068293,0.95046473604676751,0.96695195614412865,0.98191452897483344,null,0.86624111807491566,0.86624111807491566,0.86624111807491566]
["2013-02-26T23:00:02.220","2013-02-26T23:00:00",null,9.694644361772399,9.9982165634282989,10.301788765084199,10.605360966740099,10.908933168395999,11.212505370051899,11.516077571707799,11.819649773363698,12.123221975019598,null,0.60147860410035303,0.71166291485341826,0.86257144982620448,0.88897413456120078,0.91297944290448885,0.9340616344192908,0.95405028582559415,0.97212524204202511,0.98859143252191528,null,0.86257144982620448,0.86257144982620448,0.86257144982620448]
["2013-02-27T00:00:02.225","2013-02-27",null,9.5913976128031972,9.8949698144590972,10.198542016114997,10.502114217770897,10.805686419426797,11.109258621082697,11.412830822738597,11.716403024394497,12.019975226050397,null,0.59539052984246266,0.70775140600378916,0.86072084348874556,0.88905825303108532,0.91489313809436112,0.9376997582417953,0.95932871981084622,0.97895986772014043,0.9968981314230092,null,0.86072084348874556,0.86072084348874556,0.86072084348874556]
["2013-02-27T01:00:02.230","2013-02-27T01:00:00",null,9.5621034378634988,9.8656756395193987,10.169247841175299,10.472820042831199,10.776392244487099,11.079964446142998,11.383536647798898,11.687108849454798,11.990681051110698,null,0.59098482498226224,0.70549072212564334,0.86047900288782764,0.8907090780025686,0.91833148055088987,0.94283098490474959,0.96605819740160592,0.9872139925775566,1,null,0.86047900288782764,0.86047900288782764,0.86047900288782764]
["2013-02-27T02:00:02.235","2013-02-27T02:00:00",null,9.4907624773929982,9.7943346790488981,10.097906880704798,10.401479082360698,10.705051284016598,11.008623485672498,11.312195687328398,11.615767888984298,11.919340090640198,null,0.58674735706183079,0.70340878999600209,0.86041591403541429,0.89254916953129193,0.92196960437339437,0.94817250774241513,0.97299797116707687,0.99567841360968401,1,null,0.86041591403541429,0.86041591403541429,0.86041591403541429]
["2013-02-27T03:00:02.240","2013-02-27T03:00:00",null,9.3345837375911493,9.6381559392470493,9.9417281409029492,10.245300342558849,10.548872544214749,10.852444745870649,11.156016947526549,11.459589149182449,11.763161350838349,null,0.58359291444116224,0.70239936835738814,0.86142533567402824,0.89546177155104256,0.92668023868692617,0.95456551145363677,0.98098922580610404,1,1,null,0.86142533567402824,0.86142533567402824,0.86142533567402824]
["2013-02-27T04:00:02.245","2013-02-27T04:00:00",null,9.2473584562601925,9.5509306579160924,9.8545028595719923,10.158075061227892,10.461647262883792,10.765219464539692,11.068791666195592,11.372363867851492,11.675936069507392,null,0.58157407116393434,0.70251503125347936,0.86353881222987616,0.89946791367929169,0.93245286868274968,0.96202051084715023,0.99002144650995183,1,1,null,0.86353881222987616,0.86353881222987616,0.86353881222987616]
["2013-02-27T05:00:02.250","2013-02-27T05:00:00",null,9.2859917254032194,9.5895639270591193,9.8931361287150192,10.196708330370919,10.500280532026819,10.803852733682719,11.107424935338619,11.410997136994519,11.714569338650419,null,0.58129017132807415,0.70430254873852494,0.86727156933100069,0.90503024750040395,0.93973963113649417,0.97093706865490681,1,1,1,null,0.86727156933100069,0.86727156933100069,0.86727156933100069]
["2013-02-27T06:00:02.255","2013-02-27T06:00:00",null,9.3129548186940898,9.6165270203499897,9.9200992220058897,10.22367142366179,10.52724362531769,10.830815826973589,11.134388028629489,11.437960230285389,11.741532431941289,null,0.57945007979935081,0.70458644857438513,0.86954276801788211,0.90916256733347978,0.94563843883714449,0.97849721613577589,1,1,1,null,0.86954276801788211,0.86954276801788211,0.86954276801788211]
["2013-02-27T07:00:02.260","2013-02-27T07:00:00",null,9.3284188766450669,9.6319910783009668,9.9355632799568667,10.239135481612767,10.542707683268667,10.846279884924567,11.149852086580466,11.453424288236366,11.756996489892266,null,0.57669519991063356,0.70396607485898699,0.87094123757971187,0.91245370246771074,0.95070657664768532,0.98524772334400668,1,1,1,null,0.87094123757971187,0.87094123757971187,0.87094123757971187]
["2013-02-27T08:00:02.265","2013-02-27T08:00:00",null,9.3558200655168093,9.6593922671727093,9.9629644688286092,10.266536670484509,10.570108872140409,10.873681073796309,11.177253275452209,11.480825477108109,11.784397678764009,null,0.57235258390284649,0.70181053906819679,0.87083608949235625,0.91428327918769847,0.95435521527892531,0.99061027579914329,1,1,1,null,0.87083608949235625,0.87083608949235625,0.87083608949235625]
["2013-02-27T09:00:02.270","2013-02-27T09:00:00",null,9.5331278089289277,9.8367000105848277,10.140272212240728,10.443844413896628,10.747416615552527,11.050988817208427,11.354561018864327,11.658133220520227,11.961705422176127,null,0.56570722478197133,0.69738380459052518,0.86849128714432589,0.91390474607321825,0.95582728850190402,0.99383832208096079,1,1,1,null,0.86849128714432589,0.86849128714432589,0.86849128714432589]
["2013-02-27T10:00:02.275","2013-02-27T10:00:00",null,9.6795303239546584,9.9831025256105583,10.286674727266458,10.590246928922356,10.893819130578256,11.197391332234156,11.500963533890056,11.804535735545956,12.108107937201856,null,0.55466667560963123,0.68865651334000877,0.86195107611080635,0.90941492274313329,0.95328270478789801,0.99312331508694263,1,1,1,null,0.86195107611080635,0.86195107611080635,0.86195107611080635]
["2013-02-27T11:00:02.280","2013-02-27T11:00:00",null,9.8559169231311277,10.159489124787028,10.463061326442928,10.766633528098827,11.070205729754727,11.373777931410627,11.677350133066527,11.980922334722427,12.284494536378327,null,0.54155470911638537,0.67787883438605767,0.85338150699132331,0.90292728575329151,0.94876133703160637,0.9904630684768454,0.99909572644874167,1,1,null,0.85338150699132331,0.85338150699132331,0.85338150699132331]
["2013-02-27T12:00:02.285","2013-02-27T12:00:00",null,9.9907381953970713,10.294310397052971,10.597882598708871,10.901454800364771,11.205027002020671,11.508599203676571,11.812171405332471,12.115743606988371,12.419315808644271,null,0.52498337054913968,0.6637153870192557,0.84148925831140264,0.89318005805542555,0.94105398222843939,0.9846694088635507,0.99513164355543482,0.99777086054806086,0.99942168551954413,null,0.84148925831140264,0.84148925831140264,0.84148925831140264]
["2013-02-27T13:00:02.290","2013-02-27T13:00:00",null,9.9394553470909308,10.243027548746831,10.546599750402731,10.850171952058631,11.153744153714531,11.45731635537043,11.76088855702633,12.06446075868223,12.36803296033813,null,0.50738158072580886,0.64856354763131085,0.82865067684528149,0.88252855680630127,0.93246338349148528,0.97803456455141102,0.99035792038948967,0.9947531104409546,0.99807579000139224,null,0.82865067684528149,0.82865067684528149,0.82865067684528149]
["2013-02-27T14:00:02.295","2013-02-27T14:00:00",null,10.109773333692154,10.413345535348054,10.716917737003953,11.020489938659853,11.324062140315753,11.627634341971653,11.931206543627553,12.234778745283453,12.538350946939353,null,0.48823411401835048,0.63187654616797395,0.81428744811250375,0.87035240829052052,0.92235865229661018,0.96989610259008607,0.98409109438309472,0.99026328711086964,0.99526833606899723,null,0.81428744811250375,0.81428744811250375,0.81428744811250375]
["2013-02-27T15:00:02.300","2013-02-27T15:00:00",null,10.15227913941839,10.45585134107429,10.75942354273019,11.06299574438609,11.36656794604199,11.670140147697889,11.973712349353789,12.277284551009689,12.580856752665589,null,0.4668154486240107,0.6129709200614335,0.79775816878020034,0.85606278321889173,0.91019301858956492,0.95973879735153322,0.97584748433441415,0.98383873897344121,0.99056821656420102,null,0.79775816878020034,0.79775816878020034,0.79775816878020034]
["2013-02-27T16:00:02.305","2013-02-27T16:00:00",null,10.269717298982361,10.573289500638261,10.87686170229416,11.18043390395006,11.48400610560596,11.78757830726186,12.09115050891776,12.39472271057366,12.69829491222956,null,0.44300992164669833,0.59172049160686269,0.77892614633480883,0.83951247426911713,0.89579824543058051,0.94739441189598339,0.96544833849494338,0.97529019947142925,0.98378616492976356,null,0.77892614633480883,0.77892614633480883,0.77892614633480883]
["2013-02-27T17:00:02.310","2013-02-27T17:00:00",null,10.190718487318456,10.494290688974356,10.797862890630256,11.101435092286156,11.405007293942056,11.708579495597956,12.012151697253856,12.315723898909756,12.619296100565656,null,0.419635501827544,0.57090117031044996,0.7605357458563109,0.82340378728623609,0.88185560904722526,0.93550216321606272,0.95551184423983726,0.96720431155378206,0.97746676487969075,null,0.7605357458563109,0.7605357458563109,0.7605357458563109]
["2013-02-27T18:00:02.315","2013-02-27T18:00:00",null,9.9643839125256122,10.267956114181512,10.57152831583741,10.87510051749331,11.17867271914921,11.48224492080511,11.78581712246101,12.08938932411691,12.39296152577281,null,0.40070884610353241,0.55446652425676657,0.74644590215065787,0.81152205341505101,0.87207683692315263,0.92770017513427572,0.94959200692171586,0.96307199172070623,0.97503784406177596,null,0.74644590215065787,0.74644590215065787,0.74644590215065787]
["2013-02-27T19:00:02.320","2013-02-27T19:00:00",null,9.7453980463179892,10.048970247973889,10.352542449629789,10.656114651285689,10.959686852941589,11.263259054597489,11.566831256253389,11.870403457909289,12.173975659565189,null,0.38604068791742341,0.54221677207983687,0.73646734866060948,0.80367800609832174,0.86626214769238685,0.92379918109338222,0.94749955998333901,0.96270397341496161,0.97631013591877891,null,0.73646734866060948,0.73646734866060948,0.73646734866060948]
["2013-02-27T20:00:02.325","2013-02-27T20:00:00",null,9.6915475523238257,9.9951197539797256,10.298691955635626,10.602264157291525,10.905836358947425,11.209408560603325,11.512980762259225,11.816552963915125,12.120125165571025,null,0.37431667617727177,0.53282704787898005,0.72927521948548502,0.79855729424410304,0.86309719026298271,0.922484830001437,0.94794118195023258,0.96480693516207405,0.97999031897622557,null,0.72927521948548502,0.72927521948548502,0.72927521948548502]
["2013-02-27T21:00:02.330","2013-02-27T21:00:00",null,9.5583056033633707,9.8618778050192706,10.165450006675171,10.46902220833107,10.77259440998697,11.07616661164287,11.37973881329877,11.68331101495467,11.98688321661057,null,0.36623078825962457,0.52700184383947868,0.72557400681056716,0.79685389522894201,0.86327594201148727,0.92445109923498714,0.95158982058147257,0.97005382472111945,0.98676185580192755,null,0.72557400681056716,0.72557400681056716,0.72557400681056716]
["2013-02-27T22:00:02.335","2013-02-27T22:00:00",null,9.4632295942675952,9.7668017959234952,10.070373997579395,10.373946199235295,10.677518400891195,10.981090602547095,11.284662804202995,11.588235005858895,11.891807207514795,null,0.35960645875622049,0.52261716859674934,0.72328177850621467,0.79653845096687514,0.86482161889561493,0.92775274917795358,0.95656332511339337,0.97660455056337458,0.99480568448463247,null,0.72328177850621467,0.72328177850621467,0.72328177850621467]
["2013-02-27T23:00:02.340","2013-02-27T23:00:00",null,9.3508479213789766,9.6544201230348765,9.9579923246907764,10.261564526346678,10.565136728002578,10.868708929658478,11.172281131314378,11.475853332970278,11.779425534626178,null,0.35552671296682242,0.52071398821561266,0.72341847101977697,0.79859935347904532,0.86870158331903735,0.93334662742527252,0.96377648390598891,0.98534235662262659,1,null,0.72341847101977697,0.72341847101977697,0.72341847101977697]
["2013-02-28T00:00:02.345","2013-02-28",null,9.3161012267437417,9.6196734283996417,9.9232456300555416,10.226817831711442,10.530390033367341,10.833962235023241,11.137534436679141,11.441106638335041,11.744678839990941,null,0.35348684007212339,0.5207875918767616,0.72548988834068273,0.80254240675488109,0.87441112446244751,0.94071750834890144,0.97272458613995216,0.99578356169703963,1,null,0.72548988834068273,0.72548988834068273,0.72548988834068273]
["2013-02-28T01:00:02.350","2013-02-28T01:00:00",null,9.2074725976974943,9.5110447993533942,9.8146170010092941,10.118189202665194,10.421761404321094,10.725333605976994,11.028905807632894,11.332478009288794,11.636050210944694,null,0.35381279914292579,0.52318496826846972,0.72982198953973432,0.80870408467392041,0.88228671620538346,0.95021238063711388,0.98375462050355666,1,1,null,0.72982198953973432,0.72982198953973432,0.72982198953973432]
["2013-02-28T02:00:02.355","2013-02-28T02:00:00",null,9.1724531020476476,9.4760253037035476,9.7795975053594475,10.083169707015347,10.386741908671247,10.690314110327147,10.993886311983047,11.297458513638947,11.601030715294847,null,0.3562942940045184,0.52767479159855468,0.73619396363348488,0.81685306144398095,0.89209703275566277,0.96159991849772752,0.9966247463958845,1,1,null,0.73619396363348488,0.73619396363348488,0.73619396363348488]
["2013-02-28T03:00:02.360","2013-02-28T03:00:00",null,9.0293160161840156,9.3328882178399155,9.6364604194958154,9.9400326211517154,10.243604822807615,10.547177024463515,10.850749226119415,11.154321427775315,11.457893629431215,null,0.35464346903303517,0.5279166321994726,0.73820229210197719,0.82053324450142762,0.89733340750597268,0.96830836647101604,1,1,1,null,0.73820229210197719,0.73820229210197719,0.73820229210197719]
["2013-02-28T04:00:02.365","2013-02-28T04:00:00",null,9.042377873474301,9.3459500751302009,9.6495222767861009,9.9530944784420008,10.256666680097902,10.560238881753802,10.863811083409702,11.167383285065602,11.470955486721502,null,0.35221454821512033,0.52740140657143009,0.73947458395898014,0.82348790575612052,0.90187580487973551,0.97434386668522865,1,1,1,null,0.73947458395898014,0.73947458395898014,0.73947458395898014]
["2013-02-28T05:00:02.370","2013-02-28T05:00:00",null,9.1134617628252741,9.417033964481174,9.720606166137074,10.024178367792974,10.327750569448874,10.631322771104774,10.934894972760674,11.238467174416574,11.542039376072474,null,0.3541387582137282,0.53136548946473694,0.74535236204215927,0.83116371613308082,0.91123398465438565,0.98530029738768421,1,1,1,null,0.74535236204215927,0.74535236204215927,0.74535236204215927]
["2013-02-28T06:00:02.375","2013-02-28T06:00:00",null,9.0718160714255482,9.3753882730814482,9.6789604747373481,9.982532676393248,10.286104878049148,10.589677079705048,10.893249281360948,11.196821483016848,11.500393684672748,null,0.34991180510203229,0.52909429077785552,0.74493176969273678,0.83246755241629056,0.91416761629160748,0.98976909110029809,1,1,1,null,0.74493176969273678,0.74493176969273678,0.74493176969273678]
["2013-02-28T07:00:02.380","2013-02-28T07:00:00",null,9.0931806788486167,9.3967528805045166,9.7003250821604166,10.003897283816316,10.307469485472216,10.611041687128116,10.914613888784016,11.218186090439916,11.521758292095816,null,0.34898650193330283,0.53031400859118072,0.74814930116581879,0.83756723465303817,0.92103378639592948,0.99830711579357445,1,1,1,null,0.74814930116581879,0.74814930116581879,0.74814930116581879]
["2013-02-28T08:00:02.385","2013-02-28T08:00:00",null,9.2501021490087769,9.5536743506646769,9.8572465523205768,10.160818753976477,10.464390955632377,10.767963157288277,11.071535358944177,11.375107560600076,11.678679762255976,null,0.34682045133377704,0.53028246416497404,0.75012608520810442,0.841436684267725,0.92668023868692628,1,1,1,1,null,0.75012608520810442,0.75012608520810442,0.75012608520810442]
["2013-02-28T09:00:02.390","2013-02-28T09:00:00",null,9.4423906038443182,9.7459628055002181,10.049535007156118,10.353107208812018,10.656679410467918,10.960251612123818,11.263823813779718,11.567396015435618,11.870968217091518,null,0.34142635445243374,0.52708596230936322,0.74900100067339925,0.84225683934909878,0.92932997048828792,1,1,1,1,null,0.74900100067339925,0.74900100067339925,0.74900100067339925]
["2013-02-28T10:00:02.395","2013-02-28T10:00:00",null,9.6562531624057169,9.9598253640616168,10.263397565717517,10.566969767373417,10.870541969029317,11.174114170685217,11.477686372341116,11.781258573997016,12.084830775652916,null,0.33170015637203892,0.51964147772458535,0.74370153707067599,0.83898673383233902,0.92797356016140042,1,1,1,1,null,0.74370153707067599,0.74370153707067599,0.74370153707067599]
["2013-02-28T11:00:02.400","2013-02-28T11:00:00",null,9.7837733140834935,10.087345515739393,10.390917717395293,10.694489919051193,10.998062120707093,11.301634322362993,11.605206524018893,11.908778725674793,12.212350927330693,null,0.31874591200982655,0.50903203571040334,0.73531071969969752,0.8326883633997374,0.92364145896234884,0.99753953475587853,0.99930602262345292,1,1,null,0.73531071969969752,0.73531071969969752,0.73531071969969752]
["2013-02-28T12:00:02.405","2013-02-28T12:00:00",null,10.001986411755022,10.305558613410922,10.60913081506682,10.91270301672272,11.21627521837862,11.51984742003452,11.823419621690419,12.126991823346319,12.430564025002219,null,0.30156471453591827,0.49427975905440985,0.72285067134805658,0.82238385083888665,0.91538733410493267,0.99122013470580572,0.99481619929336795,0.99725563492001834,0.9989169747002371,null,0.72285067134805658,0.72285067134805658,0.72285067134805658]
["2013-02-28T13:00:02.410","2013-02-28T13:00:00",null,10.174152406909766,10.477724608565666,10.781296810221566,11.084869011877466,11.388441213533365,11.692013415189265,11.995585616845165,12.299157818501065,12.602730020156965,null,0.28269063285558449,0.47784511300072646,0.70870825359872569,0.81041799849781715,0.90548238427603323,0.98326042449298534,0.98870709541800639,0.99290250410349568,0.99624621328140439,null,0.70870825359872569,0.70870825359872569,0.70870825359872569]
["2013-02-28T14:00:02.415","2013-02-28T14:00:00",null,10.258945802324927,10.562518003980827,10.866090205636727,11.169662407292627,11.473234608948527,11.776806810604427,12.080379012260327,12.383951213916227,12.687523415572127,null,0.25935827227137243,0.45704682132178481,0.69031785312022775,0.79429879670620063,0.89150820346647131,0.97132611657812251,0.97870751231048692,0.98474301252469953,0.98984269476144715,null,0.69031785312022775,0.69031785312022775,0.69031785312022775]
["2013-02-28T15:00:02.420","2013-02-28T15:00:00",null,10.371228404430379,10.674800606086279,10.978372807742179,11.281945009398079,11.585517211053979,11.889089412709879,12.192661614365779,12.496233816021679,12.799806017677579,null,0.23394397955751908,0.43420865674814413,0.66991912417323751,0.77620281087229848,0.87558878304083043,0.9574781134733874,0.96682577843930184,0.97473291460844447,0.98162011433023766,null,0.66991912417323751,0.66991912417323751,0.66991912417323751]
["2013-02-28T16:00:02.425","2013-02-28T16:00:00",null,10.33996872965195,10.64354093130785,10.94711313296375,11.25068533461965,11.55425753627555,11.85782973793145,12.16140193958735,12.46497414124325,12.76854634289915,null,0.20655290280138008,0.40945679698463117,0.64765927408005275,0.75630879274461515,0.85792390436508625,0.94193722616222675,0.95330373440536909,0.96312456576438399,0.97184134220616503,null,0.64765927408005275,0.64765927408005275,0.64765927408005275]
["2013-02-28T17:00:02.430","2013-02-28T17:00:00",null,10.336459378005557,10.640031579661457,10.943603781317357,11.247175982973257,11.550748184629157,11.854320386285057,12.157892587940957,12.461464789596857,12.765036991252757,null,0.17933006298501009,0.38487317416088723,0.62556766092663696,0.73657249674796532,0.84042726262911105,0.92655406098209958,0.93992889769373422,0.9516634242426214,0.96220977740439029,null,0.62556766092663696,0.62556766092663696,0.62556766092663696]
["2013-02-28T18:00:02.435","2013-02-28T18:00:00",null,10.188047004886137,10.491619206542037,10.795191408197937,11.098763609853837,11.402335811509737,11.705908013165637,12.009480214821536,12.313052416477436,12.616624618133336,null,0.15598718759206245,0.36408539729068118,0.6071982900656101,0.72048483938255548,0.826505655863227,0.9146828419196501,0.9300029182473637,0.9435880511337098,0.95589037735431748,null,0.6071982900656101,0.6071982900656101,0.6071982900656101]
["2013-02-28T19:00:02.440","2013-02-28T19:00:00",null,9.9774791900385509,10.281051391694451,10.584623593350351,10.888195795006251,11.191767996662151,11.495340198318051,11.79891239997395,12.10248460162985,12.40605680328575,null,0.13635603968276822,0.34695677386045071,0.59243549860088107,0.70795118736976559,0.81607496559754944,0.90624996531372937,0.92346270721384416,0.93884587239397133,0.95286211243847563,null,0.59243549860088107,0.59243549860088107,0.59243549860088107]
["2013-02-28T20:00:02.445","2013-02-28T20:00:00",null,9.921652112414332,10.225224314070232,10.528796515726132,10.832368717382032,11.135940919037932,11.439513120693832,11.743085322349732,12.046657524005632,12.350229725661531,null,0.12589380499088404,0.33903912288257254,0.58691522401471108,0.70469159666174142,0.81494988106284427,0.90715423886498769,0.92628067595497476,0.94349341785508978,0.95924460134096179,null,0.58691522401471108,0.58691522401471108,0.58691522401471108]
["2013-02-28T21:00:02.450","2013-02-28T21:00:00",null,9.7283484008807477,10.031920602536648,10.335492804192548,10.639065005848447,10.942637207504347,11.246209409160247,11.549781610816147,11.853353812472047,12.156926014127947,null,0.11912226816518211,0.33478062534466996,0.5850120436335744,0.70500704092380828,0.81736828707202358,0.91155994372518823,0.93256853157884079,0.95156879096400138,0.96901285865629894,null,0.5850120436335744,0.5850120436335744,0.5850120436335744]
["2013-02-28T22:00:02.455","2013-02-28T22:00:00",null,9.6459731014516628,9.9495453031075627,10.253117504763464,10.556689706419364,10.860261908075264,11.163834109731164,11.467406311387064,11.770978513042964,12.074550714698864,null,0.11269772002775373,0.33074293879021416,0.58322452614852882,0.70533299999461074,0.81969205980258275,0.91577638202814859,0.93857248736684673,0.95926563095843276,0.97832897919600692,null,0.58322452614852882,0.58322452614852882,0.58322452614852882]
["2013-02-28T23:00:02.460","2013-02-28T23:00:00",null,9.4744211942335443,9.7779933958894443,10.081565597545344,10.385137799201244,10.688710000857144,10.992282202513044,11.295854404168944,11.599426605824844,11.902998807480744,null,0.10553713527883601,0.32595870081553346,0.58066942762578722,0.70488086321898158,0.82121670706923922,0.91917266524973507,0.9437352584560077,0.96611077144528357,0.98676185580192766,null,0.58066942762578722,0.58066942762578722,0.58066942762578722]
["2013-03-01T00:00:02.465","2013-03-01",null,9.4914322047862072,9.7950044064421071,10.098576608098007,10.402148809753909,10.705721011409809,11.009293213065709,11.312865414721609,11.616437616377508,11.920009818033408,null,9.9417516594738936E-2,0.32212079562705331,0.57896602861062618,0.70519630748104845,0.82342481690370728,0.92317880737798419,0.94944479959941785,0.97342907832523473,0.99560480994853529,null,0.58637896876919737,0.58798773450573838,0.58951238177239484]
["2013-03-01T01:00:02.470","2013-03-01T01:00:00",null,9.3203064483911486,9.6238786500470486,9.9274508517029485,10.231023053358848,10.534595255014748,10.838167456670648,11.141739658326548,11.445311859982448,11.748884061638348,null,9.5180048674307446E-2,0.32014401158476768,0.57910272112418848,0.70732029884563197,0.8274309590319564,0.9289514373738077,0.95689979899293132,0.98246129902908252,1,null,0.59383396816271083,0.59701995520958617,0.60005873493416351]
["2013-03-01T02:00:02.475","2013-03-01T02:00:00",null,9.2981375073565093,9.6017097090124093,9.9052819106683092,10.208854112324209,10.512426313980109,10.815998515636009,11.119570717291909,11.423142918947809,11.726715120603709,null,9.2277961463292341E-2,0.31947106382569174,0.58051170549475384,0.71068503764101176,0.83264630416479513,0.93590172594801413,0.96550091253862103,0.99261860426763537,1,null,0.60243508170840054,0.60717726044813902,0.61169862820443066]
["2013-03-01T03:00:02.480","2013-03-01T03:00:00",null,9.1873946024283413,9.4909668040842412,9.7945390057401411,10.098111207396041,10.401683409051941,10.705255610707841,11.008827812363741,11.312400014019641,11.615972215675541,null,9.1909943157547677E-2,0.32125858131073726,0.58433909587449839,0.716415608401893,0.84017490721945753,0.94512321320910198,0.97633116553624988,1,1,null,0.6132653347060294,0.61952164590368886,0.62547302764801693]
["2013-03-01T04:00:02.485","2013-03-01T04:00:00",null,9.1014885369058263,9.4050607385617262,9.7086329402176261,10.012205141873528,10.315777343529428,10.619349545185328,10.922921746841228,11.226493948497128,11.530066150153027,null,9.2593405725359207E-2,0.324097579669339,0.58918642270159249,0.72315560080138819,0.8487024171039983,0.95533309249133269,0.98812878093755041,1,1,null,0.62506295010732993,0.63282287895417477,0.64019375987780369]
["2013-03-01T05:00:02.490","2013-03-01T05:00:00",null,9.1196738170533056,9.4232460187092055,9.7268182203651055,10.030390422021005,10.333962623676905,10.637534825332805,10.941107026988705,11.244679228644605,11.548251430300505,null,9.2141268949730043E-2,0.32582200830197117,0.59296123903765929,0.72885462713606275,0.85620999054118951,0.96454406494368505,0.99894851912644367,1,1,null,0.63588268829622319,0.64516726440972461,0.65398918893886104]
["2013-03-01T06:00:02.495","2013-03-01T06:00:00",null,9.0697080676181479,9.3732802692740478,9.6768524709299477,9.9804246725858476,10.283996874241748,10.587569075897648,10.891141277553547,11.194713479209447,11.498285680865347,null,9.0669195726751362E-2,0.32657907453093166,0.59581075220499657,0.73365989472821458,0.86286586447080027,0.97294539712339911,1,1,1,null,0.64592433063868493,0.65676509844504949,0.66705909619716464]
["2013-03-01T07:00:02.500","2013-03-01T07:00:00",null,9.0721733180320836,9.3757455196879835,9.6793177213438835,9.9828899229997816,10.286462124655682,10.590034326311581,10.893606527967481,11.197178729623381,11.500750931279281,null,8.8934252285383639E-2,0.32707327054150309,0.59839739515394486,0.73821280691071289,0.86926938299075751,0.98109437389345966,1,1,1,null,0.65572413238022875,0.66812109187945645,0.67988716285455031]
["2013-03-01T08:00:02.505","2013-03-01T08:00:00",null,9.3540383824526767,9.6576105841085766,9.9611827857644766,10.264754987420377,10.568327189076276,10.871899390732176,11.175471592388076,11.479043794043976,11.782615995699876,null,8.276205955760875E-2,0.32321433573555186,0.59670451094751942,0.73855979559898643,0.87154058167763893,0.98517411968285773,1,1,1,null,0.66152830680225894,0.67554454684676324,0.68885629470598464]
["2013-03-01T09:00:02.510","2013-03-01T09:00:00",null,9.4393680246873473,9.7429402263432472,10.046512427999147,10.350084629655047,10.653656831310947,10.957229032966847,11.260801234622747,11.564373436278647,11.867945637934547,null,7.5685593278575519E-2,0.31846164218707784,0.59412838280730673,0.73803405516220832,0.87294956604820428,0.98841268077341082,1,1,1,null,0.66649129652544414,0.68214784673269613,0.69700527147604519]
["2013-03-01T10:00:02.515","2013-03-01T10:00:00",null,9.6845933138206899,9.9881655154765898,10.29173771713249,10.59530991878839,10.89888212044429,11.20245432210019,11.506026523756089,11.809598725411989,12.113170927067889,null,6.6474620826223213E-2,0.3115849572740203,0.58943877811124612,0.73540535297831777,0.8722661034803928,0.98956930973432267,1,1,1,null,0.66939338373645929,0.68671127372393004,0.70313540496887783]
["2013-03-01T11:00:02.520","2013-03-01T11:00:00",null,9.8291003686150251,10.132672570270925,10.436244771926825,10.739816973582725,11.043389175238625,11.346961376894525,11.650533578550425,11.954105780206325,12.257677981862225,null,5.3110298923323918E-2,0.30062852657156469,0.58076406090440746,0.72887565675353372,0.86776576534157224,0.98698266678537439,0.99924293377103957,1,1,null,0.66863631750749886,0.68767863612760172,0.70574307753529719]
["2013-03-01T12:00:02.525","2013-03-01T12:00:00",null,9.9087234328928258,10.212295634548726,10.515867836204624,10.819440037860524,11.123012239516424,11.426584441172324,11.730156642828224,12.033728844484123,12.337301046140023,null,3.54349054388442E-2,0.28547668718361985,0.56798856829069966,0.71835033320923614,0.85936443316185818,0.98058966307415274,0.9947531104409546,0.99731872377243169,0.99904315240506381,null,0.66414649417741389,0.68499735990003341,0.704786229940361]
["2013-03-01T13:00:02.530","2013-03-01T13:00:00",null,10.102088539199682,10.405660740855582,10.709232942511482,11.012805144167382,11.316377345823282,11.619949547479182,11.923521749135082,12.227093950790982,12.530666152446882,null,1.5046691300589485E-2,0.26765408637684224,0.55257385868436582,0.70521733709851919,0.84838697284193143,0.97166259045766057,0.9877607626318059,0.99217698230074192,0.99565738399221282,null,0.65715414636826519,0.67985561842834363,0.70140046152751001]
["2013-03-01T14:00:02.535","2013-03-01T14:00:00",null,10.069103956572906,10.372676158228806,10.676248359884706,10.979820561540606,11.283392763196506,11.586964964852406,11.890537166508306,12.194109368164206,12.497681569820106,null,1.1955337532334256E-2,0.26707577189638632,0.55437189097814688,0.70925502365297499,0.85454865076097075,0.97983259684519219,0.99783394940047432,1,1,null,0.66722733313693361,0.69173735229952871,0.7150066240313272]
["2013-03-01T15:00:02.540","2013-03-01T15:00:00",null,10.270003075974639,10.573575277630539,10.877147479286439,11.180719680942339,11.484291882598239,11.787864084254139,12.091436285910039,12.395008487565939,12.698580689221838,null,7.440278661283696E-2,0.33218346758698619,0.62199262595654603,0.77925210540561118,0.92679590158301728,1,1,1,1,null,0.74363844821826264,0.77007267737946561,0.79518204063998743]
["2013-03-01T16:00:02.545","2013-03-01T16:00:00",null,10.343613197908008,10.647185399563909,10.950757601219809,11.254329802875709,11.557902004531609,11.861474206187509,12.165046407843409,12.468618609499309,12.772190811155209,null,0.13689229492828192,0.39732270770379274,0.68962387574368078,0.84924918715824738,0.99903263759632821,1,1,1,1,null,0.82001801887338499,0.84837645803319583,0.87531539801370539]
["2013-03-01T17:00:02.550","2013-03-01T17:00:00",null,10.235260097303275,10.538832298959175,10.842404500615075,11.145976702270975,11.449548903926875,11.753121105582775,12.056693307238675,12.360265508894575,12.663837710550474,null,0.2017266055917572,0.46477520574242293,0.75954735383516803,0.92150695278902939,1,1,1,1,1,null,0.89858466974550422,0.92883577447771626,0.95758326156074247]
["2013-03-01T18:00:02.555","2013-03-01T18:00:00",null,10.145494517645675,10.449066719301575,10.752638920957475,11.056211122613375,11.359783324269275,11.663355525925175,11.966927727581075,12.270499929236975,12.574072130892874,null,0.26729695286672184,0.53296374039254246,0.83020686853814463,0.99449024022256527,1,1,1,1,1,null,0.97785581280290612,1,1]
["2013-03-01T19:00:02.560","2013-03-01T19:00:00",null,10.067298120400226,10.370870322056126,10.674442523712026,10.978014725367926,11.281586927023826,11.585159128679726,11.888731330335625,12.192303531991525,12.495875733647425,null,0.33695756073982008,0.60513738755344004,0.90474634766454365,1,1,1,1,1,1,null,1,1,1]
["2013-03-01T20:00:02.565","2013-03-01T20:00:00",null,9.8473948690664628,10.150967070722363,10.454539272378263,10.758111474034163,11.061683675690063,11.365255877345962,11.668828079001862,11.972400280657762,12.275972482313662,null,0.41075048844599416,0.6813697508862645,0.9832814541104562,1,1,1,1,1,1,null,1,1,1]
["2013-03-01T21:00:02.570","2013-03-01T21:00:00",null,9.7892542644792755,10.092826466135175,10.396398667791075,10.699970869446975,11.003543071102875,11.307115272758775,11.610687474414675,11.914259676070575,12.217831877726475,null,0.48780300686019246,0.76077758645722871,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-01T22:00:02.575","2013-03-01T22:00:00",null,9.6652159348937108,9.9687881365496107,10.272360338205511,10.575932539861411,10.879504741517311,11.18307694317321,11.48664914482911,11.79022134648501,12.09379354814091,null,0.55071310752505986,0.82597991542644866,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-01T23:00:02.580","2013-03-01T23:00:00",null,9.5336631414257624,9.8372353430816624,10.140807544737562,10.444379746393462,10.747951948049362,11.051524149705262,11.355096351361162,11.658668553017062,11.962240754672962,null,0.55270040637608109,0.83031201662550025,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T00:00:02.585","2013-03-02",null,9.4157161748457519,9.7192883765016518,10.022860578157552,10.326432779813453,10.630004981469353,10.933577183125253,11.237149384781153,11.540721586437053,11.844293788092953,null,0.55746361473329065,0.83735693847832682,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T01:00:02.590","2013-03-02T01:00:00",null,9.2122106784043645,9.5157828800602644,9.8193550817161643,10.122927283372064,10.426499485027964,10.730071686683864,11.033643888339764,11.337216089995664,11.640788291651564,null,0.5661488467488649,0.84825028032836902,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T02:00:02.595","2013-03-02T02:00:00",null,9.0416747627736367,9.3452469644295366,9.6488191660854365,9.9523913677413383,10.255963569397238,10.559535771053138,10.863107972709038,11.166680174364938,11.470252376020838,null,0.57684240723293145,0.86113092102943245,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T03:00:02.600","2013-03-02T03:00:00",null,9.0028330238461489,9.3064052255020489,9.6099774271579488,9.9135496288138505,10.21712183046975,10.52069403212565,10.82426623378155,11.12783843543745,11.43141063709335,null,0.58985974044755718,0.87626173079990621,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T04:00:02.605","2013-03-02T04:00:00",null,8.9381601070748999,9.2417323087307999,9.5453045103866998,9.8488767120425997,10.1524489136985,10.4560211153544,10.7595933170103,11.063165518666199,11.366737720322099,null,0.60272986633988501,0.89126636286555316,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T05:00:02.610","2013-03-02T05:00:00",null,8.9301719007017883,9.2337441023576883,9.5373163040135882,9.8408885056694899,10.14446070732539,10.44803290898129,10.75160511063719,11.05517731229309,11.35874951394899,null,0.61603109939037093,0.9066915872806226,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T06:00:02.615","2013-03-02T06:00:00",null,8.8597041224986146,9.1632763241545145,9.4668485258104145,9.7704207274663126,10.073992929122213,10.377565130778112,10.681137332434012,10.984709534089912,11.288281735745812,null,0.62646178965604848,0.91925678371961916,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T07:00:02.620","2013-03-02T07:00:00",null,8.7866597725122375,9.0902319741681374,9.3938041758240374,9.6973763774799373,10.000948579135835,10.304520780791735,10.608092982447635,10.911665184103535,11.215237385759435,null,0.63606181003161655,0.93099131026850634,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T08:00:02.625","2013-03-02T08:00:00",null,8.8814232992393922,9.1849955008952922,9.4885677025511921,9.792139904207092,10.095712105862992,10.399284307518892,10.702856509174792,11.006428710830692,11.310000912486592,null,0.64402152024443693,0.94111707108085252,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T09:00:02.630","2013-03-02T09:00:00",null,9.0445992230863048,9.3481714247422047,9.6517436263981047,9.9553158280540046,10.258888029709905,10.562460231365804,10.866032433021704,11.169604634677604,11.473176836333504,null,0.65028834625083187,0.94957097730424433,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T10:00:02.635","2013-03-02T10:00:00",null,9.1915574172459618,9.4951296189018617,9.7987018205577616,10.102274022213662,10.405846223869561,10.709418425525461,11.012990627181361,11.316562828837261,11.620135030493161,null,0.65189711198737288,0.95348248615387343,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T11:00:02.640","2013-03-02T11:00:00",null,9.3846321531488819,9.6882043548047818,9.9917765564606817,10.295348758116582,10.598920959772482,10.902493161428382,11.206065363084281,11.509637564740181,11.813209766396081,null,0.65021474258968293,0.95415543391294944,1,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T12:00:02.645","2013-03-02T12:00:00",null,9.5330562225699076,9.8366284242258075,10.140200625881707,10.443772827537607,10.747345029193507,11.050917230849407,11.354489432505307,11.658061634161207,11.961633835817107,null,0.6440635794793792,0.95047525085550277,0.99863307486437691,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T13:00:02.650","2013-03-02T13:00:00",null,9.7335562387029881,10.037128440358888,10.340700642014788,10.644272843670688,10.947845045326588,11.251417246982488,11.554989448638388,11.858561650294288,12.162133851950188,null,0.63852227527573802,0.94733132304356971,0.99774983093058967,1,1,1,1,1,1,null,1,1,1]
["2013-03-02T14:00:02.655","2013-03-02T14:00:00",null,9.8733613214179989,10.176933523073899,10.480505724729799,10.784077926385699,11.087650128041599,11.391222329697499,11.694794531353399,11.998366733009298,12.301938934665198,null,0.62909049183993893,0.94038103446936328,0.993133829895678,0.99758159399082069,0.99966352612046205,1,1,1,1,null,1,1,1]
["2013-03-02T15:00:02.660","2013-03-02T15:00:00",null,10.007577597308549,10.311149798964449,10.614722000620349,10.918294202276249,11.221866403932149,11.525438605588048,11.829010807243948,12.132583008899848,12.436155210555748,null,0.61618882152140431,0.93002394786483467,0.98517411968285762,0.99189308246488161,0.99612003557657769,0.99848586754207902,1,1,1,null,1,1,1]
["2013-03-02T16:00:02.665","2013-03-02T16:00:00",null,10.126771401628291,10.430343603284191,10.733915804940091,11.037488006595991,11.341060208251891,11.644632409907791,11.948204611563691,12.251776813219591,12.555349014875491,null,0.60086874519369049,0.91730102929480462,0.97489063673947796,0.98392285744332564,0.99032637596328299,0.99476362524969009,0.9982440269411611,1,1,null,0.9982440269411611,1,1]
["2013-03-02T17:00:02.670","2013-03-02T17:00:00",null,10.13090091306206,10.43447311471796,10.73804531637386,11.04161751802976,11.34518971968566,11.64876192134156,11.95233412299746,12.25590632465336,12.55947852630926,null,0.58523322460390981,0.90425215165397221,0.96429170953403143,0.9756371881597028,0.98422778689665702,0.99074696831270537,0.99619363923772652,0.99982124825149543,1,null,0.99619363923772652,0.99982124825149543,1]
["2013-03-02T18:00:02.675","2013-03-02T18:00:00",null,10.113981812069811,10.417554013725711,10.721126215381611,11.024698417037511,11.328270618693411,11.631842820349311,11.935415022005211,12.238987223661111,12.542559425317011,null,0.57055455160906521,0.8921496067993403,0.95461808549731442,0.96825579242733828,0.9790124417638183,0.98759252569203682,0.99499495104187241,1,1,null,0.99499495104187241,1,1]
["2013-03-02T19:00:02.680","2013-03-02T19:00:00",null,9.8633762164935987,10.166948418149499,10.4705206198054,10.7740928214613,11.0776650231172,11.3812372247731,11.684809426429,11.9883816280849,12.2919538297408,null,0.55785266265650635,0.88202384598699413,0.94692124550288304,0.96285118073725939,0.9757738806732652,0.9864043523049183,0.99574150246209736,1,1,null,0.99574150246209736,1,1]
["2013-03-02T20:00:02.685","2013-03-02T20:00:00",null,9.8111619098381002,10.114734111494,10.4183063131499,10.7218785148058,11.0254507164617,11.3290229181176,11.6325951197735,11.9361673214294,12.2397395230853,null,0.54798977206254917,0.87467399468083629,0.94192671135349104,0.96008578603980654,0.9751114477229248,0.98772921820559911,0.99895903393517937,1,1,null,0.99895903393517937,1,1]
["2013-03-02T21:00:02.690","2013-03-02T21:00:00",null,9.6982057515182678,10.001777953174168,10.305350154830068,10.608922356485968,10.912494558141868,11.216066759797767,11.519638961453667,11.823211163109567,12.126783364765467,null,0.54048219862535796,0.86962688648776654,0.93919286108224487,0.95953901598555735,0.97662558018084578,0.99119910508833453,1,1,1,null,1,1,1]
["2013-03-02T22:00:02.695","2013-03-02T22:00:00",null,9.6478933765490638,9.9514655782049637,10.255037779860864,10.558609981516764,10.862182183172663,11.165754384828563,11.469326586484463,11.772898788140363,12.076470989796263,null,0.53453081688102988,0.86606236632641098,0.93787850999029965,0.96033814144946006,0.97943303411324079,0.99589922459313074,1,1,1,null,1,1,1]
["2013-03-02T23:00:02.700","2013-03-02T23:00:00",null,9.4620435320866587,9.7656157337425586,10.069187935398459,10.372760137054359,10.676332338710258,10.979904540366158,11.283476742022058,11.587048943677958,11.890621145333858,null,0.52723353961854991,0.86110989141196126,0.93514465971905347,0.95968622330785525,0.98073687039645052,0.99906418202253489,1,1,1,null,1,1,1]
["2013-03-03T00:00:02.705","2013-03-03",null,9.4155840478800226,9.7191562495359225,10.022728451191822,10.326300652847722,10.629872854503622,10.933445056159522,11.237017257815422,11.540589459471322,11.844161661127222,null,0.5225229053050181,0.85868097059404647,0.93485024507445769,0.96141065194048736,0.98436447941021943,1,1,1,1,null,1,1,1]
["2013-03-03T01:00:02.710","2013-03-03T01:00:00",null,9.2537881990625266,9.5573604007184265,9.8609326023743264,10.164504804030226,10.468077005686126,10.771649207342026,11.075221408997926,11.378793610653826,11.682365812309726,null,0.51917919612710939,0.85761897491175465,0.93592275556548499,0.96449149090000708,0.98933798394214023,1,1,1,1,null,1,1,1]
["2013-03-03T02:00:02.715","2013-03-03T02:00:00",null,9.2844739081618126,9.5880461098177125,9.8916183114736125,10.195190513129512,10.498762714785412,10.802334916441312,11.105907118097212,11.409479319753112,11.713051521409012,null,0.51723395651103043,0.85787133032140817,0.93823601348730867,0.96873947362917412,0.99541554339129501,1,1,1,1,null,1,1,1]
["2013-03-03T03:00:02.720","2013-03-03T03:00:00",null,9.2066240435914803,9.5101962452473803,9.8137684469032802,10.117340648559182,10.420912850215082,10.724485051870982,11.028057253526882,11.331629455182782,11.635201656838682,null,0.51571982405310945,0.85855479288921965,0.94098037856729033,0.97341856351649925,1,1,1,1,1,null,1,1,1]
["2013-03-03T04:00:02.725","2013-03-03T04:00:00",null,9.1024297903257025,9.4060019919816025,9.7095741936375024,10.013146395293402,10.316718596949302,10.620290798605202,10.923863000261102,11.227435201917002,11.531007403572902,null,0.51624556448988757,0.86123606911678796,0.94568049807208654,0.98001134859369665,1,1,1,1,1,null,1,1,1]
["2013-03-03T05:00:02.730","2013-03-03T05:00:00",null,9.1497555506469528,9.4533277523028527,9.7568999539587526,10.060472155614653,10.364044357270553,10.667616558926452,10.971188760582352,11.274760962238252,11.578333163894152,null,0.51394282137679947,0.86117298026437461,0.94770985615805003,0.98400697591321018,1,1,1,1,1,null,1,1,1]
["2013-03-03T06:00:02.735","2013-03-03T06:00:00",null,9.1827585063224024,9.4863307079783024,9.7899029096342023,10.093475111290104,10.397047312946004,10.700619514601904,11.004191716257804,11.307763917913704,11.611336119569604,null,0.5097368978825747,0.85925928507450233,0.94794118195023236,0.9862571449826204,1,1,1,1,1,null,1,1,1]
["2013-03-03T07:00:02.740","2013-03-03T07:00:00",null,9.0766136304877492,9.3801858321436491,9.683758033799549,9.987330235455449,10.290902437111349,10.594474638767249,10.898046840423149,11.201619042079049,11.505191243734949,null,0.50508935242145625,0.85671470136049632,0.94737338227851198,0.98755046645709454,1,1,1,1,1,null,1,1,1]
["2013-03-03T08:00:02.745","2013-03-03T08:00:00",null,9.3934327356006886,9.6970049372565885,10.000577138912488,10.30414934056839,10.60772154222429,10.91129374388019,11.21486594553609,11.51843814719199,11.82201034884789,null,0.50269197602974813,0.85655697922946294,0.94932913670332653,0.99149351973293032,1,1,1,1,1,null,1,1,1]
["2013-03-03T09:00:02.750","2013-03-03T09:00:00",null,9.7832387899859174,10.086810991641817,10.390383193297717,10.693955394953617,10.997527596609517,11.301099798265417,11.604671999921317,11.908244201577217,12.211816403233117,null,0.49397519958796726,0.85019551994444797,0.9451863020615151,0.98943261722076015,0.99991588153011546,1,1,1,1,null,1,1,1]
["2013-03-03T10:00:02.755","2013-03-03T10:00:00",null,10.19657385441228,10.50014605606818,10.803718257724082,11.107290459379982,11.410862661035882,11.714434862691782,12.018007064347682,12.321579266003582,12.625151467659482,null,0.47806629397106198,0.83675759438039976,0.93407214922802606,0.98051605941300357,0.99308125585200013,0.9951421583641703,0.99701379431910042,0.9987907969954104,1,null,0.99701379431910042,0.9987907969954104,1]
["2013-03-03T11:00:02.760","2013-03-03T11:00:00",null,10.390745475344236,10.694317677000136,10.997889878656036,11.301462080311936,11.605034281967836,11.908606483623736,12.212178685279635,12.515750886935535,12.819323088591435,null,0.45952868617026621,0.82071199624993219,0.92039238306305993,0.96906543269997658,0.98374410569482107,0.98781333667548354,0.99158815301155045,0.99518421759911269,0.9981178492363344,null,0.99158815301155045,0.99518421759911269,0.9981178492363344]
["2013-03-03T12:00:02.765","2013-03-03T12:00:00",null,10.653102786422297,10.956674988078197,11.260247189734097,11.563819391389996,11.867391593045896,12.170963794701796,12.474535996357696,12.778108198013596,13.081680399669496,null,0.43500815219893563,0.79879913484502096,0.90093998690227028,0.9519473240784817,0.96883410690779415,0.97500629963556906,0.98077892963139268,0.98628868940882719,0.99103086814856556,null,0.98077892963139268,0.98628868940882719,0.99103086814856556]
["2013-03-03T13:00:02.770","2013-03-03T13:00:00",null,10.870770748498003,11.174342950153903,11.477915151809803,11.781487353465703,12.085059555121603,12.388631756777503,12.692203958433403,12.995776160089303,13.299348361745203,null,0.40355835927086969,0.7700831921882012,0.87482120200313429,0.92829951923220277,0.94752058960080998,0.95592192178052404,0.96380802833219559,0.971336631386858,0.97801353493393983,null,0.96380802833219559,0.971336631386858,0.97801353493393983]
["2013-03-03T14:00:02.775","2013-03-03T14:00:00",null,11.065952434619325,11.369524636275225,11.673096837931125,11.976669039587025,12.280241241242924,12.583813442898824,12.887385644554724,13.190957846210624,13.494530047866524,null,0.36969016033362451,0.73896987313967322,0.84632607032976126,0.9022858824204224,0.92386226994579546,0.93451377119491985,0.9445343839199104,0.9541028598692719,0.96272500303243269,null,0.9445343839199104,0.9541028598692719,0.96272500303243269]
["2013-03-03T15:00:02.780","2013-03-03T15:00:00",null,11.180032274101141,11.483604475757041,11.787176677412941,12.09074887906884,12.39432108072474,12.69789328238064,13.00146548403654,13.30503768569244,13.60860988734834,null,0.33395032544144926,0.7060164625624219,0.81600136193640049,0.87447421331486097,0.89842694761447095,0.91134964755047676,0.92352579606625751,0.93516568933652477,0.9457541017332356,null,0.92352579606625751,0.93516568933652477,0.9457541017332356]
["2013-03-03T16:00:02.785","2013-03-03T16:00:00",null,11.238128304611267,11.541700506267167,11.845272707923067,12.148844909578967,12.452417111234867,12.755989312890767,13.059561514546667,13.363133716202567,13.666705917858467,null,0.2955397291304413,0.67044486461001562,0.78311104021156253,0.84413899011276461,0.87053116003902498,0.88576711789685447,0.90015137624710317,0.91389423126448288,0.9265014869384216,null,0.90015137624710317,0.91389423126448288,0.9265014869384216]
["2013-03-03T17:00:02.790","2013-03-03T17:00:00",null,11.281542050956727,11.585114252612627,11.888686454268527,12.192258655924427,12.495830857580327,12.799403059236226,13.102975260892126,13.406547462548026,13.710119664203926,null,0.25845399872011415,0.636156073323348,0.75146146591752094,0.81500245510652236,0.84379200142449085,0.86130967277793724,0.87785998172771174,0.89368476887473269,0.90826880859095716,null,0.87785998172771174,0.89368476887473269,0.90826880859095716]
["2013-03-03T18:00:02.795","2013-03-03T18:00:00",null,11.123415138868097,11.426987340523997,11.730559542179897,12.034131743835797,12.337703945491697,12.641276147147597,12.944848348803497,13.248420550459397,13.551992752115297,null,0.22529029196815162,0.60571570203389602,0.72360773757701724,0.78959867720140453,0.82072251105866778,0.84045880705531784,0.85912259256094026,0.87696622298518911,0.89348498750875693,null,0.85912259256094026,0.87696622298518911,0.89348498750875693]
["2013-03-03T19:00:02.800","2013-03-03T19:00:00",null,10.967889789164406,11.271461990820306,11.575034192476206,11.878606394132106,12.182178595788006,12.485750797443906,12.789322999099806,13.092895200755706,13.396467402411606,null,0.19603809406581815,0.57912375074165978,0.69952882557258023,0.76790662677994015,0.80130165932408481,0.82320400592026055,0.84391817912931766,0.86372807878711655,0.88211847926561437,null,0.84391817912931766,0.86372807878711655,0.88211847926561437]
["2013-03-03T20:00:02.805","2013-03-03T20:00:00",null,10.898995215630913,11.202567417286813,11.506139618942713,11.809711820598613,12.113284022254513,12.416856223910413,12.720428425566313,13.024000627222213,13.327572828878113,null,0.17006651648898002,0.55573881611376985,0.67859384138007628,0.74929541531799537,0.7848985576966081,0.80889335123116068,0.83160533809997461,0.85332893294764578,0.87353839533739575,null,0.83160533809997461,0.85332893294764578,0.87353839533739575]
["2013-03-03T21:00:02.810","2013-03-03T21:00:00",null,10.841614953777645,11.145187155433545,11.448759357089445,11.752331558745345,12.055903760401245,12.359475962057145,12.663048163713045,12.966620365368945,13.270192567024845,null,0.14682878918338801,0.53502464290471274,0.66026652975399169,0.7332393023787922,0.77098746573945953,0.7970326469774468,0.82168987346233968,0.84527458945620526,0.86725053971352972,null,0.82168987346233968,0.84527458945620526,0.86725053971352972]
["2013-03-03T22:00:02.815","2013-03-03T22:00:00",null,10.749571778394175,11.053143980050075,11.356716181705975,11.660288383361875,11.963860585017775,12.267432786673675,12.571004988329575,12.874577189985475,13.178149391641375,null,0.12690322662949802,0.51751748636000205,0.6450516015136335,0.72020093954669528,0.76001000541953279,0.7880109410823346,0.81452928871342201,0.83989100738359757,0.86357035665608306,null,0.81452928871342201,0.83989100738359757,0.86357035665608306]
["2013-03-03T23:00:02.820","2013-03-03T23:00:00",null,11.408909820626803,11.712482022282703,12.016054223938603,12.319626425594503,12.623198627250403,12.926770828906303,13.230343030562203,13.533915232218103,13.837487433874003,null,7.5517356338806532E-2,0.46921245502883024,0.59965917220221232,0.67759493455019804,0.72004321741566168,0.75056770717499832,0.77948343119779384,0.80714789298105749,0.83301432247053986,null,0.77948343119779384,0.80714789298105749,0.83301432247053986]
["2013-03-04T00:00:02.825","2013-03-04",null,11.321799503580609,11.625371705236509,11.928943906892409,12.232516108548309,12.536088310204208,12.839660511860108,13.143232713516008,13.446804915171908,13.750377116827808,null,2.6360625500054191E-2,0.42305244467971309,0.5563486750204325,0.63698674321345761,0.68201115421913394,0.71498559441385656,0.74624612078468233,0.77613972201988513,0.80414065768268661,null,0.74624612078468233,0.77613972201988513,0.80414065768268661]
["2013-03-04T01:00:02.830","2013-03-04T01:00:00",null,11.021434642054972,11.325006843710872,11.628579045366772,11.932151247022672,12.235723448678572,12.539295650334472,12.842867851990372,13.146440053646272,13.450012255302171,null,0,0.38978358984039491,0.52564543351259152,0.6087229373322669,0.65607112106850252,0.69125367109769309,0.7246171592156313,0.75650857411059091,0.78643371977200016,null,0.7246171592156313,0.75650857411059091,0.78643371977200016]
["2013-03-04T02:00:02.835","2013-03-04T02:00:00",null,10.697616330754435,11.001188532410335,11.304760734066235,11.608332935722135,11.911905137378035,12.215477339033935,12.519049540689835,12.822621742345735,13.126193944001635,null,0,0.36831235040237731,0.50649796680513315,0.59178358045927648,0.64122421113388894,0.67839406001410074,0.71365021370444015,0.74733966089318082,0.7789892351872223,null,0.71365021370444015,0.74733966089318082,0.7789892351872223]
["2013-03-04T03:00:02.840","2013-03-04T03:00:00",null,10.5440530769839,10.8476252786398,11.1511974802957,11.4547696819516,11.7583418836075,12.0619140852634,12.3654862869193,12.6690584885752,12.972630690231099,null,0,0.35087879751881551,0.49130406818224603,0.57872418800970848,0.63018366196154885,0.66926720603163292,0.70635293644196018,0.74177732707206856,0.7750777263375932,null,0.70635293644196018,0.74177732707206856,0.7750777263375932]
["2013-03-04T04:00:02.845","2013-03-04T04:00:00",null,10.486907302683463,10.790479504339363,11.094051705995263,11.397623907651163,11.701196109307062,12.004768310962962,12.308340512618862,12.611912714274762,12.915484915930662,null,0,0.33630527261132659,0.47890710868301845,0.56839864583138655,0.62181387420804146,0.66275853942432006,0.7016107577022217,0.73871751773002003,0.77362668273208568,null,0.7016107577022217,0.73871751773002003,0.77362668273208568]
["2013-03-04T05:00:02.850","2013-03-04T05:00:00",null,10.509327606069114,10.812899807725014,11.116472009380914,11.420044211036814,11.723616412692714,12.027188614348614,12.330760816004513,12.634333017660413,12.937905219316313,null,0,0.32059614836039696,0.46540609426655682,0.55699007835330183,0.61238209077224237,0.65520890675218657,0.69584864251513368,0.73466931636682864,0.77119776191417089,null,0.69584864251513368,0.73466931636682864,0.77119776191417089]
["2013-03-04T06:00:02.855","2013-03-04T06:00:00",null,10.548748987278971,10.852321188934871,11.155893390590771,11.459465592246671,11.763037793902571,12.066609995558471,12.370182197214371,12.673754398870271,12.977326600526171,null,0,0.30299435853706619,0.45005447351263633,0.54377296377270035,0.60119433427760438,0.64594536025615645,0.68840415793035581,0.72897029003215408,0.76716007535971509,null,0.68840415793035581,0.72897029003215408,0.76716007535971509]
["2013-03-04T07:00:02.860","2013-03-04T07:00:00",null,10.532901935547251,10.836474137203151,11.140046338859051,11.443618540514951,11.747190742170851,12.050762943826751,12.354335145482651,12.657907347138551,12.961479548794451,null,0,0.28619169417763812,0.43548094860514741,0.53132343022979489,0.59075312920319134,0.6374073355628801,0.68167468033959611,0.7239652410740266,0.76380585137307078,null,0.68167468033959611,0.7239652410740266,0.76380585137307078]
["2013-03-04T08:00:02.865","2013-03-04T08:00:00",null,10.637252700370727,10.940824902026627,11.244397103682527,11.547969305338427,11.851541506994327,12.155113708650227,12.458685910306126,12.762258111962026,13.065830313617926,null,0,0.26770666042052016,0.41925659872617527,0.51724410133287735,0.57870315839223729,0.62728157475053392,0.67338901105597326,0.71742503004050706,0.7589374949285056,null,0.67338901105597326,0.71742503004050706,0.7589374949285056]
["2013-03-04T09:00:02.870","2013-03-04T09:00:00",null,10.833891855084785,11.137464056740685,11.441036258396585,11.744608460052484,12.048180661708384,12.351752863364284,12.655325065020184,12.958897266676084,13.262469468331984,null,0,0.24311252278804066,0.39703880786793277,0.49728699435278068,0.56089107239419522,0.61150936164719094,0.65955152275997364,0.70543814808196637,0.74871710083753928,null,0.65955152275997364,0.70543814808196637,0.74871710083753928]
["2013-03-04T10:00:02.875","2013-03-04T10:00:00",null,11.047162030735647,11.350734232391547,11.654306434047447,11.957878635703347,12.261450837359247,12.565023039015147,12.868595240671047,13.172167442326947,13.475739643982847,null,0,0.21525879444753693,0.37161400034534386,0.47415441513454426,0.53994557339295568,0.59264579477559276,0.64267525473939668,0.6904545456337905,0.73553153068314459,null,0.64267525473939668,0.6904545456337905,0.73553153068314459]
["2013-03-04T11:00:02.880","2013-03-04T11:00:00",null,11.377689540864147,11.681261742520046,11.984833944175946,12.288406145831846,12.591978347487746,12.895550549143646,13.199122750799546,13.502694952455446,13.806267154111346,null,0,0.17900373392731916,0.33792455315660325,0.44291491838118957,0.51102984937016016,0.5659381805872653,0.61808111710691716,0.66787925127853887,0.71489096113523642,null,0.61808111710691716,0.66787925127853887,0.71489096113523642]
["2013-03-04T12:00:02.885","2013-03-04T12:00:00",null,11.796979635528704,12.100551837184604,12.404124038840504,12.707696240496404,13.011268442152303,13.314840643808203,13.618412845464103,13.921985047120003,14.225557248775903,null,0,0.13106672090189203,0.29275293482862891,0.40038251704584127,0.47101048732261119,0.52831619493142445,0.5827513597554288,0.63473657414404749,0.68385124574785738,null,0.5827513597554288,0.63473657414404749,0.68385124574785738]
["2013-03-04T13:00:02.890","2013-03-04T13:00:00",null,11.958696286002361,12.262268487658261,12.565840689314161,12.869412890970061,13.172985092625961,13.476557294281861,13.780129495937761,14.083701697593661,14.387273899249561,null,0,7.6557952416738628E-2,0.24113573874575506,0.35152020085168467,0.42478738812108063,0.48459562020895769,0.54143867623340569,0.59571611892637688,0.64702838555591924,null,0.54143867623340569,0.59571611892637688,0.64702838555591924]
["2013-03-04T14:00:02.895","2013-03-04T14:00:00",null,12.006440123665916,12.310012325321816,12.613584526977716,12.917156728633616,13.220728930289516,13.524301131945416,13.827873333601316,14.131445535257216,14.435017736913116,null,0,2.473046015915354E-2,0.19216827446424284,0.30526555722394744,0.38112990225102722,0.44341962920049693,0.50262851719044632,0.55917715857029893,0.61266599060810267,null,0.50262851719044632,0.55917715857029893,0.61266599060810267]
["2013-03-04T15:00:02.900","2013-03-04T15:00:00",null,12.128758981029417,12.432331182685317,12.735903384341217,13.039475585997117,13.343047787653017,13.646619989308917,13.950192190964817,14.253764392620717,14.557336594276617,null,0,0,0.14102424477446929,0.25692898146656895,0.33547460272121704,0.40031942819342831,0.46197826661876362,0.52087171034664659,0.57661071145386056,null,0.46197826661876362,0.52087171034664659,0.57661071145386056]
["2013-03-04T16:00:02.905","2013-03-04T16:00:00",null,12.173150702377916,12.476722904033815,12.780295105689715,13.083867307345615,13.387439509001515,13.691011710657415,13.994583912313315,14.298156113969215,14.601728315625115,null,0,0,8.8092697599650188E-2,0.20683643265035159,0.28809487455877469,0.35552634297993418,0.41966667626686216,0.48092595196024657,0.53893615175434195,null,0.41966667626686216,0.48092595196024657,0.53893615175434195]
["2013-03-04T17:00:02.910","2013-03-04T17:00:00",null,11.923811688101118,12.227383889757018,12.530956091412918,12.834528293068818,13.138100494724718,13.441672696380618,13.745244898036518,14.048817099692418,14.352389301348317,null,0,0,5.5938412486301596E-2,0.17734239414710018,0.26114541976952932,0.33099529419986806,0.39744888540861967,0.46092678574520762,0.52106097690388653,null,0.39744888540861967,0.46092678574520762,0.52106097690388653]
["2013-03-04T18:00:02.915","2013-03-04T18:00:00",null,12.343216883480022,12.646789085135921,12.950361286791821,13.253933488447721,13.557505690103621,13.861077891759521,14.164650093415421,14.468222295071321,14.771794496727221,null,1.479433589093573E-2,1.7969808129075455E-2,7.6925970722483347E-2,0.20121100997682592,0.28776891548797229,0.36025800691093712,0.42922463740748801,0.49512094375325522,0.55756839283375781,null,0.42922463740748801,0.49512094375325522,0.55756839283375781]
["2013-03-04T19:00:02.920","2013-03-04T19:00:00",null,12.017303560325269,12.320875761981169,12.624447963637069,12.928020165292969,13.231592366948869,13.535164568604769,13.838736770260669,14.142308971916568,14.445881173572468,null,4.3047626963390817E-2,4.914621603001678E-2,0.11089931774708417,0.23783408880278836,0.32693657802794074,0.40184407546008483,0.47312396387845934,0.54123889486743015,0.60581033531251627,null,0.47312396387845934,0.54123889486743015,0.60581033531251627]
["2013-03-04T20:00:02.925","2013-03-04T20:00:00",null,11.890479252615819,12.194051454271719,12.497623655927619,12.801195857583519,13.104768059239419,13.408340260895319,13.711912462551219,14.015484664207118,14.319056865863018,null,7.6705529725924773E-2,8.5632602342416902E-2,0.15007749509578816,0.27957787948296947,0.37111980433477226,0.44836158930621112,0.52187061717652472,0.59212005433881465,0.65874188248733534,null,0.52187061717652472,0.59212005433881465,0.65874188248733534]
["2013-03-04T21:00:02.930","2013-03-04T21:00:00",null,11.734645460775058,12.038217662430958,12.341789864086858,12.645362065742757,12.948934267398657,13.252506469054557,13.556078670710457,13.859650872366357,14.163223074022257,null,0.11390692303234312,0.12560990515502363,0.19269401490102095,0.32470743857600159,0.4186467398195125,0.49818075309530385,0.57387686118261438,0.64620823047454556,0.71482787228282307,null,0.57387686118261438,0.64620823047454556,0.71482787228282307]
["2013-03-04T22:00:02.935","2013-03-04T22:00:00",null,11.303339699244891,11.606911900900791,11.910484102556691,12.21405630421259,12.51762850586849,12.82120070752439,13.12477290918029,13.42834511083619,13.73191731249209,null,0.16092914769777639,0.17518722834319844,0.24468974409837502,0.37899539607770816,0.47512177753821599,0.55673772294364865,0.63442112988198041,0.70865567955504827,0.77908386846584243,null,0.63442112988198041,0.70865567955504827,0.77908386846584243]
["2013-03-04T23:00:02.940","2013-03-04T23:00:00",null,11.094926269491737,11.398498471147636,11.702070672803536,12.005642874459436,12.309215076115336,12.612787277771236,12.916359479427136,13.219931681083036,13.523503882738936,null,0.21287230285145264,0.22954878950605398,0.30135404837431862,0.43784678057064863,0.53604457935206218,0.61963730879978052,0.69920286650177788,0.7752354484686268,0.84737755120331759,null,0.69920286650177788,0.7752354484686268,0.84737755120331759]
["2013-03-05","2013-03-05",null,10.663894174378163,10.967466376034062,11.271038577689962,11.574610779345862,11.878182981001762,12.181755182657662,12.485327384313562,12.788899585969462,13.092471787625362,null,0.27202861679772444,0.29102887618288498,0.36503173007688205,0.50360639440285337,0.60378097722655255,0.68925585743793649,0.77059841781624383,0.84833439879825379,0.92209578207822118,null,0.77059841781624383,0.84833439879825379,0.92209578207822118]
["2013-03-05T01:00:00","2013-03-05T01:00:00",null,10.28732651232273,10.59089871397863,10.89447091563453,11.19804311729043,11.50161531894633,11.80518752060223,12.10875972225813,12.41233192391403,12.71590412556993,null,0.33607431680603256,0.35733526006933891,0.43347262013665511,0.57406612773985433,0.67616492056216138,0.76344834787606197,0.84651533688700142,0.92589162803175906,1,null,0.84651533688700142,0.92589162803175906,1]
["2013-03-05T02:00:00","2013-03-05T02:00:00",null,10.094672795614368,10.398244997270268,10.701817198926168,11.005389400582068,11.308961602237968,11.612533803893868,11.916106005549768,12.219678207205668,12.523250408861568,null,0.40287489670305793,0.42635446460956788,0.50458427161526087,0.64716507806948131,0.75113550684671848,0.84019593683692895,0.92495581005429395,1,1,null,0.92495581005429395,1,1]
["2013-03-05T03:00:00","2013-03-05T03:00:00",null,10.01259663367653,10.31616883533243,10.61974103698833,10.92331323864423,11.22688544030013,11.53045764195603,11.83402984361193,12.13760204526783,12.44117424692373,null,0.47042202802030819,0.49613073537875729,0.57645298932282718,0.72101057981933325,0.82685264455150043,0.91767956240928528,1,1,1,null,1,1,1]
["2013-03-05T04:00:00","2013-03-05T04:00:00",null,9.9473600792994183,10.250932280955318,10.554504482611218,10.858076684267118,11.161648885923018,11.465221087578918,11.768793289234818,12.072365490890718,12.375937692546618,null,0.53780092239778943,0.56574928401691327,0.64818501451683108,0.79472990386435838,0.90246463416892675,0.99506855470302158,1,1,1,null,1,1,1]
["2013-03-05T05:00:00","2013-03-05T05:00:00",null,9.8908969051441495,10.194469106800049,10.498041308455949,10.801613510111849,11.105185711767749,11.408757913423649,11.712330115079549,12.015902316735449,12.319474518391349,null,0.60448583939872358,0.63471591451346443,0.71929666599543685,0.86786039862019204,0.97750882411463269,1,1,1,1,null,1,1,1]
["2013-03-05T06:00:00","2013-03-05T06:00:00",null,9.7646986078593798,10.06827080951528,10.37184301117118,10.67541521282708,10.97898741448298,11.282559616138879,11.586131817794779,11.889704019450679,12.193276221106579,null,0.67037163093575503,0.70292547878105505,0.78969331048002445,0.94031794561694981,1,1,1,1,1,null,1,1,1]
["2013-03-05T07:00:00","2013-03-05T07:00:00",null,9.6855220509125264,9.9890942525684263,10.292666454224326,10.596238655880226,10.899810857536126,11.203383059192026,11.506955260847926,11.810527462503826,12.114099664159726,null,0.68527111491404635,0.72015925029864114,0.80911416221460741,0.96179969986370295,1,1,1,1,1,null,1,1,1]
["2013-03-05T08:00:00","2013-03-05T08:00:00",null,9.7454625233291221,10.049034724985022,10.352606926640922,10.656179128296822,10.959751329952722,11.263323531608622,11.566895733264522,11.870467934920422,12.174040136576322,null,0.68066562868787017,0.71785650718555305,0.80896695489230952,0.96369236543610415,1,1,1,1,1,null,1,1,1]
["2013-03-05T09:00:00","2013-03-05T09:00:00",null,9.7937202978805331,10.097292499536433,10.400864701192333,10.704436902848233,11.008009104504133,11.311581306160033,11.615153507815933,11.918725709471833,12.222297911127733,null,0.67347349951274582,0.71304072478466562,0.80636979713462575,0.96319816942553271,1,1,1,1,1,null,1,1,1]
["2013-03-05T10:00:00","2013-03-05T10:00:00",null,9.7253439353987901,10.02891613705469,10.33248833871059,10.63606054036649,10.93963274202239,11.24320494367829,11.54677714533419,11.85034934699009,12.15392154864599,null,0.66235934667925678,0.70442909643024032,0.80010297112823081,0.95916048287107691,0.99805476038392105,1,1,1,1,null,1,1,1]
["2013-03-05T11:00:00","2013-03-05T11:00:00",null,9.8639146456611293,10.167486847317029,10.471059048972929,10.774631250628829,11.078203452284729,11.381775653940629,11.685347855596529,11.988920057252429,12.292492258908329,null,0.64755449597958548,0.6922003738707817,0.79030316938668699,0.9516529094338857,0.99271323754625551,0.99670886486576904,0.9986541044818481,1,1,null,0.9986541044818481,1,1]
["2013-03-05T12:00:00","2013-03-05T12:00:00",null,9.9783182062313927,10.281890407887293,10.585462609543193,10.889034811199092,11.192607012854992,11.496179214510892,11.799751416166792,12.103323617822692,12.406895819478592,null,0.63041535774061941,0.67767942300697059,0.77824268376699735,0.94192671135349082,0.9851951493003287,0.99127270874948348,0.99519473240784817,0.99842277868966567,1,null,0.99519473240784817,0.99842277868966567,1]
["2013-03-05T13:00:00","2013-03-05T13:00:00",null,10.012381353120773,10.315953554776673,10.619525756432573,10.923097958088473,11.226670159744373,11.530242361400273,11.833814563056173,12.137386764712073,12.440958966367972,null,0.61142561316419441,0.66134992504064283,0.76442622508846891,0.93047608464046383,0.97598417684797634,0.98418572766171464,0.99012659459730734,0.99526833606899712,0.99866461929058359,null,0.99012659459730734,0.99526833606899712,0.99866461929058359]
["2013-03-05T14:00:00","2013-03-05T14:00:00",null,10.161730198854187,10.465302400510087,10.768874602165987,11.072446803821887,11.376019005477787,11.679591207133686,11.983163408789586,12.286735610445486,12.590307812101386,null,0.58847178569446257,0.64112994784215716,0.74679289083893141,0.91529270082631231,0.9631140509556485,0.97351319679511916,0.98153599586035323,0.98865452137432863,0.99393295535958071,null,0.98153599586035323,0.98865452137432863,0.99393295535958071]
["2013-03-05T15:00:00","2013-03-05T15:00:00",null,10.257276290951069,10.560848492606969,10.864420694262868,11.167992895918768,11.471565097574668,11.775137299230568,12.078709500886468,12.382281702542368,12.685853904198268,null,0.56427721079393445,0.61967973802161069,0.72793983877606872,0.89890011400757119,0.94904523686746656,0.96165249254140528,0.97176773854501608,0.9808840777187483,0.98805517727640157,null,0.97176773854501608,0.9808840777187483,0.98805517727640157]
["2013-03-05T16:00:00","2013-03-05T16:00:00",null,10.266293058588941,10.569865260244841,10.873437461900741,11.177009663556641,11.480581865212541,11.784154066868441,12.087726268524341,12.39129847018024,12.69487067183614,null,0.53964101392651265,0.59780893585164174,0.70867670917251913,0.88209744964814307,0.9345768600473332,0.94940274036447558,0.96162094811519871,0.97273510094868776,0.98181989569621331,null,0.96162094811519871,0.97273510094868776,0.98181989569621331]
["2013-03-05T17:00:00","2013-03-05T17:00:00",null,10.309145737134576,10.612717938790476,10.916290140446376,11.219862342102276,11.523434543758176,11.827006745414076,12.130578947069976,12.434151148725876,12.737723350381776,null,0.5127861924158873,0.573772083082147,0.68728958820438601,0.8632233679678093,0.91808963994997195,0.93516568933652466,0.9495289180693024,0.96268294379749053,0.97371297816109503,null,0.9495289180693024,0.96268294379749053,0.97371297816109503]
["2013-03-05T18:00:00","2013-03-05T18:00:00",null,10.153080320511167,10.456652522167067,10.760224723822967,11.063796925478867,11.367369127134767,11.670941328790667,11.974513530446567,12.278085732102467,12.581657933758366,null,0.49025295729557794,0.5539726982330837,0.67006633149553552,0.84842903207687359,0.90559804717212433,0.92486117677567392,0.94129582282935731,0.95642663259983118,0.96932830291836569,null,0.94129582282935731,0.95642663259983118,0.96932830291836569]
["2013-03-05T19:00:00","2013-03-05T19:00:00",null,9.9434180838367858,10.246990285492686,10.550562487148586,10.854134688804486,11.157706890460386,11.461279092116285,11.764851293772185,12.068423495428085,12.371995697083985,null,0.47493288096786412,0.54122875004558257,0.65975130412594918,0.84039571820290426,0.89973078389768069,0.92104430120466496,0.9394241868744273,0.95639508817362451,0.97105273155099781,null,0.9394241868744273,0.95639508817362451,0.97105273155099781]
["2013-03-05T20:00:00","2013-03-05T20:00:00",null,9.8018003708527921,10.105372572508692,10.408944774164592,10.712516975820492,11.016089177476392,11.319661379132292,11.623233580788192,11.926805782444092,12.230377984099992,null,0.463461224637366,0.53224910338541265,0.6531164598138095,0.83596898372523265,0.89739649635838592,0.92069731251639142,0.94094883414108377,0.95970725292532655,0.9760472657003898,null,0.94094883414108377,0.95970725292532655,0.9760472657003898]
["2013-03-05T21:00:00","2013-03-05T21:00:00",null,9.7175435206831082,10.021115722339008,10.324687923994908,10.628260125650808,10.931832327306708,11.235404528962608,11.538976730618508,11.842548932274408,12.146121133930308,null,0.45277817896203498,0.52405806738040983,0.64727022615683705,0.83233085990272815,0.89584030466552278,0.92111790486581391,0.94324106244543626,0.96377648390598902,0.98179886607874223,null,0.94324106244543626,0.96377648390598902,0.98179886607874223]
["2013-03-05T22:00:00","2013-03-05T22:00:00",null,9.5339713130976413,9.8375435147535413,10.141115716409441,10.444687918065341,10.748260119721241,11.051832321377141,11.355404523033041,11.658976724688941,11.962548926344841,null,0.44324124743888027,0.51699211591011218,0.64251753260836297,0.82975473176251546,0.89532507903748026,0.92254791885385035,0.94651116796219603,0.9687815328641165,0.98846525481708858,null,0.94651116796219603,0.9687815328641165,0.98846525481708858]
["2013-03-05T23:00:00","2013-03-05T23:00:00",null,9.4893872880001293,9.7929594896560292,10.096531691311929,10.400103892967829,10.703676094623729,11.007248296279629,11.310820497935529,11.614392699591429,11.917964901247329,null,0.435397200122151,0.51154544498509102,0.63932103075275215,0.82868222127148816,0.89625038220620967,0.92535537278624536,0.95110613937963662,0.97507990329671812,0.99636187617749561,null,0.95110613937963662,0.97507990329671812,0.99636187617749561]
["2013-03-06","2013-03-06",null,9.26187566243755,9.5654478640934499,9.8690200657493499,10.17259226740525,10.47616446906115,10.77973667071705,11.08330887237295,11.38688107402885,11.690453275684749,null,0.42869926695759802,0.50726591782971731,0.63731270228425985,0.82880839897631486,0.89838488837952879,0.92938254453196556,0.95693134341913799,0.98259799154264493,1,null,0.95693134341913799,0.98259799154264493,1]
["2013-03-06T01:00:00","2013-03-06T01:00:00",null,9.2267297924640275,9.5303019941199274,9.8338741957758273,10.137446397431727,10.441018599087627,10.744590800743527,11.048163002399427,11.351735204055327,11.655307405711227,null,0.42400966226153736,0.50494214509915814,0.63719703938816863,0.83077466820986501,0.90231742684662897,0.93516568933652466,0.9644599464738004,0.9917879343775261,1,null,0.9644599464738004,0.9917879343775261,1]
["2013-03-06T02:00:00","2013-03-06T02:00:00",null,9.2015281151833666,9.5051003168392665,9.8086725184951664,10.112244720151068,10.415816921806968,10.719389123462868,11.022961325118768,11.326533526774668,11.630105728430568,null,0.42071852712730645,0.50396426788675086,0.63839572758402274,0.8340237441091537,0.90749071274452542,0.94215803714567337,0.97316620810684573,1,1,null,0.97316620810684573,1,1]
["2013-03-06T03:00:00","2013-03-06T03:00:00",null,9.0311911276618346,9.3347633293177346,9.6383355309736345,9.9419077326295344,10.245479934285434,10.549052135941334,10.852624337597234,11.156196539253134,11.459768740909034,null,0.41942520565283231,0.50497368952536481,0.64156068501342689,0.83920754481578574,0.91457769383229426,0.95103253571848767,0.98373359088608558,1,1,null,0.98373359088608558,1,1]
["2013-03-06T04:00:00","2013-03-06T04:00:00",null,9.0956239699214017,9.3991961715773016,9.7027683732332015,10.006340574889101,10.309912776545001,10.613484978200901,10.917057179856801,11.220629381512701,11.524201583168601,null,0.41841578401421836,0.50623546657363228,0.64495696823501336,0.84460164169712904,0.92185394147730315,0.96008578603980654,0.99446921060509441,1,1,null,0.99446921060509441,1,1]
["2013-03-06T05:00:00","2013-03-06T05:00:00",null,9.0885352529331911,9.392107454589091,9.695679656244991,9.9992518579008909,10.302824059556791,10.606396261212691,10.909968462868591,11.213540664524491,11.517112866180391,null,0.41779541029882022,0.50787577673637996,0.64872126976234457,0.85035324207548146,0.92947717781058559,0.96947551024066336,1,1,1,null,1,1,1]
["2013-03-06T06:00:00","2013-03-06T06:00:00",null,9.0880491236177718,9.3916213252736718,9.6951935269295717,9.9987657285854716,10.302337930241372,10.605910131897271,10.909482333553171,11.213054535209071,11.516626736864971,null,0.41726966986204211,0.50961072017774767,0.6525802045682958,0.85619947573245392,0.93719504742248805,0.97895986772014032,1,1,1,null,1,1,1]
["2013-03-06T07:00:00","2013-03-06T07:00:00",null,8.9963222680680879,9.2998944697239878,9.6034666713798877,9.9070388730357877,10.210611074691688,10.514183276347588,10.817755478003487,11.121327679659387,11.424899881315287,null,0.41394699030160453,0.50866438739154707,0.65385249642529875,0.85956421452783371,0.94252605545141799,0.98614148208652919,1,1,1,null,1,1,1]
["2013-03-06T08:00:00","2013-03-06T08:00:00",null,9.2980541885931043,9.6016263902490042,9.9051985919049041,10.208770793560804,10.512342995216704,10.815915196872604,11.119487398528504,11.423059600184404,11.726631801840304,null,0.40912069309198157,0.50619340733869,0.65357911139817415,0.86136224682161477,0.9462798421700136,0.99173536033384813,1,1,1,null,1,1,1]
["2013-03-06T09:00:00","2013-03-06T09:00:00",null,9.470360349406107,9.773932551062007,10.077504752717907,10.381076954373807,10.684649156029707,10.988221357685607,11.291793559341507,11.595365760997407,11.898937962653306,null,0.40235967107501519,0.50179821728722507,0.65141306079864836,0.86128864316046583,0.94817250774241479,0.99549966186117933,1,1,1,null,1,1,1]
["2013-03-06T10:00:00","2013-03-06T10:00:00",null,9.6498897087254143,9.9534619103813142,10.257034112037216,10.560606313693116,10.864178515349016,11.167750717004916,11.471322918660816,11.774895120316716,12.078467321972616,null,0.38941594152153836,0.49136752702154757,0.64334820249847235,0.85545292431222897,0.94443975064129027,0.99375420361107603,1,1,1,null,1,1,1]
["2013-03-06T11:00:00","2013-03-06T11:00:00",null,9.812733381670931,10.116305583326831,10.419877784982729,10.723449986638629,11.027022188294529,11.330594389950429,11.634166591606329,11.937738793262229,12.241310994918129,null,0.37140407415752064,0.4759738470326848,0.63042550256246666,0.84485399710678244,0.9360489332703118,0.98744531836973881,0.99566789880094841,0.99753953475587853,0.999327052240924,null,0.99566789880094841,0.99753953475587853,0.999327052240924]
["2013-03-06T12:00:00","2013-03-06T12:00:00",null,10.069585115923994,10.373157317579894,10.676729519235794,10.980301720891694,11.283873922547594,11.587446124203494,11.891018325859394,12.194590527515293,12.498162729171193,null,0.34731464734434808,0.45461827049075837,0.6116565689694885,0.82851398433171908,0.92202217841707212,0.97559512892476041,0.98589964148561127,0.98973754667409153,0.993396700114067,null,0.98589964148561127,0.98973754667409153,0.993396700114067]
["2013-03-06T13:00:00","2013-03-06T13:00:00",null,10.267618398552514,10.571190600208414,10.874762801864314,11.178335003520214,11.481907205176114,11.785479406832014,12.089051608487914,12.392623810143814,12.696196011799714,null,0.31675861315880494,0.42693277909002364,0.58667338341379316,0.80609641210750094,0.90203352701076878,0.95789870582280956,0.97039029860065729,0.97631013591877891,0.98194607340104001,null,0.97039029860065729,0.97631013591877891,0.98194607340104001]
["2013-03-06T14:00:00","2013-03-06T14:00:00",null,10.415422230601672,10.718994432257572,11.022566633913472,11.326138835569372,11.629711037225272,11.933283238881172,12.236855440537072,12.540427642192972,12.843999843848872,null,0.28253291072455061,0.39564070829299114,0.55815722212294905,0.78020895300054727,0.87862756276540777,0.93685857354294999,0.95158982058147246,0.9596441640729132,0.96730945964113768,null,0.95158982058147246,0.9596441640729132,0.96730945964113768]
["2013-03-06T15:00:00","2013-03-06T15:00:00",null,10.475948369940546,10.779520571596446,11.083092773252346,11.386664974908246,11.690237176564146,11.993809378220046,12.297381579875946,12.600953781531846,12.904525983187746,null,0.24533151741813225,0.36144655028494355,0.52680206247350314,0.75153506957866967,0.85249826305753618,0.91314767984425771,0.93018166999586827,0.94042309370430588,0.95017032140217161,null,0.93018166999586827,0.94042309370430588,0.95017032140217161]
["2013-03-06T16:00:00","2013-03-06T16:00:00",null,10.475667604790676,10.779239806446576,11.082812008102476,11.386384209758376,11.689956411414276,11.993528613070175,12.297100814726075,12.600673016381975,12.904245218037875,null,0.21176824793421836,0.33078536801204478,0.49888524528058603,0.72620489533470078,0.82962855405768887,0.89262277319244065,0.91187538798725487,0.92423028825154041,0.93598584441789845,null,0.91187538798725487,0.92423028825154041,0.93598584441789845]
["2013-03-06T17:00:00","2013-03-06T17:00:00",null,10.363410920302641,10.666983121958541,10.970555323614441,11.274127525270341,11.577699726926241,11.881271928582141,12.184844130238041,12.488416331893941,12.791988533549841,null,0.18017124768385456,0.30206942535522496,0.4728821232775412,0.7027673866631331,0.80863048101277157,0.87393795806934693,0.89538816788989362,0.90982500028382052,0.92356785530119978,null,0.89538816788989362,0.90982500028382052,0.92356785530119978]
["2013-03-06T18:00:00","2013-03-06T18:00:00",null,10.278343320779941,10.581915522435841,10.885487724091741,11.189059925747641,11.492632127403541,11.79620432905944,12.09977653071534,12.40334873237124,12.70692093402714,null,0.15284325978012894,0.27751734695768771,0.45095874706389444,0.68332550531107894,0.79153340200874778,0.85907001851726228,0.88263370489365689,0.89907886575607621,0.91473541596332775,null,0.88263370489365689,0.89907886575607621,0.91473541596332775]
["2013-03-06T19:00:00","2013-03-06T19:00:00",null,10.127590553968723,10.431162755624623,10.734734957280523,11.038307158936423,11.341879360592323,11.645451562248223,11.949023763904123,12.252595965560023,12.556168167215922,null,0.12947935476971018,0.25685574779230835,0.4328417316125211,0.66761638106014931,0.77809547644469956,0.84779814355273986,0.87340170282383345,0.89180261811106731,0.90930977465577778,null,0.87340170282383345,0.89180261811106731,0.90930977465577778]
["2013-03-06T20:00:00","2013-03-06T20:00:00",null,9.9462907461400505,10.24986294779595,10.55343514945185,10.85700735110775,11.16057955276365,11.46415175441955,11.76772395607545,12.07129615773135,12.37486835938725,null,0.10818686708019713,0.23825505113909917,0.41676458905584679,0.65393661489518318,0.76667639415787925,0.83851356743923866,0.86615699960503123,0.88648212489087297,0.90581885815557117,null,0.86615699960503123,0.88648212489087297,0.90581885815557117]
["2013-03-06T21:00:00","2013-03-06T21:00:00",null,9.8345413766276515,10.138113578283551,10.441685779939451,10.745257981595351,11.048830183251251,11.352402384907151,11.655974586563051,11.959546788218951,12.263118989874851,null,8.8902707859176422E-2,0.22162062371944008,0.40263268611525149,0.64216002911135373,0.75712894782598894,0.83106908285446079,0.86071032868001007,0.8829386343469886,0.90407339990546787,null,0.86071032868001007,0.8829386343469886,0.90407339990546787]
["2013-03-06T22:00:00","2013-03-06T22:00:00",null,9.8331613620388172,10.136733563694717,10.440305765350617,10.743877967006517,11.047450168662417,11.351022370318317,11.654594571974217,11.958166773630117,12.261738975286017,null,7.3635205575140403E-2,0.20889770514941006,0.39229662912819407,0.63407414119370653,0.75117756608166086,0.82712602957862502,0.85868097059404658,0.88271782336354176,0.90557701755465325,null,0.85868097059404658,0.88271782336354176,0.90557701755465325]
["2013-03-06T23:00:00","2013-03-06T23:00:00",null,9.6773188865995543,9.9808910882554542,10.284463289911354,10.588035491567254,10.891607693223154,11.195179894879054,11.498752096534954,11.802324298190854,12.105896499846754,null,6.3067822795900591E-2,0.20075924318808508,0.38645039547122162,0.63038344332752427,0.74952674111017759,0.82739941460574962,0.86077341753242342,0.88654521374328632,0.91105523290588108,null,0.86077341753242342,0.88654521374328632,0.91105523290588108]
["2013-03-07","2013-03-07",null,9.6390053742979021,9.942577575953802,10.246149777609702,10.549721979265602,10.853294180921502,11.156866382577402,11.460438584233302,11.764010785889202,12.067582987545102,null,5.4582372146302058E-2,0.19465013931272357,0.38258094585653479,0.62861695545994989,0.74974755209362443,0.82950237635286206,0.86465338195584585,0.89211806237313418,0.91823684727226995,null,0.86465338195584585,0.89211806237313418,0.91823684727226995]
["2013-03-07T01:00:00","2013-03-07T01:00:00",null,9.4052234597180657,9.7087956613739657,10.012367863029866,10.315940064685767,10.619512266341667,10.923084467997567,11.226656669653467,11.530228871309367,11.833801072965267,null,4.7516420676004395E-2,0.18998156423413404,0.38015202503861995,0.62830151119788302,0.75142992149131438,0.83305638170548202,0.86999490479351138,0.89914195460848956,0.92685899043543074,null,0.86999490479351138,0.89914195460848956,0.92685899043543074]
["2013-03-07T02:00:00","2013-03-07T02:00:00",null,9.4564725941050778,9.7600447957609777,10.063616997416878,10.367189199072778,10.670761400728678,10.974333602384577,11.277905804040477,11.581478005696377,11.885050207352277,null,4.1522979696734054E-2,0.18633292560289402,0.37871149624184797,0.62893239972201676,0.75401656444026266,0.83749363099188923,0.87617761233002178,0.90698600192521883,0.93626974425375875,null,0.87617761233002178,0.90698600192521883,0.93626974425375875]
["2013-03-07T03:00:00","2013-03-07T03:00:00",null,9.4399060866834077,9.7434782883393076,10.047050489995208,10.350622691651109,10.654194893307009,10.957767094962909,11.261339296618809,11.564911498274709,11.868483699930609,null,3.6581019591019913E-2,0.18370422341900353,0.37826987427495434,0.63054116545855776,0.75756005498414702,0.84285618344702584,0.88327510822652611,0.91571329317573524,0.94655322719713841,null,0.88327510822652611,0.91571329317573524,0.94655322719713841]
["2013-03-07T04:00:00","2013-03-07T04:00:00",null,9.419694795924892,9.7232669975807919,10.026839199236692,10.330411400892592,10.633983602548492,10.937555804204392,11.241128005860292,11.544700207516192,11.848272409172091,null,3.2732599593804222E-2,0.18214803172614036,0.3788587035641458,0.63315935283371272,0.76208142274043866,0.84917558349709865,0.89129790729175995,0.92535537278624558,0.95773046888304081,null,0.89129790729175995,0.92535537278624558,0.95773046888304081]
["2013-03-07T05:00:00","2013-03-07T05:00:00",null,9.3720103971425175,9.6755825987984174,9.9791548004543174,10.282727002110217,10.586299203766117,10.889871405422017,11.193443607077917,11.497015808733817,11.800588010389717,null,2.7632917357056655E-2,0.17938263702868756,0.37829090389242548,0.6346629704828981,0.765530280005703,0.85446453229108632,0.89832179952711533,0.93403008999308423,0.9679613777827426,null,0.89832179952711533,0.93403008999308423,0.9679613777827426]
["2013-03-07T06:00:00","2013-03-07T06:00:00",null,9.4019590634549566,9.7055312651108565,10.009103466766756,10.312675668422656,10.616247870078556,10.919820071734456,11.223392273390356,11.526964475046256,11.830536676702156,null,2.0787776870205794E-2,0.17492435812480928,0.37607227924922187,0.63454730758680689,0.76740191596063301,0.85821831900968193,0.90384207411328532,0.94123273397694418,0.97676227269440796,null,0.90384207411328532,0.94123273397694418,0.97676227269440796]
["2013-03-07T07:00:00","2013-03-07T07:00:00",null,9.3453648612028886,9.6489370628587885,9.9525092645146884,10.256081466170588,10.559653667826488,10.863225869482388,11.166798071138288,11.470370272794188,11.773942474450088,null,1.3269688624278965E-2,0.16982467588806172,0.37325431050809127,0.6338638450189954,0.76873729667004942,0.86145688010023502,0.90887866749761947,0.94797272637643937,0.98512154563917975,null,0.90887866749761947,0.94797272637643937,0.98512154563917975]
["2013-03-07T08:00:00","2013-03-07T08:00:00",null,9.7388692313476923,10.042441433003592,10.346013634659492,10.649585836315392,10.953158037971292,11.256730239627192,11.560302441283092,11.863874642938992,12.167446844594892,null,3.1439278119327618E-3,0.1621068062761592,0.36779712477433457,0.63054116545855776,0.76743346038683968,0.86205622419816208,0.91128655869806319,0.95209453140077971,0.99087314601753218,null,0.91128655869806319,0.95209453140077971,0.99087314601753218]
["2013-03-07T09:00:00","2013-03-07T09:00:00",null,10.05385312010324,10.357425321759139,10.660997523415039,10.964569725070939,11.268141926726839,11.571714128382739,11.875286330038639,12.178858531694539,12.482430733350439,null,0,0.14884763246061553,0.35689326811555677,0.62186644825171911,0.76086170492711347,0.85747176758945709,0.90859476766175928,0.95120077265825698,0.99169330109890597,null,0.90859476766175928,0.95120077265825698,0.99169330109890597]
["2013-03-07T10:00:00","2013-03-07T10:00:00",null,10.42351482920995,10.727087030865849,11.030659232521749,11.334231434177649,11.637803635833549,11.941375837489449,12.244948039145349,12.548520240801249,12.852092442457149,null,0,0.12778647056328485,0.33832411588855427,0.60566312799021804,0.74688752411755155,0.84562157814447869,0.89876342149400879,0.94328312168037876,0.98560522684101559,null,0.89876342149400879,0.94328312168037876,0.98560522684101559]
["2013-03-07T11:00:00","2013-03-07T11:00:00",null,10.810053728555229,11.113625930211128,11.417198131867028,11.720770333522928,12.024342535178828,12.327914736834728,12.631486938490628,12.935059140146528,13.238631341802428,null,0,9.8471183808538004E-2,0.31162701650896235,0.58145803828095433,0.72504826637378927,0.82603248947012664,0.88130883899297585,0.92786841207404491,0.9721357568507607,null,0.88130883899297585,0.92786841207404491,0.9721357568507607]
["2013-03-07T12:00:00","2013-03-07T12:00:00",null,10.963811775197694,11.267383976853594,11.570956178509494,11.874528380165394,12.178100581821294,12.481672783477194,12.785244985133094,13.088817186788994,13.392389388444894,null,0,0,0.21511158712523876,0.48749770741997234,0.63350634152198648,0.73680382254014753,0.79427776708872921,0.84292978710817512,0.88919494554464762,null,0.79427776708872921,0.84292978710817512,0.88919494554464762]
["2013-03-07T13:00:00","2013-03-07T13:00:00",null,11.142871372378307,11.446443574034207,11.750015775690107,12.053587977346007,12.357160179001907,12.660732380657807,12.964304582313707,13.267876783969607,13.571448985625507,null,0,0,0.11062593271995919,0.38564075519858326,0.5341519137796612,0.63983625638079478,0.69958139961625787,0.75039947023522957,0.79873604599260772,null,0.69958139961625787,0.75039947023522957,0.79873604599260772]
["2013-03-07T14:00:00","2013-03-07T14:00:00",null,11.161442524699519,11.465014726355419,11.768586928011318,12.072159129667218,12.375731331323118,12.679303532979018,12.982875734634918,13.286447936290818,13.590020137946718,null,0,0,4.7242665661991465E-2,0.32490721994197719,0.47594193261959,0.58402365161243175,0.64605050834351174,0.69904514437074483,0.74946365225776423,null,0.64605050834351174,0.69904514437074483,0.74946365225776423]
["2013-03-07T15:00:00","2013-03-07T15:00:00",null,11.260598855105897,11.564171056761797,11.867743258417697,12.171315460073597,12.474887661729497,12.778459863385397,13.082032065041297,13.385604266697197,13.689176468353097,null,0,0,9.2000876567281606E-3,0.28959849220796002,0.4432303626432566,0.55379357649769101,0.61817575038553685,0.67343107029091576,0.72599459915998987,null,0.61817575038553685,0.67343107029091576,0.72599459915998987]
["2013-03-07T16:00:00","2013-03-07T16:00:00",null,11.319013853517216,11.622586055173116,11.926158256829016,12.229730458484916,12.533302660140816,12.836874861796716,13.140447063452616,13.444019265108516,13.747591466764415,null,0,0,0,0.25489962338060546,0.41110762195611472,0.52412078624593506,0.59083724767307566,0.64833222183912931,0.70303025688152243,null,0.59083724767307566,0.64833222183912931,0.70303025688152243]
["2013-03-07T17:00:00","2013-03-07T17:00:00",null,11.211752321705875,11.515324523361775,11.818896725017675,12.122468926673575,12.426041128329475,12.729613329985375,13.033185531641275,13.336757733297175,13.640329934953074,null,0,0,0,0.22164128335002287,0.38041489525700922,0.49586749517347994,0.56490772933117972,0.62462132814043703,0.68143283973867808,null,0.56490772933117972,0.62462132814043703,0.68143283973867808]
["2013-03-07T18:00:00","2013-03-07T18:00:00",null,11.034904652347132,11.338476854003032,11.642049055658932,11.945621257314832,12.249193458970732,12.552765660626632,12.856337862282532,13.159910063938431,13.463482265594331,null,0,0,0,0.19284122222331856,0.35410684380063312,0.47192527568260528,0.54321567890971534,0.60508481350976284,0.66394671281143847,null,0.54321567890971534,0.60508481350976284,0.66394671281143847]
["2013-03-07T19:00:00","2013-03-07T19:00:00",null,10.915562868264615,11.219135069920515,11.522707271576415,11.826279473232315,12.129851674888215,12.433423876544115,12.736996078200015,13.040568279855915,13.344140481511815,null,0,0,0,0.16922496180324631,0.3328669301547979,0.45295656072365142,0.52640249974155173,0.59032202204503381,0.65115019058025947,null,0.52640249974155173,0.59032202204503381,0.65115019058025947]
["2013-03-07T20:00:00","2013-03-07T20:00:00",null,10.707958186619971,11.011530388275871,11.315102589931771,11.61867479158767,11.92224699324357,12.22581919489947,12.52939139655537,12.83296359821127,13.13653579986717,null,0,0,0,0.14846872935924693,0.31446601486756443,0.43678478488835709,0.51235471527084087,0.57829308085155084,0.64105597419411997,null,0.51235471527084087,0.57829308085155084,0.64105597419411997]
["2013-03-07T21:00:00","2013-03-07T21:00:00",null,10.641140857467882,10.944713059123782,11.248285260779681,11.551857462435581,11.855429664091481,12.159001865747381,12.462574067403281,12.766146269059181,13.069718470715081,null,0,0,0,0.13073024702235383,0.29901976083502385,0.42350458145534231,0.5011459291587318,0.56905056397299181,0.63368509327049105,null,0.5011459291587318,0.56905056397299181,0.63368509327049105]
["2013-03-07T22:00:00","2013-03-07T22:00:00",null,10.624215601637152,10.927787803293052,11.231360004948952,11.534932206604852,11.838504408260752,12.142076609916652,12.445648811572552,12.749221013228452,13.052793214884352,null,0,0,0,0.117018936431181,0.28748501565211232,0.41405176840207208,0.4936699001477472,0.56344617091693727,0.62987873250821758,null,0.4936699001477472,0.56344617091693727,0.62987873250821758]
["2013-03-07T23:00:00","2013-03-07T23:00:00",null,10.641545349624225,10.945117551280125,11.248689752936025,11.552261954591925,11.855834156247825,12.159406357903725,12.462978559559625,12.766550761215525,13.070122962871425,null,0,0,0,0.1056734578055096,0.27826352839102447,0.40683860960947654,0.48837043654502393,0.55997628403420185,0.62814378906684987,null,0.48837043654502393,0.55997628403420185,0.62814378906684987]
["2013-03-08","2013-03-08",null,10.562713848682522,10.866286050338422,11.169858251994322,11.473430453650222,11.777002655306122,12.080574856962022,12.384147058617922,12.687719260273822,12.991291461929722,null,0,0,0,9.8092280707169396E-2,0.27272222418738329,0.40323203021317877,0.48660394867744949,0.55995525441673077,0.62979461403833314,null,0.48660394867744949,0.55995525441673077,0.62979461403833314]
["2013-03-08T01:00:00","2013-03-08T01:00:00",null,10.582211366273501,10.885783567929401,11.189355769585301,11.492927971241201,11.796500172897101,12.100072374553001,12.403644576208901,12.707216777864801,13.010788979520701,null,0,0,0,9.291899480927289E-2,0.26952572233177247,0.40190716431249796,0.4870666002618142,0.56211079020752097,0.63356943037439994,null,0.4870666002618142,0.56211079020752097,0.63356943037439994]
["2013-03-08T02:00:00","2013-03-08T02:00:00",null,10.552399421382852,10.855971623038752,11.15954382469465,11.46311602635055,11.76668822800645,12.070260429662349,12.373832631318249,12.677404832974149,12.980977034630049,null,0,0,0,8.9028515577114956E-2,0.26758048271569351,0.40181253103387787,0.48872794004203302,0.56544398457669409,0.63849036086264299,null,0.48872794004203302,0.56544398457669409,0.63849036086264299]
["2013-03-08T03:00:00","2013-03-08T03:00:00",null,10.560304667234343,10.863876868890243,11.167449070546143,11.471021272202043,11.774593473857943,12.078165675513842,12.381737877169742,12.685310078825642,12.988882280481542,null,2.1387120968133104E-2,2.3689864081221181E-2,2.5855914680746953E-2,0.11694533277003205,0.29745305433342517,0.4335357089890684,0.52220709105606244,0.60060550498841336,0.67525013220216779,null,0.52220709105606244,0.60060550498841336,0.67525013220216779]
["2013-03-08T04:00:00","2013-03-08T04:00:00",null,10.635263874088793,10.938836075744693,11.242408277400592,11.545980479056492,11.849552680712392,12.153124882368292,12.456697084024192,12.760269285680092,13.063841487335992,null,7.0838266451481169E-2,7.5527871147541836E-2,7.9944090816477867E-2,0.17317852988781762,0.35571560953717418,0.49372247419142529,0.58423394778714266,0.66437781996959688,0.74068378696357007,null,0.58423394778714266,0.66437781996959688,0.74068378696357007]
["2013-03-08T05:00:00","2013-03-08T05:00:00",null,10.706127500537129,11.009699702193029,11.31327190384893,11.61684410550483,11.92041630716073,12.22398850881663,12.52756071047253,12.83113291212843,13.13470511378433,null,0.11942719761851317,0.12648263428007528,0.13314902301842158,0.22850745345434487,0.41306337638092933,0.55298393622505271,0.64532498654075787,0.7272038021645798,0.80517110893877175,null,0.64532498654075787,0.7272038021645798,0.80517110893877175]
["2013-03-08T06:00:00","2013-03-08T06:00:00",null,10.759641774431895,11.063213976087795,11.366786177743695,11.670358379399595,11.973930581055495,12.277502782711395,12.581074984367294,12.884647186023194,13.188219387679094,null,0.16533485255797686,0.17482972484618936,0.18379885669762372,0.28133385254180832,0.46796119278929849,0.60985853667570755,0.70407122294634272,0.78773755605521023,0.86740826184456321,null,0.70407122294634272,0.78773755605521023,0.86740826184456321]
["2013-03-08T07:00:00","2013-03-08T07:00:00",null,10.782903389851445,11.086475591507345,11.390047793163244,11.693619994819144,11.997192196475044,12.300764398130944,12.604336599786844,12.907908801442744,13.211481003098644,null,0.21022257105009104,0.22217790858242503,0.23348132797315416,0.33321391884307122,0.52194422083767378,0.66582886357510407,0.76193421541814044,0.8474090956295246,0.92880423005150969,null,0.76193421541814044,0.8474090956295246,0.92880423005150969]
["2013-03-08T08:00:00","2013-03-08T08:00:00",null,10.866804702861895,11.170376904517795,11.473949106173695,11.777521307829595,12.081093509485495,12.384665711141395,12.688237912797295,12.991810114453195,13.295382316109094,null,0.254395282548187,0.26881108532464248,0.28243827744593081,0.38437897815031591,0.57521224189203091,0.72108418348048242,0.81909271570465547,0.90637614301855629,0.9894957060731735,null,0.81909271570465547,0.90637614301855629,0.9894957060731735]
["2013-03-08T09:00:00","2013-03-08T09:00:00",null,11.021047636064576,11.324619837720476,11.628192039376376,11.931764241032276,12.235336442688176,12.538908644344076,12.842480845999976,13.146053047655876,13.449625249311776,null,0.29464597038791834,0.31158532726090871,0.32760989577390515,0.4318323099739072,0.62482110950641245,0.77275395360703403,0.87271824025602163,0.96187330352485256,1,null,0.87271824025602163,0.96187330352485256,1]
["2013-03-08T10:00:00","2013-03-08T10:00:00",null,11.129856785147219,11.433428986803118,11.737001188459018,12.040573390114918,12.344145591770818,12.647717793426718,12.951289995082618,13.254862196738518,13.558434398394418,null,0.33307759631639744,0.35257205171212935,0.37101502623430505,0.47754018354739519,0.67270554848816178,0.8227203247184246,0.92467191021843342,1,1,null,0.92467191021843342,1,1]
["2013-03-08T11:00:00","2013-03-08T11:00:00",null,11.187832421997273,11.491404623653173,11.794976825309073,12.098549026964973,12.402121228620873,12.705693430276773,13.009265631932672,13.312837833588572,13.616410035244472,null,0.36884897563477936,0.39095110359693064,0.41187557298069899,0.52074553264181944,0.71815055184326071,0.87028931943810706,0.97428077783281497,1,1,null,0.97428077783281497,1,1]
["2013-03-08T12:00:00","2013-03-08T12:00:00",null,11.362659049031365,11.666231250687265,11.969803452343164,12.273375653999064,12.576947855654964,12.880520057310864,13.184092258966764,13.487664460622664,13.791236662278564,null,0.40319034096512485,0.42790014149369549,0.4513061057390565,0.56252086774820731,0.76216554121032321,0.91643881497848867,1,1,1,null,1,1,1]
["2013-03-08T13:00:00","2013-03-08T13:00:00",null,11.416105336943076,11.719677538598976,12.023249740254876,12.326821941910776,12.630394143566676,12.933966345222576,13.237538546878476,13.541110748534376,13.844682950190276,null,0.43850958350787761,0.46579551217666093,0.49164091204867233,0.60517944678838231,0.80703223008496627,0.96341898040897966,1,1,1,null,1,1,1]
["2013-03-08T14:00:00","2013-03-08T14:00:00",null,11.526510356845879,11.830082558501779,12.133654760157679,12.437226961813579,12.740799163469479,13.044371365125379,13.347943566781279,13.651515768437179,13.955087970093079,null,0.47215697146167601,0.50202954307940761,0.53033540819554048,0.64621874528328083,0.85030066803180393,1,1,1,1,null,1,1,1]
["2013-03-08T15:00:00","2013-03-08T15:00:00",null,11.529009271216811,11.832581472872711,12.136153674528611,12.439725876184511,12.743298077840411,13.046870279496311,13.350442481152211,13.654014682808111,13.957586884464011,null,0.50564663728444093,0.5381163666598564,0.56888269702011074,0.68711083645588145,0.89342189865634369,1,1,1,1,null,1,1,1]
["2013-03-08T16:00:00","2013-03-08T16:00:00",null,11.584387945824165,11.887960147480065,12.191532349135965,12.495104550791865,12.798676752447765,13.102248954103665,13.405821155759565,13.709393357415465,14.012965559071365,null,0.53672841190676224,0.57184787308353924,0.60512724273159291,0.72574224375033625,0.93433501944641539,1,1,1,1,null,1,1,1]
["2013-03-08T17:00:00","2013-03-08T17:00:00",null,11.680835332858983,11.984407534514883,12.287979736170783,12.591551937826683,12.895124139482583,13.198696341138483,13.502268542794383,13.805840744450283,14.109412946106183,null,0.57623254832626869,0.61400174130440732,0.64980466504899581,0.77280652765071178,0.98369153165114342,1,1,1,1,null,1,1,1]
["2013-03-08T18:00:00","2013-03-08T18:00:00",null,11.640096002387919,11.943668204043819,12.247240405699719,12.550812607355619,12.854384809011519,13.157957010667419,13.461529212323319,13.765101413979218,14.068673615635118,null,0.6206260708078114,0.66100293635236951,0.69928735495855054,0.82465504952576796,1,1,1,1,1,null,1,1,1]
["2013-03-08T19:00:00","2013-03-08T19:00:00",null,11.556824488228166,11.860396689884066,12.163968891539966,12.467541093195866,12.771113294851766,13.074685496507666,13.378257698163566,13.681829899819466,13.985402101475366,null,0.64410563871432136,0.68710069163403442,0.72786660510180801,0.85560013163452697,1,1,1,1,1,null,1,1,1]
["2013-03-08T20:00:00","2013-03-08T20:00:00",null,11.646067594788752,11.949639796444652,12.253211998100552,12.556784199756452,12.860356401412352,13.163928603068252,13.467500804724152,13.771073006380051,14.074645208035951,null,0.61890164217517929,0.66451488247004731,0.70777280560814904,0.83787216410636944,0.98453271634998829,0.986677737332043,0.98873863984421306,0.99070490907776321,0.99257654503269321,null,0.98873863984421306,0.99070490907776321,0.99257654503269321]
["2013-03-08T21:00:00","2013-03-08T21:00:00",null,11.540585287932258,11.844157489588158,12.147729691244058,12.451301892899957,12.754874094555857,13.058446296211757,13.362018497867657,13.665590699523557,13.969162901179457,null,0.59512765962407366,0.64334857248536104,0.68907747567631983,0.82153215133130608,0.97043235783559967,0.9747118849909735,0.97881266039784254,0.98273468405620723,0.98646744115733165,null,0.97881266039784254,0.98273468405620723,0.98646744115733165]
["2013-03-08T22:00:00","2013-03-08T22:00:00",null,11.517482868893676,11.821055070549576,12.124627272205476,12.428199473861376,12.731771675517276,13.035343877173176,13.338916078829076,13.642488280484976,13.946060482140876,null,0.57417164581409863,0.62489508315444975,0.67300033311964558,0.80771569265277765,0.95876092013912584,0.96509083499793424,0.97114736482961783,0.97694102444291253,0.98246129902908252,null,0.97114736482961783,0.97694102444291253,0.98246129902908252]
["2013-03-08T23:00:00","2013-03-08T23:00:00",null,11.437436739358715,11.741008941014615,12.044581142670514,12.348153344326414,12.651725545982314,12.955297747638214,13.258869949294114,13.562442150950014,13.866014352605914,null,0.55209054746941844,0.60524290562768435,0.65565089870596827,0.79255333845609721,0.94568049807208676,0.9539871969731808,0.96193639237726547,0.96953859909307694,0.97679381712061464,null,0.96193639237726547,0.96953859909307694,0.97679381712061464]
["2013-03-09","2013-03-09",null,11.331551098876702,11.635123300532602,11.938695502188502,12.242267703844401,12.545839905500301,12.849412107156201,13.152984308812101,13.456556510468001,13.760128712123901,null,0.53144997792151027,0.58701022728021979,0.63969993385412072,0.77876842420377546,0.93395648633193518,0.94422945446657924,0.95405028582559392,0.96345052483518656,0.9724091418778853,null,0.95405028582559392,0.96345052483518656,0.9724091418778853]
["2013-03-09T01:00:00","2013-03-09T01:00:00",null,11.296871521641373,11.600443723297273,11.904015924953173,12.207588126609073,12.511160328264973,12.814732529920873,13.118304731576773,13.421876933232673,13.725449134888573,null,0.51249177777129196,0.57041785909550291,0.62535773473881417,0.76656073126178803,0.92377815147591114,0.93598584441789867,0.94765728211437228,0.9588240089915393,0.96946499543192799,null,0.94765728211437228,0.9588240089915393,0.96946499543192799]
["2013-03-09T02:00:00","2013-03-09T02:00:00",null,11.285910357885088,11.589482559540988,11.893054761196888,12.196626962852788,12.500199164508688,12.803771366164588,13.107343567820488,13.410915769476388,13.714487971132288,null,0.49398571439670286,0.55426711287767971,0.61144664278166561,0.75477363066922298,0.91402040896930958,0.92815231190990499,0.94166384113510193,0.95457602626237226,0.9668993821004509,null,0.94166384113510193,0.95457602626237226,0.9668993821004509]
["2013-03-09T03:00:00","2013-03-09T03:00:00",null,11.371918500398811,11.675490702054713,11.979062903710613,12.282635105366513,12.586207307022413,12.889779508678313,13.193351710334213,13.496923911990113,13.800496113646012,null,0.47481721807177335,0.53745393370951611,0.59687311787417663,0.74232409712631753,0.90360023351236762,0.91965634645157091,0.93500796720549118,0.9496761253916004,0.96368185062736889,null,0.93500796720549118,0.9496761253916004,0.96368185062736889]
["2013-03-09T04:00:00","2013-03-09T04:00:00",null,11.419075749004731,11.722647950660633,12.026220152316533,12.329792353972433,12.633364555628333,12.936936757284233,13.240508958940133,13.544081160596033,13.847653362251933,null,0.45348267114731805,0.51851676317676898,0.5802176608370464,0.72784520549744869,0.89118224439566895,0.90921514137715786,0.92643839808600814,0.94290458856589843,0.95862422762556354,null,0.92643839808600814,0.94290458856589843,0.95862422762556354]
["2013-03-09T05:00:00","2013-03-09T05:00:00",null,11.497763470590494,11.801335672246394,12.104907873902294,12.408480075558193,12.712052277214093,13.015624478869993,13.319196680525893,13.622768882181793,13.926341083837693,null,0.42852051520909384,0.49603610210013743,0.56009231691718075,0.70995951583825778,0.87543106090979705,0.89549331597724946,0.91466181230217869,0.9329786091195279,0.950475250855503,null,0.91466181230217869,0.9329786091195279,0.950475250855503]
["2013-03-09T06:00:00","2013-03-09T06:00:00",null,11.633012482730081,11.936584684385981,12.240156886041881,12.54372908769778,12.84730128935368,13.15087349100958,13.45444569266548,13.75801789432138,14.06159009597728,null,0.40072987572100349,0.47076901670858196,0.53722260791733345,0.68937152033402738,0.85701963081382804,0.8791533032021861,0.90030909837813655,0.92051856076788696,0.93982374960637871,null,0.90030909837813655,0.92051856076788696,0.93982374960637871]
["2013-03-09T07:00:00","2013-03-09T07:00:00",null,11.699682027630015,12.003254229285915,12.306826430941815,12.610398632597715,12.913970834253615,13.217543035909515,13.521115237565414,13.824687439221314,14.128259640877214,null,0.37012126749178254,0.44274705142830922,0.51165059307244665,0.66614430783717093,0.83602155776891074,0.86027922152185232,0.88346437478376627,0.90561907678959563,0.92678538677428179,null,0.88346437478376627,0.90561907678959563,0.92678538677428179]
["2013-03-09T08:00:00","2013-03-09T08:00:00",null,11.778814841997775,12.082387043653675,12.385959245309575,12.689531446965475,12.993103648621375,13.296675850277275,13.600248051933175,13.903820253589075,14.207392455244975,null,0.33599019833614829,0.41127622888277215,0.48270332462344445,0.63960493058861245,0.81177440882470475,0.83821915279464321,0.86348623818619852,0.88763875385178459,0.91071875902634303,null,0.86348623818619852,0.88763875385178459,0.91071875902634303]
["2013-03-09T09:00:00","2013-03-09T09:00:00",null,11.97611595650609,12.27968815816199,12.58326035981789,12.88683256147379,13.19040476312969,13.49397696478559,13.79754916644149,14.10112136809739,14.40469356975329,null,0.2974218798941069,0.37544176071197688,0.44948704382780408,0.60887014465456468,0.78341596966489402,0.81213191232171389,0.83956504831279499,0.86578898129928672,0.89085628532486638,null,0.83956504831279499,0.86578898129928672,0.89085628532486638]
["2013-03-09T10:00:00","2013-03-09T10:00:00",null,12.136631557547149,12.440203759203049,12.743775960858949,13.047348162514849,13.350920364170749,13.654492565826649,13.958064767482549,14.261636969138449,14.565209170794349,null,0.25645618506035733,0.33727300500188684,0.41397853472781121,0.57590621926857777,0.75287045028808641,0.78389965086672997,0.81355141150101462,0.84188882104335427,0.86899599796363303,null,0.81355141150101462,0.84188882104335427,0.86899599796363303]
["2013-03-09T11:00:00","2013-03-09T11:00:00",null,12.337956179220239,12.641528380876139,12.945100582532039,13.248672784187939,13.552244985843839,13.855817187499738,14.159389389155638,14.462961590811538,14.766533792467438,null,0.21339804328823095,0.29702231716215549,0.37639860830691263,0.5408708765616852,0.72026402839910864,0.75362751651704696,0.78549790179453516,0.81596981751019393,0.84512738213390726,null,0.78549790179453516,0.81596981751019393,0.84512738213390726]
["2013-03-09T12:00:00","2013-03-09T12:00:00",null,12.368843387117948,12.672415588773848,12.975987790429748,13.279559992085648,13.583132193741548,13.886704395397448,14.190276597053348,14.493848798709248,14.797421000365148,null,0.16912018370277937,0.25557294112657009,0.33764102330763113,0.50467890489388079,0.68652200716669021,0.72224081244139438,0.75635085197955731,0.78897830348600628,0.82019677062188978,null,0.75635085197955731,0.78897830348600628,0.82019677062188978]
["2013-03-09T13:00:00","2013-03-09T13:00:00",null,12.48779381802211,12.79136601967801,13.09493822133391,13.39851042298981,13.70208262464571,14.00565482630161,14.30922702795751,14.61279922961341,14.91637143126931,null,0.12302326220607557,0.21231501798846802,0.29709592082330405,0.46670993054976639,0.65102401287543288,0.68910865011563849,0.72548988834068284,0.7602833904466576,0.79358378971218235,null,0.72548988834068284,0.7602833904466576,0.79358378971218235]
["2013-03-09T14:00:00","2013-03-09T14:00:00",null,12.607886667761759,12.911458869417659,13.215031071073559,13.518603272729459,13.822175474385359,14.125747676041259,14.429319877697159,14.732892079353059,15.036464281008959,null,7.2226221204575558E-2,0.16444109381545424,0.2520084209652142,0.42429319211050931,0.6111518581501818,0.6516759310170378,0.69039145678137692,0.72742461314802631,0.76288054820434137,null,0.69039145678137692,0.72742461314802631,0.76288054820434137]
["2013-03-09T15:00:00","2013-03-09T15:00:00",null,12.723017525928846,13.026589727584746,13.330161929240646,13.633734130896546,13.937306332552446,14.240878534208345,14.544450735864245,14.848022937520145,15.151595139176045,null,1.9841444084005684E-2,0.11498994833210617,0.20535421460552561,0.38032026197838903,0.56973402654080307,0.61270804984304506,0.65376837795541443,0.69305170339147415,0.730673689047315,null,0.65376837795541443,0.69305170339147415,0.730673689047315]
["2013-03-09T16:00:00","2013-03-09T16:00:00",null,12.841463086100644,13.145035287756544,13.448607489412444,13.752179691068344,14.055751892724244,14.359324094380144,14.662896296036044,14.966468497691944,15.270040699347843,null,0,6.1185672032235426E-2,0.15443099589919884,0.33214140835204398,0.52418387509834852,0.56968145249712532,0.6131496718099384,0.6547567699765573,0.69459738027560181,null,0.6131496718099384,0.6547567699765573,0.69459738027560181]
["2013-03-09T17:00:00","2013-03-09T17:00:00",null,12.782817945368041,13.086390147023941,13.389962348679841,13.693534550335741,13.997106751991641,14.300678953647541,14.604251155303441,14.907823356959341,15.211395558615241,null,0,9.5684759493615823E-3,0.10565279817492673,0.28607603128154685,0.48071565578553521,0.52869472804590467,0.57454980894169028,0.61843862060392618,0.66047682592870316,null,0.57454980894169028,0.61843862060392618,0.66047682592870316]
["2013-03-09T18:00:00","2013-03-09T18:00:00",null,12.714983073406078,13.018555275061978,13.322127476717878,13.625699678373778,13.929271880029678,14.232844081685577,14.536416283341477,14.839988484997377,15.143560686653277,null,0,0,5.9356095312247253E-2,0.24245008983770011,0.43964481286443002,0.49007383556018547,0.53827371880400143,0.58440218472691197,0.62859592584247914,null,0.53827371880400143,0.58440218472691197,0.62859592584247914]
["2013-03-09T19:00:00","2013-03-09T19:00:00",null,12.64334270460046,12.94691490625636,13.25048710791226,13.55405930956816,13.85763151122406,14.16120371287996,14.46477591453586,14.76834811619176,15.07192031784766,null,0,0,1.5782727912078333E-2,0.20149490981268614,0.40120267212721539,0.45402907121467895,0.504531697571583,0.55286827332896149,0.5991754910003767,null,0.504531697571583,0.55286827332896149,0.5991754910003767]
["2013-03-09T20:00:00","2013-03-09T20:00:00",null,12.265531715443137,12.569103917099037,12.872676118754937,13.176248320410837,13.479820522066737,13.783392723722637,14.086964925378537,14.390537127034436,14.694109328690336,null,0,0,0,0.17199035650069916,0.37402189154578763,0.42906691527645474,0.48169353299794232,0.53205946684128425,0.58031192412877852,null,0.48169353299794232,0.53205946684128425,0.58031192412877852]
["2013-03-09T21:00:00","2013-03-09T21:00:00",null,11.867258672805274,12.170830874461174,12.474403076117074,12.777975277772974,13.081547479428874,13.385119681084774,13.688691882740674,13.992264084396574,14.295836286052474,null,0,0,0,0.14391581717674862,0.34830266937860299,0.40559786217868038,0.46038001569095816,0.51280685204647025,0.56302557856751456,null,0.46038001569095816,0.51280685204647025,0.56302557856751456]
["2013-03-09T22:00:00","2013-03-09T22:00:00",null,11.973960253357717,12.277532455013617,12.581104656669517,12.884676858325417,13.188249059981317,13.491821261637217,13.795393463293117,14.098965664949016,14.402537866604916,null,0,0,0,0.12036264560908974,0.32697863726288323,0.38641885104501528,0.44324087745199209,0.49762346823231873,0.54971383070829305,null,0.44324087745199209,0.49762346823231873,0.54971383070829305]
["2013-03-09T23:00:00","2013-03-09T23:00:00",null,11.818076644938134,12.121648846594034,12.425221048249934,12.728793249905834,13.032365451561734,13.335937653217634,13.639509854873534,13.943082056529434,14.246654258185334,null,0,0,0,0.10018472764554627,0.30898779951633665,0.37050994542811,0.42932978549484357,0.48561555665630696,0.53952498104353352,null,0.42932978549484357,0.48561555665630696,0.53952498104353352]
["2013-03-11","2013-03-11",null,9.5857994852765245,9.8893716869324244,10.192943888588324,10.496516090244224,10.800088291900124,11.103660493556024,11.407232695211924,11.710804896867824,12.014377098523724,null,0,0,0,9.6020863386263713E-2,0.30673763044692637,0.37007883826995197,0.43062310696931771,0.48853867348479318,0.54399377475614741,null,0.43062310696931771,0.48853867348479318,0.54399377475614741]
["2013-03-11T01:00:00","2013-03-11T01:00:00",null,9.3240405474938246,9.6276127491497245,9.9311849508056245,10.234757152461524,10.538329354117424,10.841901555773324,11.145473757429224,11.449045959085124,11.752618160741024,null,3.4173128390576494E-3,5.4256413075499908E-3,7.3077920712155886E-3,0.10510565813378928,0.31748376497467073,0.38240219410803061,0.4444395656478462,0.50377463134262257,0.56056511332339309,null,0.4444395656478462,0.50377463134262257,0.56056511332339309]
["2013-03-11T02:00:00","2013-03-11T02:00:00",null,9.3046285030547917,9.6082007047106917,9.9117729063665916,10.215345108022492,10.518917309678391,10.822489511334291,11.126061712990191,11.429633914646091,11.733206116301991,null,4.1428346418114275E-3,8.2541248574161674E-3,1.210254485463186E-2,0.11176153206340002,0.3258850971543848,0.3924543512592279,0.45605842930064222,0.51686556821839724,0.57506503456973312,null,0.45605842930064222,0.51686556821839724,0.57506503456973312]
["2013-03-11T03:00:00","2013-03-11T03:00:00",null,9.3435801439109607,9.6471523455668606,9.9507245472227606,10.254296748878662,10.557868950534562,10.861441152190462,11.165013353846362,11.468585555502262,11.772157757158162,null,2.6602466100971861E-3,8.9375874252276971E-3,1.4815365508406855E-2,0.11638804790704729,0.33230964529181317,0.40058229841181731,0.46580565699850818,0.52813744318291966,0.58777743833102758,null,0.46580565699850818,0.52813744318291966,0.58777743833102758]
["2013-03-11T04:00:00","2013-03-11T04:00:00",null,9.2982949612130223,9.6018671628689223,9.9054393645248222,10.209011566180722,10.512583767836622,10.816155969492522,11.119728171148422,11.423300372804322,11.726872574460222,null,0,8.2225804312094815E-3,1.6182290644029915E-2,0.11971072746748489,0.33748293118970968,0.40749052775108152,0.47436471130925562,0.53825268918653035,0.59937527236635246,null,0.47436471130925562,0.53825268918653035,0.59937527236635246]
["2013-03-11T05:00:00","2013-03-11T05:00:00",null,9.2910290328714638,9.5946012345273637,9.8981734361832636,10.201745637839164,10.505317839495063,10.808890041150963,11.112462242806863,11.416034444462763,11.719606646118663,null,0,7.9491954040848689E-3,1.7980322937811016E-2,0.12345399937734496,0.34306629462829308,0.41480883463103269,0.48331281354321887,0.54875698311335674,0.61135163951615756,null,0.48331281354321887,0.54875698311335674,0.61135163951615756]
["2013-03-11T06:00:00","2013-03-11T06:00:00",null,9.2453557067669969,9.5489279084228968,9.8525001100787968,10.156072311734697,10.459644513390597,10.763216715046497,11.066788916702397,11.370361118358296,11.673933320014196,null,0,6.3614592850150071E-3,1.8516578183324677E-2,0.12598806828261538,0.34747199948849355,0.42099154216754314,0.49116737566868368,0.55819928135789143,0.62229755540987763,null,0.49116737566868368,0.55819928135789143,0.62229755540987763]
["2013-03-11T07:00:00","2013-03-11T07:00:00",null,9.2142450110387788,9.5178172126946787,9.8213894143505787,10.124961616006479,10.428533817662379,10.732106019318278,11.035678220974178,11.339250422630078,11.642822624285978,null,0,2.5971577576838121E-3,1.6949871681725938E-2,0.12648226429318679,0.34991143511514394,0.42526055451418132,0.49717133145668957,0.56584354730864506,0.6314980130534944,null,0.49717133145668957,0.56584354730864506,0.6314980130534944]
["2013-03-11T08:00:00","2013-03-11T08:00:00",null,9.2091560957724763,9.5127282974283762,9.8163004990842762,10.119872700740176,10.423444902396076,10.727017104051976,11.030589305707876,11.334161507363776,11.637733709019676,null,0,0,1.5719639059665183E-2,0.12730241937456063,0.3526663150038612,0.42984501112288637,0.50348021669802678,0.57379274271272995,0.64099288534170684,null,0.50348021669802678,0.57379274271272995,0.64099288534170684]
["2013-03-11T09:00:00","2013-03-11T09:00:00",null,9.2819483180919882,9.5855205197478881,9.889092721403788,10.192664923059688,10.496237124715588,10.799809326371488,11.103381528027388,11.406953729683288,11.710525931339188,null,0,0,1.4279110262893189E-2,0.12790176347248766,0.35520038390913161,0.43419814193940903,0.50955777614718167,0.58150009751589693,0.65024591702900136,null,0.50955777614718167,0.58150009751589693,0.65024591702900136]
["2013-03-11T10:00:00","2013-03-11T10:00:00",null,9.4670612305770856,9.7706334322329855,10.074205633888885,10.377777835544787,10.681350037200687,10.984922238856587,11.288494440512487,11.592066642168387,11.895638843824287,null,0,0,1.0146790429817323E-2,0.12585137576905306,0.35512678024798267,0.43598565942445455,0.51310126669106604,0.58671544264873565,0.65703848347217442,null,0.51310126669106604,0.58671544264873565,0.65703848347217442]
["2013-03-11T11:00:00","2013-03-11T11:00:00",null,9.5552496284041695,9.8588218300600694,10.162394031715969,10.465966233371871,10.769538435027771,11.073110636683671,11.376682838339571,11.680255039995471,11.983827241651371,null,0,0,4.9945341493919443E-3,0.12280208123574007,0.35405426975695536,0.43679529969709285,0.51567739483127872,0.59097394018663829,0.66289523193788247,null,0.51567739483127872,0.59097394018663829,0.66289523193788247]
["2013-03-11T12:00:00","2013-03-11T12:00:00",null,9.7206807178312911,10.024252919487191,10.327825121143091,10.631397322798991,10.934969524454891,11.238541726110791,11.542113927766691,11.845686129422591,12.149258331078491,null,0,0,0,0.11473722293556401,0.34808185839515615,0.43279967237757927,0.5135639182754308,0.59063746630710035,0.66424112745603436,null,0.5135639182754308,0.59063746630710035,0.66424112745603436]
["2013-03-11T13:00:00","2013-03-11T13:00:00",null,9.8253886290096819,10.128960830665582,10.432533032321482,10.736105233977382,11.039677435633282,11.343249637289182,11.646821838945081,11.950394040600981,12.253966242256881,null,0,0,0,0.1049479360027558,0.34040604801819591,0.42713219046911133,0.50979961674809959,0.5886817118822858,0.66399928685511644,null,0.50979961674809959,0.5886817118822858,0.66399928685511644]
["2013-03-11T14:00:00","2013-03-11T14:00:00",null,10.041751941980264,10.345324143636164,10.648896345292064,10.952468546947964,11.256040748603864,11.559612950259764,11.863185151915664,12.166757353571564,12.470329555227464,null,0,0,0,9.1310229072731897E-2,0.32894490649643332,0.41774246626825445,0.50237616178079281,0.58311937806117353,0.66021395571031416,null,0.50237616178079281,0.58311937806117353,0.66021395571031416]
["2013-03-11T15:00:00","2013-03-11T15:00:00",null,10.250473211100859,10.554045412756759,10.857617614412657,11.161189816068557,11.464762017724457,11.768334219380357,12.071906421036257,12.375478622692157,12.679050824348057,null,0,0,0,7.4412931434683763E-2,0.31427674831032432,0.40518778463799343,0.49182980861902414,0.57448672008927715,0.65338984484093443,null,0.49182980861902414,0.57448672008927715,0.65338984484093443]
["2013-03-11T16:00:00","2013-03-11T16:00:00",null,10.403071581582436,10.706643783238338,11.010215984894238,11.313788186550138,11.617360388206038,11.920932589861938,12.224504791517838,12.528076993173737,12.831649194829637,null,0,0,0,5.3866995165395615E-2,0.29603355515412427,0.38913167169879026,0.47784511300072668,0.56247880851326537,0.64326408402858826,null,0.47784511300072668,0.56247880851326537,0.64326408402858826]
["2013-03-11T17:00:00","2013-03-11T17:00:00",null,10.54108849127973,10.84466069293563,11.14823289459153,11.45180509624743,11.75537729790333,12.05894949955923,12.36252170121513,12.66609390287103,12.969666104526929,null,0,0,0,3.380474009794332E-2,0.27832661724343788,0.37366438804877855,0.4645018207152985,0.55116487431380068,0.63387435982773144,null,0.4645018207152985,0.55116487431380068,0.63387435982773144]
["2013-03-11T18:00:00","2013-03-11T18:00:00",null,10.581526705228843,10.885098906884743,11.188671108540643,11.492243310196542,11.795815511852442,12.099387713508342,12.402959915164242,12.706532116820142,13.010104318476042,null,0,0,0,1.1954967545445488E-2,0.25887422108264818,0.35648319057487027,0.44948667384091595,0.5382106299515883,0.6228863846990691,null,0.44948667384091595,0.5382106299515883,0.6228863846990691]
["2013-03-11T19:00:00","2013-03-11T19:00:00",null,10.392464147684874,10.696036349340773,10.999608550996673,11.303180752652572,11.606752954308472,11.910325155964372,12.213897357620272,12.517469559276172,12.821041760932072,null,0,0,0,0,0.24145118300782195,0.34132083637818988,0.43645882581755463,0.52722265482292596,0.61384364918648582,null,0.43645882581755463,0.52722265482292596,0.61384364918648582]
["2013-03-11T20:00:00","2013-03-11T20:00:00",null,10.4867279124196,10.790300114075499,11.093872315731399,11.397444517387299,11.701016719043199,12.004588920699099,12.308161122354999,12.611733324010899,12.915305525666799,null,0,0,0,0,0.21982222143877092,0.32203667715716916,0.41940380604847305,0.51229162641842796,0.6009419788679512,null,0.41940380604847305,0.51229162641842796,0.6009419788679512]
["2013-03-11T21:00:00","2013-03-11T21:00:00",null,10.183943385698809,10.487515587354709,10.791087789010609,11.094659990666509,11.398232192322409,11.701804393978309,12.005376595634209,12.308948797290109,12.612520998946009,null,0,0,0,0,0.20553259636714216,0.30996567672874398,0.40943576736716025,0.50432140139687198,0.5948749342275319,null,0.40943576736716025,0.50432140139687198,0.5948749342275319]
["2013-03-11T22:00:00","2013-03-11T22:00:00",null,10.071515204665094,10.375087406320993,10.678659607976892,10.982231809632792,11.285804011288691,11.589376212944591,11.892948414600491,12.196520616256391,12.500092817912291,null,0,0,0,0,0.19643728681088105,0.30296281411085968,0.40443071840903272,0.50120901801114559,0.59356058313558668,null,0.40443071840903272,0.50120901801114559,0.59356058313558668]
["2013-03-11T23:00:00","2013-03-11T23:00:00",null,9.7009443201991559,10.004516521855056,10.308088723510956,10.611660925166856,10.915233126822756,11.218805328478656,11.522377530134555,11.825949731790455,12.129521933446355,null,0,0,0,0,0.19493366916169569,0.30332031760786876,0.40655470977361624,0.50500486396468347,0.59894416520819438,null,0.40655470977361624,0.50500486396468347,0.59894416520819438]
["2013-03-12","2013-03-12",null,9.6146858066254257,9.9182580082813256,10.221830209937226,10.525402411593126,10.828974613249025,11.132546814904925,11.436119016560825,11.739691218216725,12.043263419872625,null,0,0,0,0,0.19435535468123977,0.30459260946487177,0.40958297468945809,0.50969446866074408,0.60521099121458932,null,0.40958297468945809,0.50969446866074408,0.60521099121458932]
["2013-03-12T01:00:00","2013-03-12T01:00:00",null,9.5881319023385441,9.891704103994444,10.195276305650344,10.498848507306244,10.802420708962144,11.105992910618044,11.409565112273944,11.713137313929844,12.016709515585744,null,0,0,0,0,0.1951229357189358,0.30717925241381999,0.41389404627103848,0.51563533559633656,0.61269753503430946,null,0.41389404627103848,0.51563533559633656,0.61269753503430946]
["2013-03-12T02:00:00","2013-03-12T02:00:00",null,9.5280275662763465,9.8315997679322464,10.135171969588146,10.438744171244046,10.742316372899946,11.045888574555846,11.349460776211746,11.653032977867646,11.956605179523546,null,0,0,0,0,0.19543837998100266,0.30933478820461019,0.41779504031193199,0.52118715460871334,0.61981606054828497,null,0.41779504031193199,0.52118715460871334,0.61981606054828497]
["2013-03-12T03:00:00","2013-03-12T03:00:00",null,9.5126494269381858,9.8162216285940858,10.119793830249986,10.423366031905886,10.726938233561786,11.030510435217685,11.334082636873585,11.637654838529485,11.941227040185385,null,0,0,0,0,0.1965319200895011,0.31224739022436088,0.42243207096431484,0.52746449542384388,0.62763907824754306,null,0.42243207096431484,0.52746449542384388,0.62763907824754306]
["2013-03-12T04:00:00","2013-03-12T04:00:00",null,9.4571801024232709,9.7607523040791708,10.064324505735071,10.367896707390971,10.671468909046871,10.975041110702771,11.27861331235867,11.58218551401457,11.88575771567047,null,0,0,0,0,0.19699457167386583,0.31455013333744897,0.42649078713624178,0.53317403656725404,0.63492584070128755,null,0.42649078713624178,0.53317403656725404,0.63492584070128755]
["2013-03-12T05:00:00","2013-03-12T05:00:00",null,9.5127642141971673,9.8163364158530673,10.119908617508967,10.423480819164867,10.727053020820767,11.030625222476667,11.334197424132567,11.637769625788467,11.941341827444367,null,0,0,0,0,0.19463925451709996,0.31410851137055534,0.42786822708060041,0.53627590514424484,0.63965750463229043,null,0.42786822708060041,0.53627590514424484,0.63965750463229043]
["2013-03-12T06:00:00","2013-03-12T06:00:00",null,9.4593436314236854,9.7629158330795853,10.066488034735485,10.370060236391385,10.673632438047285,10.977204639703185,11.280776841359085,11.584349043014985,11.887921244670885,null,0,0,0,0,0.19148481189643135,0.31289930836596569,0.42849911560473414,0.53866276672721736,0.64369519118674623,null,0.42849911560473414,0.53866276672721736,0.64369519118674623]
["2013-03-12T07:00:00","2013-03-12T07:00:00",null,9.4502227286163798,9.7537949302722797,10.05736713192818,10.36093933358408,10.66451153523998,10.968083736895879,11.271655938551779,11.575228140207679,11.878800341863579,null,0,0,0,0,0.18874044681644966,0.31208966809332739,0.42952956686081922,0.54142816142467021,0.64811141085568225,null,0.42952956686081922,0.54142816142467021,0.64811141085568225]
["2013-03-12T08:00:00","2013-03-12T08:00:00",null,9.8058042569264963,10.109376458582396,10.412948660238296,10.716520861894196,11.020093063550096,11.323665265205996,11.627237466861896,11.930809668517796,12.234381870173696,null,0,0,0,0,0.18534416359486314,0.310586050444142,0.42982398150541495,0.54342597508442703,0.65172850506071556,null,0.42982398150541495,0.54342597508442703,0.65172850506071556]
["2013-03-12T09:00:00","2013-03-12T09:00:00",null,9.9738573150185772,10.277429516674477,10.581001718330377,10.884573919986277,11.188146121642177,11.491718323298077,11.795290524953977,12.098862726609877,12.402434928265777,null,0,0,0,0,0.18049683676776906,0.30764190399818464,0.42868838216197425,0.54400428956488289,0.65393661489518362,null,0.42868838216197425,0.54400428956488289,0.65393661489518362]
["2013-03-12T10:00:00","2013-03-12T10:00:00",null,10.198080470264429,10.501652671920329,10.805224873576229,11.108797075232129,11.412369276888029,11.715941478543929,12.019513680199829,12.323085881855729,12.626658083511629,null,0,0,0,0,0.16824708459083934,0.29745305433342506,0.42045528692202921,0.53763231547113233,0.64933112866900744,null,0.42045528692202921,0.53763231547113233,0.64933112866900744]
["2013-03-12T11:00:00","2013-03-12T11:00:00",null,10.483620287979281,10.787192489635181,11.090764691291081,11.394336892946981,11.697909094602881,12.001481296258781,12.305053497914681,12.608625699570581,12.912197901226481,null,0,0,0,0,0.14928888444062105,0.28068193440020367,0.40575558430971354,0.52490939690110228,0.63847984605390751,null,0.40575558430971354,0.52490939690110228,0.63847984605390751]
["2013-03-12T12:00:00","2013-03-12T12:00:00",null,10.70773192306644,11.01130412472234,11.31487632637824,11.61844852803414,11.92202072969004,12.22559293134594,12.52916513300184,12.83273733465774,13.13630953631364,null,0,0,0,0,0.12670307527663388,0.26032526468815564,0.38752290596224903,0.50870607663960121,0.62420073579101432,null,0.38752290596224903,0.50870607663960121,0.62420073579101432]
["2013-03-12T13:00:00","2013-03-12T13:00:00",null,10.842108526017638,11.145680727673538,11.449252929329438,11.752825130985338,12.056397332641238,12.359969534297138,12.663541735953038,12.967113937608937,13.270686139264837,null,0,0,0,0,0.10133084179772278,0.2372347447048615,0.36659843657848068,0.48984250976800298,0.60731395296170176,null,0.36659843657848068,0.48984250976800298,0.60731395296170176]
["2013-03-12T14:00:00","2013-03-12T14:00:00",null,10.989302563119681,11.292874764775581,11.596446966431481,11.900019168087381,12.203591369743281,12.507163571399181,12.810735773055081,13.114307974710981,13.41788017636688,null,0,0,0,0,7.3960794659054904E-2,0.21219898510548837,0.34377078681357559,0.46913885136768141,0.58862913783860804,null,0.34377078681357559,0.46913885136768141,0.58862913783860804]
["2013-03-12T15:00:00","2013-03-12T15:00:00",null,11.043507674809312,11.347079876465212,11.650652078121112,11.954224279777012,12.257796481432912,12.561368683088812,12.864940884744712,13.168513086400612,13.472085288056512,null,0,0,0,0,4.5066100253730534E-2,0.18568063747440103,0.31951312306063406,0.44703672340553008,0.56858791238862683,null,0.31951312306063406,0.44703672340553008,0.56858791238862683]
["2013-03-12T16:00:00","2013-03-12T16:00:00",null,11.081971259070553,11.385543460726453,11.689115662382353,11.992687864038253,12.296260065694153,12.599832267350052,12.903404469005952,13.206976670661852,13.510548872317752,null,0,0,0,0,1.4594184538071864E-2,0.15761661295918605,0.29374132684977161,0.4234520074116645,0.54709564333313809,null,0.29374132684977161,0.4234520074116645,0.54709564333313809]
["2013-03-12T17:00:00","2013-03-12T17:00:00",null,11.104222617322677,11.407794818978577,11.711367020634476,12.014939222290376,12.318511423946276,12.622083625602176,12.925655827258076,13.229228028913976,13.532800230569876,null,0,0,0,0,0,0.12865882970144832,0.26709680151385751,0.39900507710148286,0.52476218957880438,null,0.26709680151385751,0.39900507710148286,0.52476218957880438]
["2013-03-12T18:00:00","2013-03-12T18:00:00",null,10.938357978961337,11.241930180617237,11.545502382273137,11.849074583929037,12.152646785584936,12.456218987240836,12.759791188896736,13.063363390552636,13.366935592208536,null,0,0,0,0,0,0.10060531999496891,0.2413670645379373,0.37548344996003069,0.50335403899320019,null,0.2413670645379373,0.37548344996003069,0.50335403899320019]
["2013-03-12T19:00:00","2013-03-12T19:00:00",null,10.756027301013422,11.059599502669322,11.363171704325222,11.666743905981122,11.970316107637021,12.273888309292921,12.577460510948821,12.881032712604721,13.184604914260621,null,0,0,0,0,0,7.7157296514665658E-2,0.22015869531830876,0.35640958691372121,0.48632004884158975,null,0.22015869531830876,0.35640958691372121,0.48632004884158975]
["2013-03-12T20:00:00","2013-03-12T20:00:00",null,10.530337775333203,10.833909976989105,11.137482178645005,11.441054380300905,11.744626581956805,12.048198783612705,12.351770985268605,12.655343186924505,12.958915388580404,null,0,0,0,0,0,5.7368426474337979E-2,0.20256742030371352,0.34090024402876729,0.47279800480765699,null,0.20256742030371352,0.34090024402876729,0.47279800480765699]
["2013-03-12T21:00:00","2013-03-12T21:00:00",null,10.370233302403403,10.673805504059303,10.977377705715202,11.280949907371102,11.584522109027002,11.888094310682902,12.191666512338802,12.495238713994702,12.798810915650602,null,0,0,0,0,0,4.1438491239961552E-2,0.18876147643392063,0.32912365824493783,0.46294562902243541,null,0.18876147643392063,0.32912365824493783,0.46294562902243541]
["2013-03-12T22:00:00","2013-03-12T22:00:00",null,10.263105802511365,10.566678004167265,10.870250205823165,11.173822407479065,11.477394609134965,11.780966810790865,12.084539012446765,12.388111214102665,12.691683415758565,null,0,0,0,0,0,3.0387427258885893E-2,0.17972925573007287,0.32201564753969791,0.45766719503718328,null,0.17972925573007287,0.32201564753969791,0.45766719503718328]
["2013-03-12T23:00:00","2013-03-12T23:00:00",null,10.20372440275775,10.50729660441365,10.81086880606955,11.11444100772545,11.41801320938135,11.72158541103725,12.02515761269315,12.32872981434905,12.63230201600495,null,0,0,0,0,0,2.2038669122849665E-2,0.17334676682758673,0.31749427978340627,0.45492282995720162,null,0.17334676682758673,0.31749427978340627,0.45492282995720162]
["2013-03-13","2013-03-13",null,10.082860630932121,10.386432832588021,10.690005034243921,10.993577235899821,11.297149437555721,11.600721639211621,11.904293840867521,12.20786604252342,12.51143824417932,null,0,0,0,0,0,1.6097802187257135E-2,0.16933010989060204,0.3153071995664094,0.45447069318157246,null,0.16933010989060204,0.3153071995664094,0.45447069318157246]
["2013-03-13T01:00:00","2013-03-13T01:00:00",null,9.9892668823371746,10.292839083993075,10.596411285648974,10.899983487304874,11.203555688960774,11.507127890616674,11.810700092272574,12.114272293928474,12.417844495584374,null,0,0,0,0,0,1.1292534595105302E-2,0.16642802267958692,0.31422417426664651,0.45511209651444173,null,0.16642802267958692,0.31422417426664651,0.45511209651444173]
["2013-03-13T02:00:00","2013-03-13T02:00:00",null,9.9540077768888828,10.257579978544783,10.561152180200683,10.864724381856583,11.168296583512483,11.471868785168382,11.775440986824282,12.079013188480182,12.382585390136082,null,0,0,0,0,0,8.1906660181145126E-3,0.16518727524879062,0.31476042951216016,0.45734123596638088,null,0.16518727524879062,0.31476042951216016,0.45734123596638088]
["2013-03-13T03:00:00","2013-03-13T03:00:00",null,9.9243960926358561,10.227968294291756,10.531540495947656,10.835112697603556,11.138684899259456,11.442257100915356,11.745829302571256,12.049401504227156,12.352973705883056,null,0,0,0,0,0,6.4557225767467828E-3,0.16529242333614624,0.31661103584961908,0.46085318208405857,null,0.16529242333614624,0.31661103584961908,0.46085318208405857]
["2013-03-13T04:00:00","2013-03-13T04:00:00",null,9.994992630369298,10.298564832025198,10.602137033681096,10.905709235336996,11.209281436992896,11.512853638648796,11.816425840304696,12.119998041960596,12.423570243616496,null,0,0,0,0,0,4.6787199004368054E-3,0.16534499737982405,0.3183985533346646,0.46429152454058736,null,0.16534499737982405,0.3183985533346646,0.46429152454058736]
["2013-03-13T05:00:00","2013-03-13T05:00:00",null,9.9633022749930511,10.266874476648951,10.570446678304851,10.874018879960751,11.177591081616651,11.481163283272551,11.784735484928451,12.088307686584351,12.391879888240251,null,0,0,0,0,0,1.1036849303457264E-3,0.16364159836466302,0.31848267180454909,0.46607904202563288,null,0.16364159836466302,0.31848267180454909,0.46607904202563288]
["2013-03-13T06:00:00","2013-03-13T06:00:00",null,9.8982101611355056,10.201782362791405,10.505354564447307,10.808926766103207,11.112498967759107,11.416071169415007,11.719643371070907,12.023215572726807,12.326787774382707,null,0,0,0,0,0,0,0.15851037170170876,0.31522308109652486,0.46460696880265423,null,0.15851037170170876,0.31522308109652486,0.46460696880265423]
["2013-03-13T07:00:00","2013-03-13T07:00:00",null,10.00982126213599,10.31339346379189,10.61696566544779,10.92053786710369,11.22411006875959,11.52768227041549,11.831254472071389,12.134826673727289,12.438398875383189,null,0,0,0,0,0,0,0.15464092208702193,0.31318320820182582,0.4643125541580585,null,0.15464092208702193,0.31318320820182582,0.4643125541580585]
["2013-03-13T08:00:00","2013-03-13T08:00:00",null,10.186694650867622,10.490266852523522,10.793839054179422,11.097411255835322,11.400983457491222,11.704555659147122,12.008127860803022,12.311700062458922,12.615272264114822,null,0,0,0,0,0,0,0.15216994203416487,0.31247871601654315,0.46530094617920131,null,0.15216994203416487,0.31247871601654315,0.46530094617920131]
["2013-03-13T09:00:00","2013-03-13T09:00:00",null,10.349763021967508,10.653335223623408,10.956907425279308,11.260479626935208,11.564051828591108,11.867624030247008,12.171196231902908,12.474768433558808,12.778340635214708,null,0,0,0,0,0,0,0.14548252367834744,0.30764190399818464,0.46223062202841719,null,0.14548252367834744,0.30764190399818464,0.46223062202841719]
["2013-03-13T10:00:00","2013-03-13T10:00:00",null,10.562040500705706,10.865612702361606,11.169184904017506,11.472757105673406,11.776329307329306,12.079901508985206,12.383473710641105,12.687045912297005,12.990618113952905,null,0,0,0,0,0,0,0.13554602942324134,0.29960859012421526,0.45600585525696447,null,0.13554602942324134,0.29960859012421526,0.45600585525696447]
["2013-03-13T11:00:00","2013-03-13T11:00:00",null,10.76537428650272,11.068946488158621,11.372518689814521,11.676090891470421,11.979663093126321,12.283235294782221,12.586807496438121,12.890379698094021,13.193951899749921,null,0,0,0,0,0,0,0.119206016648178,0.28526639100890872,0.4435773513315302,null,0.119206016648178,0.28526639100890872,0.4435773513315302]
["2013-03-13T12:00:00","2013-03-13T12:00:00",null,10.946121992411751,11.249694194067651,11.553266395723551,11.856838597379451,12.16041079903535,12.46398300069125,12.76755520234715,13.07112740400305,13.37469960565895,null,0,0,0,0,0,0,9.8008162237285007E-2,0.26615046872765702,0.42644872790129973,null,9.8008162237285007E-2,0.26615046872765702,0.42644872790129973]
["2013-03-13T13:00:00","2013-03-13T13:00:00",null,11.021341763997677,11.324913965653577,11.628486167309477,11.932058368965377,12.235630570621277,12.539202772277177,12.842774973933077,13.146347175588977,13.449919377244877,null,0,0,0,0,0,0,7.3687409631930101E-2,0.24397473710435677,0.40631286917269849,null,7.3687409631930101E-2,0.24397473710435677,0.40631286917269849]
["2013-03-13T14:00:00","2013-03-13T14:00:00",null,11.32375207999759,11.62732428165349,11.93089648330939,12.234468684965289,12.538040886621189,12.841613088277089,13.145185289932989,13.448757491588889,13.752329693244789,null,0,0,0,0,0,0,4.2900049654204575E-2,0.21542703138730596,0.37989966962896676,null,4.2900049654204575E-2,0.21542703138730596,0.37989966962896676]
["2013-03-13T15:00:00","2013-03-13T15:00:00",null,11.429400204689127,11.732972406345027,12.036544608000927,12.340116809656827,12.643689011312727,12.947261212968627,13.250833414624527,13.554405616280427,13.857977817936327,null,0,0,0,0,0,0,6.4977818116889394E-3,0.18133802146661396,0.3480187695427428,null,6.4977818116889394E-3,0.18133802146661396,0.3480187695427428]
["2013-03-13T16:00:00","2013-03-13T16:00:00",null,11.5181797739417,11.8217519755976,12.1253241772535,12.4288963789094,12.7324685805653,13.0360407822212,13.3396129838771,13.643185185533,13.946757387188899,null,0,0,0,0,0,0,0,0.14616598624615906,0.31505484415675594,null,-3.0987511330589586E-2,0.14616598624615906,0.31505484415675594]
["2013-03-13T17:00:00","2013-03-13T17:00:00",null,11.919729533689459,12.223301735345359,12.526873937001259,12.830446138657159,13.134018340313059,13.437590541968959,13.741162743624859,14.044734945280759,14.348307146936659,null,0,0,0,0,0,0,0,9.6210129943504002E-2,0.26755945309822238,null,-5.2521469634132179E-2,9.6210129943504002E-2,0.26755945309822238]
["2013-03-13T18:00:00","2013-03-13T18:00:00",null,12.436403919257135,12.739976120913035,13.043548322568935,13.347120524224835,13.650692725880734,13.954264927536634,14.257837129192534,14.561409330848434,14.864981532504334,null,0,0,0,0,0,0,0,3.0082497805554595E-2,0.20417618604025467,null,-6.8977145305286702E-2,3.0082497805554595E-2,0.20417618604025467]
["2013-03-13T19:00:00","2013-03-13T19:00:00",null,11.790467403376045,12.094039605031945,12.397611806687845,12.701184008343745,13.004756209999645,13.308328411655545,13.611900613311445,13.915472814967345,14.219045016623244,null,6.0460150229481487E-3,9.5895055668325426E-3,1.2954244362212382E-2,1.6171775835294354E-2,1.9231585177342893E-2,2.2144187197093566E-2,2.4941126320753057E-2,5.7683870736404838E-2,0.23433265749384649,null,2.4941126320753057E-2,5.7683870736404838E-2,0.23433265749384649]
["2013-03-13T20:00:00","2013-03-13T20:00:00",null,11.236589782059937,11.540161983715837,11.843734185371737,12.147306387027637,12.450878588683537,12.754450790339437,13.058022991995337,13.361595193651237,13.665167395307137,null,3.2175314730819714E-2,3.8904792321579396E-2,4.5287281224065522E-2,5.1375355481955924E-2,5.7169015095250582E-2,6.267877487268507E-2,6.7957208857937185E-2,0.10306578523909042,0.28198577068341346,null,6.7957208857937185E-2,0.10306578523909042,0.28198577068341346]
["2013-03-13T21:00:00","2013-03-13T21:00:00",null,10.940882735937379,11.244454937593279,11.548027139249179,11.851599340905079,12.155171542560979,12.458743744216878,12.762315945872778,13.065888147528678,13.369460349184578,null,6.8209564267590672E-2,7.7946277156721089E-2,8.7167764417808963E-2,9.5947629712003241E-2,0.10430690265677502,0.1122560980608599,0.1198583047766712,0.15717499099229246,0.33820845299246349,null,0.1198583047766712,0.15717499099229246,0.33820845299246349]
["2013-03-13T22:00:00","2013-03-13T22:00:00",null,10.820692782750942,11.124264984406842,11.427837186062742,11.731409387718642,12.034981589374542,12.338553791030442,12.642125992686342,12.945698194342242,13.249270395998142,null,0.11104689505627025,0.12365415073020909,0.1356094882625431,0.14696548169695006,0.15778521988584332,0.16806870282922298,0.17788953418823786,0.2173196969597071,0.4003825170458416,null,0.17788953418823786,0.2173196969597071,0.4003825170458416]
["2013-03-13T23:00:00","2013-03-13T23:00:00",null,10.746140802344236,11.049713004000136,11.353285205656036,11.656857407311936,11.960429608967836,12.264001810623736,12.567574012279636,12.871146213935535,13.174718415591435,null,0.15868949343710165,0.17418832151332006,0.18888802412563574,0.20284117531772652,0.21613189355947685,0.22876017885088684,0.24081014966184083,0.28236430379789362,0.46745648196999157,null,0.24081014966184083,0.28236430379789362,0.46745648196999157]
["2013-03-14","2013-03-14",null,10.658808514202606,10.962380715858506,11.265952917514406,11.569525119170306,11.873097320826206,12.176669522482106,12.480241724138006,12.783813925793906,13.087386127449806,null,0.21049595607721561,0.22880223808582908,0.24615167249950637,0.26261786297939649,0.27829544280411939,0.29318441197367517,0.30738991857541942,0.35100497522364232,0.53805290782055482,null,0.30738991857541942,0.35100497522364232,0.53805290782055482]
["2013-03-14T01:00:00","2013-03-14T01:00:00",null,10.454824585485216,10.758396787141116,11.061968988797016,11.365541190452916,11.669113392108816,11.972685593764716,12.276257795420616,12.579829997076516,12.883402198732416,null,0.26507832822351796,0.2861605197383198,0.30613865633588755,0.32508634167737033,0.34311923865885907,0.36023734728035406,0.37656684524668183,0.42221125998086817,0.61118340257638848,null,0.37656684524668183,0.42221125998086817,0.61118340257638848]
["2013-03-14T02:00:00","2013-03-14T02:00:00",null,10.418761150574074,10.722333352229974,11.025905553885874,11.329477755541774,11.633049957197674,11.936622158853574,12.240194360509474,12.543766562165374,12.847338763821273,null,0.3214902770898081,0.34530631887585606,0.36786058361363649,0.3892582193905052,0.40960437429381757,0.42893059274978057,0.44734202284574964,0.49498425123969275,0.6858490594076142,null,0.44734202284574964,0.49498425123969275,0.6858490594076142]
["2013-03-14T03:00:00","2013-03-14T03:00:00",null,10.313601857611815,10.617174059267715,10.920746260923615,11.224318462579514,11.527890664235414,11.831462865891314,12.135035067547214,12.438607269203114,12.742179470859014,null,0.37950047688390365,0.40603985413246213,0.43114921739298417,0.45497577398776767,0.47761415719543254,0.49911694105965687,0.51959978847653165,0.56921880091276045,0.76195524503561196,null,0.51959978847653165,0.56921880091276045,0.76195524503561196]
["2013-03-14T04:00:00","2013-03-14T04:00:00",null,10.234583702357,10.5381559040129,10.8417281056688,11.1453003073247,11.4488725089806,11.7524447106365,12.056016912292399,12.359589113948299,12.663161315604199,null,0.43789972460121496,0.46716243731228402,0.49484792871301875,0.52110340612571704,0.54604453244647,0.56972388171895572,0.59228866126547175,0.64387394293525069,0.8384925378217678,null,0.59228866126547175,0.64387394293525069,0.8384925378217678]
["2013-03-14T05:00:00","2013-03-14T05:00:00",null,10.276277277996369,10.579849479652269,10.883421681308169,11.186993882964069,11.490566084619969,11.794138286275869,12.097710487931769,12.401282689587669,12.704854891243569,null,0.49422755499762056,0.52626617721487801,0.55656985599076769,0.58529631345632305,0.61258224212510637,0.63849073084953112,0.66316898695189519,0.71676259709016643,0.91329488716655582,null,0.66316898695189519,0.71676259709016643,0.91329488716655582]
["2013-03-14T06:00:00","2013-03-14T06:00:00",null,10.266893124527563,10.570465326183463,10.874037527839363,11.177609729495263,11.481181931151163,11.784754132807063,12.088326334462963,12.391898536118862,12.695470737774762,null,0.55437226096503522,0.58907112979238985,0.62187733304734327,0.65298013728713566,0.68251623502532921,0.71054871511433748,0.73725632930266505,0.79277414943954416,0.99113601623592129,null,0.73725632930266505,0.79277414943954416,0.99113601623592129]
["2013-03-14T07:00:00","2013-03-14T07:00:00",null,10.152585975560182,10.456158177216082,10.759730378871982,11.063302580527882,11.366874782183782,11.670446983839682,11.974019185495582,12.277591387151482,12.581163588807382,null,0.58773574908297344,0.62494765719812739,0.66013020722731786,0.69347266572778488,0.72513275483056194,0.75518407819679811,0.78380538757499796,0.84113175481439384,1,null,0.78380538757499796,0.84113175481439384,1]
["2013-03-14T08:00:00","2013-03-14T08:00:00",null,10.344084914586295,10.647657116242195,10.951229317898095,11.254801519553995,11.558373721209895,11.861945922865795,12.165518124521695,12.469090326177595,12.772662527833495,null,0.57906103187613478,0.6186072275305835,0.65599788739424203,0.6914222780243503,0.72506966597814859,0.75699262529931477,0.78740145216256019,0.84642070360838151,1,null,0.78740145216256019,0.84642070360838151,1]
["2013-03-14T09:00:00","2013-03-14T09:00:00",null,10.62262756312048,10.92619976477638,11.229771966432279,11.533344168088179,11.836916369744079,12.140488571399979,12.444060773055879,12.747632974711779,13.051205176367679,null,0.56204807134199541,0.60397061377068118,0.64360092789501444,0.68114930988970623,0.71681554112073242,0.75065219563177088,0.78288008440626855,0.84363427929345758,0.99887491546529483,null,0.78288008440626855,0.84363427929345758,0.99887491546529483]
["2013-03-14T10:00:00","2013-03-14T10:00:00",null,11.293136207523906,11.596708409179806,11.900280610835706,12.203852812491606,12.507425014147506,12.810997215803406,13.114569417459306,13.418141619115206,13.721713820771106,null,0.52343769366501181,0.56815717521735698,0.61044773595178747,0.65051967204301409,0.6885832796657485,0.72471216248113945,0.759127131472634,0.82196325848946428,0.97919119351232276,null,0.759127131472634,0.82196325848946428,0.97919119351232276]
["2013-03-14T11:00:00","2013-03-14T11:00:00",null,11.397822387435214,11.701394589091114,12.004966790747014,12.308538992402914,12.612111194058814,12.915683395714714,13.219255597370614,13.522827799026514,13.826400000682414,null,0.48350245008734732,0.53103990038082316,0.57599070772535077,0.61860722753058339,0.65907872635376152,0.69751035228224056,0.73412291629946758,0.7990514902546747,0.95828775374602548,null,0.73412291629946758,0.7990514902546747,0.95828775374602548]
["2013-03-14T12:00:00","2013-03-14T12:00:00",null,11.668759907405768,11.972332109061668,12.275904310717568,12.579476512373468,12.883048714029368,13.186620915685268,13.490193117341168,13.793765318997067,14.097337520652967,null,0.43812053558466174,0.48853904347168159,0.5362342158961908,0.5814584082678429,0.62441140195261358,0.66521937465532965,0.70409262255070248,0.7711872471054354,0.93249492791769195,null,0.70409262255070248,0.7711872471054354,0.93249492791769195]
["2013-03-14T13:00:00","2013-03-14T13:00:00",null,11.813949496897745,12.117521698553645,12.421093900209545,12.724666101865445,13.028238303521345,13.331810505177245,13.635382706833145,13.938954908489045,14.242527110144945,null,0.39291737283048073,0.44618539388483786,0.49658287215438651,0.54438319266625124,0.5897966515951435,0.63293891183715434,0.67406232880193739,0.74329145952998943,0.90664952804568055,null,0.67406232880193739,0.74329145952998943,0.90664952804568055]
["2013-03-14T14:00:00","2013-03-14T14:00:00",null,11.94546300129603,12.24903520295193,12.55260740460783,12.85617960626373,13.15975180791963,13.46332400957553,13.76689621123143,14.07046841288733,14.37404061454323,null,0.34525374483217819,0.40139230867134373,0.45452363721213851,0.50493163029042265,0.55282658408090746,0.59834519109715534,0.64173980674881981,0.71313498807639764,0.87857498872173001,null,0.64173980674881981,0.71313498807639764,0.87857498872173001]
["2013-03-14T15:00:00","2013-03-14T15:00:00",null,12.01917602260327,12.32274822425917,12.62632042591507,12.92989262757097,13.23346482922687,13.53703703088277,13.84060923253867,14.14418143419457,14.44775363585047,null,0.29460391115297602,0.35366559182062784,0.40959385948508209,0.4626620991734634,0.51309112186921868,0.56103864970338135,0.60674652327686951,0.68036032924765089,0.84792432125756678,null,0.60674652327686951,0.68036032924765089,0.84792432125756678]
["2013-03-14T16:00:00","2013-03-14T16:00:00",null,12.113183973113552,12.416756174769452,12.720328376425352,13.023900578081252,13.327472779737151,13.631044981393051,13.934617183048951,14.238189384704851,14.541761586360751,null,0.24008462785908707,0.30214302901637408,0.36093132465690114,0.41673341461652857,0.46975959506996767,0.5201991325744586,0.56828335292218368,0.64417887238858207,0.81391942980675924,null,0.56828335292218368,0.64417887238858207,0.81391942980675924]
["2013-03-14T17:00:00","2013-03-14T17:00:00",null,12.193931475205362,12.497503676861262,12.801075878517162,13.104648080173062,13.408220281828962,13.711792483484862,14.015364685140762,14.318936886796662,14.622509088452562,null,0.18794169133943511,0.2530599018387707,0.31477131430778399,0.37335982858233535,0.42903574083713603,0.48201986205563296,0.53253300322127284,0.61075229541823051,0.78272199228834682,null,0.53253300322127284,0.61075229541823051,0.78272199228834682]
["2013-03-14T18:00:00","2013-03-14T18:00:00",null,12.140059642899965,12.443631844555865,12.747204046211765,13.050776247867665,13.354348449523565,13.657920651179465,13.961492852835365,14.265065054491265,14.568637256147165,null,0.13656633585747918,0.20478641493380556,0.26945248865751176,0.33084845686445818,0.38921616015556276,0.44476589470553679,0.49773950111529819,0.57830359566028622,0.75253397640854836,null,0.49773950111529819,0.57830359566028622,0.75253397640854836]
["2013-03-14T19:00:00","2013-03-14T19:00:00",null,11.881260014426275,12.184832216082174,12.488404417738074,12.791976619393974,13.095548821049874,13.399121022705774,13.702693224361674,14.006265426017574,14.309837627673474,null,8.9659774088137106E-2,0.16092914769777647,0.22850782344123333,0.29267970115436814,0.35368662143809876,0.41175991008460766,0.46714140769481277,0.55000824535288884,0.72644673593561904,null,0.46714140769481277,0.55000824535288884,0.72644673593561904]
["2013-03-14T20:00:00","2013-03-14T20:00:00",null,11.742023415371509,12.045595617027409,12.349167818683309,12.652740020339209,12.956312221995109,13.259884423651009,13.563456625306909,13.867028826962809,14.170601028618709,null,4.7285094883822258E-2,0.12157221860056791,0.19203195193756875,0.25893767992194971,0.32256278758083523,0.38312808589767233,0.44088593028211448,0.52602396662707196,0.70463902261806344,null,0.44088593028211448,0.52602396662707196,0.70463902261806344]
["2013-03-14T21:00:00","2013-03-14T21:00:00",null,11.569310087701737,11.872882289357637,12.176454491013537,12.480026692669437,12.783598894325337,13.087171095981237,13.390743297637137,13.694315499293037,13.997887700948937,null,1.2417989116698676E-2,8.9575655618252759E-2,0.16277975403523529,0.23228263977730004,0.29838924229777819,0.36132037258011673,0.42133890084270476,0.50863247297845238,0.68930843148161403,null,0.42133890084270476,0.50863247297845238,0.68930843148161403]
["2013-03-14T22:00:00","2013-03-14T22:00:00",null,11.351864860490629,11.655437062146529,11.959009263802429,12.262581465458329,12.566153667114229,12.869725868770129,13.173298070426029,13.476870272081928,13.780442473737828,null,0,6.3909007494745929E-2,0.13974180809561895,0.21173670350801191,0.28021965280272704,0.345421981771947,0.40759604582532521,0.49695052047324301,0.67960326301869034,null,0.40759604582532521,0.49695052047324301,0.67960326301869034]
["2013-03-14T23:00:00","2013-03-14T23:00:00",null,11.228828222086221,11.532400423742121,11.835972625398021,12.139544827053921,12.443117028709821,12.746689230365721,13.050261432021621,13.353833633677521,13.657405835333421,null,0,4.3668000678789079E-2,0.12201384056746142,0.19639559756282696,0.2671497455444235,0.3345181251131692,0.39875309167871759,0.49007383556018547,0.67460872886929835,null,0.39875309167871759,0.49007383556018547,0.67460872886929835]
["2013-03-15","2013-03-15",null,11.142293455897992,11.445865657553892,11.749437859209792,12.053010060865692,12.356582262521592,12.660154464177491,12.963726665833391,13.267298867489291,13.570871069145191,null,0,2.4099941621908202E-2,0.10495882079837987,0.18173795418545352,0.25476330085393145,0.32428721621346734,0.39058308529118591,0.48388061321493947,0.67028714247898236,null,0.39058308529118591,0.48388061321493947,0.67028714247898236]
["2013-03-15T01:00:00","2013-03-15T01:00:00",null,11.190571145687764,11.494143347343664,11.797715548999564,12.101287750655464,12.404859952311364,12.708432153967264,13.012004355623164,13.315576557279064,13.619148758934964,null,0,5.5833634385835246E-3,8.8913222667912267E-2,0.16804767321175179,0.24331267414090443,0.31497109567375942,0.38329632283744142,0.47852857556853839,0.66679622597877575,null,0.38329632283744142,0.47852857556853839,0.66679622597877575]
["2013-03-15T02:00:00","2013-03-15T02:00:00",null,11.133972146072882,11.437544347728782,11.741116549384682,12.044688751040582,12.348260952696481,12.651833154352381,12.955405356008281,13.258977557664181,13.562549759320081,null,0,0,7.5454267486392917E-2,0.1568914611433205,0.23434354228947005,0.30808389595196628,0.37839642196666951,0.47552134027016768,0.66559753778292163,null,0.37839642196666951,0.47552134027016768,0.66559753778292163]
["2013-03-15T03:00:00","2013-03-15T03:00:00",null,11.036237286706218,11.339809488362118,11.643381690018018,11.946953891673918,12.250526093329817,12.554098294985717,12.857670496641617,13.161242698297517,13.464814899953417,null,0,0,6.3130911648314261E-2,0.14686033360959436,0.22648898016400523,0.30230075114740718,0.37459006120439609,0.47359713027155981,0.66547136007809493,null,0.37459006120439609,0.47359713027155981,0.66547136007809493]
["2013-03-15T04:00:00","2013-03-15T04:00:00",null,11.054662106888513,11.358234308544413,11.661806510200313,11.965378711856212,12.268950913512112,12.572523115168012,12.876095316823912,13.179667518479812,13.483239720135712,null,0,0,4.9945341493919514E-2,0.13597750656828769,0.21780374814843101,0.29570796607020983,0.3699845749782199,0.47088430961778482,0.6645776013355722,null,0.3699845749782199,0.47088430961778482,0.6645776013355722]
["2013-03-15T05:00:00","2013-03-15T05:00:00",null,11.095682645463771,11.399254847119671,11.702827048775571,12.006399250431471,12.309971452087371,12.613543653743271,12.917115855399171,13.220688057055071,13.524260258710971,null,0,0,3.4961739045743664E-2,0.12333870646814217,0.20739408750022464,0.28742229678658698,0.36371774897182496,0.46655220841873329,0.66208559166524406,null,0.36371774897182496,0.46655220841873329,0.66208559166524406]
["2013-03-15T06:00:00","2013-03-15T06:00:00",null,11.099172086989947,11.402744288645847,11.706316490301747,12.009888691957647,12.313460893613547,12.617033095269447,12.920605296925347,13.224177498581247,13.527749700237147,null,0,0,1.9778355231592139E-2,0.11051063981075654,0.19679516029477814,0.27894736094572403,0.35727217121692545,0.4620413554711772,0.65941483024641134,null,0.35727217121692545,0.4620413554711772,0.65941483024641134]
["2013-03-15T07:00:00","2013-03-15T07:00:00",null,11.006217869550911,11.309790071206811,11.613362272862711,11.916934474518611,12.22050667617451,12.52407887783041,12.82765107948631,13.13122328114221,13.43479548279811,null,0,0,5.6149078647901272E-3,9.8691994791984858E-2,0.18720565472794559,0.27147133193473943,0.35181498548316875,0.45850837973602837,0.65772194603998591,null,0.35181498548316875,0.45850837973602837,0.65772194603998591]
["2013-03-15T08:00:00","2013-03-15T08:00:00",null,11.208764118832676,11.512336320488576,11.815908522144476,12.119480723800375,12.423052925456275,12.726625127112175,13.030197328768075,13.333769530423975,13.637341732079875,null,0,0,0,8.735703097504903E-2,0.1780472563192711,0.26439486565570619,0.34671530324642119,0.45529084826294641,0.65631296166942055,null,0.34671530324642119,0.45529084826294641,0.65631296166942055]
["2013-03-15T09:00:00","2013-03-15T09:00:00",null,11.447051157450836,11.750623359106736,12.054195560762636,12.357767762418536,12.661339964074436,12.964912165730336,13.268484367386236,13.572056569042136,13.875628770698036,null,0,0,0,7.1889747325037334E-2,0.1648196269299341,0.25330174243968828,0.33765153811636672,0.44817232274897095,0.65105555730163955,null,0.33765153811636672,0.44817232274897095,0.65105555730163955]
["2013-03-15T10:00:00","2013-03-15T10:00:00",null,11.752675041277628,12.056247242933528,12.359819444589428,12.663391646245328,12.966963847901228,13.270536049557128,13.574108251213028,13.877680452868928,14.181252654524828,null,0,0,0,4.9650926849323707E-2,0.1449256088022508,0.23563686376394413,0.32212116561394166,0.43468182314124493,0.63952081211872802,null,0.32212116561394166,0.43468182314124493,0.63952081211872802]
["2013-03-15T11:00:00","2013-03-15T11:00:00",null,12.024954233731997,12.328526435387896,12.632098637043796,12.935670838699696,13.239243040355596,13.542815242011496,13.846387443667396,14.149959645323296,14.453531846979196,null,0,0,0,2.2428087032953695E-2,0.12011066018632449,0.21312465826110588,0.30180655513683591,0.41647017441125156,0.62332800666596255,null,0.30180655513683591,0.41647017441125156,0.62332800666596255]
["2013-03-15T12:00:00","2013-03-15T12:00:00",null,12.237278921336941,12.540851122992841,12.844423324648741,13.147995526304641,13.451567727960541,13.75513992961644,14.05871213127234,14.36228433292824,14.66585653458414,null,0,0,0,0,8.9975218350203806E-2,0.18537607800795777,0.27633968837930473,0.39317987306198171,0.60213015225506961,null,0.27633968837930473,0.39317987306198171,0.60213015225506961]
["2013-03-15T13:00:00","2013-03-15T13:00:00",null,12.197736365247115,12.501308566903015,12.804880768558915,13.108452970214815,13.412025171870715,13.715597373526615,14.019169575182515,14.322741776838415,14.626313978494315,null,0,0,0,0,8.6620994363559523E-2,0.18444026003049274,0.27771712832366335,0.39677593764954389,0.60785020820721536,null,0.27771712832366335,0.39677593764954389,0.60785020820721536]
["2013-03-15T14:00:00","2013-03-15T14:00:00",null,12.644670205116228,12.948242406772128,13.251814608428027,13.555386810083927,13.858959011739827,14.162531213395727,14.466103415051627,14.769675616707527,15.073247818363427,null,8.4854506495985315E-3,1.1776585783829438E-2,1.4931028404498036E-2,1.793826370286877E-2,0.10742980085123671,0.20800394640688719,0.30390951688394829,0.42550239511509924,0.63899507168195002,null,0.30390951688394829,0.42550239511509924,0.63899507168195002]
["2013-03-15T15:00:00","2013-03-15T15:00:00",null,12.501098679968138,12.804670881624038,13.108243083279937,13.411815284935837,13.715387486591737,14.018959688247637,14.322531889903537,14.626104091559437,14.929676293215337,null,2.295382746973184E-2,2.9451979268309156E-2,3.5666231231026295E-2,4.1586068549147703E-2,0.13386403001243957,0.23710893698692279,0.33556960598672547,0.45961243465326235,0.67546042837687903,null,0.33556960598672547,0.45961243465326235,0.67546042837687903]
["2013-03-15T16:00:00","2013-03-15T16:00:00",null,12.527468687680637,12.831040889336537,13.134613090992437,13.438185292648336,13.741757494304236,14.045329695960136,14.348901897616036,14.652474099271936,14.956046300927836,null,3.6002705110564276E-2,4.5728903190959125E-2,5.5013479304460371E-2,6.3866948259803574E-2,0.15895236365549051,0.26487854685754203,0.36591534399755737,0.49241863790821577,0.7106324635973339,null,0.36591534399755737,0.49241863790821577,0.7106324635973339]
["2013-03-15T17:00:00","2013-03-15T17:00:00",null,12.614810894750024,12.918383096405924,13.221955298061824,13.525527499717724,13.829099701373623,14.132671903029523,14.436244104685423,14.739816306341323,15.043388507997223,null,4.8736138489329853E-2,6.1669353234071113E-2,7.4024253498356465E-2,8.5800839282185903E-2,0.18368319380153234,0.29228013842241662,0.39588254889390906,0.52484630804868893,0.74541545089457295,null,0.39588254889390906,0.52484630804868893,0.74541545089457295]
["2013-03-15T18:00:00","2013-03-15T18:00:00",null,12.513948087114029,12.817520288769929,13.121092490425829,13.424664692081729,13.728236893737629,14.031809095393529,14.335381297049429,14.638953498705328,14.942525700361228,null,5.9293006459834097E-2,7.5517356338806269E-2,9.1005669606289086E-2,0.10576846107101814,0.20651084356643742,0.31784163845856783,0.42406223630521522,0.55553903474779442,0.77851606879412216,null,0.42406223630521522,0.55553903474779442,0.77851606879412216]
["2013-03-15T19:00:00","2013-03-15T19:00:00",null,12.317837417202533,12.621409618858433,12.924981820514333,13.228554022170233,13.532126223826133,13.835698425482033,14.139270627137932,14.442842828793832,14.746415030449732,null,7.4455360656514494E-2,9.3907756817304205E-2,0.11247690904430668,0.13017333214625754,0.23371265376533631,0.34772472488503503,0.45651093606315957,0.5904376849411247,0.81577003614421828,null,0.45651093606315957,0.5904376849411247,0.81577003614421828]
["2013-03-15T20:00:00","2013-03-15T20:00:00",null,12.007570684855814,12.311142886511714,12.614715088167614,12.918287289823514,13.221859491479414,13.525431693135314,13.829003894791214,14.132576096447114,14.436148298103014,null,9.578990758096978E-2,0.1183967463624281,0.13996261907906574,0.16051907015708947,0.26679224204741436,0.38341198573353247,0.4946902065819852,0.63100381704292285,0.85861788174163345,null,0.4946902065819852,0.63100381704292285,0.85861788174163345]
["2013-03-15T21:00:00","2013-03-15T21:00:00",null,11.776720917664893,12.080293119320793,12.383865320976692,12.687437522632592,12.991009724288492,13.294581925944392,13.598154127600292,13.901726329256192,14.205298530912092,null,0.12354900264285346,0.14920513595762475,0.17367309588527752,0.19699494166075404,0.305907330543705,0.42504011351762239,0.53872622556651883,0.67733206433180904,0.9071437240562521,null,0.53872622556651883,0.67733206433180904,0.9071437240562521]
["2013-03-15T22:00:00","2013-03-15T22:00:00",null,11.559094651809122,11.862666853465022,12.166239055120922,12.469811256776822,12.773383458432722,13.076955660088622,13.380527861744522,13.684100063400422,13.987672265056322,null,0.16069782190559401,0.18922449800517371,0.2164263082040726,0.24234531173723295,0.35372868067304097,0.47521678080372426,0.59115306192203099,0.73190392166937579,0.96377648390598902,null,0.59115306192203099,0.73190392166937579,0.96377648390598902]
["2013-03-15T23:00:00","2013-03-15T23:00:00",null,11.508538403115189,11.812110604771089,12.115682806426989,12.419255008082889,12.722827209738789,13.026399411394689,13.329971613050589,13.633543814706488,13.937116016362388,null,0.20338794537197571,0.23465898655153711,0.26446846931685536,0.29286896771160836,0.40660765380418229,0.53034592300427585,0.64842722510463724,0.79122847255541662,1,null,0.64842722510463724,0.79122847255541662,1]
["2013-03-16","2013-03-16",null,11.491776082045913,11.795348283701813,12.098920485357713,12.402492687013613,12.706064888669513,13.009637090325413,13.313209291981313,13.616781493637212,13.920353695293112,null,0.25006318134913541,0.28397343952132287,0.31629596157444045,0.34708332155216604,0.46309320633162132,0.58899752613124068,0.70915024555250783,0.85392827704557284,1,null,0.70915024555250783,0.85392827704557284,1]
["2013-03-16T01:00:00","2013-03-16T01:00:00",null,11.380088621360752,11.683660823016652,11.987233024672552,12.290805226328452,12.594377427984352,12.897949629640252,13.201521831296152,13.505094032952051,13.808666234607951,null,0.29847336076766284,0.33500180631500526,0.36981633803845104,0.40296952998167807,0.52122958383054363,0.64927892461221759,0.77148203173691932,0.91821581765479887,1,null,0.77148203173691932,0.91821581765479887,1]
["2013-03-16T02:00:00","2013-03-16T02:00:00",null,11.419669889252038,11.723242090907938,12.026814292563838,12.330386494219738,12.633958695875638,12.937530897531538,13.241103099187438,13.544675300843338,13.848247502499238,null,0.34506447827493802,0.38425317043237767,0.42160177106109387,0.45715233939602906,0.57769410674051158,0.70793052773918241,0.83220505218478991,0.98092613695369058,1,null,0.83220505218478991,0.98092613695369058,1]
["2013-03-16T03:00:00","2013-03-16T03:00:00",null,11.302807451417088,11.606379653072988,11.909951854728888,12.213524056384788,12.517096258040688,12.820668459696588,13.124240661352488,13.427812863008388,13.731385064664288,null,0.39357980578082108,0.43539720012215122,0.47524832522993116,0.51317524033910333,0.63597769156173178,0.76836964835119281,0.89469456050023488,1,1,null,0.89469456050023488,1,1]
["2013-03-16T04:00:00","2013-03-16T04:00:00",null,11.299211759738213,11.602783961394113,11.906356163050013,12.209928364705913,12.513500566361813,12.817072768017713,13.120644969673613,13.424217171329513,13.727789372985413,null,0.4422738850352087,0.48671998156042934,0.52907363114727302,0.56936637822194669,0.69442951332272096,0.82897700590297219,0.95735230575544883,1,1,null,0.95735230575544883,1,1]
["2013-03-16T05:00:00","2013-03-16T05:00:00",null,11.370355014489256,11.673927216145156,11.977499417801056,12.281071619456956,12.584643821112856,12.888216022768756,13.191788224424656,13.495360426080556,13.798932627736455,null,0.47311381905661204,0.52016758814825204,0.56500273259668832,0.60766131163686343,0.73496410099831244,0.87165661456061838,1,1,1,null,1,1,1]
["2013-03-16T06:00:00","2013-03-16T06:00:00",null,11.355916166588408,11.659488368244308,11.963060569900207,12.266632771556107,12.570204973212007,12.873777174867907,13.177349376523807,13.480921578179707,13.784493779835607,null,0.44347257323106276,0.49320761855027107,0.54058734671271336,0.58567484657080326,0.71528037904534036,0.85417048763337877,0.98461683481987283,0.98661464847962954,0.98852834366950182,null,0.98461683481987283,0.98661464847962954,0.98852834366950182]
["2013-03-16T07:00:00","2013-03-16T07:00:00",null,11.428293425114873,11.731865626770773,12.035437828426673,12.339010030082573,12.642582231738473,12.946154433394373,13.249726635050273,13.553298836706173,13.856871038362073,null,0.41392596068413356,0.46633176742217458,0.51624556448988734,0.56374095554842096,0.69563871632731056,0.83671590513234584,0.96924418444848115,0.97323981176799468,0.97705668733900364,null,0.96924418444848115,0.97323981176799468,0.97705668733900364]
["2013-03-16T08:00:00","2013-03-16T08:00:00",null,11.536530086881811,11.840102288537711,12.143674490193611,12.447246691849511,12.750818893505411,13.054391095161311,13.357963296817211,13.661535498473111,13.96510770012901,null,0.38284418606181231,0.43794178383615717,0.49040016461787594,0.54032447649432436,0.67452498038630204,0.81781027902580539,0.95244152008905303,0.95844547587705897,0.9641865614466758,null,0.95244152008905303,0.95844547587705897,0.9641865614466758]
["2013-03-16T09:00:00","2013-03-16T09:00:00",null,11.752485610408414,12.056057812064314,12.359630013720214,12.663202215376113,12.966774417032013,13.270346618687913,13.573918820343813,13.877491021999713,14.181063223655613,null,0.34869208728870693,0.40650250571682678,0.46153701463875824,0.51391127695059258,0.65045658319060062,0.79597102128204311,0.93273676851860987,0.94078059720131479,0.94847743719574618,null,0.93273676851860987,0.94078059720131479,0.94847743719574618]
["2013-03-16T10:00:00","2013-03-16T10:00:00",null,11.987716550444498,12.291288752100398,12.594860953756298,12.898433155412198,13.202005357068098,13.505577558723997,13.809149760379897,14.112721962035797,14.416294163691697,null,0.31296276720526728,0.37352806552210438,0.43118076181919074,0.48604703380135328,0.62497920162433385,0.77276483840265775,0.9117071510474859,0.92183291185983207,0.93151705070528468,null,0.9117071510474859,0.92183291185983207,0.93151705070528468]
["2013-03-16T11:00:00","2013-03-16T11:00:00",null,12.324520619453272,12.628092821109172,12.931665022765072,13.235237224420972,13.538809426076872,13.842381627732772,14.145953829388672,14.449526031044572,14.753098232700472,null,0.27160802444830195,0.33504386554994747,0.39541989730954441,0.45289384185812631,0.59431801935143502,0.74448000290399596,0.88569351423570553,0.89800635526504857,0.90978294104887802,null,0.88569351423570553,0.89800635526504857,0.90978294104887802]
["2013-03-16T12:00:00","2013-03-16T12:00:00",null,12.454302890674224,12.757875092330124,13.061447293986024,13.365019495641924,13.668591697297824,13.972163898953724,14.275736100609624,14.579308302265524,14.882880503921424,null,0.22561625103895377,0.29194366454287884,0.35507457619119304,0.41517722292366543,0.55910392489603788,0.71167379964904254,0.85519005409384019,0.86970049014891571,0.88359055248859308,null,0.85519005409384019,0.86970049014891571,0.88359055248859308]
["2013-03-16T13:00:00","2013-03-16T13:00:00",null,12.654502230066823,12.958074431722723,13.261646633378623,13.565218835034523,13.868791036690423,14.172363238346323,14.475935440002223,14.779507641658123,15.083079843314023,null,0.17384133282504649,0.24312340758366449,0.30908280278184486,0.3718772405506211,0.51838007066320624,0.67342092546906795,0.81929249707063156,0.83607413181258838,0.85214075956052715,null,0.81929249707063156,0.83607413181258838,0.85214075956052715]
["2013-03-16T14:00:00","2013-03-16T14:00:00",null,12.945843645745921,13.249415847401821,13.552988049057721,13.856560250713621,14.16013245236952,14.46370465402542,14.76727685568132,15.07084905733722,15.37442125899312,null,0.11597834035324882,0.18827816521897311,0.25710810320196192,0.32265742085945537,0.47178895315593106,0.62935336205832759,0.77764333966907051,0.7967487471415865,0.81504451434146441,null,0.77764333966907051,0.7967487471415865,0.81504451434146441]
["2013-03-16T15:00:00","2013-03-16T15:00:00",null,13.03794904724181,13.34152124889771,13.64509345055361,13.94866565220951,14.25223785386541,14.555810055521309,14.859382257177209,15.162954458833109,15.466526660489009,null,5.4698035042393497E-2,0.13006818405890189,0.20183175367911249,0.270188525269001,0.422001333793045,0.58214187083565427,0.73290282849925426,0.75437406793727169,0.7749410338240309,null,0.73290282849925426,0.75437406793727169,0.7749410338240309]
["2013-03-16T16:00:00","2013-03-16T16:00:00",null,13.160048791019774,13.463620992675674,13.767193194331574,14.070765395987474,14.374337597643374,14.677909799299274,14.981482000955173,15.285054202611073,15.588626404266973,null,0,6.4655558914970698E-2,0.13947893787722984,0.21076934110434015,0.36540011836951475,0.52823244644842793,0.6815695322522406,0.70552226655185069,0.72847609402158242,null,0.6815695322522406,0.70552226655185069,0.72847609402158242]
["2013-03-16T17:00:00","2013-03-16T17:00:00",null,13.115570796528225,13.419142998184125,13.722715199840025,14.026287401495924,14.329859603151824,14.633431804807724,14.937004006463624,15.240576208119524,15.544148409775424,null,0,8.2015508137381343E-4,7.8682313768210374E-2,0.15288531901507135,0.31029200578643434,0.47579509528418024,0.63169779441947005,0.65811099396320161,0.68343065339843478,null,0.63169779441947005,0.65811099396320161,0.68343065339843478]
["2013-03-16T18:00:00","2013-03-16T18:00:00",null,12.992578331530453,13.296150533186353,13.599722734842253,13.903294936498153,14.206867138154053,14.510439339809952,14.814011541465852,15.117583743121752,15.421155944777652,null,0,0,1.6771119933221335E-2,9.3939301243510798E-2,0.25417447156473993,0.42239038171626087,0.58090075341796998,0.6098059626320298,0.63753351326770669,null,0.58090075341796998,0.6098059626320298,0.63753351326770669]
["2013-03-16T19:00:00","2013-03-16T19:00:00",null,12.69634349870009,12.99991570035599,13.30348790201189,13.60706010366779,13.91063230532369,14.214204506979589,14.517776708635489,14.821348910291389,15.124921111947289,null,0,0,0,4.2763727127530557E-2,0.20572223291127026,0.37654581562921058,0.53755871180998338,0.56885078260701583,0.59888107635578081,null,0.53755871180998338,0.56885078260701583,0.59888107635578081]
["2013-03-16T20:00:00","2013-03-16T20:00:00",null,12.536854554898445,12.840426756554345,13.143998958210245,13.447571159866145,13.751143361522045,14.054715563177945,14.358287764833845,14.661859966489745,14.965432168145645,null,0,0,0,0,0.16402050146603137,0.33735712347177099,0.50076739604425191,0.53437272476310804,0.56661112834634109,null,0.50076739604425191,0.53437272476310804,0.56661112834634109]
["2013-03-16T21:00:00","2013-03-16T21:00:00",null,12.314652170685662,12.618224372341562,12.921796573997462,13.225368775653362,13.528940977309261,13.832513178965161,14.136085380621061,14.439657582276961,14.743229783932861,null,0,0,0,0,0.13038362832096853,0.30615968595335852,0.47189373125639866,0.50772819942719394,0.54211162399248158,null,0.47189373125639866,0.50772819942719394,0.54211162399248158]
["2013-03-16T22:00:00","2013-03-16T22:00:00",null,12.078194098618539,12.381766300274439,12.685338501930339,12.988910703586239,13.292482905242139,13.596055106898039,13.899627308553939,14.203199510209839,14.506771711865738,null,0,0,0,0,0.10343417353172313,0.28154451870340791,0.44951821826712274,0.48748719261123707,0.5239210048799593,null,0.44951821826712274,0.48748719261123707,0.5239210048799593]
["2013-03-16T23:00:00","2013-03-16T23:00:00",null,12.118805912309295,12.422378113965195,12.725950315621095,13.029522517276995,13.333094718932895,13.636666920588794,13.940239122244694,14.243811323900594,14.547383525556494,null,0,0,0,0,8.0606523766818039E-2,0.2609565231991775,0.43107524374494699,0.4710946057924959,0.50949468729476821,null,0.43107524374494699,0.4710946057924959,0.50949468729476821]
["2013-03-17","2013-03-17",null,12.133249996047072,12.436822197702972,12.740394399358872,13.043966601014771,13.347538802670671,13.651111004326571,13.954683205982471,14.258255407638371,14.561827609294271,null,0,0,0,0,5.7211074330192596E-2,0.23981124283196231,0.412085499168522,0.45416576372824108,0.49454262927279907,null,0.412085499168522,0.45416576372824108,0.49454262927279907]
["2013-03-17T01:00:00","2013-03-17T01:00:00",null,12.217335723771162,12.520907925427062,12.824480127082962,13.128052328738862,13.431624530394762,13.735196732050662,14.038768933706562,14.342341135362462,14.645913337018362,null,0,0,0,0,3.34160621616158E-2,0.21826639973279577,0.39268567705141011,0.43682684412329936,0.47916997890140745,null,0.39268567705141011,0.43682684412329936,0.47916997890140745]
["2013-03-17T02:00:00","2013-03-17T02:00:00",null,12.231692946726325,12.535265148382225,12.838837350038125,13.142409551694024,13.445981753349924,13.749553955005824,14.053126156661724,14.356698358317624,14.660270559973524,null,0,0,0,0,9.0953095562609013E-3,0.19620633100558671,0.37278114411499125,0.41899372850778621,0.46331364732817998,null,0.37278114411499125,0.41899372850778621,0.46331364732817998]
["2013-03-17T03:00:00","2013-03-17T03:00:00",null,12.160802631456063,12.464374833111963,12.767947034767863,13.071519236423763,13.375091438079663,13.678663639735563,13.982235841391462,14.285808043047362,14.589380244703262,null,0,0,0,0,0,0.17397802533860865,0.35271888904753895,0.40101340556997522,0.44732062324139016,null,0.35271888904753895,0.40101340556997522,0.44732062324139016]
["2013-03-17T04:00:00","2013-03-17T04:00:00",null,12.16471034403896,12.46828254569486,12.77185474735076,13.07542694900666,13.37899915066256,13.68257135231846,13.98614355397436,14.28971575563026,14.59328795728616,null,0,0,0,0,0,0.15164457158427497,0.33256200070146658,0.38293844935354415,0.43123296587598031,null,0.33256200070146658,0.38293844935354415,0.43123296587598031]
["2013-03-17T05:00:00","2013-03-17T05:00:00",null,12.285618981953368,12.589191183609268,12.892763385265168,13.196335586921068,13.499907788576968,13.803479990232868,14.107052191888767,14.410624393544667,14.714196595200567,null,0,0,0,0,0,0.1247687204561785,0.30793631864278037,0.36046830308564815,0.41083423692899002,null,0.30793631864278037,0.36046830308564815,0.41083423692899002]
["2013-03-17T06:00:00","2013-03-17T06:00:00",null,12.339259492213396,12.642831693869296,12.946403895525195,13.249976097181095,13.553548298836995,13.857120500492895,14.160692702148795,14.464264903804695,14.767837105460595,null,0,0,0,0,0,9.5895055668325249E-2,0.28135488215927962,0.33607394681914432,0.38854284240959858,null,0.28135488215927962,0.33607394681914432,0.38854284240959858]
["2013-03-17T07:00:00","2013-03-17T07:00:00",null,12.312107227650776,12.615679429306676,12.919251630962576,13.222823832618475,13.526396034274375,13.829968235930275,14.133540437586175,14.437112639242075,14.740684840897975,null,0,0,0,0,0,9.1552439660538137E-2,0.27928346483837391,0.3361685800977644,0.39072992262659545,null,0.27928346483837391,0.3361685800977644,0.39072992262659545]
["2013-03-17T08:00:00","2013-03-17T08:00:00",null,12.03327820746501,12.33685040912091,12.64042261077681,12.94399481243271,13.247567014088609,13.551139215744509,13.854711417400409,14.158283619056309,14.461855820712209,null,2.5540470418680093E-2,2.8631824186935318E-2,3.1586485441628238E-2,3.4393939374023297E-2,3.7075215601591605E-2,0.13118275378487132,0.32136372939809305,0.38059364700551385,0.43740515860375517,null,0.32136372939809305,0.38059364700551385,0.43740515860375517]
["2013-03-17T09:00:00","2013-03-17T09:00:00",null,11.696884110274187,12.000456311930087,12.304028513585987,12.607600715241887,12.911172916897787,13.214745118553687,13.518317320209587,13.821889521865486,14.125461723521386,null,6.195325306993129E-2,6.7957208857937185E-2,7.367726481008291E-2,7.9113420926368472E-2,8.4297221633000546E-2,0.18080213620798838,0.37326482531682709,0.43468182314124476,0.49357526686912734,null,0.37326482531682709,0.43468182314124476,0.49357526686912734]
["2013-03-17T10:00:00","2013-03-17T10:00:00",null,11.605442242417709,11.909014444073609,12.212586645729509,12.516158847385409,12.819731049041309,13.123303250697209,13.426875452353109,13.730447654009009,14.034019855664909,null,0.10075289730415507,0.10965894030317606,0.11815490576151016,0.12621976406168622,0.13390608924738207,0.23280838021407801,0.42755278281853371,0.49115686085994825,0.55213223671747214,null,0.42755278281853371,0.49115686085994825,0.55213223671747214]
["2013-03-17T11:00:00","2013-03-17T11:00:00",null,11.802830849709244,12.106403051365143,12.409975253021043,12.713547454676943,13.017119656332843,13.320691857988743,13.624264059644643,13.927836261300543,14.231408462956443,null,0.14329581344823891,0.15503033999712609,0.16622861130049962,0.1768590829321528,0.1869953585532346,0.28823193705922528,0.48520547911562012,0.55094406333035373,0.6139698268913123,null,0.48520547911562012,0.55094406333035373,0.6139698268913123]
["2013-03-17T12:00:00","2013-03-17T12:00:00",null,12.021864577445003,12.325436779100903,12.629008980756803,12.932581182412703,13.236153384068603,13.539725585724502,13.843297787380402,14.146869989036302,14.450442190692202,null,0.17981374418684573,0.19448190237295471,0.20847711279998773,0.22176783104173808,0.23444869037682589,0.33811418970073137,0.53740098967894989,0.6053581985368871,0.67051846827116468,null,0.53740098967894989,0.6053581985368871,0.67051846827116468]
["2013-03-17T13:00:00","2013-03-17T13:00:00",null,11.841834557855901,12.1454067595118,12.4489789611677,12.7525511628236,13.0561233644795,13.3596955661354,13.6632677677913,13.9668399694472,14.2704121711031,null,0.21121096307123385,0.22899150464306919,0.24594137632479512,0.26203954849894051,0.27740168406159665,0.38363279671697925,0.58535903232184816,0.65566104352781573,0.72306096752276794,null,0.58535903232184816,0.65566104352781573,0.72306096752276794]
["2013-03-17T14:00:00","2013-03-17T14:00:00",null,11.87921038886677,12.18278259052267,12.48635479217857,12.78992699383447,13.09349919549037,13.39707139714627,13.70064359880217,14.00421580045807,14.30778800211397,null,0.24416437364848514,0.26500472456236901,0.28485668345511006,0.30372025032670824,0.32172160288199048,0.43047626963390795,0.63461039643922057,0.70722566556701172,0.77682318458769639,null,0.63461039643922057,0.70722566556701172,0.77682318458769639]
["2013-03-17T15:00:00","2013-03-17T15:00:00",null,12.030778739794197,12.334350941450097,12.637923143105997,12.941495344761897,13.245067546417797,13.548639748073697,13.852211949729597,14.155784151385497,14.459356353041397,null,0.27717035826941427,0.30102845929040439,0.32375096096795386,0.34535889291953376,0.36596791804123535,0.47722510927221662,0.68374609766050176,0.75864308028390992,0.83042767952159147,null,0.68374609766050176,0.75864308028390992,0.83042767952159147]
["2013-03-17T16:00:00","2013-03-17T16:00:00",null,12.2645220206915,12.568094222347399,12.871666424003299,13.175238625659199,13.478810827315099,13.782383028970999,14.085955230626899,14.389527432282799,14.693099633938699,null,0.30684314852117023,0.33374002926673779,0.35936461815530235,0.38373794480433504,0.40698618691866273,0.52076693224617887,0.72970632664364321,0.80691656718887506,0.88090927626102467,null,0.72970632664364321,0.80691656718887506,0.88090927626102467]
["2013-03-17T17:00:00","2013-03-17T17:00:00",null,12.331189038584172,12.634761240240072,12.938333441895972,13.241905643551872,13.545477845207772,13.849050046863672,14.152622248519572,14.456194450175472,14.759766651831372,null,0.33386620697156455,0.36385444148538737,0.39242317681990929,0.41960395740133699,0.44553347574323299,0.56187983440222633,0.77327969404381214,0.85284525174580983,0.92908812988736977,null,0.77327969404381214,0.85284525174580983,0.92908812988736977]
["2013-03-17T18:00:00","2013-03-17T18:00:00",null,12.354777327635581,12.658349529291481,12.961921730947381,13.265493932603281,13.569066134259181,13.872638335915081,14.176210537570981,14.479782739226881,14.783354940882781,null,0.35704084542474318,0.3901309485155568,0.42166485991350722,0.45167412404480106,0.48029543342300096,0.59922843503094259,0.81309927472538546,0.89503066439288459,0.97353422641259035,null,0.81309927472538546,0.89503066439288459,0.97353422641259035]
["2013-03-17T19:00:00","2013-03-17T19:00:00",null,12.130587185401586,12.434159387057486,12.737731588713386,13.041303790369286,13.344875992025186,13.648448193681086,13.952020395336985,14.255592596992885,14.559164798648785,null,0.3829913933841102,0.41918336505191461,0.4536614228958224,0.48647814095951125,0.51778072656527951,0.63926882669596263,0.85558961682579149,0.93986580884132098,1,null,0.85558961682579149,0.93986580884132098,1]
["2013-03-17T20:00:00","2013-03-17T20:00:00",null,11.820108715544944,12.123680917200844,12.427253118856743,12.730825320512643,13.034397522168543,13.337969723824443,13.641541925480343,13.945114127136243,14.248686328792143,null,0.41524031177607884,0.45443951874225397,0.49177760456223463,0.527317658088434,0.56121740145188614,0.68518699644416192,0.9038841333482277,0.99042100924190302,1,null,0.9038841333482277,0.99042100924190302,1]
["2013-03-17T21:00:00","2013-03-17T21:00:00",null,11.452262849169035,11.755835050824935,12.059407252480835,12.362979454136735,12.666551655792635,12.970123857448534,13.273696059104434,13.577268260760334,13.880840462416234,null,0.42112860466799357,0.46318783961024157,0.50324926089273281,0.54136544255914487,0.57772565116671848,0.70404004850702462,0.92497683967176503,1,1,null,0.92497683967176503,1,1]
["2013-03-17T22:00:00","2013-03-17T22:00:00",null,11.173434275247139,11.477006476903039,11.780578678558939,12.084150880214839,12.387723081870739,12.691295283526639,12.994867485182539,13.298439686838439,13.602011888494339,null,0.39196052523554459,0.43679566968398098,0.47948579315036272,0.52010449929583846,0.55884105467764911,0.68741613589610107,0.91050846285163167,0.98759252569203682,0.98955879492558696,null,0.91050846285163167,0.98759252569203682,0.98955879492558696]
["2013-03-17T23:00:00","2013-03-17T23:00:00",null,11.17014266092729,11.47371486258319,11.77728706423909,12.08085926589499,12.38443146755089,12.68800366920679,12.99157587086269,13.29514807251859,13.598720274174489,null,0.36637799558192224,0.41389441625792694,0.45912912343831469,0.50215572078423409,0.54319501927913283,0.67395718071458166,0.89913143979975363,0.97820280149118,0.98207225110586682,null,0.89913143979975363,0.97820280149118,0.98207225110586682]
["2013-03-18","2013-03-18",null,11.030008106822837,11.333580308478737,11.637152510134637,11.940724711790537,12.244296913446437,12.547869115102337,12.851441316758237,13.155013518414137,13.458585720070037,null,0.34049053647496863,0.39073029261348385,0.43854112793408428,0.48401767571538967,0.52738074694084758,0.66036153301949996,0.88763875385178437,0.96872895882043863,0.97451210362499774,null,0.88763875385178437,0.96872895882043863,0.97451210362499774]
["2013-03-18T01:00:00","2013-03-18T01:00:00",null,11.219446893506641,11.523019095162541,11.826591296818441,12.13016349847434,12.43373570013024,12.73730790178614,13.04088010344204,13.34445230509794,13.64802450675384,null,0.3159069136512247,0.36878588678236596,0.41910976139076572,0.46696265594630809,0.51258641104991187,0.64772273291935445,0.87706085626380903,0.96011733046601333,0.96777211122550255,null,0.87706085626380903,0.96011733046601333,0.96777211122550255]
["2013-03-18T02:00:00","2013-03-18T02:00:00",null,11.22693037853255,11.53050258018845,11.83407478184435,12.13764698350025,12.44121918515615,12.74479138681205,13.04836358846795,13.35193579012385,13.65550799177975,null,0.29096578733047163,0.34649449226297452,0.39933140615917362,0.44957116229768856,0.4974661160881737,0.63476848855714207,0.86616751441376683,0.95119025784952116,0.96072718937267598,null,0.86616751441376683,0.95119025784952116,0.96072718937267598]
["2013-03-18T03:00:00","2013-03-18T03:00:00",null,11.214453516674171,11.518025718330071,11.821597919985971,12.125170121641871,12.428742323297771,12.73231452495367,13.03588672660957,13.33945892826547,13.64303112992137,null,0.26668709396005896,0.32485501588518795,0.38019445426045079,0.43280004236446717,0.48295568003309813,0.62241358829285676,0.85586300185291608,0.94284149971348497,0.9542500671915698,null,0.85586300185291608,0.94284149971348497,0.9542500671915698]
["2013-03-18T04:00:00","2013-03-18T04:00:00",null,11.221361575237227,11.524933776893127,11.828505978549027,12.132078180204926,12.435650381860826,12.739222583516726,13.042794785172626,13.346366986828526,13.649939188484426,null,0.24201935266643052,0.3028370063929211,0.36067896924724774,0.4156714189342367,0.46808774048101348,0.6097011845315623,0.8452115006037918,0.93415626769791071,0.94743647113092566,null,0.8452115006037918,0.93415626769791071,0.94743647113092566]
["2013-03-18T05:00:00","2013-03-18T05:00:00",null,11.644650940553911,11.948223142209811,12.251795343865711,12.55536754552161,12.85893974717751,13.16251194883341,13.46608415048931,13.76965635214521,14.07322855380111,null,0.21470187957144043,0.27813772067308595,0.33846117838900525,0.39582997485023119,0.45049646546641825,0.59426544530775727,0.83182614908342134,0.9227371854110904,0.93788902479903535,null,0.83182614908342134,0.9227371854110904,0.93788902479903535]
["2013-03-18T06:00:00","2013-03-18T06:00:00",null,12.069679688326833,12.373251889982733,12.676824091638633,12.980396293294532,13.283968494950432,13.587540696606332,13.891112898262232,14.194685099918132,14.498257301574032,null,0.17864660041719835,0.24482680659882555,0.30775793688116421,0.36761874301271835,0.42466158040314245,0.57069124412262728,0.81042851330655263,0.90341096695512746,0.92055010519409364,null,0.81042851330655263,0.90341096695512746,0.92055010519409364]
["2013-03-18T07:00:00","2013-03-18T07:00:00",null,12.230943461990051,12.534515663645951,12.838087865301851,13.141660066957751,13.445232268613651,13.748804470269551,14.052376671925451,14.355948873581351,14.659521075237251,null,0.1359354473333455,0.20498619629978115,0.27064066204463033,0.33310914074260389,0.39264398780335619,0.54104999829707801,0.78306898097662037,0.87822800003345647,0.89745958521079949,null,0.78306898097662037,0.87822800003345647,0.89745958521079949]
["2013-03-18T08:00:00","2013-03-18T08:00:00",null,11.649697337920571,11.953269539576471,12.256841741232371,12.560413942888271,12.863986144544171,13.167558346200071,13.471130547855971,13.774702749511871,14.078274951167771,null,9.5590126214994117E-2,0.16759553643612268,0.23604694130463136,0.30118618142143766,0.36325509738746042,0.51409002869909703,0.75842226930046308,0.85579991300050273,0.87714497473369368,null,0.75842226930046308,0.85579991300050273,0.87714497473369368]
["2013-03-18T09:00:00","2013-03-18T09:00:00",null,11.178773579176349,11.482345780832249,11.785917982488149,12.089490184144049,12.393062385799949,12.696634587455849,13.000206789111749,13.303778990767649,13.607351192423549,null,6.6232780225305016E-2,0.14101409995262196,0.2121047218137567,0.27974648640962674,0.34419174914988654,0.49729787914840451,0.74378565554056075,0.84322420175277057,0.86654604752824715,null,0.74378565554056075,0.84322420175277057,0.86654604752824715]
["2013-03-18T10:00:00","2013-03-18T10:00:00",null,11.287712445058309,11.591284646714209,11.894856848370109,12.198429050026009,12.502001251681909,12.805573453337809,13.109145654993709,13.412717856649609,13.716290058305509,null,3.8494714780892461E-2,0.1159888551619844,0.18964509035459626,0.25972629057711671,0.32649532604793569,0.48182008068965726,0.73041081882892589,0.83186820831836361,0.85711426409244806,null,0.73041081882892589,0.83186820831836361,0.85711426409244806]
["2013-03-18T11:00:00","2013-03-18T11:00:00",null,11.453551309714047,11.757123511369947,12.060695713025847,12.364267914681747,12.667840116337647,12.971412317993547,13.274984519649447,13.578556721305347,13.882128922961247,null,6.6348443121396067E-3,8.6904894199419908E-2,0.16320034638465783,0.23578407108624205,0.3049399681400336,0.46254643627737213,0.7133032250161665,0.81683203182650999,0.84406538645161566,null,0.7133032250161665,0.81683203182650999,0.84406538645161566]
["2013-03-18T12:00:00","2013-03-18T12:00:00",null,11.553215779001736,11.856787980657636,12.160360182313536,12.463932383969436,12.767504585625336,13.071076787281235,13.374648988937135,13.678221190593035,13.981793392248935,null,0,5.3562435698952811E-2,0.1325812233467013,0.20775159099723378,0.27937846810388239,0.43934025339798682,0.69233669639745588,0.79801052418985396,0.82730478132712981,null,0.69233669639745588,0.79801052418985396,0.82730478132712981]
["2013-03-18T13:00:00","2013-03-18T13:00:00",null,11.604466932828736,11.908039134484635,12.211611336140535,12.515183537796435,12.818755739452335,13.122327941108235,13.425900142764135,13.729472344420035,14.033044546075935,null,0,1.803289698148882E-2,9.9817079326690122E-2,0.1776161491611131,0.25174555074682547,0.41410471243263802,0.66938286892772403,0.77723326212838351,0.80861996620403609,null,0.66938286892772403,0.77723326212838351,0.80861996620403609]
["2013-03-18T14:00:00","2013-03-18T14:00:00",null,11.692441977641273,11.996014179297173,12.299586380953073,12.603158582608973,12.906730784264873,13.210302985920773,13.513875187576673,13.817447389232573,14.121019590888473,null,0,0,6.6485135634958586E-2,0.14691290765327206,0.2235448337180482,0.3882908569868333,0.64585072697753632,0.75587768558645707,0.7893568366004865,null,0.64585072697753632,0.75587768558645707,0.7893568366004865]
["2013-03-18T15:00:00","2013-03-18T15:00:00",null,11.756824260699222,12.060396462355122,12.363968664011022,12.667540865666922,12.971113067322822,13.274685268978722,13.578257470634622,13.881829672290522,14.185401873946422,null,0,0,3.0535004568072115E-2,0.1136440528139539,0.19282056259273606,0.36000602148817151,0.6198896642094337,0.7321457622702936,0.76774890464890655,null,0.6198896642094337,0.7321457622702936,0.76774890464890655]
["2013-03-18T16:00:00","2013-03-18T16:00:00",null,11.881868162334801,12.185440363990701,12.4890125656466,12.7925847673025,13.0961569689584,13.3997291706143,13.7033013722702,14.0068735739261,14.310445775582,null,0,0,0,7.8345839888672275E-2,0.16008796299893155,0.3297338871384885,0.59197284701651665,0.70646859933805117,0.74422727750745432,null,0.59197284701651665,0.70646859933805117,0.74422727750745432]
["2013-03-18T17:00:00","2013-03-18T17:00:00",null,11.8930542043095,12.1966264059654,12.5001986076213,12.8037708092772,13.1073430109331,13.410915212589,13.7144874142449,14.0180596159008,14.3216318175567,null,0,0,0,3.9661858550539685E-2,0.12405371346216058,0.29623370650698799,0.56089107239419533,0.67770008263755355,0.71767738545016024,null,0.56089107239419533,0.67770008263755355,0.71767738545016024]
["2013-03-18T18:00:00","2013-03-18T18:00:00",null,11.765807714507833,12.069379916163733,12.372952117819633,12.676524319475533,12.980096521131433,13.283668722787333,13.587240924443233,13.890813126099133,14.194385327755032,null,0,0,0,3.0598093420483724E-3,9.0080366437559761E-2,0.26477339877018652,0.53182814104910192,0.65091886478807715,0.69309376262641631,null,0.53182814104910192,0.65091886478807715,0.69309376262641631]
["2013-03-18T19:00:00","2013-03-18T19:00:00",null,11.527708433141139,11.831280634797039,12.134852836452939,12.438425038108839,12.741997239764739,13.045569441420639,13.349141643076539,13.652713844732439,13.956286046388339,null,0,0,0,0,5.971359880925671E-2,0.23687761119474054,0.50628767063042179,0.62762856343880735,0.67195899706793671,null,0.50628767063042179,0.62762856343880735,0.67195899706793671]
["2013-03-18T20:00:00","2013-03-18T20:00:00",null,11.172477091463394,11.476049293119294,11.779621494775194,12.083193696431094,12.386765898086994,12.690338099742894,12.993910301398794,13.297482503054693,13.601054704710593,null,0,0,0,0,3.4825046532181464E-2,0.214396950118109,0.48609923785814274,0.60963772569226082,0.65605009145103144,null,0.48609923785814274,0.60963772569226082,0.65605009145103144]
["2013-03-18T21:00:00","2013-03-18T21:00:00",null,10.992524380478365,11.296096582134265,11.599668783790165,11.903240985446065,12.206813187101965,12.510385388757864,12.813957590413764,13.117529792069664,13.421101993725564,null,0,0,0,0,1.4426317585191188E-2,0.19633250871041349,0.47025342109365081,0.59590538548361682,0.64434710932835093,null,0.47025342109365081,0.59590538548361682,0.64434710932835093]
["2013-03-18T22:00:00","2013-03-18T22:00:00",null,10.812038431237793,11.115610632893693,11.419182834549593,11.722755036205493,12.026327237861393,12.329899439517293,12.633471641173193,12.937043842829093,13.240616044484993,null,0,0,0,0,0,0.18294715719004306,0.45900257574659947,0.58670492784000006,0.63709189130081312,null,0.45900257574659947,0.58670492784000006,0.63709189130081312]
["2013-03-18T23:00:00","2013-03-18T23:00:00",null,10.675186770246485,10.978758971902387,11.282331173558287,11.585903375214187,11.889475576870087,12.193047778525987,12.496619980181887,12.800192181837787,13.103764383493687,null,0,0,0,0,0,0.1723692596020677,0.45051712509700093,0.58021729085015827,0.63250743469210813,null,0.45051712509700093,0.58021729085015827,0.63250743469210813]
["2013-03-19","2013-03-19",null,10.500670615856919,10.804242817512819,11.107815019168719,11.411387220824619,11.714959422480518,12.018531624136418,12.322103825792318,12.625676027448218,12.929248229104118,null,0,0,0,0,0,0.16323189081086431,0.44347220324417441,0.57515966784835293,0.62934247726270398,null,0.44347220324417441,0.57515966784835293,0.62934247726270398]
["2013-03-19T01:00:00","2013-03-19T01:00:00",null,10.494919000746108,10.798491202402008,11.102063404057908,11.405635605713808,11.709207807369708,12.012780009025608,12.316352210681508,12.619924412337408,12.923496613993308,null,0,0,0,0,0,0.15445202551667003,0.43677427007962144,0.57044903353482113,0.62652450852157338,null,0.43677427007962144,0.57044903353482113,0.62652450852157338]
["2013-03-19T02:00:00","2013-03-19T02:00:00",null,10.317145734916945,10.620717936572845,10.924290138228745,11.227862339884645,11.531434541540545,11.835006743196445,12.138578944852345,12.442151146508245,12.745723348164145,null,0,0,0,0,0,0.14727041115028119,0.43166407303413828,0.56731562053162365,0.62526273147330591,null,0.43166407303413828,0.56731562053162365,0.62526273147330591]
["2013-03-19T03:00:00","2013-03-19T03:00:00",null,10.274510847479384,10.578083049135284,10.881655250791184,11.185227452447084,11.488799654102984,11.792371855758883,12.095944057414783,12.399516259070683,12.703088460726583,null,0,0,0,0,0,0.14193940312135125,0.42836242309117184,0.56594869539600057,0.62573589786640615,null,0.42836242309117184,0.56594869539600057,0.62573589786640615]
["2013-03-19T04:00:00","2013-03-19T04:00:00",null,10.235100739709427,10.538672941365327,10.842245143021227,11.145817344677127,11.449389546333027,11.752961747988927,12.056533949644827,12.360106151300727,12.663678352956627,null,0,0,0,0,0,0.13842745700367354,0.42684829063325092,0.56632722851048078,0.62792297808340303,null,0.42684829063325092,0.56632722851048078,0.62792297808340303]
["2013-03-19T05:00:00","2013-03-19T05:00:00",null,10.122572561721848,10.426144763377748,10.729716965033647,11.033289166689547,11.336861368345447,11.640433570001347,11.944005771657247,12.247577973313147,12.551150174969047,null,0,0,0,0,0,0.13688178011954594,0.42725836817393781,0.56860894200609768,0.63197117944659442,null,0.42725836817393781,0.56860894200609768,0.63197117944659442]
["2013-03-19T06:00:00","2013-03-19T06:00:00",null,10.251719546155069,10.555291747810969,10.858863949466869,11.162436151122769,11.466008352778669,11.769580554434569,12.073152756090469,12.376724957746369,12.680297159402269,null,0,0,0,0,0,0.13267585662532114,0.42507128795694094,0.56832504217023749,0.63350634152198648,null,0.42507128795694094,0.56832504217023749,0.63350634152198648]
["2013-03-19T07:00:00","2013-03-19T07:00:00",null,10.326239965058951,10.629812166714853,10.933384368370753,11.236956570026653,11.540528771682553,11.844100973338453,12.147673174994353,12.451245376650252,12.754817578306152,null,0,0,0,0,0,0.12827015176512066,0.42267391156523282,0.56783084615966606,0.6348206926139317,null,0.42267391156523282,0.56783084615966606,0.6348206926139317]
["2013-03-19T08:00:00","2013-03-19T08:00:00",null,10.452250228230197,10.755822429886098,11.059394631541998,11.362966833197898,11.666539034853798,11.970111236509698,12.273683438165598,12.577255639821498,12.880827841477398,null,0,0,0,0,0,0.12453739466399615,0.42090742369765838,0.56793599424702168,0.63670284337759731,null,0.42090742369765838,0.56793599424702168,0.63670284337759731]
["2013-03-19T09:00:00","2013-03-19T09:00:00",null,10.78781093066342,11.09138313231932,11.39495533397522,11.69852753563112,12.00209973728702,12.30567193894292,12.60924414059882,12.91281634225472,13.21638854391062,null,0,0,0,0,0,0.11827056865760119,0.41661738173354906,0.56552810304657797,0.63608246966219917,null,0.41661738173354906,0.56552810304657797,0.63608246966219917]
["2013-03-19T10:00:00","2013-03-19T10:00:00",null,10.939983137930708,11.243555339586608,11.547127541242508,11.850699742898408,12.154271944554308,12.457844146210208,12.761416347866108,13.064988549522008,13.368560751177908,null,0,0,0,0,0,0.10549507604389335,0.40594485086695364,0.55686390064847491,0.62933196245396839,null,0.40594485086695364,0.55686390064847491,0.62933196245396839]
["2013-03-19T11:00:00","2013-03-19T11:00:00",null,10.955486876182224,11.259059077838124,11.562631279494024,11.866203481149924,12.169775682805824,12.473347884461724,12.776920086117624,13.080492287773524,13.384064489429424,null,0,0,0,0,0,8.8944767094118776E-2,0.39159213694291151,0.54459311885407402,0.61905899431932432,null,0.39159213694291151,0.54459311885407402,0.61905899431932432]
["2013-03-19T12:00:00","2013-03-19T12:00:00",null,11.231675998149404,11.535248199805304,11.838820401461204,12.142392603117104,12.445964804773004,12.749537006428904,13.053109208084804,13.356681409740704,13.660253611396604,null,0,0,0,0,0,6.9997081752636053E-2,0.37485256143589679,0.52995650509417169,0.60643070902791441,null,0.37485256143589679,0.52995650509417169,0.60643070902791441]
["2013-03-19T13:00:00","2013-03-19T13:00:00",null,11.510533834797327,11.814106036453227,12.117678238109127,12.421250439765027,12.724822641420927,13.028394843076827,13.331967044732727,13.635539246388626,13.939111448044526,null,0,0,0,0,0,3.9830095490308678E-2,0.34709346637401312,0.50450015314537611,0.58318246691358677,null,0.34709346637401312,0.50450015314537611,0.58318246691358677]
["2013-03-19T14:00:00","2013-03-19T14:00:00",null,11.563476495070203,11.867048696726103,12.170620898382003,12.474193100037903,12.777765301693803,13.081337503349703,13.384909705005603,13.688481906661503,13.992054108317403,null,0,0,0,0,0,1.0535838353032952E-2,0.32017555601097442,0.47986395627795436,0.56072283545442636,null,0.32017555601097442,0.47986395627795436,0.56072283545442636]
["2013-03-19T15:00:00","2013-03-19T15:00:00",null,11.61691849795643,11.92049069961233,12.22406290126823,12.52763510292413,12.83120730458003,13.13477950623593,13.43835170789183,13.741923909547729,14.045496111203629,null,0,0,0,0,0,0,0.29400419706816061,0.45594276640455084,0.53895718137181303,null,0.29400419706816061,0.45594276640455084,0.53895718137181303]
["2013-03-19T16:00:00","2013-03-19T16:00:00",null,11.570320650149315,11.873892851805214,12.177465053461114,12.481037255117014,12.784609456772914,13.088181658428814,13.391753860084714,13.695326061740614,13.998898263396514,null,0,0,0,0,0,0,0.26954675194924338,0.43370394592883721,0.51884235226068298,null,0.26954675194924338,0.43370394592883721,0.51884235226068298]
["2013-03-19T17:00:00","2013-03-19T17:00:00",null,11.47606589032185,11.77963809197775,12.08321029363365,12.38678249528955,12.69035469694545,12.99392689860135,13.29749910025725,13.60107130191315,13.90464350356905,null,0,0,0,0,0,0,0.24602512480779118,0.41239042862185304,0.49965282631828234,null,0.24602512480779118,0.41239042862185304,0.49965282631828234]
["2013-03-19T18:00:00","2013-03-19T18:00:00",null,11.333581142628445,11.637153344284345,11.940725545940245,12.244297747596145,12.547869949252044,12.851442150907944,13.155014352563844,13.458586554219744,13.762158755875644,null,0,0,0,0,0,0,0.22511117023275837,0.39365303945508157,0.48299736928115211,null,0.22511117023275837,0.39365303945508157,0.48299736928115211]
["2013-03-19T19:00:00","2013-03-19T19:00:00",null,11.174152511463792,11.477724713119692,11.781296914775591,12.084869116431491,12.388441318087391,12.692013519743291,12.995585721399191,13.299157923055091,13.602730124710991,null,0,0,0,0,0,0,0.20777225062781662,0.37843811121472337,0.46981179912675736,null,0.20777225062781662,0.37843811121472337,0.46981179912675736]
["2013-03-19T20:00:00","2013-03-19T20:00:00",null,10.977267806715561,11.280840008371461,11.584412210027361,11.887984411683261,12.191556613339161,12.495128814995061,12.798701016650961,13.102273218306861,13.405845419962761,null,0,0,0,0,0,0,0.19254680757872286,0.36531562991274202,0.45869764629326831,null,0.19254680757872286,0.36531562991274202,0.45869764629326831]
["2013-03-19T21:00:00","2013-03-19T21:00:00",null,10.865419626791738,11.168991828447638,11.472564030103538,11.776136231759438,12.079708433415338,12.383280635071237,12.686852836727137,12.990425038383037,13.293997240038937,null,0,0,0,0,0,0,0.17907733758846794,0.35392809205212838,0.4492974072836759,null,0.17907733758846794,0.35392809205212838,0.4492974072836759]
["2013-03-19T22:00:00","2013-03-19T22:00:00",null,10.687071183762443,10.990643385418343,11.294215587074243,11.597787788730143,11.901359990386043,12.204932192041943,12.508504393697843,12.812076595353743,13.115648797009642,null,0,0,0,0,0,0,0.1701502649719758,0.34700934790412857,0.44429235832554836,null,0.1701502649719758,0.34700934790412857,0.44429235832554836]
["2013-03-19T23:00:00","2013-03-19T23:00:00",null,10.527915370081237,10.831487571737139,11.135059773393039,11.438631975048938,11.742204176704838,12.045776378360738,12.349348580016638,12.652920781672538,12.956492983328438,null,0,0,0,0,0,0,0.16498749388281486,0.34378130162231102,0.44291491838118974,null,0.16498749388281486,0.34378130162231102,0.44291491838118974]
["2013-03-20","2013-03-20",null,10.505958597243007,10.809530798898907,11.113103000554807,11.416675202210707,11.720247403866606,12.023819605522506,12.327391807178406,12.630964008834306,12.934536210490206,null,0,0,0,0,0,0,0.16081311481479674,0.34153113255290074,0.44249432603176725,null,0.16081311481479674,0.34153113255290074,0.44249432603176725]
["2013-03-20T01:00:00","2013-03-20T01:00:00",null,10.389822223350841,10.693394425006741,10.99696662666264,11.30053882831854,11.60411102997444,11.90768323163034,12.21125543328624,12.51482763494214,12.81839983659804,null,0,0,0,0,0,0,0.15868912345021322,0.34129980676071836,0.44406103253336598,null,0.15868912345021322,0.34129980676071836,0.44406103253336598]
["2013-03-20T02:00:00","2013-03-20T02:00:00",null,10.329990648387529,10.633562850043429,10.937135051699329,11.240707253355229,11.544279455011129,11.847851656667029,12.151423858322929,12.454996059978829,12.758568261634728,null,0,0,0,0,0,0,0.15919383426952019,0.34364460910874867,0.4481512931314996,null,0.15919383426952019,0.34364460910874867,0.4481512931314996]
["2013-03-20T03:00:00","2013-03-20T03:00:00",null,10.248666864029305,10.552239065685205,10.855811267341103,11.159383468997003,11.462955670652903,11.766527872308803,12.070100073964703,12.373672275620603,12.677244477276503,null,6.026036886350581E-2,6.2794437768776246E-2,6.5181299351748823E-2,6.7441983229894656E-2,6.9576489403213745E-2,7.1605847489177199E-2,0.23272389175730523,0.41901475812525707,0.52525638558937571,null,0.23272389175730523,0.41901475812525707,0.52525638558937571]
["2013-03-20T04:00:00","2013-03-20T04:00:00",null,10.293103821833,10.5966760234889,10.9002482251448,11.2038204268007,11.5073926284566,11.8109648301125,12.1145370317684,12.4181092334243,12.7216814350802,null,0.12014220461253139,0.12536806455410571,0.13029950985108429,0.13495757012093823,0.13936327498113871,0.14355868366662794,0.30672711563819055,0.49496322162222139,0.6030659702325345,null,0.30672711563819055,0.49496322162222139,0.6030659702325345]
["2013-03-20T05:00:00","2013-03-20T05:00:00",null,10.274470791888426,10.578042993544326,10.881615195200226,11.185187396856126,11.488759598512026,11.792331800167926,12.095904001823826,12.399476203479725,12.703048405135625,null,0.18596490729714948,0.19375638057020095,0.20110623187635879,0.20805652045056522,0.21462827591029149,0.2208740722992153,0.38599825869559246,0.57608497101708223,0.68595420749496971,null,0.38599825869559246,0.57608497101708223,0.68595420749496971]
["2013-03-20T06:00:00","2013-03-20T06:00:00",null,10.225983941465749,10.529556143121649,10.833128344777549,11.136700546433449,11.440272748089349,11.743844949745249,12.047417151401149,12.350989353057049,12.654561554712949,null,0.25065201063832687,0.26105115647779775,0.27086147302807706,0.28013553433284272,0.288915399627037,0.29725364295433765,0.46435461339300044,0.65633399128689141,0.76800126005855995,null,0.46435461339300044,0.65633399128689141,0.76800126005855995]
["2013-03-20T07:00:00","2013-03-20T07:00:00",null,10.217482825525451,10.521055027181351,10.824627228837251,11.128199430493151,11.431771632149051,11.735343833804951,12.038916035460851,12.342488237116751,12.646060438772651,null,0.31563352862409999,0.32862983222125469,0.34089009920691998,0.35248793324224481,0.36345487875343602,0.37387505421037792,0.54295280869132634,0.73681433734888291,0.85026912360559703,null,0.54295280869132634,0.73681433734888291,0.85026912360559703]
["2013-03-20T08:00:00","2013-03-20T08:00:00",null,10.416923451287023,10.720495652942923,11.024067854598822,11.327640056254722,11.631212257910622,11.934784459566522,12.238356661222422,12.541928862878322,12.845501064534222,null,0.38130902398642025,0.39683939648884536,0.41148652505748323,0.42534504297095388,0.43845700946419974,0.45090654300710509,0.62191902229539697,0.81762064248167687,0.9328314017972299,null,0.62191902229539697,0.81762064248167687,0.9328314017972299]
["2013-03-20T09:00:00","2013-03-20T09:00:00",null,10.495890764921173,10.799462966577073,11.103035168232973,11.406607369888873,11.710179571544773,12.013751773200672,12.317323974856572,12.620896176512472,12.924468378168372,null,0.44306249569037587,0.46122157037669148,0.47833967899818641,0.49454299925968737,0.50988410520487237,0.52444711530362564,0.69746792306040994,0.89508323843656212,1,null,0.69746792306040994,0.89508323843656212,1]
["2013-03-20T10:00:00","2013-03-20T10:00:00",null,10.715839959815396,11.019412161471296,11.322984363127196,11.626556564783096,11.930128766438996,12.233700968094896,12.537273169750796,12.840845371406695,13.144417573062595,null,0.50120938799803372,0.52203922410318204,0.54169140162994744,0.56029209828315651,0.57790440291522294,0.594633463613502,0.76970465907372088,0.96928624368342309,1,null,0.76970465907372088,0.96928624368342309,1]
["2013-03-20T11:00:00","2013-03-20T11:00:00",null,11.005172486547185,11.308744688203085,11.612316889858985,11.915889091514885,12.219461293170784,12.523033494826684,12.826605696482584,13.130177898138484,13.433750099794384,null,0.55257422867125405,0.57619048909132631,0.59848188361071775,0.61959561955172615,0.63958427095802961,0.65858453034319009,0.83581126159419916,1,1,null,0.83581126159419916,1,1]
["2013-03-20T12:00:00","2013-03-20T12:00:00",null,11.268645936241837,11.572218137897737,11.875790339553637,12.179362541209537,12.482934742865437,12.786506944521337,13.090079146177237,13.393651347833137,13.697223549489037,null,0.59210990951696718,0.61875443485288129,0.64393740177455228,0.66778498798680674,0.69038131195952968,0.7118630662062827,0.89145562942279322,1,1,null,0.89145562942279322,1,1]
["2013-03-20T13:00:00","2013-03-20T13:00:00",null,11.184818341761382,11.488390543417282,11.791962745073182,12.095534946729082,12.399107148384982,12.702679350040881,13.006251551696781,13.309823753352681,13.613395955008581,null,0.55542374183859133,0.58503344323793394,0.61302386409200005,0.63954221172308723,0.66467260460108057,0.68857276485701291,0.87046807118661151,0.98121003678955065,0.9833129985366631,null,0.87046807118661151,0.98121003678955065,0.9833129985366631]
["2013-03-20T14:00:00","2013-03-20T14:00:00",null,11.357995493600377,11.661567695256277,11.965139896912177,12.268712098568077,12.572284300223977,12.875856501879877,13.179428703535777,13.483000905191677,13.786573106847577,null,0.50662451449684809,0.53943071775180151,0.57047043313918067,0.5998698383638118,0.6277551111305224,0.65427345876160969,0.83867128957027204,0.9518001167561837,0.95619530680764875,null,0.83867128957027204,0.9518001167561837,0.95619530680764875]
["2013-03-20T15:00:00","2013-03-20T15:00:00",null,11.261482543641566,11.565054745297466,11.868626946953366,12.172199148609266,12.475771350265166,12.779343551921066,13.082915753576966,13.386487955232866,13.690060156888766,null,0.46202069584059408,0.49794979729000943,0.53195468874081708,0.56416154789784323,0.59471758208338665,0.62379102823721544,0.81061777986379258,0.92607037978026352,0.93267367966619652,null,0.81061777986379258,0.92607037978026352,0.93267367966619652]
["2013-03-20T16:00:00","2013-03-20T16:00:00",null,11.235145191328229,11.538717392984129,11.842289594640029,12.145861796295929,12.449433997951829,12.753006199607729,13.056578401263629,13.360150602919528,13.663722804575428,null,0.41517722292366538,0.45429231141995602,0.49131495297786998,0.52639235491970449,0.55968223937649408,0.59135284328800664,0.78066108977617643,0.89847952165814882,0.90734350542222764,null,0.78066108977617643,0.89847952165814882,0.90734350542222764]
["2013-03-20T17:00:00","2013-03-20T17:00:00",null,11.195244429702283,11.498816631358183,11.802388833014083,12.105961034669983,12.409533236325883,12.713105437981783,13.016677639637683,13.320249841293583,13.623822042949483,null,0.37017384153546001,0.41244337265241926,0.45245221989123285,0.4903686201916691,0.52635029568476255,0.56059702773648779,0.75234470985130797,0.87250794408131072,0.88360106729732868,null,0.75234470985130797,0.87250794408131072,0.88360106729732868]
["2013-03-20T18:00:00","2013-03-20T18:00:00",null,11.153331548297373,11.456903749953273,11.760475951609173,12.064048153265073,12.367620354920973,12.671192556576873,12.974764758232773,13.278336959888673,13.581909161544573,null,0.32705261091092025,0.37243452541360589,0.41538751909837679,0.4561113733312081,0.49475329543439872,0.53153409639139437,0.72570018451539386,0.8481766766672203,0.86146739490897062,null,0.72570018451539386,0.8481766766672203,0.86146739490897062]
["2013-03-20T19:00:00","2013-03-20T19:00:00",null,10.774313116425638,11.077885318081538,11.381457519737438,11.685029721393338,11.988601923049238,12.292174124705138,12.595746326361038,12.899318528016938,13.202890729672838,null,0.28756950410888493,0.3360743168060325,0.38197145693676077,0.42549225029325155,0.4667944190065394,0.50609877406006987,0.70267275338451307,0.82743095903195651,0.84290875749070371,null,0.70267275338451307,0.82743095903195651,0.84290875749070371]
["2013-03-20T20:00:00","2013-03-20T20:00:00",null,10.645973433176586,10.949545634832486,11.253117836488386,11.556690038144286,11.860262239800186,12.163834441456086,12.467406643111985,12.770978844767885,13.074551046423785,null,0.25403777905117775,0.3055287974292249,0.35424390630108377,0.40044597588514286,0.44428221350370117,0.4860049745664109,0.6848711821952066,0.81181646805964691,0.82937619864803547,null,0.6848711821952066,0.81181646805964691,0.82937619864803547]
["2013-03-20T21:00:00","2013-03-20T21:00:00",null,10.547351844433397,10.850924046089297,11.154496247745197,11.458068449401097,11.761640651056997,12.065212852712897,12.368785054368796,12.672357256024696,12.975929457680596,null,0.22536389562930018,0.27972545679215577,0.33116390112652516,0.37995261365953253,0.42622828690474124,0.47027482069801013,0.67134913816127384,0.8003973857728266,0.81996544482970746,null,0.67134913816127384,0.8003973857728266,0.81996544482970746]
["2013-03-20T22:00:00","2013-03-20T22:00:00",null,10.433330597576767,10.736902799232666,11.040475000888566,11.344047202544466,11.647619404200366,11.951191605856266,12.254763807512166,12.558336009168066,12.861908210823966,null,0.20224183121979933,0.2593582722713722,0.31339387436342536,0.36464305214055426,0.41325301292505773,0.45951817136153023,0.66269545057190626,0.79374151184321584,0.81522326608996898,null,0.66269545057190626,0.79374151184321584,0.81522326608996898]
["2013-03-20T23:00:00","2013-03-20T23:00:00",null,10.442041300433832,10.745613502089732,11.049185703745632,11.352757905401532,11.656330107057432,11.959902308713332,12.263474510369232,12.567046712025132,12.870618913681032,null,0.18229523904843822,0.24207192671010827,0.29862056808996074,0.35225660745006221,0.40311673730397596,0.45152691672250311,0.65673355401884259,0.78971434009749564,0.81304670068170759,null,0.65673355401884259,0.78971434009749564,0.81304670068170759]
["2013-03-21","2013-03-21",null,10.392140630624684,10.695712832280584,10.999285033936484,11.302857235592384,11.606429437248284,11.910001638904184,12.213573840560084,12.517146042215984,12.820718243871884,null,0.16126562157731422,0.22374461508402371,0.28284835498661776,0.33890280035589848,0.39205515851416473,0.44263138853221767,0.64990944314946286,0.78485649846166594,0.81006049500080801,null,0.64990944314946286,0.78485649846166594,0.81006049500080801]
["2013-03-21T01:00:00","2013-03-21T01:00:00",null,10.345837971936106,10.649410173592006,10.952982375247906,11.256554576903806,11.560126778559706,11.863698980215606,12.167271181871506,12.470843383527406,12.774415585183306,null,0.14252823241054274,0.20765695771861387,0.26926322210027165,0.32768349943505382,0.3830755118539948,0.43578624804536681,0.64508314593983995,0.78195441125065079,0.80898798450978071,null,0.64508314593983995,0.78195441125065079,0.80898798450978071]
["2013-03-21T02:00:00","2013-03-21T02:00:00",null,10.330968111011801,10.634540312667699,10.938112514323599,11.241684715979499,11.545256917635399,11.848829119291299,12.152401320947199,12.455973522603099,12.759545724258999,null,0.12450585023778948,0.1922632777297511,0.25635103697300149,0.31712663146454956,0.37473726852669414,0.42956148127391408,0.64086670763687958,0.7796516681375627,0.80850430330794487,null,0.64086670763687958,0.7796516681375627,0.80850430330794487]
["2013-03-21T03:00:00","2013-03-21T03:00:00",null,10.30811798495769,10.61169018661359,10.91526238826949,11.21883458992539,11.52240679158129,11.825978993237189,12.129551194893089,12.433123396548989,12.736695598204889,null,0.10773473030456809,0.17808931555421353,0.24463754004158542,0.30773690726369268,0.36755565416030528,0.42446179903716652,0.63775432425115319,0.77843195032423751,0.80908261778840074,null,0.63775432425115319,0.77843195032423751,0.80908261778840074]
["2013-03-21T04:00:00","2013-03-21T04:00:00",null,10.214906817140008,10.518479018795908,10.822051220451808,11.125623422107708,11.429195623763608,11.732767825419508,12.036340027075408,12.339912228731308,12.643484430387208,null,9.1994061627431789E-2,0.16493528982602548,0.23393346474878329,0.29934608989271422,0.36136243181505928,0.42033999401282623,0.63560930326909859,0.77816908010584851,0.81059675024632172,null,0.63560930326909859,0.77816908010584851,0.81059675024632172]
["2013-03-21T05:00:00","2013-03-21T05:00:00",null,10.306894027012046,10.610466228667946,10.914038430323846,11.217610631979746,11.521182833635645,11.824755035291545,12.128327236947445,12.431899438603345,12.735471640259245,null,7.5212426885474845E-2,0.15076132765048791,0.22220945300863165,0.2899458508831218,0.35417030263993488,0.41522979696734308,0.63248640507463672,0.77692833267505224,0.8111540351093065,null,0.63248640507463672,0.77692833267505224,0.8111540351093065]
["2013-03-21T06:00:00","2013-03-21T06:00:00",null,10.367672521065476,10.671244722721376,10.974816924377276,11.278389126033176,11.581961327689076,11.885533529344976,12.189105731000875,12.492677932656775,12.796250134312675,null,5.5339438375262673E-2,0.1335591005591085,0.20753078001378711,0.27766455427998538,0.34414968991494427,0.40736472003314272,0.62666120103513534,0.77304836825162981,0.80912467702334301,null,0.62666120103513534,0.77304836825162981,0.80912467702334301]
["2013-03-21T07:00:00","2013-03-21T07:00:00",null,10.413785597449039,10.717357799104938,11.020930000760838,11.324502202416738,11.628074404072638,11.931646605728538,12.235218807384438,12.538791009040338,12.842363210696238,null,3.3184736369433546E-2,0.11413824882452549,0.1906860564194168,0.26325926631226543,0.33205765986904795,0.39747028501297887,0.61884869814461274,0.76722316421212844,0.80519213855624283,null,0.61884869814461274,0.76722316421212844,0.80519213855624283]
["2013-03-21T08:00:00","2013-03-21T08:00:00",null,10.51168746920067,10.81525967085657,11.11883187251247,11.422404074168369,11.725976275824269,12.029548477480169,12.333120679136069,12.636692880791969,12.940265082447869,null,9.7998017415436636E-3,9.3497679276617285E-2,0.17263212982045684,0.24765529014869142,0.31877745643603317,0.3863981914144321,0.60987956629317841,0.76025184602045082,0.800124000745702,null,0.60987956629317841,0.76025184602045082,0.800124000745702]
["2013-03-21T09:00:00","2013-03-21T09:00:00",null,10.561200419944527,10.864772621600428,11.168344823256328,11.471917024912228,11.775489226568128,12.079061428224028,12.382633629879928,12.686205831535828,12.989778033191728,null,0,7.3887560984794154E-2,0.15557711005137528,0.23300816158005355,0.3064225561717478,0.37621985655840806,0.60177264875806014,0.75411119771888258,0.79585498839906388,null,0.60177264875806014,0.75411119771888258,0.79585498839906388]
["2013-03-21T10:00:00","2013-03-21T10:00:00",null,10.992126523787061,11.295698725442961,11.599270927098861,11.90284312875476,12.20641533041066,12.50998753206656,12.81355973372246,13.11713193537836,13.42070413703426,null,0,5.0912703897591186E-2,0.13514683667817831,0.21498577940730029,0.29069240230334703,0.36267678290700422,0.59030099242756195,0.74462684023940562,0.78826329649198812,null,0.59030099242756195,0.74462684023940562,0.78826329649198812]
["2013-03-21T11:00:00","2013-03-21T11:00:00",null,11.314858564052489,11.618430765708389,11.922002967364289,12.225575169020189,12.529147370676089,12.832719572331989,13.136291773987889,13.439863975643789,13.743436177299689,null,0,2.3258756923063131E-2,0.11007953265259851,0.19238945543457756,0.27044088067865463,0.34465440073425097,0.57441311642812776,0.73077883713467051,0.77636053300333197,null,0.57441311642812776,0.73077883713467051,0.77636053300333197]
["2013-03-21T12:00:00","2013-03-21T12:00:00",null,11.543363938675842,11.846936140331742,12.150508341987642,12.454080543643542,12.757652745299442,13.061224946955342,13.364797148611242,13.668369350267142,13.971941551923042,null,0,0,8.45706066601251E-2,0.16930945026001898,0.24967413342591968,0.32609576331598406,0.55795744075697318,0.71634200474074394,0.76384791060801316,null,0.55795744075697318,0.71634200474074394,0.76384791060801316]
["2013-03-21T13:00:00","2013-03-21T13:00:00",null,11.766568060995954,12.070140262651854,12.373712464307754,12.677284665963654,12.980856867619554,13.284429069275454,13.588001270931354,13.891573472587254,14.195145674243154,null,0,0,5.2731765808843374E-2,0.14001519312274324,0.22279828229782322,0.30153317010971126,0.53560295738516839,0.69609048311605148,0.74561523226054871,null,0.53560295738516839,0.69609048311605148,0.74561523226054871]
["2013-03-21T14:00:00","2013-03-21T14:00:00",null,11.823074556056834,12.126646757712734,12.430218959368634,12.733791161024534,13.037363362680434,13.340935564336334,13.644507765992234,13.948079967648134,14.251652169304034,null,0,0,1.8653270696886937E-2,0.1085128261509995,0.19376689537893654,0.27484658553885488,0.51116654188372235,0.67379908859666005,0.72538474025332744,null,0.51116654188372235,0.67379908859666005,0.72538474025332744]
["2013-03-21T15:00:00","2013-03-21T15:00:00",null,11.850812607490122,12.154384809146022,12.457957010801922,12.761529212457821,13.065101414113721,13.368673615769621,13.672245817425521,13.975818019081421,14.279390220737321,null,0,0,0,7.8776947046830165E-2,0.16643890747521092,0.24983185555695289,0.4883494069275528,0.65309543019633842,0.70669992513023372,null,0.4883494069275528,0.65309543019633842,0.70669992513023372]
["2013-03-21T16:00:00","2013-03-21T16:00:00",null,11.921654963021336,12.225227164677236,12.528799366333136,12.832371567989036,13.135943769644935,13.439515971300835,13.743088172956735,14.046660374612635,14.350232576268535,null,0,0,0,4.9093641986338643E-2,0.13916349361516311,0.22484867000125758,0.46555330158885438,0.6323917717960168,0.68800459519840451,null,0.46555330158885438,0.6323917717960168,0.68800459519840451]
["2013-03-21T17:00:00","2013-03-21T17:00:00",null,12.025592602053843,12.329164803709743,12.632737005365643,12.936309207021543,13.239881408677443,13.543453610333342,13.847025811989242,14.150598013645142,14.454170215301042,null,0,0,0,1.8253707964935303E-2,0.11073145079420348,0.19871937029338602,0.44162159690671526,0.6105735436697256,0.66819469554060573,null,0.44162159690671526,0.6105735436697256,0.66819469554060573]
["2013-03-21T18:00:00","2013-03-21T18:00:00",null,12.115501690536581,12.419073892192481,12.722646093848381,13.026218295504281,13.329790497160181,13.633362698816081,13.93693490047198,14.24050710212788,14.54407930378378,null,0,0,0,0,7.8840035899243932E-2,0.16919378736392793,0.41435669785540302,0.58547469521793916,0.64516726440972494,null,0.41435669785540302,0.58547469521793916,0.64516726440972494]
["2013-03-21T19:00:00","2013-03-21T19:00:00",null,12.060250964518174,12.363823166174074,12.667395367829974,12.970967569485873,13.274539771141773,13.578111972797673,13.881684174453573,14.185256376109473,14.488828577765373,null,0,0,0,0,4.6128465922910554E-2,0.13886907897056713,0.38632421776639475,0.55962929534592776,0.62141431147609039,null,0.38632421776639475,0.55962929534592776,0.62141431147609039]
["2013-03-21T20:00:00","2013-03-21T20:00:00",null,11.964913603983103,12.268485805639003,12.572058007294903,12.875630208950803,13.179202410606703,13.482774612262602,13.786346813918502,14.089919015574402,14.393491217230302,null,0,0,0,0,1.7202227091379498E-2,0.11226661286959527,0.36194037630862647,0.53736944525274299,0.60119433427760471,null,0.36194037630862647,0.53736944525274299,0.60119433427760471]
["2013-03-21T21:00:00","2013-03-21T21:00:00",null,11.97563253249,12.2792047341459,12.5827769358018,12.886349137457699,13.189921339113599,13.493493540769499,13.797065742425399,14.100637944081299,14.404210145737199,null,0,0,0,0,0,8.7935345455504813E-2,0.33977515949406178,0.51728616056781962,0.58308783363496697,null,0.33977515949406178,0.51728616056781962,0.58308783363496697]
["2013-03-21T22:00:00","2013-03-21T22:00:00",null,11.885133666310729,12.188705867966629,12.492278069622529,12.795850271278429,13.099422472934329,13.402994674590229,13.706566876246129,14.010139077902029,14.313711279557928,null,0,0,0,0,0,6.7231687055183231E-2,0.3211744628408526,0.50069379238310274,0.56841967544885796,null,0.3211744628408526,0.50069379238310274,0.56841967544885796]
["2013-03-21T23:00:00","2013-03-21T23:00:00",null,11.90289283908605,12.20646504074195,12.51003724239785,12.81360944405375,13.11718164570965,13.42075384736555,13.72432604902145,14.02789825067735,14.331470452333249,null,0,0,0,0,0,4.8536357123353996E-2,0.30452952061245797,0.4860151193882582,0.55562315321767897,null,0.30452952061245797,0.4860151193882582,0.55562315321767897]
["2013-03-22","2013-03-22",null,11.910161143195069,12.213733344850969,12.517305546506869,12.820877748162768,13.124449949818668,13.428022151474568,13.731594353130468,14.035166554786368,14.338738756442268,null,0,0,0,0,0,2.9704334677962459E-2,0.28775840067923658,0.4712102686885869,0.54271096809040886,null,0.28775840067923658,0.4712102686885869,0.54271096809040886]
["2013-03-22T01:00:00","2013-03-22T01:00:00",null,11.935502762603026,12.239074964258926,12.542647165914826,12.846219367570725,13.149791569226625,13.453363770882525,13.756935972538425,14.060508174194325,14.364080375850225,null,0,0,0,0,0,9.8313461677502836E-3,0.26995682948993011,0.45539599635030165,0.52879987613326029,null,0.26995682948993011,0.45539599635030165,0.52879987613326029]
["2013-03-22T02:00:00","2013-03-22T02:00:00",null,12.026147615859104,12.329719817515004,12.633292019170904,12.936864220826804,13.240436422482704,13.544008624138604,13.847580825794504,14.151153027450404,14.454725229106304,null,0,0,0,0,0,0,0.25136664764545646,0.43879311335684923,0.51410017352094461,null,0.25136664764545646,0.43879311335684923,0.51410017352094461]
["2013-03-22T03:00:00","2013-03-22T03:00:00",null,12.017051850667769,12.320624052323669,12.624196253979569,12.927768455635469,13.231340657291369,13.534912858947269,13.838485060603169,14.142057262259069,14.445629463914969,null,0,0,0,0,0,0,0.2331760285329342,0.42258979309534817,0.49980003364058029,null,0.2331760285329342,0.42258979309534817,0.49980003364058029]
["2013-03-22T04:00:00","2013-03-22T04:00:00",null,12.044503278666781,12.348075480322681,12.651647681978581,12.955219883634481,13.258792085290381,13.562364286946281,13.865936488602181,14.16950869025808,14.47308089191398,null,0,0,0,0,0,0,0.21388135450317794,0.40530344753408426,0.48442738326918866,null,0.21388135450317794,0.40530344753408426,0.48442738326918866]
["2013-03-22T05:00:00","2013-03-22T05:00:00",null,12.165045252589808,12.468617454245708,12.772189655901608,13.075761857557508,13.379334059213408,13.682906260869308,13.986478462525207,14.290050664181107,14.593622865837007,null,0,0,0,0,0,0,0.19024406446563458,0.38374808962618218,0.46486983902104334,null,0.19024406446563458,0.38374808962618218,0.46486983902104334]
["2013-03-22T06:00:00","2013-03-22T06:00:00",null,12.222436671741781,12.52600887339768,12.82958107505358,13.13315327670948,13.43672547836538,13.74029768002128,14.04386988167718,14.34744208333308,14.65101428498898,null,0,0,0,0,0,0,0.16434609054994537,0.35997410707507649,0.44312521455590115,null,0.16434609054994537,0.35997410707507649,0.44312521455590115]
["2013-03-22T07:00:00","2013-03-22T07:00:00",null,10.97990943016425,11.28348163182015,11.58705383347605,11.89062603513195,12.19419823678785,12.49777043844375,12.80134264009965,13.10491484175555,13.40848704341145,null,0,0,0,0,0,0,0.1445572205096177,0.34235128763427458,0.42758432724474049,null,0.1445572205096177,0.34235128763427458,0.42758432724474049]
["2013-03-22T08:00:00","2013-03-22T08:00:00",null,10.410906045148492,10.714478246804392,11.018050448460292,11.321622650116192,11.625194851772092,11.928767053427991,12.232339255083891,12.535911456739791,12.839483658395691,null,3.8515744398363597E-2,4.1039298494898478E-2,4.3415645269135487E-2,4.5676329147281321E-2,4.7810835320600403E-2,4.9840193406563871E-2,0.19632162391478941,0.39594526775943406,0.48292376562000328,null,0.19632162391478941,0.39594526775943406,0.48292376562000328]
["2013-03-22T09:00:00","2013-03-22T09:00:00",null,10.460896805691773,10.764469007347673,11.068041209003573,11.371613410659473,11.675185612315373,11.978757813971272,12.282330015627172,12.585902217283072,12.889474418938972,null,6.7810001535639319E-2,7.2920198581122447E-2,7.7735980982009845E-2,8.2299407973243754E-2,8.6620994363559745E-2,9.0732284579164477E-2,0.23919049912967566,0.44068577892925037,0.5294623090836007,null,0.23919049912967566,0.44068577892925037,0.5294623090836007]
["2013-03-22T10:00:00","2013-03-22T10:00:00",null,10.390253836721273,10.693826038377173,10.997398240033073,11.300970441688973,11.604542643344873,11.908114845000773,12.211687046656673,12.515259248312573,12.818831449968473,null,5.0996822367475686E-2,5.8599029083287006E-2,6.5780643449675852E-2,7.2573209892848906E-2,7.9008272839012864E-2,8.5127891523109928E-2,0.23548928645475783,0.43880362816558477,0.52930458695256732,null,0.23548928645475783,0.43880362816558477,0.52930458695256732]
["2013-03-22T11:00:00","2013-03-22T11:00:00",null,10.402846605639935,10.706418807295835,11.009991008951735,11.313563210607635,11.617135412263535,11.920707613919435,12.224279815575334,12.527852017231234,12.831424218887134,null,3.722242292388947E-2,4.7232520840144489E-2,5.6685333893414722E-2,6.5633436127377986E-2,7.4108371968240966E-2,8.2162715459681443E-2,0.23436420192005269,0.4394345166897185,0.53160733006565541,null,0.23436420192005269,0.4394345166897185,0.53160733006565541]
["2013-03-22T12:00:00","2013-03-22T12:00:00",null,10.417399661247616,10.720971862903516,11.024544064559416,11.328116266215316,11.631688467871216,11.935260669527116,12.238832871183016,12.542405072838916,12.845977274494816,null,2.2617353590193855E-2,3.5056372324363698E-2,4.680141368198644E-2,5.7926081324211044E-2,6.8451404868508606E-2,7.8461502784763618E-2,0.2325135955825938,0.43935039821983402,0.53320558099346083,null,0.2325135955825938,0.43935039821983402,0.53320558099346083]
["2013-03-22T13:00:00","2013-03-22T13:00:00",null,10.421578516935744,10.725150718591644,11.028722920247544,11.332295121903444,11.635867323559344,11.939439525215244,12.243011726871144,12.546583928527044,12.850156130182944,null,7.886106551671497E-3,2.275404610375616E-2,3.6791315765731414E-2,5.0092548816217358E-2,6.267877487268507E-2,7.4644627213754616E-2,0.23055784115777928,0.43916113166259391,0.53470919864264621,null,0.23055784115777928,0.43916113166259391,0.53470919864264621]
["2013-03-22T14:00:00","2013-03-22T14:00:00",null,10.418381539435293,10.721953741091193,11.025525942747093,11.329098144402993,11.632670346058893,11.936242547714793,12.239814749370693,12.543386951026593,12.846959152682492,null,0,9.6315648017747876E-3,2.5971577576838118E-2,4.1438861226849838E-2,5.6085989795487699E-2,7.0007596561371774E-2,0.22777141684285535,0.43814119521524442,0.53537163159298662,null,0.22777141684285535,0.43814119521524442,0.53537163159298662]
["2013-03-22T15:00:00","2013-03-22T15:00:00",null,10.390218232180045,10.693790433835945,10.997362635491845,11.300934837147745,11.604507038803645,11.908079240459545,12.211651442115445,12.515223643771344,12.818795845427244,null,0,0,1.3606162503817208E-2,3.1207952327148014E-2,4.7884438981749343E-2,6.3730255746241263E-2,0.22332365274771263,0.43542837456146943,0.5343201507194304,null,0.22332365274771263,0.43542837456146943,0.5343201507194304]
["2013-03-22T16:00:00","2013-03-22T16:00:00",null,10.326954560554524,10.630526762210424,10.934098963866324,11.237671165522224,11.541243367178124,11.844815568834024,12.148387770489924,12.451959972145824,12.755532173801724,null,0,0,9.5684759493612492E-4,2.0714173209057142E-2,3.944104756709306E-2,5.7232103947663947E-2,0.21866559247785866,0.43252628735045434,0.53308991809736961,null,0.21866559247785866,0.43252628735045434,0.53308991809736961]
["2013-03-22T17:00:00","2013-03-22T17:00:00",null,10.339279469009055,10.642851670664955,10.946423872320855,11.249996073976755,11.553568275632655,11.857140477288555,12.160712678944455,12.464284880600355,12.767857082256254,null,0,0,0,9.6000203755681104E-3,3.038779724577418E-2,5.0134608051159602E-2,0.21341870291881324,0.42904588565898333,0.53129188580358855,null,0.21341870291881324,0.42904588565898333,0.53129188580358855]
["2013-03-22T18:00:00","2013-03-22T18:00:00",null,10.319975754871747,10.623547956527647,10.927120158183547,11.230692359839447,11.534264561495347,11.837836763151246,12.141408964807146,12.444981166463046,12.748553368118946,null,0,0,0,0,2.1218884028364117E-2,4.2900419641092945E-2,0.20802460603746992,0.42539724702774334,0.52931510176130292,null,0.20802460603746992,0.42539724702774334,0.52931510176130292]
["2013-03-22T19:00:00","2013-03-22T19:00:00",null,10.362417304706558,10.665989506362457,10.969561708018357,11.273133909674257,11.576706111330157,11.880278312986057,12.183850514641957,12.487422716297857,12.790994917953757,null,0,0,0,0,1.3301233050485932E-2,3.6875434235615921E-2,0.20380816773450955,0.4228947225486796,0.52844237263625127,null,0.20380816773450955,0.4228947225486796,0.52844237263625127]
["2013-03-22T20:00:00","2013-03-22T20:00:00",null,10.366395828328976,10.669968029984876,10.973540231640776,11.277112433296676,11.580684634952576,11.884256836608476,12.187829038264375,12.491401239920275,12.794973441576175,null,0,0,0,0,5.0471081930697648E-3,3.0513974950600913E-2,0.19925525555201121,0.42005572419007786,0.52724368444039715,null,0.19925525555201121,0.42005572419007786,0.52724368444039715]
["2013-03-22T21:00:00","2013-03-22T21:00:00",null,10.37787531522363,10.68144751687953,10.98501971853543,11.28859192019133,11.59216412184723,11.895736323503129,12.199308525159029,12.502880726814929,12.806452928470829,null,0,0,0,0,0,2.3700378889956738E-2,0.19426072140261927,0.41678561867331809,0.52562440389512055,null,0.19426072140261927,0.41678561867331809,0.52562440389512055]
["2013-03-22T22:00:00","2013-03-22T22:00:00",null,10.311258868766968,10.614831070422868,10.918403272078768,11.221975473734668,11.525547675390568,11.829119877046468,12.132692078702368,12.436264280358268,12.739836482014168,null,0,0,0,0,0,2.0114829111130095E-2,0.19243114468263148,0.41661738173354912,0.52704390307442139,null,0.19243114468263148,0.41661738173354912,0.52704390307442139]
["2013-03-22T23:00:00","2013-03-22T23:00:00",null,10.228320359592693,10.531892561248593,10.835464762904493,11.139036964560393,11.442609166216293,11.746181367872193,12.049753569528093,12.353325771183993,12.656897972839893,null,0,0,0,0,0,1.7023475342874867E-2,0.19108524916447955,0.41693282599561599,0.52893656864682259,null,0.19108524916447955,0.41693282599561599,0.52893656864682259]
["2013-03-23","2013-03-23",null,10.24933357282692,10.55290577448282,10.85647797613872,11.16005017779462,11.46362237945052,11.76719458110642,12.07076678276232,12.37433898441822,12.67791118607412,null,0,0,0,0,0,1.6192805452765469E-2,0.19193694867206007,0.41939329123973751,0.53292168115760064,null,0.19193694867206007,0.41939329123973751,0.53292168115760064]
["2013-03-23T01:00:00","2013-03-23T01:00:00",null,10.213687815487225,10.517260017143125,10.820832218799024,11.124404420454924,11.427976622110824,11.731548823766724,12.035121025422624,12.338693227078524,12.642265428734424,null,0,0,0,0,0,1.6970901299197056E-2,0.19435535468123932,0.42338891855925109,0.53841041131756395,null,0.19435535468123932,0.42338891855925109,0.53841041131756395]
["2013-03-23T02:00:00","2013-03-23T02:00:00",null,10.209962685578683,10.513534887234583,10.817107088890484,11.120679290546384,11.424251492202284,11.727823693858184,12.031395895514084,12.334968097169984,12.638540298825884,null,0,0,0,0,0,1.8022382172753256E-2,0.19705766052627877,0.42764741609715368,0.54416201169591638,null,0.19705766052627877,0.42764741609715368,0.54416201169591638]
["2013-03-23T03:00:00","2013-03-23T03:00:00",null,10.156189065595683,10.459761267251583,10.763333468907485,11.066905670563385,11.370477872219285,11.674050073875184,11.977622275531084,12.281194477186984,12.584766678842884,null,0,0,0,0,0,1.8464004139646859E-2,0.19917113708212672,0.43134862877207147,0.54936684202001962,null,0.19917113708212672,0.43134862877207147,0.54936684202001962]
["2013-03-23T04:00:00","2013-03-23T04:00:00",null,10.141552006357394,10.445124208013294,10.748696409669195,11.052268611325095,11.355840812980995,11.659413014636895,11.962985216292795,12.266557417948695,12.570129619604595,null,0,0,0,0,0,1.9452396160789687E-2,0.20181035407475278,0.43556506707503184,0.55507638316342978,null,0.20181035407475278,0.43556506707503184,0.55507638316342978]
["2013-03-23T05:00:00","2013-03-23T05:00:00",null,10.251379190485803,10.554951392141703,10.858523593797603,11.162095795453503,11.465667997109403,11.769240198765303,12.072812400421203,12.376384602077103,12.679956803733003,null,0,0,0,0,0,1.8569152227002478E-2,0.20261999434739106,0.43797295827547555,0.55901943643926555,null,0.20261999434739106,0.43797295827547555,0.55901943643926555]
["2013-03-23T06:00:00","2013-03-23T06:00:00",null,10.239590777688212,10.543162979344112,10.846735181000012,11.150307382655912,11.453879584311812,11.757451785967712,12.061023987623612,12.364596189279512,12.668168390935412,null,0,0,0,0,0,1.5067720918060332E-2,0.20087453609728775,0.43789935461432661,0.56053356889718653,null,0.20087453609728775,0.43789935461432661,0.56053356889718653]
["2013-03-23T07:00:00","2013-03-23T07:00:00",null,10.29872694332327,10.60229914497917,10.905871346635072,11.209443548290972,11.513015749946872,11.816587951602772,12.120160153258672,12.423732354914572,12.727304556570472,null,0,0,0,0,0,1.1976367149805104E-2,0.19951812577040026,0.43820428406765788,0.56240520485211654,null,0.19951812577040026,0.43820428406765788,0.56240520485211654]
["2013-03-23T08:00:00","2013-03-23T08:00:00",null,10.309061580153788,10.612633781809688,10.916205983465588,11.219778185121488,11.523350386777388,11.826922588433288,12.130494790089188,12.434066991745087,12.737639193400987,null,0,0,0,0,0,8.5275098845407696E-3,0.19781472675523923,0.43816222483271561,0.56395088173624419,null,0.19781472675523923,0.43816222483271561,0.56395088173624419]
["2013-03-23T09:00:00","2013-03-23T09:00:00",null,10.446659525239639,10.750231726895539,11.053803928551439,11.357376130207339,11.660948331863239,11.964520533519138,12.268092735175038,12.571664936830938,12.875237138486838,null,0,0,0,0,0,4.9840193406563765E-3,0.19599566484398701,0.43798347308421104,0.56533883648933836,null,0.19599566484398701,0.43798347308421104,0.56533883648933836]
["2013-03-23T10:00:00","2013-03-23T10:00:00",null,10.550187978085937,10.853760179741837,11.157332381397737,11.460904583053637,11.764476784709537,12.068048986365437,12.371621188021336,12.675193389677236,12.978765591333136,null,0,0,0,0,0,0,0.19252577796125156,0.43618544079042992,0.56512854031462711,null,0.19252577796125156,0.43618544079042992,0.56512854031462711]
["2013-03-23T11:00:00","2013-03-23T11:00:00",null,10.617228264025549,10.920800465681449,11.224372667337349,11.527944868993249,11.831517070649149,12.135089272305049,12.438661473960948,12.742233675616848,13.045805877272748,null,0,0,0,0,0,0,0.18599608173646756,0.43139068800701363,0.56198461250269405,null,0.18599608173646756,0.43139068800701363,0.56198461250269405]
["2013-03-23T12:00:00","2013-03-23T12:00:00",null,10.614884174499124,10.918456376155024,11.222028577810926,11.525600779466826,11.829172981122726,12.132745182778626,12.436317384434526,12.739889586090426,13.043461787746326,null,0,0,0,0,0,0,0.1798133741999571,0.42694292391187089,0.55918767337903452,null,0.1798133741999571,0.42694292391187089,0.55918767337903452]
["2013-03-23T13:00:00","2013-03-23T13:00:00",null,10.626511073245901,10.930083274901801,11.233655476557701,11.537227678213601,11.8407998798695,12.1443720815254,12.4479442831813,12.7515164848372,13.0550886864931,null,0,0,0,0,0,0,0.17305235218299075,0.42191684533627227,0.55582293458365473,null,0.17305235218299075,0.42191684533627227,0.55582293458365473]
["2013-03-23T14:00:00","2013-03-23T14:00:00",null,10.790964089462991,11.094536291118891,11.39810849277479,11.70168069443069,12.00525289608659,12.30882509774249,12.61239729939839,12.91596950105429,13.21954170271019,null,0,0,0,0,0,0,0.16221158437662633,0.41289513944116008,0.54852565732117475,null,0.16221158437662633,0.41289513944116008,0.54852565732117475]
["2013-03-23T15:00:00","2013-03-23T15:00:00",null,10.755792810572689,11.059365012228589,11.362937213884489,11.666509415540389,11.970081617196289,12.273653818852189,12.577226020508089,12.880798222163989,13.184370423819889,null,0,0,0,0,0,0,0.15282186017576946,0.40529293272534878,0.54262684962052443,null,0.15282186017576946,0.40529293272534878,0.54262684962052443]
["2013-03-23T16:00:00","2013-03-23T16:00:00",null,10.707538133702265,11.011110335358165,11.314682537014065,11.618254738669965,11.921826940325865,12.225399141981764,12.528971343637664,12.832543545293564,13.136115746949464,null,0,0,0,0,0,0,0.14242271433629863,0.39670233398839461,0.53576067951620243,null,0.14242271433629863,0.39670233398839461,0.53576067951620243]
["2013-03-23T17:00:00","2013-03-23T17:00:00",null,10.725595483222442,11.029167684878342,11.332739886534242,11.636312088190142,11.939884289846042,12.243456491501941,12.547028693157841,12.850600894813741,13.154173096469641,null,0,0,0,0,0,0,0.13130856150280959,0.38741775787489335,0.52822156165280443,null,0.13130856150280959,0.38741775787489335,0.52822156165280443]
["2013-03-23T18:00:00","2013-03-23T18:00:00",null,10.675151464196585,10.978723665852485,11.282295867508385,11.585868069164285,11.889440270820185,12.193012472476084,12.496584674131984,12.800156875787884,13.103729077443784,null,0,0,0,0,0,0,0.1225076665911442,0.38039386563953792,0.52290106843261008,null,0.1225076665911442,0.38039386563953792,0.52290106843261008]
["2013-03-23T19:00:00","2013-03-23T19:00:00",null,10.565610898338631,10.869183099994531,11.172755301650431,11.476327503306331,11.779899704962231,12.083471906618131,12.387044108274031,12.690616309929931,12.994188511585831,null,0,0,0,0,0,0,0.11546274473831766,0.37510491684555025,0.51929448903631237,null,0.11546274473831766,0.37510491684555025,0.51929448903631237]
["2013-03-23T20:00:00","2013-03-23T20:00:00",null,10.564635497886506,10.868207699542406,11.171779901198306,11.475352102854206,11.778924304510106,12.082496506166006,12.386068707821906,12.689640909477806,12.993213111133706,null,0,0,0,0,0,0,0.10839679326802,0.36979493843409145,0.51565636521380787,null,0.10839679326802,0.36979493843409145,0.51565636521380787]
["2013-03-23T21:00:00","2013-03-23T21:00:00",null,10.617188097416102,10.920760299072002,11.224332500727902,11.527904702383802,11.831476904039702,12.135049105695602,12.438621307351502,12.742193509007402,13.045765710663302,null,0,0,0,0,0,0,0.10203533398300499,0.36516842259044419,0.51267015953290829,null,0.10203533398300499,0.36516842259044419,0.51267015953290829]
["2013-03-23T22:00:00","2013-03-23T22:00:00",null,10.573297264821614,10.876869466477514,11.180441668133414,11.484013869789313,11.787586071445213,12.091158273101113,12.394730474757013,12.698302676412913,13.001874878068813,null,0,0,0,0,0,0,9.7482421800506647E-2,0.36230839461437131,0.51141889729337642,null,9.7482421800506647E-2,0.36230839461437131,0.51141889729337642]
["2013-03-23T23:00:00","2013-03-23T23:00:00",null,10.478765153501687,10.782337355157587,11.085909556813485,11.389481758469385,11.693053960125285,11.996626161781185,12.300198363437085,12.603770565092985,12.907342766748885,null,0,0,0,0,0,0,9.417025704880462E-2,0.36066808445162363,0.51137683805843415,null,9.417025704880462E-2,0.36066808445162363,0.51137683805843415]
["2013-03-24","2013-03-24",null,10.292848380921512,10.596420582577412,10.899992784233312,11.203564985889212,11.507137187545112,11.810709389201012,12.114281590856912,12.417853792512812,12.721425994168712,null,0,0,0,0,0,0,9.3034657705363927E-2,0.36118331007966614,0.5134587701880754,null,9.3034657705363927E-2,0.36118331007966614,0.5134587701880754]
["2013-03-24T01:00:00","2013-03-24T01:00:00",null,9.9588832396820468,10.262455441337947,10.566027642993848,10.869599844649748,11.173172046305648,11.476744247961548,11.780316449617448,12.083888651273348,12.387460852929248,null,0,0,0,0,0,7.3603661148933987E-5,9.4811660381673907E-2,0.36457959330125267,0.51840073029378952,null,9.4811660381673907E-2,0.36457959330125267,0.51840073029378952]
["2013-03-24T02:00:00","2013-03-24T02:00:00",null,9.8432953508305037,10.146867552486404,10.450439754142304,10.754011955798203,11.057584157454103,11.361156359110003,11.664728560765903,11.968300762421803,12.271872964077703,null,0,0,0,0,5.888292891914719E-4,2.4184060091792595E-3,9.8817802509923031E-2,0.37017347154857166,0.52548771138155836,null,9.8817802509923031E-2,0.37017347154857166,0.52548771138155836]
["2013-03-24T03:00:00","2013-03-24T03:00:00",null,9.6627951375746619,9.9663673392305618,10.269939540886462,10.573511742542362,10.877083944198262,11.180656145854162,11.484228347510061,11.787800549165961,12.091372750821861,null,0,0,0,1.0725104910273237E-3,3.4909165002065833E-3,7.0344070440909769E-3,0.10506359889884685,0.37797545963035867,0.53475125787758848,null,0.10506359889884685,0.37797545963035867,0.53475125787758848]
["2013-03-24T04:00:00","2013-03-24T04:00:00",null,9.515079098509398,9.818651300165298,10.122223501821198,10.425795703477098,10.729367905132998,11.032940106788898,11.336512308444798,11.640084510100698,11.943656711756597,null,0,0,0,2.754879888717243E-3,7.0028626178842909E-3,1.2270781794400852E-2,0.11194028381190439,0.38639782142754381,0.54464569289775233,null,0.11194028381190439,0.38639782142754381,0.54464569289775233]
["2013-03-24T05:00:00","2013-03-24T05:00:00",null,9.3645123059765041,9.668084507632404,9.9716567092883039,10.275228910944204,10.578801112600104,10.882373314256004,11.185945515911904,11.489517717567804,11.793089919223704,null,0,0,4.8368120183585187E-4,5.1838007066320642E-3,1.1261360155786899E-2,1.826422277367119E-2,0.11956352014518684,0.39557724945368944,0.55529719414687662,null,0.11956352014518684,0.39557724945368944,0.55529719414687662]
["2013-03-24T06:00:00","2013-03-24T06:00:00",null,9.2918059265970729,9.5953781282529729,9.8989503299088728,10.202522531564773,10.506094733220673,10.809666934876573,11.113239136532473,11.416811338188372,11.720383539844272,null,0,0,1.1881733871185057E-3,7.8335325079936877E-3,1.5751183485871872E-2,2.4488989545123893E-2,0.12742859707938722,0.40498800327201745,0.56618002118818334,null,0.12742859707938722,0.40498800327201745,0.56618002118818334]
["2013-03-24T07:00:00","2013-03-24T07:00:00",null,9.2734169292193958,9.5769891308752957,9.8805613325311956,10.184133534187096,10.487705735842995,10.791277937498895,11.094850139154795,11.398422340810695,11.701994542466595,null,0,0,2.9441464459573595E-3,1.1513715565440386E-2,2.1239913645835235E-2,3.169163352898386E-2,0.13625052160852374,0.41533457506781046,0.57797763658948387,null,0.13625052160852374,0.41533457506781046,0.57797763658948387]
["2013-03-24T08:00:00","2013-03-24T08:00:00",null,9.2931698812377714,9.5967420828936714,9.9003142845495713,10.203886486205473,10.507458687861373,10.811030889517273,11.114603091173173,11.418175292829073,11.721747494484973,null,0,0,3.6486386312400134E-3,1.416344736680201E-2,2.5729736975920209E-2,3.791640030043656E-2,0.14412611335145969,0.42475584369487401,0.58887097843952607,null,0.14412611335145969,0.42475584369487401,0.58887097843952607]
["2013-03-24T09:00:00","2013-03-24T09:00:00",null,9.3638249988014106,9.6673972004573105,9.9709694021132105,10.27454160376911,10.57811380542501,10.88168600708091,11.18525820873681,11.48883041039271,11.79240261204861,null,0,0,4.0902605981336174E-3,1.6550308949774585E-2,2.994617527888057E-2,4.3867782044764651E-2,0.15170729044979989,0.43388269767734183,0.5994699056449726,null,0.15170729044979989,0.43388269767734183,0.5994699056449726]
["2013-03-24T10:00:00","2013-03-24T10:00:00",null,9.4966933141039505,9.8002655157598504,10.10383771741575,10.407409919071648,10.710982120727548,11.014554322383448,11.318126524039348,11.621698725695248,11.925270927351148,null,0,0,1.1040549172340098E-3,1.5593461354838443E-2,3.0892508065081151E-2,4.6612147124746331E-2,0.15615505454494261,0.43994974231776113,0.60707211236078396,null,0.15615505454494261,0.43994974231776113,0.60707211236078396]
["2013-03-24T11:00:00","2013-03-24T11:00:00",null,9.5675515115048704,9.8711237131607703,10.17469591481667,10.47826811647257,10.78184031812847,11.08541251978437,11.38898472144027,11.69255692309617,11.99612912475207,null,0,0,0,1.4447347202662185E-2,3.1639059485306056E-2,4.9156730838752334E-2,0.16039252246537408,0.44579597597473358,0.61445350809314847,null,0.16039252246537408,0.44579597597473358,0.61445350809314847]
["2013-03-24T12:00:00","2013-03-24T12:00:00",null,9.6694857797226721,9.973057981378572,10.276630183034472,10.580202384690372,10.883774586346272,11.187346788002172,11.490918989658072,11.794491191313972,12.098063392969872,null,0,0,0,1.1608348844060446E-2,3.0734785934047725E-2,5.007151919874623E-2,0.16303173945800015,0.4500755031301073,0.62028922694138533,null,0.16303173945800015,0.4500755031301073,0.62028922694138533]
["2013-03-24T13:00:00","2013-03-24T13:00:00",null,9.853248369691519,10.156820571347419,10.460392773003319,10.763964974659219,11.067537176315119,11.371109377971019,11.674681579626919,11.978253781282818,12.281825982938718,null,0,0,0,6.3299148588083229E-3,2.7422621182345695E-2,4.8620475593238677E-2,0.16333666891133145,0.45205228717239293,0.62385374710274089,null,0.16333666891133145,0.45205228717239293,0.62385374710274089]
["2013-03-24T14:00:00","2013-03-24T14:00:00",null,9.9013282379556902,10.20490043961159,10.50847264126749,10.81204484292339,11.11561704457929,11.41918924623519,11.72276144789109,12.02633364954699,12.32990585120289,null,0,0,0,0,2.1786683700084464E-2,4.4887718492114169E-2,0.16142297372145917,0.45186302061515282,0.62529427589951292,null,0.16142297372145917,0.45186302061515282,0.62529427589951292]
["2013-03-24T15:00:00","2013-03-24T15:00:00",null,9.9728303222400445,10.276402523895944,10.579974725551843,10.883546927207743,11.187119128863642,11.490691330519542,11.794263532175442,12.097835733831342,12.401407935487242,null,0,0,0,0,1.5961479660583117E-2,4.0965694833749546E-2,0.15930949716561121,0.45146345788320147,0.62652450852157371,null,0.15930949716561121,0.45146345788320147,0.62652450852157371]
["2013-03-24T16:00:00","2013-03-24T16:00:00",null,10.01886789505093,10.322440096706829,10.626012298362729,10.929584500018629,11.233156701674529,11.536728903330429,11.840301104986329,12.143873306642229,12.447445508298129,null,0,0,0,0,7.5916919070757663E-3,3.455166150505673E-2,0.1547460701743773,0.448666518759542,0.62539942398686854,null,0.1547460701743773,0.448666518759542,0.62539942398686854]
["2013-03-24T17:00:00","2013-03-24T17:00:00",null,10.025753537431957,10.329325739087857,10.632897940743756,10.936470142399656,11.240042344055556,11.543614545711456,11.847186747367356,12.150758949023256,12.454331150679156,null,0,0,0,0,0,2.7159750963956647E-2,0.14921528077947169,0.44490221723221079,0.62331749185722729,null,0.14921528077947169,0.44490221723221079,0.62331749185722729]
["2013-03-24T18:00:00","2013-03-24T18:00:00",null,9.9829308586690981,10.286503060324998,10.590075261980898,10.893647463636798,11.197219665292698,11.500791866948598,11.804364068604498,12.107936270260398,12.411508471916298,null,0,0,0,0,0,1.5204413431622656E-2,0.13924724209815892,0.4368163293145636,0.61702963623336127,null,0.13924724209815892,0.4368163293145636,0.61702963623336127]
["2013-03-24T19:00:00","2013-03-24T19:00:00",null,9.8108204649896376,10.114392666645537,10.417964868301437,10.721537069957337,11.025109271613237,11.328681473269137,11.632253674925037,11.935825876580937,12.239398078236837,null,0,0,0,0,0,4.7106343135317821E-3,0.13071973221361813,0.43017097019368844,0.61216127978879609,null,0.13071973221361813,0.43017097019368844,0.61216127978879609]
["2013-03-24T20:00:00","2013-03-24T20:00:00",null,9.7096468130736664,10.013219014729566,10.316791216385466,10.620363418041366,10.923935619697266,11.227507821353166,11.531080023009066,11.834652224664966,12.138224426320866,null,0,0,0,0,0,0,0.12371686959573384,0.42501871391326307,0.60876499656720962,null,0.12371686959573384,0.42501871391326307,0.60876499656720962]
["2013-03-24T21:00:00","2013-03-24T21:00:00",null,9.5306029995565602,9.8341752012124601,10.13774740286836,10.44131960452426,10.74489180618016,11.04846400783606,11.35203620949196,11.65560841114786,11.95918061280376,null,0,0,0,0,0,0,0.11879593910749082,0.42192736014500787,0.60740858624032212,null,0.11879593910749082,0.42192736014500787,0.60740858624032212]
["2013-03-24T22:00:00","2013-03-24T22:00:00",null,9.4003408899087599,9.7039130915646599,10.00748529322056,10.31105749487646,10.61462969653236,10.91820189818826,11.22177409984416,11.525346301500059,11.828918503155959,null,0,0,0,0,0,0,0.11681915506520517,0.42171706397029662,0.60888065946330083,null,0.11681915506520517,0.42171706397029662,0.60888065946330083]
["2013-03-24T23:00:00","2013-03-24T23:00:00",null,9.3282856909106879,9.6318578925665879,9.9354300942224878,10.23900229587839,10.542574497534289,10.846146699190189,11.149718900846089,11.453291102501989,11.756863304157889,null,0,0,0,0,0,0,0.11841740599301059,0.42499768429579199,0.61375953071660161,null,0.11841740599301059,0.42499768429579199,0.61375953071660161]
["2013-03-25","2013-03-25",null,9.2168497445065967,9.5204219461624966,9.8239941478183965,10.127566349474296,10.431138551130196,10.734710752786096,11.038282954441996,11.341855156097896,11.645427357753796,null,0,0,0,0,2.6287021838904996E-4,2.1029617471123997E-3,0.12225531118149072,0.43048641445575536,0.62080445256942818,null,0.12225531118149072,0.43048641445575536,0.62080445256942818]
["2013-03-25T01:00:00","2013-03-25T01:00:00",null,9.1087606199145803,9.4123328215704802,9.7159050232263802,10.01947722488228,10.32304942653818,10.62662162819408,10.93019382984998,11.23376603150588,11.53733823316178,null,0,0,0,5.3625524551366183E-4,2.7023058450394333E-3,6.3299148588083221E-3,0.12818566330834769,0.43801501751041777,0.62985770289074705,null,0.12818566330834769,0.43801501751041777,0.62985770289074705]
["2013-03-25T02:00:00","2013-03-25T02:00:00",null,9.0570371664364355,9.3606093680923355,9.6641815697482354,9.9677537714041335,10.271325973060033,10.574898174715933,10.878470376371833,11.182042578027733,11.485614779683633,null,0,0,1.3774399443586217E-3,3.8589348059512528E-3,7.8440473167292503E-3,1.3196084963130307E-2,0.13668162876668177,0.44804614504414392,0.64135038883871631,null,0.13668162876668177,0.44804614504414392,0.64135038883871631]
["2013-03-25T03:00:00","2013-03-25T03:00:00",null,8.9184954206070692,9.2220676222629692,9.5256398239188691,9.8292120255747673,10.132784227230667,10.436356428886567,10.739928630542467,11.043500832198367,11.347073033854267,null,0,0,2.7548798887172435E-3,7.2026439838599682E-3,1.3038362832096877E-2,2.0125343919865663E-2,0.14526171269490037,0.45817190585649015,0.6529482228740412,null,0.14526171269490037,0.45817190585649015,0.6529482228740412]
["2013-03-25T04:00:00","2013-03-25T04:00:00",null,8.9189636624268278,9.2225358640827277,9.5261080657386277,9.8296802673945276,10.133252469050428,10.436824670706327,10.740396872362227,11.043969074018127,11.347541275674027,null,0,0,4.2374679204314853E-3,1.0651501249124304E-2,1.8337826434820126E-2,2.7170265772692201E-2,0.1539469447104746,0.46841332956492754,0.6646512049967217,null,0.1539469447104746,0.46841332956492754,0.6646512049967217]
["2013-03-25T05:00:00","2013-03-25T05:00:00",null,8.8906526641362653,9.1942248657921652,9.4977970674480652,9.8013692691039651,10.104941470759865,10.408513672415765,10.712085874071665,11.015658075727565,11.319230277383465,null,0,1.1986881958540678E-3,7.4760290109845808E-3,1.5814272338285244E-2,2.5309144626497731E-2,3.5834468170795289E-2,0.16421991284511867,0.48020043015749253,0.67786831957732319,null,0.16421991284511867,0.48020043015749253,0.67786831957732319]
["2013-03-25T06:00:00","2013-03-25T06:00:00",null,8.8289151091265925,9.1324873107824924,9.4360595124383924,9.7396317140942923,10.043203915750192,10.346776117406092,10.650348319061992,10.953920520717892,11.257492722373792,null,0,1.9031803811367216E-3,1.026245332590851E-2,2.053542146055258E-2,3.1859870468752854E-2,4.4109622645682578E-2,0.17411434786528251,0.49161951244431285,0.69073844546965102,null,0.17411434786528251,0.49161951244431285,0.69073844546965102]
["2013-03-25T07:00:00","2013-03-25T07:00:00",null,8.9139099319012285,9.2174821335571284,9.5210543352130284,9.8246265368689283,10.128198738524828,10.431770940180728,10.735343141836628,11.038915343492528,11.342487545148428,null,0,1.7033990151610436E-3,1.2144604089574107E-2,2.4383841457768271E-2,3.7548381994691897E-2,5.153307761298935E-2,0.18316759818660139,0.50221843964975932,0.70279893108934066,null,0.18316759818660139,0.50221843964975932,0.70279893108934066]
["2013-03-25T08:00:00","2013-03-25T08:00:00",null,9.0993765125693944,9.4029487142252943,9.7065209158811943,10.010093117537096,10.313665319192996,10.617237520848896,10.920809722504796,11.224381924160696,11.527954125816596,null,0,2.4814948615926313E-3,1.4931028404498036E-2,2.906293134509336E-2,4.4004474558326963E-2,5.9671539574314335E-2,0.19289379626699624,0.51343774057060398,0.71543773118948617,null,0.19289379626699624,0.51343774057060398,0.71543773118948617]
["2013-03-25T09:00:00","2013-03-25T09:00:00",null,9.3206345383172362,9.6242067399731361,9.9277789416290361,10.231351143284936,10.534923344940836,10.838495546596736,11.142067748252636,11.445639949908536,11.749212151564436,null,0,2.2081098344680196E-3,1.6655457037130204E-2,3.2669510741391128E-2,4.9377541822199146E-2,6.6716461427140869E-2,0.20152645423889265,0.52356350138295016,0.7269829911811333,null,0.20152645423889265,0.52356350138295016,0.7269829911811333]
["2013-03-25T10:00:00","2013-03-25T10:00:00",null,9.4644855620599913,9.7680577637158912,10.071629965371791,10.375202167027693,10.678774368683593,10.982346570339493,11.285918771995393,11.589490973651293,11.893063175307192,null,0,0,1.4342199115306565E-2,3.2333036861853147E-2,5.0902189088855639E-2,7.0007596561371774E-2,0.20647892915334234,0.53009319760773421,0.73501630505510263,null,0.20647892915334234,0.53009319760773421,0.73501630505510263]
["2013-03-25T11:00:00","2013-03-25T11:00:00",null,9.6018381958759988,9.9054103975318988,10.208982599187799,10.512554800843699,10.816127002499599,11.119699204155499,11.423271405811398,11.726843607467298,12.030415809123198,null,0,0,8.2961840923584159E-3,2.8337409542339587E-2,4.8851801385421049E-2,6.979730038666053E-2,0.20800357641999884,0.53326866984587395,0.7397584837948411,null,0.20800357641999884,0.53326866984587395,0.7397584837948411]
["2013-03-25T12:00:00","2013-03-25T12:00:00",null,9.3028854370225584,9.6064576386784584,9.9100298403343583,10.213602041990258,10.517174243646158,10.820746445302058,11.124318646957958,11.427890848613858,11.731463050269758,null,0,0,3.2595907080242188E-3,2.4814948615926317E-2,4.675935444704421E-2,6.9050748966435621E-2,0.20852931685677695,0.53500361328724166,0.74263954138838506,null,0.20852931685677695,0.53500361328724166,0.74263954138838506]
["2013-03-25T13:00:00","2013-03-25T13:00:00",null,9.7776466009451077,10.081218802601008,10.384791004256908,10.688363205912808,10.991935407568707,11.295507609224607,11.599079810880507,11.902652012536407,12.206224214192307,null,0,0,0,2.0766747252734946E-2,4.4772055596022993E-2,6.9019204540228932E-2,0.21034837876802917,0.5385786482573327,0.74788643094743046,null,0.21034837876802917,0.5385786482573327,0.74788643094743046]
["2013-03-25T14:00:00","2013-03-25T14:00:00",null,9.8209900223085462,10.124562223964446,10.428134425620344,10.731706627276244,11.035278828932144,11.338851030588044,11.642423232243944,11.945995433899844,12.249567635555744,null,0,0,0,1.7969808129075455E-2,4.3993959749591402E-2,7.0154803883669625E-2,0.21329252521398653,0.54324722333592224,0.75418480138003208,null,0.21329252521398653,0.54324722333592224,0.75418480138003208]
["2013-03-25T15:00:00","2013-03-25T15:00:00",null,9.9441005060454568,10.247672707701357,10.551244909357255,10.854817111013155,11.158389312669055,11.461961514324955,11.765533715980855,12.069105917636755,12.372678119292654,null,0,0,0,1.2481077969112093E-2,4.0576646910533753E-2,6.8693245469426512E-2,0.21369208794593789,0.54541327393544803,0.75803322137724782,null,0.21369208794593789,0.54541327393544803,0.75803322137724782]
["2013-03-25T16:00:00","2013-03-25T16:00:00",null,9.91075820280561,10.21433040446151,10.51790260611741,10.82147480777331,11.12504700942921,11.42861921108511,11.73219141274101,12.03576361439691,12.339335816052809,null,0,0,0,5.2258599415743144E-3,3.5445420247579497E-2,6.5570347274964594E-2,0.21248288494134826,0.54601261803337509,0.76035699410780699,null,0.21248288494134826,0.54601261803337509,0.76035699410780699]
["2013-03-25T17:00:00","2013-03-25T17:00:00",null,9.860204820113756,10.163777021769656,10.467349223425556,10.770921425081456,11.074493626737356,11.378065828393256,11.681638030049156,11.985210231705056,12.288782433360955,null,0,0,0,0,2.9367860798424662E-2,6.1543175529244348E-2,0.21039043800297141,0.54576026262372157,0.76186061175699238,null,0.21039043800297141,0.54576026262372157,0.76186061175699238]
["2013-03-25T18:00:00","2013-03-25T18:00:00",null,9.7799858426856918,10.083558044341592,10.387130245997492,10.690702447653392,10.994274649309292,11.297846850965191,11.601419052621091,11.904991254276991,12.208563455932891,null,0,0,0,0,2.3868615829725739E-2,5.809431826398001E-2,0.20888682035378606,0.54609673650325952,0.76394254388663363,null,0.20888682035378606,0.54609673650325952,0.76394254388663363]
["2013-03-25T19:00:00","2013-03-25T19:00:00",null,9.6322169294415154,9.9357891310974153,10.239361332753315,10.542933534409215,10.846505736065115,11.150077937721015,11.453650139376915,11.757222341032815,12.060794542688715,null,0,0,0,0,2.234396856306925E-2,5.8535940230873613E-2,0.21118956346687415,0.55016596748392199,0.76968362945625046,null,0.21118956346687415,0.55016596748392199,0.76968362945625046]
["2013-03-25T20:00:00","2013-03-25T20:00:00",null,9.4875787427467113,9.7911509444026112,10.094723146058511,10.398295347714411,10.701867549370311,11.005439751026211,11.309011952682111,11.612584154338011,11.916156355993911,null,0,0,0,2.9441464459573595E-4,2.4636196867421765E-2,6.2710319298891731E-2,0.21715146001993779,0.5578207482434111,0.77894717595228058,null,0.21715146001993779,0.5578207482434111,0.77894717595228058]
["2013-03-25T21:00:00","2013-03-25T21:00:00",null,9.3103198453984479,9.6138920470543479,9.9174642487102478,10.221036450366148,10.524608652022048,10.828180853677948,11.131753055333848,11.435325256989747,11.738897458645647,null,0,0,3.0492945333129791E-4,2.6812762275683095E-3,2.8999842492679995E-2,6.8924571261608877E-2,0.2251216850414938,0.56746282785392144,0.79016647687312525,null,0.2251216850414938,0.56746282785392144,0.79016647687312525]
["2013-03-25T22:00:00","2013-03-25T22:00:00",null,9.2026039760388016,9.5061761776947016,9.8097483793506015,10.113320581006501,10.416892782662401,10.720464984318301,11.024037185974201,11.327609387630101,11.631181589286001,null,0,2.7338502712461192E-4,2.7548798887172435E-3,7.1816143663888448E-3,3.5424390630108375E-2,7.7168181310289491E-2,0.235079208914071,0.57905014708051072,0.80329947298384219,null,0.235079208914071,0.57905014708051072,0.80329947298384219]
["2013-03-25T23:00:00","2013-03-25T23:00:00",null,9.132388200689137,9.435960402345037,9.7395326040009369,10.043104805656837,10.346677007312737,10.650249208968637,10.953821410624537,11.257393612280437,11.560965813936336,null,2.1765654082613337E-3,4.6475454611184025E-3,9.2004576436167489E-3,1.5561916928631757E-2,4.5634269912339077E-2,8.9102489225152362E-2,0.24864331218294597,0.5941494124247777,0.81986029674235228,null,0.24864331218294597,0.5941494124247777,0.81986029674235228]
["2013-03-26","2013-03-26",null,9.0257058104066736,9.3292780120625736,9.6328502137184735,9.9364224153743734,10.239994617030273,10.543566818686173,10.847139020342073,11.150711221997973,11.454283423653873,null,6.676903547081869E-3,1.1303419390729147E-2,1.7875174850455398E-2,2.6129299707871565E-2,5.7989170176624423E-2,0.10312924407839207,0.26425780315525554,0.61126752104627258,0.83839790454314811,null,0.26425780315525554,0.61126752104627258,0.83839790454314811]
["2013-03-26T01:00:00","2013-03-26T01:00:00",null,9.0814366737640171,9.385008875419917,9.6885810770758169,9.9921532787317169,10.295725480387617,10.599297682043517,10.902869883699417,11.206442085355317,11.510014287011217,null,1.4131902940595326E-2,2.0871895340090565E-2,2.9430949650838034E-2,3.9546195654448675E-2,7.3162039182040381E-2,0.11995293805529127,0.28263768882501794,0.63112999474774922,0.85965884780645452,null,0.28263768882501794,0.63112999474774922,0.85965884780645452]
["2013-03-26T02:00:00","2013-03-26T02:00:00",null,8.944605745825065,9.2481779474809649,9.5517501491368648,9.8553223507927648,10.158894552448665,10.462466754104565,10.766038955760465,11.069611157416364,11.373183359072264,null,2.4446930310181643E-2,3.3331943691731536E-2,4.3899326470971341E-2,5.5907238046983145E-2,9.1289569442149263E-2,0.13975232290435452,0.30401429498441546,0.65399970374759653,0.88393754117686718,null,0.30401429498441546,0.65399970374759653,0.88393754117686718]
["2013-03-26T03:00:00","2013-03-26T03:00:00",null,8.853723139410226,9.157295341066126,9.4608675427220259,9.7644397443779258,10.068011946033826,10.371584147689726,10.675156349345626,10.978728551001526,11.282300752657425,null,3.7527352377220768E-2,4.8536357123354183E-2,6.1091038753615205E-2,7.4949556667085915E-2,0.1120878611210909,0.16219092474604382,0.32800908851896793,0.67945605569639211,0.91078184787875693,null,0.32800908851896793,0.67945605569639211,0.91078184787875693]
["2013-03-26T04:00:00","2013-03-26T04:00:00",null,8.8388098643770814,9.1423820660329813,9.4459542676888812,9.7495264693447812,10.053098671000681,10.356670872656581,10.660243074312481,10.963815275968381,11.267387477624281,null,5.1648740509080533E-2,6.475019219359078E-2,7.9271143057401905E-2,9.4959237690860399E-2,0.13382197077749755,0.18555482975646259,0.35289764079604319,0.70579565157897495,0.93848836889696274,null,0.35289764079604319,0.70579565157897495,0.93848836889696274]
["2013-03-26T05:00:00","2013-03-26T05:00:00",null,8.7113657063133463,9.0149379079692462,9.3185101096251461,9.6220823112810461,9.925654512936946,10.229226714592846,10.532798916248746,10.836371117904646,11.139943319560546,null,6.5307477056575566E-2,8.0543434914404896E-2,9.7062199437972813E-2,0.11463244483509689,0.15525115098057291,0.20863483493102117,0.37754435247220053,0.73191443647811094,0.9659951085491929,null,0.37754435247220053,0.73191443647811094,0.9659951085491929]
["2013-03-26T06:00:00","2013-03-26T06:00:00",null,8.8538344941821148,9.1574066958380147,9.4609788974939146,9.7645510991498146,10.068123300805714,10.371695502461614,10.675267704117514,10.978839905773414,11.282412107429314,null,5.5192231052964925E-2,7.2552180275377784E-2,9.1047728841231357E-2,0.11047909538454991,0.15285377458886476,0.20787776870206071,0.37834347793610323,0.73417512035625676,0.96964374718043289,null,0.37834347793610323,0.73417512035625676,0.96964374718043289]
["2013-03-26T07:00:00","2013-03-26T07:00:00",null,8.8619270276855087,9.1654992293414086,9.4690714309973085,9.7726436326532067,10.076215834309107,10.379788035965007,10.683360237620906,10.986932439276806,11.290504640932706,null,0,1.0220394090966263E-2,3.0713756316576614E-2,5.2027273623560757E-2,9.6157925886714471E-2,0.15284325978012919,0.32487567551577046,0.68217939115890269,0.91904648754490859,null,0.32487567551577046,0.68217939115890269,0.91904648754490859]
["2013-03-26T08:00:00","2013-03-26T08:00:00",null,9.0119215871718925,9.3154937888277924,9.6190659904836924,9.9226381921395941,10.226210393795494,10.529782595451394,10.833354797107294,11.136926998763194,11.440499200419094,null,0,0,0,0,3.8589348059512536E-2,9.6936021733146055E-2,0.27053514397038603,0.62932144764523257,0.86758701359306811,null,0.27053514397038603,0.62932144764523257,0.86758701359306811]
["2013-03-26T09:00:00","2013-03-26T09:00:00",null,9.2125155879862159,9.5160877896421159,9.8196599912980158,10.123232192953916,10.426804394609816,10.730376596265716,11.033948797921616,11.337520999577515,11.641093201233415,null,0,0,0,0,0,3.7537867185956329E-2,0.2127667847772084,0.57309876533618254,0.81283640450699679,null,0.2127667847772084,0.57309876533618254,0.81283640450699679]
["2013-03-26T10:00:00","2013-03-26T10:00:00",null,9.2778652916449964,9.5814374933008963,9.8850096949567963,10.188581896612698,10.492154098268598,10.795726299924498,11.099298501580398,11.402870703236298,11.706442904892198,null,0,0,0,0,0,0,0.15509305886265085,0.51696020149701705,0.75814888427333882,null,0.15509305886265085,0.51696020149701705,0.75814888427333882]
["2013-03-26T11:00:00","2013-03-26T11:00:00",null,9.338949570461299,9.642521772117199,9.9460939737730989,10.249666175428999,10.553238377084899,10.856810578740799,11.160382780396699,11.463954982052599,11.767527183708498,null,0,0,0,0,0,0,9.7713747592689026E-2,0.46110553749371169,0.70373474906680544,null,9.7713747592689026E-2,0.46110553749371169,0.70373474906680544]
["2013-03-26T12:00:00","2013-03-26T12:00:00",null,9.5459136700828982,9.8494858717387981,10.153058073394698,10.456630275050598,10.760202476706498,11.063774678362398,11.367346880018298,11.670919081674198,11.974491283330098,null,0,0,0,0,0,0,3.6759401352636126E-2,0.40172841256399311,0.64587175659500773,null,3.6759401352636126E-2,0.40172841256399311,0.64587175659500773]
["2013-03-26T13:00:00","2013-03-26T13:00:00",null,9.7405318692097698,10.04410407086567,10.34767627252157,10.651248474177468,10.954820675833368,11.258392877489268,11.561965079145168,11.865537280801068,12.169109482456967,null,0,0,0,0,0,0,0,0.34610507435287013,0.59179409526801241,null,-2.049373221249895E-2,0.34610507435287013,0.59179409526801241]
["2013-03-26T14:00:00","2013-03-26T14:00:00",null,10.394804257096446,10.698376458752346,11.001948660408246,11.305520862064146,11.609093063720046,11.912665265375946,12.216237467031846,12.519809668687746,12.823381870343646,null,0,0,0,0,0,0,0,0.33409716277685836,0.58186811582164188,null,-1.4205506601744258E-2,0.33409716277685836,0.58186811582164188]
["2013-03-26T15:00:00","2013-03-26T15:00:00",null,10.489177596636939,10.792749798292839,11.096321999948739,11.399894201604639,11.703466403260538,12.007038604916438,12.310610806572338,12.614183008228238,12.917755209884138,null,0,0,0,0,0,0,0,0.31942900459074935,0.56922931572149638,null,-1.6792149550692512E-2,0.31942900459074935,0.56922931572149638]
["2013-03-26T16:00:00","2013-03-26T16:00:00",null,10.469156809185709,10.772729010841608,11.076301212497508,11.379873414153408,11.683445615809308,11.987017817465208,12.290590019121108,12.594162220777008,12.897734422432908,null,0,0,0,0,0,0,0,0.30553894225107198,0.5573475818503113,null,-1.5993024086789799E-2,0.30553894225107198,0.5573475818503113]
["2013-03-26T17:00:00","2013-03-26T17:00:00",null,10.477621369284487,10.781193570940388,11.084765772596288,11.388337974252188,11.691910175908088,11.995482377563988,12.299054579219888,12.602626780875788,12.906198982531688,null,0,0,0,0,0,0,0,0.29132292084059214,0.54515040371705936,null,-1.6329497966327784E-2,0.29132292084059214,0.54515040371705936]
["2013-03-26T18:00:00","2013-03-26T18:00:00",null,10.405710758962128,10.709282960618026,11.012855162273926,11.316427363929826,11.619999565585726,11.923571767241626,12.227143968897526,12.530716170553426,12.834288372209326,null,0,0,0,0,0,0,0,0.2771699882825257,0.53301631443622077,null,-1.6287438731385533E-2,0.2771699882825257,0.53301631443622077]
["2013-03-26T19:00:00","2013-03-26T19:00:00",null,10.195950371035476,10.499522572691374,10.803094774347274,11.106666976003174,11.410239177659074,11.713811379314974,12.017383580970874,12.320955782626774,12.624527984282674,null,0,0,0,0,0,0,0,0.26598223178788771,0.52381585679260401,null,-1.3280203433014804E-2,0.26598223178788771,0.52381585679260401]
["2013-03-26T20:00:00","2013-03-26T20:00:00",null,10.100773113041914,10.404345314697814,10.707917516353714,11.011489718009614,11.315061919665514,11.618634121321413,11.922206322977313,12.225778524633213,12.529350726289113,null,0,0,0,0,0,0,0,0.25896885436126788,0.51870565974712091,null,-9.0217058951121941E-3,0.25896885436126788,0.51870565974712091]
["2013-03-26T21:00:00","2013-03-26T21:00:00",null,9.888467322508081,10.192039524163981,10.495611725819883,10.799183927475783,11.102756129131683,11.406328330787582,11.709900532443482,12.013472734099382,12.317044935755282,null,0,0,0,0,0,0,0,0.25518352321646554,0.51678144974851303,null,-5.7305707608812885E-3,0.25518352321646554,0.51678144974851303]
["2013-03-26T22:00:00","2013-03-26T22:00:00",null,9.7306184836374783,10.034190685293378,10.33776288694928,10.64133508860518,10.94490729026108,11.24847949191698,11.55205169357288,11.85562389522878,12.15919609688468,null,0,0,0,0,0,0,0,0.25548845266979681,0.51886338187815428,null,-1.5667065015987375E-3,0.25548845266979681,0.51886338187815428]
["2013-03-26T23:00:00","2013-03-26T23:00:00",null,9.5801250535477784,9.8836972552036784,10.187269456859578,10.490841658515478,10.794413860171378,11.097986061827278,11.401558263483178,11.705130465139078,12.008702666794978,null,0,0,0,0,0,4.3110715815804191E-4,2.3237727305592017E-3,0.25961025769413709,0.52468858591765566,null,2.3237727305592017E-3,0.25961025769413709,0.52468858591765566]
["2013-03-27","2013-03-27",null,9.4812622004691356,9.7848344021250355,10.088406603780935,10.391978805436835,10.695551007092735,10.999123208748635,11.302695410404535,11.606267612060435,11.909839813716335,null,0,0,0,1.4510436055075557E-3,3.4383424565287732E-3,5.741085569616851E-3,9.4107538183279878E-3,0.26839012298833137,0.53506670213965535,null,9.4107538183279878E-3,0.26839012298833137,0.53506670213965535]
["2013-03-27T01:00:00","2013-03-27T01:00:00",null,9.3677823779696894,9.6713545796255893,9.9749267812814892,10.278498982937389,10.582071184593289,10.885643386249189,11.189215587905089,11.492787789560989,11.796359991216889,null,8.7272912505164584E-4,3.1965018556108474E-3,5.3940968813433049E-3,8.8955281902854504E-3,1.2828066657385638E-2,1.6960386490461502E-2,2.2364998180540371E-2,0.28299519232202697,0.55122796316621414,null,2.2364998180540371E-2,0.28299519232202697,0.55122796316621414]
["2013-03-27T02:00:00","2013-03-27T02:00:00",null,9.3586744486086211,9.662246650264521,9.9658188519204209,10.269391053576321,10.572963255232221,10.876535456888121,11.180107658544021,11.483679860199921,11.787252061855821,null,4.9629897231852635E-3,9.6000203755681034E-3,1.3974180809561894E-2,1.952599982193863E-2,2.5382748287646664E-2,3.1334130031974751E-2,3.8463170354685786E-2,0.3007231598501845,0.57051212238723481,null,3.8463170354685786E-2,0.3007231598501845,0.57051212238723481]
["2013-03-27T03:00:00","2013-03-27T03:00:00",null,9.4080951760689704,9.7116673777248703,10.01523957938077,10.31881178103667,10.62238398269257,10.92595618434847,11.22952838600437,11.53310058766027,11.83667278931617,null,1.0157305238552891E-2,1.7065534577817121E-2,2.3574201185129998E-2,3.1134348665999075E-2,3.8873247895372706E-2,4.6612147124746331E-2,5.5434071653882852E-2,0.319292312077187,0.59060592188089378,null,5.5434071653882852E-2,0.319292312077187,0.59060592188089378]
["2013-03-27T04:00:00","2013-03-27T04:00:00",null,9.2942397393485319,9.5978119410044318,9.9013841426603317,10.204956344316232,10.508528545972132,10.812100747628032,11.115672949283931,11.419245150939831,11.722817352595731,null,1.4026754853239707E-2,2.3269271731798699E-2,3.197553336484403E-2,4.1607098166618825E-2,5.1291237012071424E-2,6.08702277701684E-2,7.1427095740672658E-2,0.33692564632672445,0.60980596263203002,null,7.1427095740672658E-2,0.33692564632672445,0.60980596263203002]
["2013-03-27T05:00:00","2013-03-27T05:00:00",null,9.3874369224791945,9.6910091241350944,9.9945813257909943,10.298153527446894,10.601725729102794,10.905297930758694,11.208870132414594,11.512442334070494,11.816014535726394,null,1.6476705288625652E-2,2.8074539323950532E-2,3.8999425600199443E-2,5.0723437340351077E-2,6.2373845419353771E-2,7.3813957323645221E-2,8.6126798352988337E-2,0.35328668871925895,0.62774422633489879,null,8.6126798352988337E-2,0.35328668871925895,0.62774422633489879]
["2013-03-27T06:00:00","2013-03-27T06:00:00",null,9.4894642530174593,9.7930364546733593,10.096608656329259,10.400180857985159,10.703753059641059,11.007325261296959,11.310897462952859,11.614469664608759,11.918041866264659,null,1.709707900402381E-2,3.1092289431056824E-2,4.4267344776716004E-2,5.8104833072715599E-2,7.1753054811475078E-2,8.5085832288167684E-2,9.9186190802556334E-2,0.36803896537525244,0.64410526872743323,null,9.9186190802556334E-2,0.36803896537525244,0.64410526872743323]
["2013-03-27T07:00:00","2013-03-27T07:00:00",null,9.3160094569135925,9.6195816585694924,9.9231538602253924,10.226726061881292,10.530298263537192,10.833870465193092,11.137442666848992,11.441014868504892,11.744587070160792,null,2.5025244790637557E-2,4.1144446582254093E-2,5.6317315587670051E-2,7.2026439838599687E-2,8.7441149444933586E-2,0.10243526670184498,0.11811284652656792,0.38845872393971381,0.66593401166245991,null,0.11811284652656792,0.38845872393971381,0.66593401166245991]
["2013-03-27T08:00:00","2013-03-27T08:00:00",null,9.4042850066873545,9.7078572083432544,10.011429409999154,10.315001611655054,10.618573813310952,10.922146014966852,11.225718216622752,11.529290418278652,11.832862619934552,null,4.0187598987317955E-2,5.807328864650891E-2,7.4896982623408104E-2,9.2172813375936469E-2,0.10905959620524905,0.12544166821525463,0.14242308432318726,0.41402022397586502,0.69267317027699404,null,0.14242308432318726,0.41402022397586502,0.69267317027699404]
["2013-03-27T09:00:00","2013-03-27T09:00:00",null,9.8857595642513374,10.189331765907237,10.492903967563137,10.796476169219037,11.100048370874937,11.403620572530837,11.707192774186737,12.010764975842637,12.314337177498537,null,4.696965062175544E-2,6.6779550279554248E-2,8.5422306167705658E-2,0.10441205074413064,0.12291811411871977,0.14083534820411739,0.15927832272629314,0.43225290232332952,0.71222019971640382,null,0.15927832272629314,0.43225290232332952,0.71222019971640382]
["2013-03-27T10:00:00","2013-03-27T10:00:00",null,10.621684876259167,10.925257077915067,11.228829279570967,11.532401481226866,11.835973682882766,12.139545884538666,12.443118086194566,12.746690287850466,13.050262489506366,null,2.2501690694102672E-2,4.498235177073423E-2,6.6138146946684961E-2,8.7525267914818072E-2,0.10829201516755303,0.12836478504374085,0.14884763246061564,0.42377796648246657,0.70560638502173534,null,0.14884763246061564,0.42377796648246657,0.70560638502173534]
["2013-03-27T11:00:00","2013-03-27T11:00:00",null,11.443956259392591,11.747528461048491,12.051100662704391,12.354672864360291,12.658245066016191,12.961817267672091,13.265389469327991,13.56896167098389,13.87253387263979,null,0,0,1.4047784470710825E-2,3.8463170354685793E-2,6.2121490009700298E-2,8.4949139774605359E-2,0.10806068937537064,0.38550406268502091,0.66972985761599779,null,0.10806068937537064,0.38550406268502091,0.66972985761599779]
["2013-03-27T12:00:00","2013-03-27T12:00:00",null,11.236492492339373,11.540064693995273,11.843636895651173,12.147209097307073,12.450781298962973,12.754353500618873,13.057925702274773,13.361497903930672,13.665070105586572,null,0,0,0,4.1428346418114353E-3,3.0387797245774187E-2,5.5665397446065197E-2,8.1121749394860804E-2,0.36080477696518576,0.64716507806948176,null,8.1121749394860804E-2,0.36080477696518576,0.64716507806948176]
["2013-03-27T13:00:00","2013-03-27T13:00:00",null,11.271885806376861,11.575458008032761,11.879030209688661,12.182602411344561,12.486174613000461,12.789746814656361,13.093319016312261,13.396891217968161,13.700463419624061,null,0,0,0,0,3.2280462818175468E-3,3.0850448830138884E-2,5.8535940230873634E-2,0.34035347397451765,0.62875364797351274,null,5.8535940230873634E-2,0.34035347397451765,0.62875364797351274]
["2013-03-27T14:00:00","2013-03-27T14:00:00",null,11.448321388392108,11.751893590048008,12.055465791703908,12.359037993359808,12.662610195015708,12.966182396671607,13.269754598327507,13.573326799983407,13.876899001639307,null,0,0,0,0,0,4.731663931002883E-3,3.464629478367677E-2,0.31859833470063986,0.60903838159433399,null,3.464629478367677E-2,0.31859833470063986,0.60903838159433399]
["2013-03-27T15:00:00","2013-03-27T15:00:00",null,11.448841100996036,11.752413302651936,12.055985504307836,12.359557705963736,12.663129907619636,12.966702109275536,13.270274310931436,13.573846512587336,13.877418714243236,null,0,0,0,0,0,0,1.0840767806364407E-2,0.29692731389664656,0.58940723368503978,null,1.0840767806364407E-2,0.29692731389664656,0.58940723368503978]
["2013-03-27T16:00:00","2013-03-27T16:00:00",null,11.466188762708857,11.769760964364757,12.073333166020657,12.376905367676557,12.680477569332457,12.984049770988356,13.287621972644256,13.591194174300156,13.894766375956056,null,0,0,0,0,0,0,0,0.27723307713493894,0.57171081058308892,null,-1.0935401084984489E-2,0.27723307713493894,0.57171081058308892]
["2013-03-27T17:00:00","2013-03-27T17:00:00",null,11.479274388611486,11.782846590267386,12.086418791923286,12.389990993579186,12.693563195235086,12.997135396890986,13.300707598546886,13.604279800202786,13.907852001858686,null,0,0,0,0,0,0,0,0.25705515917139549,0.55353070627930223,null,-2.227036490192031E-2,0.25705515917139549,0.55353070627930223]
["2013-03-27T18:00:00","2013-03-27T18:00:00",null,11.382431959579739,11.686004161235639,11.989576362891539,12.293148564547439,12.596720766203338,12.900292967859238,13.203865169515138,13.507437371171038,13.811009572826938,null,0,0,0,0,0,0,0,0.23780254437658147,0.53627590514424495,null,-2.1334546924455293E-2,0.23780254437658147,0.53627590514424495]
["2013-03-27T19:00:00","2013-03-27T19:00:00",null,11.269740888198056,11.573313089853956,11.876885291509856,12.180457493165756,12.484029694821656,12.787601896477556,13.091174098133456,13.394746299789356,13.698318501445256,null,0,0,0,0,0,0,0,0.2230187232943813,0.52340577925191711,null,-1.6792149550692512E-2,0.2230187232943813,0.52340577925191711]
["2013-03-27T20:00:00","2013-03-27T20:00:00",null,11.078836391417671,11.382408593073571,11.68598079472947,11.98955299638537,12.29312519804127,12.59669739969717,12.90026960135307,13.20384180300897,13.50741400466487,null,0,0,0,0,0,0,0,0.21307171423053964,0.51529886171679884,null,-1.1860704253713933E-2,0.21307171423053964,0.51529886171679884]
["2013-03-27T21:00:00","2013-03-27T21:00:00",null,10.953512160080264,11.257084361736164,11.560656563392063,11.864228765047963,12.167800966703863,12.471373168359763,12.774945370015663,13.078517571671563,13.382089773327463,null,0,0,0,0,0,0,0,0.20535384461863712,0.50937902439867744,null,-9.6000203755681034E-3,0.20535384461863712,0.50937902439867744]
["2013-03-27T22:00:00","2013-03-27T22:00:00",null,10.844866176697618,11.148438378353518,11.452010580009418,11.755582781665318,12.059154983321218,12.362727184977118,12.666299386633018,12.969871588288918,13.273443789944817,null,0,0,0,0,0,0,0,0.20215734276302627,0.50788592155822765,null,-4.9945341493919486E-3,0.20215734276302627,0.50788592155822765]
["2013-03-27T23:00:00","2013-03-27T23:00:00",null,10.793645639537555,11.097217841193455,11.400790042849355,11.704362244505255,12.007934446161155,12.311506647817055,12.615078849472955,12.918651051128855,13.222223252784755,null,0,0,0,0,0,0,0,0.20109534708073451,0.50849578046489019,null,-2.8074539323950532E-3,0.20109534708073451,0.50849578046489019]
["2013-03-28","2013-03-28",null,10.678175093973216,10.981747295629116,11.285319497285016,11.588891698940916,11.892463900596816,12.196036102252716,12.499608303908616,12.803180505564516,13.106752707220416,null,0,0,0,0,0,0,0,0.20208373910187732,0.51111396784004515,null,-7.2552180275377786E-4,0.20208373910187732,0.51111396784004515]
["2013-03-28T01:00:00","2013-03-28T01:00:00",null,10.606889695522614,10.910461897178514,11.214034098834414,11.517606300490314,11.821178502146214,12.124750703802114,12.428322905458014,12.731895107113914,13.035467308769814,null,0,0,0,0,0,5.888292891914719E-4,2.3237727305592017E-3,0.20605833680391977,0.51665527204368633,null,2.3237727305592017E-3,0.20605833680391977,0.51665527204368633]
["2013-03-28T02:00:00","2013-03-28T02:00:00",null,10.567897798914204,10.871470000570104,11.175042202226004,11.478614403881904,11.782186605537804,12.085758807193704,12.389331008849604,12.692903210505504,12.996475412161404,null,0,0,0,0,5.6779967172034787E-4,2.9336316372217974E-3,6.3614592850150089E-3,0.21170478909491658,0.52384740121881079,null,6.3614592850150089E-3,0.21170478909491658,0.52384740121881079]
["2013-03-28T03:00:00","2013-03-28T03:00:00",null,10.53264637548688,10.83621857714278,11.13979077879868,11.44336298045458,11.74693518211048,12.05050738376638,12.35407958542228,12.65765178707818,12.96122398873408,null,0,0,0,4.1007754068691788E-4,2.8179687411306158E-3,6.9292589567353565E-3,1.2018426384747365E-2,0.21893897750498323,0.5325852072780628,null,1.2018426384747365E-2,0.21893897750498323,0.5325852072780628]
["2013-03-28T04:00:00","2013-03-28T04:00:00",null,10.538182032713419,10.841754234369319,11.145326436025217,11.448898637681117,11.752470839337017,12.056043040992916,12.359615242648816,12.663187444304716,12.966759645960616,null,0,0,0,4.4162196689360387E-4,4.7001195047962135E-3,1.0556867970504246E-2,1.7307375178735047E-2,0.22581566241804077,0.54097602464904126,null,1.7307375178735047E-2,0.22581566241804077,0.54097602464904126]
["2013-03-28T05:00:00","2013-03-28T05:00:00",null,10.515184214135745,10.818756415791645,11.122328617447545,11.425900819103445,11.729473020759345,12.033045222415245,12.336617424071145,12.640189625727045,12.943761827382945,null,0,0,0,0,4.5318825650272213E-3,1.2186663324516355E-2,2.0661599165379324E-2,0.23081019656743271,0.5475267504912964,null,2.0661599165379324E-2,0.23081019656743271,0.5475267504912964]
["2013-03-28T06:00:00","2013-03-28T06:00:00",null,10.507294181571082,10.810866383226982,11.114438584882881,11.418010786538781,11.721582988194681,12.025155189850581,12.328727391506481,12.632299593162381,12.935871794818281,null,0,0,0,0,1.5036176491853661E-3,1.1040549172340097E-2,2.1303002498248607E-2,0.23315499891546304,0.55149083338460325,null,2.1303002498248607E-2,0.23315499891546304,0.55149083338460325]
["2013-03-28T07:00:00","2013-03-28T07:00:00",null,10.577427047338714,10.880999248994614,11.184571450650514,11.488143652306414,11.791715853962314,12.095288055618214,12.398860257274114,12.702432458930014,13.006004660585914,null,0,0,0,0,0,9.9785534900483364E-3,2.2018009492266823E-2,0.23556289011590673,0.55551800513032346,null,2.2018009492266823E-2,0.23556289011590673,0.55551800513032346]
["2013-03-28T08:00:00","2013-03-28T08:00:00",null,10.750242793912932,11.053814995568832,11.35738719722473,11.66095939888063,11.96453160053653,12.26810380219243,12.57167600384833,12.87524820550423,13.17882040716013,null,0,0,0,0,0,7.3288216886867128E-3,2.1166309984686302E-2,0.23641458962348724,0.55799949999191611,null,2.1166309984686302E-2,0.23641458962348724,0.55799949999191611]
["2013-03-28T09:00:00","2013-03-28T09:00:00",null,11.149073794793411,11.452645996449313,11.756218198105213,12.059790399761113,12.363362601417013,12.666934803072913,12.970507004728812,13.274079206384712,13.577651408040612,null,0,0,0,0,0,0,1.5004632065646971E-2,0.23201939957202233,0.55530770895561221,null,1.5004632065646971E-2,0.23201939957202233,0.55530770895561221]
["2013-03-28T10:00:00","2013-03-28T10:00:00",null,11.552355316974699,11.855927518630599,12.159499720286499,12.463071921942399,12.766644123598299,13.070216325254199,13.373788526910099,13.677360728565999,13.980932930221899,null,0,0,0,0,0,0,1.1566289609118204E-3,0.22006406203968834,0.54517143333453044,null,1.1566289609118204E-3,0.22006406203968834,0.54517143333453044]
["2013-03-28T11:00:00","2013-03-28T11:00:00",null,11.742787468653871,12.046359670309771,12.349931871965671,12.653504073621571,12.957076275277471,13.260648476933371,13.564220678589271,13.867792880245171,14.171365081901071,null,0,0,0,0,0,0,0,0.20344014942876482,0.53044018629600809,null,-1.7444067692297352E-2,0.20344014942876482,0.53044018629600809]
["2013-03-28T12:00:00","2013-03-28T12:00:00",null,11.921502160353658,12.225074362009558,12.528646563665458,12.832218765321358,13.135790966977257,13.439363168633157,13.742935370289057,14.046507571944957,14.350079773600857,null,0,0,0,3.1544426206685992E-4,2.7233354625105575E-3,5.0155637668630728E-3,7.2026439838599682E-3,0.21273524035100161,0.54174360568673718,null,7.2026439838599682E-3,0.21273524035100161,0.54174360568673718]
["2013-03-28T13:00:00","2013-03-28T13:00:00",null,12.110753119292868,12.414325320948768,12.717897522604668,13.021469724260568,13.325041925916468,13.628614127572368,13.932186329228267,14.235758530884167,14.539330732540067,null,3.7432719098600714E-2,4.0292747074673577E-2,4.3005567728448574E-2,4.590765493946368E-2,5.0786526192764449E-2,5.5434071653882852E-2,5.9881835749025579E-2,0.26758048271569301,0.5986497505635987,null,5.9881835749025579E-2,0.26758048271569301,0.5986497505635987]
["2013-03-28T14:00:00","2013-03-28T14:00:00",null,12.067428984750768,12.371001186406668,12.674573388062568,12.978145589718467,13.281717791374367,13.585289993030267,13.888862194686167,14.192434396342067,14.496006597997967,null,7.6999944370520518E-2,8.2677941087724E-2,8.8072037969067291E-2,9.352922370282396E-2,0.10084753058277512,0.10782936358318829,0.11450626713027015,0.3243289054615211,0.65744856101286142,null,0.11450626713027015,0.3243289054615211,0.65744856101286142]
["2013-03-28T15:00:00","2013-03-28T15:00:00",null,12.073410521786025,12.376982723441925,12.680554925097825,12.984127126753725,13.287699328409625,13.591271530065525,13.894843731721425,14.198415933377325,14.501988135033224,null,0.11732423587140078,0.12582020132973487,0.13390608924738204,0.14191837350388026,0.15168663081921738,0.16100275135892531,0.16990879435794631,0.38186593886251635,0.71703598211729125,null,0.16990879435794631,0.38186593886251635,0.71703598211729125]
["2013-03-28T16:00:00","2013-03-28T16:00:00",null,12.115092318334957,12.418664519990857,12.722236721646757,13.025808923302657,13.329381124958557,13.632953326614457,13.936525528270357,14.240097729926257,14.543669931582157,null,0.15916265983020197,0.17043453479472442,0.18117015451373322,0.19170599286676632,0.20388214138254712,0.21550100503534314,0.22660464306009659,0.44066474931177901,0.77785363584378187,null,0.22660464306009659,0.44066474931177901,0.77785363584378187]
["2013-03-28T17:00:00","2013-03-28T17:00:00",null,12.141669623005173,12.445241824661073,12.748814026316973,13.052386227972873,13.355958429628773,13.659530631284673,13.963102832940573,14.266675034596473,14.570247236252373,null,0.19986548444556246,0.2139342985337444,0.22734067967158594,0.24041058692988948,0.25501565626358513,0.26895829264694032,0.28227004050616178,0.49845413812242778,0.83768289754912961,null,0.28227004050616178,0.49845413812242778,0.83768289754912961]
["2013-03-28T18:00:00","2013-03-28T18:00:00",null,12.154915091371059,12.458487293026959,12.762059494682859,13.065631696338759,13.369203897994659,13.672776099650559,13.976348301306459,14.279920502962359,14.583492704618259,null,0.24006359824161597,0.25693986626219301,0.27301700881886726,0.28864201459991234,0.30568651956025839,0.3219529286741728,0.3374938159853334,0.55581241977491846,0.89708105209631939,null,0.3374938159853334,0.55581241977491846,0.89708105209631939]
["2013-03-28T19:00:00","2013-03-28T19:00:00",null,12.108540475673824,12.412112677329723,12.715684878985623,13.019257080641523,13.322829282297423,13.626401483953323,13.929973685609223,14.233545887265123,14.537118088921023,null,0.28198614067030164,0.30163831819706705,0.32035467774636739,0.33849272281521176,0.35794511897600151,0.37650375639426847,0.39424223873116149,0.61466380426785894,0.95794076505775227,null,0.39424223873116149,0.61466380426785894,0.95794076505775227]
["2013-03-28T20:00:00","2013-03-28T20:00:00",null,11.984030260192371,12.287602461848271,12.591174663504171,12.894746865160071,13.198319066815971,13.501891268471871,13.805463470127771,14.109035671783671,14.412607873439571,null,0.3259906152286286,0.34839767264411126,0.3697322195685665,0.39036227430773907,0.41219101724276586,0.43302085334791418,0.45293590109306858,0.67542888395067169,1,null,0.45293590109306858,0.67542888395067169,1]
["2013-03-28T21:00:00","2013-03-28T21:00:00",null,11.931218971805642,12.234791173461542,12.538363375117441,12.841935576773341,13.145507778429241,13.449079980085141,13.752652181741041,14.056224383396941,14.359796585052841,null,0.37229783290004365,0.39740719616056575,0.42131787122523368,0.44439787639979217,0.46857142168284927,0.49163039723993673,0.51367995115841025,0.73821280691071234,1,null,0.51367995115841025,0.73821280691071234,1]
["2013-03-28T22:00:00","2013-03-28T22:00:00",null,11.836383912878416,12.139956114534316,12.443528316190216,12.747100517846116,13.050672719502016,13.354244921157916,13.657817122813816,13.961389324469716,14.264961526125616,null,0.42276891483074125,0.45050698027515385,0.47690966501014997,0.50236601695894545,0.52881076092888391,0.55403578708549717,0.57815675832487645,0.80466639811946417,1,null,0.57815675832487645,0.80466639811946417,1]
["2013-03-28T23:00:00","2013-03-28T23:00:00",null,11.743317625379918,12.046889827035818,12.350462028691718,12.654034230347618,12.957606432003518,13.261178633659418,13.564750835315317,13.868323036971217,14.171895238627117,null,0.47716202041980349,0.5074341547694865,0.53625524551366188,0.56401434057554545,0.59265667957121637,0.61997415266620648,0.64609293756534247,0.87451627254980258,1,null,0.64609293756534247,0.87451627254980258,1]
["2013-03-29","2013-03-29",null,11.686973761700655,11.990545963356555,12.294118165012454,12.597690366668354,12.901262568324254,13.204834769980154,13.508406971636054,13.811979173291954,14.115551374947854,null,0.53409970972287169,0.56686385374288295,0.59805077645255977,0.62806004058385356,0.65885791537031468,0.68822577616873937,0.71630031549268991,0.94659528643208013,1,null,0.71630031549268991,0.94659528643208013,1]
["2013-03-29T01:00:00","2013-03-29T01:00:00",null,11.56241105283231,11.86598325448821,12.16955545614411,12.47312765780001,12.77669985945591,13.08027206111181,13.38384426276771,13.68741646442361,13.99098866607951,null,0.52820090202222136,0.56334139281646967,0.59678899940429231,0.62894328451764081,0.66178103219880091,0.69310464742204014,0.7230403078921851,0.9551122815078853,1,null,0.7230403078921851,0.9551122815078853,1]
["2013-03-29T02:00:00","2013-03-29T02:00:00",null,11.508538287545539,11.812110489201439,12.115682690857339,12.419254892513239,12.722827094169139,13.026399295825039,13.329971497480939,13.633543699136839,13.937115900792739,null,0.51239714449267171,0.54994552648736372,0.58568536137953886,0.62001621190114864,0.65492537690321451,0.68821526136000377,0.72004358740254992,0.95391359331203118,1,null,0.72004358740254992,0.95391359331203118,1]
["2013-03-29T03:00:00","2013-03-29T03:00:00",null,11.407877146143957,11.711449347799856,12.015021549455756,12.318593751111656,12.622165952767556,12.925738154423456,13.229310356079356,13.532882557735256,13.836454759391156,null,0.49777104554150498,0.53771680392790511,0.57572783750696166,0.61222473862809723,0.64918429133359767,0.68444044502393697,0.71812989221267765,0.95378741560720448,1,null,0.71812989221267765,0.95378741560720448,1]
["2013-03-29T04:00:00","2013-03-29T04:00:00",null,11.456749097459483,11.760321299115384,12.063893500771284,12.367465702427184,12.671037904083084,12.974610105738984,13.278182307394884,13.581754509050784,13.885326710706684,null,0.48112610331311034,0.52351129732616086,0.56383558882704099,0.60254059978264463,0.64160311423525751,0.67885708158535352,0.71446022396396647,0.95193680926974555,0.99989485191264438,null,0.71446022396396647,0.95193680926974555,0.99989485191264438]
["2013-03-29T05:00:00","2013-03-29T05:00:00",null,11.524833716475422,11.828405918131322,12.131978119787222,12.435550321443122,12.739122523099022,13.042694724754922,13.346266926410822,13.649839128066722,13.953411329722622,null,0.46128465922910483,0.50618289252995474,0.5488835308050718,0.58985974044755685,0.63107779069095993,0.67038214574449051,0.7079515573566536,0.9472997786173627,0.99705585355404269,null,0.7079515573566536,0.9472997786173627,0.99705585355404269]
["2013-03-29T06:00:00","2013-03-29T06:00:00",null,11.533134049876683,11.836706251532583,12.140278453188483,12.443850654844383,12.747422856500283,13.050995058156182,13.354567259812082,13.658139461467982,13.961711663123882,null,0.44104365241314797,0.48845492500179721,0.53354242485988679,0.57678983318925325,0.62017393403218213,0.66153919159788288,0.70107487244359601,0.9423052444679707,0.99385935169843187,null,0.70107487244359601,0.9423052444679707,0.99385935169843187]
["2013-03-29T07:00:00","2013-03-29T07:00:00",null,11.476447763767126,11.780019965423026,12.083592167078926,12.387164368734826,12.690736570390726,12.994308772046626,13.297880973702526,13.601453175358426,13.905025377014326,null,0.42004557936823067,0.47000143567088593,0.51749682672941921,0.56304697817187377,0.60861815923179952,0.65207586373587711,0.69359884343261147,0.93673239583812284,0.99010556497983626,null,0.69359884343261147,0.93673239583812284,0.99010556497983626]
["2013-03-29T08:00:00","2013-03-29T08:00:00",null,11.592044732005652,11.895616933661552,12.199189135317452,12.502761336973352,12.806333538629252,13.109905740285152,13.413477941941052,13.717050143596952,14.020622345252852,null,0.39721792960332558,0.44974991404619352,0.4996847407313772,0.54755866490439098,0.59533795579878468,0.64090913685871032,0.68445095983267257,0.92950872223679171,0.98472198290722857,null,0.68445095983267257,0.92950872223679171,0.98472198290722857]
["2013-03-29T10:00:00","2013-03-29T10:00:00",null,11.810792300968728,12.114364502624628,12.417936704280528,12.721508905936428,13.025081107592328,13.328653309248228,13.632225510904128,13.935797712560028,14.239369914215928,null,0.36479025946285237,0.42008763860317311,0.47265116747224728,0.5230276161243248,0.57319376860169113,0.62103614834849818,0.66675453673072171,0.9138942312644821,0.97109479078594019,null,0.66675453673072171,0.9138942312644821,0.97109479078594019]
["2013-03-29T11:00:00","2013-03-29T11:00:00",null,11.935820995589417,12.239393197245317,12.542965398901217,12.846537600557117,13.150109802213017,13.453682003868916,13.757254205524816,14.060826407180716,14.364398608836616,null,0.3301649942966467,0.38824879775189136,0.44346205842232717,0.49636206117093956,0.54894661965748515,0.59908122770864469,0.64700772592533629,0.89625038220620912,0.9554697850048951,null,0.64700772592533629,0.89625038220620912,0.9554697850048951]
["2013-03-29T12:00:00","2013-03-29T12:00:00",null,12.219147105803264,12.522719307459164,12.826291509115064,13.129863710770964,13.433435912426864,13.737008114082764,14.040580315738664,14.344152517394564,14.647724719050464,null,0.29306874907758396,0.35393897684775255,0.41180196931954999,0.46723604097343285,0.52223900546915769,0.57467635663340533,0.62482147949330047,0.87617761233002123,0.93742637321467071,null,0.62482147949330047,0.87617761233002123,0.93742637321467071]
["2013-03-29T13:00:00","2013-03-29T13:00:00",null,12.314584534530569,12.618156736186469,12.921728937842369,13.225301139498269,13.528873341154169,13.832445542810069,14.136017744465969,14.439589946121869,14.743162147777769,null,0.25212408386130553,0.31584382479881146,0.37643015273311942,0.4344613821446861,0.4919458415020036,0.54675953944048827,0.59917586098726472,0.85270855923224687,0.91603925224653759,null,0.59917586098726472,0.85270855923224687,0.91603925224653759]
["2013-03-29T14:00:00","2013-03-29T14:00:00",null,12.496636097230148,12.800208298886048,13.103780500541948,13.407352702197848,13.710924903853748,14.014497105509648,14.318069307165548,14.621641508821448,14.925213710477347,null,0.20694195072459562,0.27358480849058781,0.3369470459310841,0.39763852195274796,0.45765705021533593,0.51489966897173545,0.56965027805780666,0.82541211575472795,0.89087731494233768,null,0.56965027805780666,0.82541211575472795,0.89087731494233768]
["2013-03-29T15:00:00","2013-03-29T15:00:00",null,12.533821192003648,12.837393393659548,13.140965595315448,13.444537796971348,13.748109998627248,14.051682200283148,14.355254401939048,14.658826603594948,14.962398805250848,null,0.15731205349274299,0.22697266136584146,0.2932054415911462,0.35664128269279172,0.41928851313927018,0.47904417118346904,0.53619215666124842,0.7942567374712578,0.86194056130207108,null,0.53619215666124842,0.7942567374712578,0.86194056130207108]
["2013-03-29T16:00:00","2013-03-29T16:00:00",null,12.604551386967904,12.908123588623804,13.211695790279704,13.515267991935604,13.818840193591504,14.122412395247403,14.425984596903303,14.729556798559203,15.033129000215103,null,0.10492727637217311,0.17764769358732013,0.2468035906411111,0.31303637086641611,0.37834384792299175,0.44065460448993221,0.50025254040309752,0.76066192356113727,0.83059591646136077,null,0.50025254040309752,0.76066192356113727,0.83059591646136077]
["2013-03-29T17:00:00","2013-03-29T17:00:00",null,12.547142676052376,12.850714877708276,13.154287079364176,13.457859281020076,13.761431482675976,14.065003684331876,14.368575885987775,14.672148087643675,14.975720289299575,null,5.4677005424922327E-2,0.13041517274717562,0.20246264220324617,0.27145030231726841,0.33938648155773454,0.40421027741247434,0.4662266193348189,0.72894926041468233,0.80110187795810939,null,0.4662266193348189,0.72894926041468233,0.80110187795810939]
["2013-03-29T18:00:00","2013-03-29T18:00:00",null,12.572611477905841,12.876183679561741,13.179755881217641,13.483328082873541,13.786900284529441,14.090472486185341,14.394044687841241,14.697616889497141,15.001189091153041,null,6.4455777548994425E-3,8.514892114058123E-2,0.16003538895525352,0.23172535491431517,0.30224817710372959,0.36955346782006199,0.43393564170790799,0.69892948147465284,0.77326917923507676,null,0.43393564170790799,0.69892948147465284,0.77326917923507676]
["2013-03-29T19:00:00","2013-03-29T19:00:00",null,12.493404002749154,12.796976204405054,13.100548406060954,13.404120607716854,13.707692809372753,14.011265011028653,14.314837212684553,14.618409414340453,14.921981615996353,null,0,3.9987817621342452E-2,0.11772379860335204,0.19212658521618869,0.26525707997202247,0.33504386554994753,0.40180238621203052,0.66907793947439231,0.74561523226054871,null,0.40180238621203052,0.66907793947439231,0.74561523226054871]
["2013-03-29T20:00:00","2013-03-29T20:00:00",null,12.323481821620049,12.627054023275949,12.930626224931849,13.234198426587749,13.537770628243649,13.841342829899549,14.144915031555449,14.448487233211349,14.752059434867249,null,0,0,7.9092391308897253E-2,0.15616593934056666,0.23185153261914199,0.30407775382371743,0.37317056202509519,0.64268576954813172,0.72136808331634272,null,0.37317056202509519,0.64268576954813172,0.72136808331634272]
["2013-03-29T21:00:00","2013-03-29T21:00:00",null,12.333908318138326,12.637480519794225,12.941052721450125,13.244624923106025,13.548197124761925,13.851769326417825,14.155341528073725,14.458913729729625,14.762485931385525,null,0,0,4.2900419641092855E-2,0.12258164023918164,0.20075924318808516,0.27537232597563316,0.34674684767262787,0.61844913541266133,0.69923441092798466,null,0.34674684767262787,0.61844913541266133,0.69923441092798466]
["2013-03-29T22:00:00","2013-03-29T22:00:00",null,12.164859884365182,12.468432086021082,12.772004287676982,13.075576489332882,13.379148690988782,13.682720892644681,13.986293094300581,14.289865295956481,14.593437497612381,null,0,0,1.0514808735561904E-2,9.2751127856392251E-2,0.17336816643194616,0.25031553675878893,0.32392971271645832,0.5977665066298109,0.68060216984856881,null,0.32392971271645832,0.5977665066298109,0.68060216984856881]
["2013-03-29T23:00:00","2013-03-29T23:00:00",null,12.035914669257288,12.339486870913188,12.643059072569088,12.946631274224988,13.250203475880888,13.553775677536787,13.857347879192687,14.160920080848587,14.464492282504487,null,0,0,0,6.7936179240465938E-2,0.15090853497278572,0.2300955595603032,0.30586527130876279,0.58175245292555,0.66655438537785794,null,0.30586527130876279,0.58175245292555,0.66655438537785794]
["2013-03-30","2013-03-30",null,11.963205831237712,12.266778032893612,12.570350234549512,12.873922436205412,13.177494637861312,13.481066839517212,13.784639041173111,14.088211242829011,14.391783444484911,null,0,0,0,4.6117951114174792E-2,0.13139304995958265,0.21276715476409702,0.290639828259669,0.56853533834494852,0.65525096598712884,null,0.290639828259669,0.56853533834494852,0.65525096598712884]
["2013-03-30T01:00:00","2013-03-30T01:00:00",null,11.707511959876607,12.011084161532507,12.314656363188407,12.618228564844307,12.921800766500207,13.225372968156107,13.528945169812006,13.832517371467906,14.136089573123806,null,0,0,0,2.5782311019597888E-2,0.11336015297809382,0.19693185280834066,0.27690748805102505,0.55681132660479693,0.64545116424558502,null,0.27690748805102505,0.55681132660479693,0.64545116424558502]
["2013-03-30T02:00:00","2013-03-30T02:00:00",null,11.455048680323266,11.758620881979166,12.062193083635066,12.365765285290966,12.669337486946866,12.972909688602765,13.276481890258665,13.580054091914565,13.883626293570465,null,0,0,0,1.2964759170947813E-2,0.10270865172896952,0.18835176888012206,0.27030418816509211,0.55209017748252964,0.64252804741709879,null,0.27030418816509211,0.55209017748252964,0.64252804741709879]
["2013-03-30T03:00:00","2013-03-30T03:00:00",null,11.244779328240188,11.548351529896088,11.851923731551988,12.155495933207888,12.459068134863788,12.762640336519688,13.066212538175588,13.369784739831488,13.673356941487388,null,0,0,0,3.1123833857262199E-3,9.4990782117067019E-2,0.18267377216291858,0.26656091625523204,0.55019751191012845,0.64240186971227209,null,0.26656091625523204,0.55019751191012845,0.64240186971227209]
["2013-03-30T04:00:00","2013-03-30T04:00:00",null,11.231616006468116,11.535188208124016,11.838760409779916,12.142332611435815,12.445904813091715,12.749477014747615,13.053049216403515,13.356621418059415,13.660193619715315,null,0,0,0,0,8.7914315838033788E-2,0.17761614916111326,0.26342750325203457,0.5489041904356543,0.64287503610537233,null,0.26342750325203457,0.5489041904356543,0.64287503610537233]
["2013-03-30T05:00:00","2013-03-30T05:00:00",null,11.276726660386018,11.580298862041918,11.883871063697818,12.187443265353718,12.491015467009618,12.794587668665518,13.098159870321417,13.401732071977317,13.705304273633217,null,0,0,0,0,7.5916919070757552E-2,0.16774274375842055,0.25559397074404089,0.54300538273500398,0.63883734955091653,null,0.25559397074404089,0.54300538273500398,0.63883734955091653]
["2013-03-30T06:00:00","2013-03-30T06:00:00",null,11.223921741950498,11.527493943606398,11.831066145262298,12.134638346918198,12.438210548574098,12.741782750229998,13.045354951885898,13.348927153541798,13.652499355197698,null,0,0,0,0,6.2994219134751853E-2,0.15697557961320507,0.24688770911099556,0.5362653903355088,0.63397950791508684,null,0.24688770911099556,0.5362653903355088,0.63397950791508684]
["2013-03-30T07:00:00","2013-03-30T07:00:00",null,11.341744919234859,11.645317120890759,11.948889322546659,12.252461524202559,12.556033725858459,12.859605927514359,13.163178129170259,13.466750330826159,13.770322532482059,null,0,0,0,0,5.112300007230236E-2,0.14721783710660355,0.23914880988162193,0.53045070110474302,0.63000491021304439,null,0.23914880988162193,0.53045070110474302,0.63000491021304439]
["2013-03-30T08:00:00","2013-03-30T08:00:00",null,11.691360563013752,11.994932764669652,12.298504966325552,12.602077167981452,12.905649369637352,13.209221571293252,13.512793772949152,13.816365974605052,14.119938176260952,null,0,0,0,0,3.6665138060904615E-2,0.13487345165105377,0.22883378251203562,0.52207039854250015,0.62347521398826034,null,0.22883378251203562,0.52207039854250015,0.62347521398826034]
["2013-03-30T09:00:00","2013-03-30T09:00:00",null,12.068788932055195,12.372361133711095,12.675933335366995,12.979505537022895,13.283077738678795,13.586649940334695,13.890222141990595,14.193794343646495,14.497366545302395,null,0,0,0,0,1.5824787147020736E-2,0.11624121057163792,0.21231501798846772,0.50755996248742463,0.61089950274052818,null,0.21231501798846772,0.50755996248742463,0.61089950274052818]
["2013-03-30T10:00:00","2013-03-30T10:00:00",null,12.450535002074849,12.754107203730749,13.057679405386649,13.361251607042549,13.664823808698449,13.968396010354349,14.271968212010249,14.575540413666149,14.879112615322049,null,0,0,0,0,0,8.8702926493201051E-2,0.18701638817070554,0.48441686846045268,0.58981731122572634,null,0.18701638817070554,0.48441686846045268,0.58981731122572634]
["2013-03-30T11:00:00","2013-03-30T11:00:00",null,12.630449197654951,12.934021399310851,13.237593600966751,13.54116580262265,13.84473800427855,14.14831020593445,14.45188240759035,14.75545460924625,15.05902681090215,null,0,0,0,0,0,5.7358281652490739E-2,0.15797448644308329,0.45757256175856287,0.56507596627094892,null,0.15797448644308329,0.45757256175856287,0.56507596627094892]
["2013-03-30T12:00:00","2013-03-30T12:00:00",null,12.869719016048599,13.173291217704499,13.476863419360399,13.780435621016299,14.084007822672199,14.387580024328098,14.691152225983998,14.994724427639898,15.298296629295798,null,0,0,0,0,0,2.0114829111130141E-2,0.12310738067595971,0.42498716948705623,0.5346776542164392,null,0.12310738067595971,0.42498716948705623,0.5346776542164392]
["2013-03-30T13:00:00","2013-03-30T13:00:00",null,12.891575938408636,13.195148140064536,13.498720341720436,13.802292543376335,14.105864745032235,14.409436946688135,14.713009148344035,15.016581349999935,15.320153551655835,null,0,0,0,0,0,0,8.4938624965869652E-2,0.38915270131626095,0.50110386992378975,null,8.4938624965869652E-2,0.38915270131626095,0.50110386992378975]
["2013-03-30T14:00:00","2013-03-30T14:00:00",null,13.022827653930751,13.326399855586651,13.629972057242551,13.933544258898451,14.237116460554351,14.54068866221025,14.84426086386615,15.14783306552205,15.45140526717795,null,0,0,0,0,0,0,4.4887718492114002E-2,0.35145711199927121,0.46567947929368136,null,4.4887718492114002E-2,0.35145711199927121,0.46567947929368136]
["2013-03-30T15:00:00","2013-03-30T15:00:00",null,13.055450316411779,13.359022518067679,13.662594719723579,13.966166921379479,14.269739123035379,14.573311324691279,14.876883526347179,15.180455728003079,15.484027929658978,null,0,0,0,0,0,0,3.8379051884799634E-3,0.31278364546987419,0.4292877262599013,null,3.8379051884799634E-3,0.31278364546987419,0.4292877262599013]
["2013-03-30T16:00:00","2013-03-30T16:00:00",null,12.81601946819713,13.11959166985303,13.42316387150893,13.72673607316483,14.03030827482073,14.333880476476629,14.637452678132529,14.941024879788429,15.244597081444329,null,0,0,0,0,0,0,0,0.30112272258213596,0.41978233916295327,null,-1.0073186768668559E-2,0.30112272258213596,0.41978233916295327]
["2013-03-30T17:00:00","2013-03-30T17:00:00",null,13.308099191725031,13.611671393380931,13.915243595036831,14.218815796692731,14.522387998348631,14.825960200004531,15.12953240166043,15.43310460331633,15.73667680497223,null,1.3700795782437283E-2,1.6865753211841444E-2,1.9883503318947737E-2,2.2785590529962849E-2,2.5561500036151215E-2,2.8221746646248401E-2,3.0776845168989968E-2,0.33434951818651187,0.45537496673283062,null,3.0776845168989968E-2,0.33434951818651187,0.45537496673283062]
["2013-03-30T18:00:00","2013-03-30T18:00:00",null,13.139377871198228,13.442950072854128,13.746522274510028,14.050094476165928,14.353666677821828,14.657238879477728,14.960811081133627,15.264383282789527,15.567955484445427,null,3.0745300742783283E-2,3.7043671175384915E-2,4.3047626963390817E-2,4.8809742150478792E-2,5.4330016736648841E-2,5.9618965530636524E-2,6.4697618149912969E-2,0.37068869717661412,0.4940379184534921,null,6.4697618149912969E-2,0.37068869717661412,0.4940379184534921]
["2013-03-30T19:00:00","2013-03-30T19:00:00",null,12.941430992628488,13.245003194284388,13.548575395940288,13.852147597596188,14.155719799252088,14.459292000907988,14.762864202563888,15.066436404219788,15.370008605875688,null,4.9177760456223463E-2,5.8609543892022574E-2,6.7620734978399211E-2,7.6253392950295609E-2,8.4518032616447331E-2,9.2435683594325524E-2,0.10003789031013685,0.40844737534601727,0.53413088416219001,null,0.10003789031013685,0.40844737534601727,0.53413088416219001]
["2013-03-30T20:00:00","2013-03-30T20:00:00",null,12.583500967587735,12.887073169243635,13.190645370899535,13.494217572555435,13.797789774211335,14.101361975867235,14.404934177523135,14.708506379179035,15.012078580834935,null,7.068054432044775E-2,8.309853343714646E-2,9.4948722882124845E-2,0.10629420150779624,0.11715599893163177,0.12755514477110258,0.13753369826115094,0.44822489679264832,0.57609548582581793,null,0.13753369826115094,0.44822489679264832,0.57609548582581793]
["2013-03-30T21:00:00","2013-03-30T21:00:00",null,12.658072025474574,12.961644227130474,13.265216428786374,13.568788630442274,13.872360832098174,14.175933033754074,14.479505235409974,14.783077437065874,15.086649638721774,null,9.3960330860982016E-2,0.10940658489352258,0.12414834674078051,0.1382592200639047,0.1517602344803663,0.164682934416372,0.17707989391559961,0.49009486517765621,0.62019459366276497,null,0.17707989391559961,0.49009486517765621,0.62019459366276497]
["2013-03-30T22:00:00","2013-03-30T22:00:00",null,12.464230398709866,12.767802600365766,13.071374802021666,13.374947003677566,13.678519205333465,13.982091406989365,14.285663608645265,14.589235810301165,14.892808011957065,null,0.12384341728744921,0.14218124372226931,0.15967788545824452,0.17642797577399477,0.19244202947825567,0.20777262061470506,0.2224828380357563,0.53770591913228094,0.66992963898197322,null,0.2224828380357563,0.53770591913228094,0.66992963898197322]
["2013-03-30T23:00:00","2013-03-30T23:00:00",null,12.234526363813711,12.53809856546961,12.84167076712551,13.14524296878141,13.44881517043731,13.75238737209321,14.05595957374911,14.35953177540501,14.66310397706091,null,0.15669167977734488,0.17790004899697343,0.19813054100419475,0.21748830388636436,0.23599436726095346,0.2537118199803754,0.27069323608830809,0.5881033974018296,0.72241956418989872,null,0.27069323608830809,0.5881033974018296,0.72241956418989872]
["2013-03-31","2013-03-31",null,12.146760207555776,12.450332409211676,12.753904610867576,13.057476812523475,13.361049014179375,13.664621215835275,13.968193417491175,14.271765619147075,14.575337820802975,null,0.19299931434124046,0.2170046226845285,0.23990587611058256,0.26180822270675819,0.28274320689926213,0.30278443234924324,0.32198447310037953,0.6415291405872201,0.77787466546125272,null,0.32198447310037953,0.6415291405872201,0.77787466546125272]
["2013-03-31T01:00:00","2013-03-31T01:00:00",null,12.097265567941042,12.400837769596942,12.704409971252842,13.007982172908742,13.311554374564642,13.615126576220542,13.918698777876441,14.222270979532341,14.525843181188241,null,0.23446971999429697,0.26116681937388886,0.2866231713226845,0.31096495354551051,0.33423422527730923,0.35649407537049393,0.37782862229494929,0.6994131626764889,0.83770392716660047,null,0.37782862229494929,0.6994131626764889,0.83770392716660047]
["2013-03-31T02:00:00","2013-03-31T02:00:00",null,11.969518479690379,12.273090681346279,12.576662883002179,12.880235084658079,13.183807286313979,13.487379487969879,13.790951689625778,14.094523891281678,14.398096092937578,null,0.27816926509929263,0.30752661108898172,0.33551703194304777,0.3622667053663175,0.3878387202112043,0.41229616533012148,0.43573367400168922,0.75932654285172119,0.89954151734044063,null,0.43573367400168922,0.75932654285172119,0.89954151734044063]
["2013-03-31T03:00:00","2013-03-31T03:00:00",null,12.032598835538682,12.336171037194582,12.639743238850482,12.943315440506382,13.246887642162282,13.550459843818182,13.854032045474082,14.157604247129981,14.461176448785881,null,0.32232094697991748,0.3543175099622326,0.3848104552953624,0.4139575051103403,0.44181123345084405,0.46844524397802256,0.49396468477923156,0.81955536728902034,0.96167352215887647,null,0.49396468477923156,0.81955536728902034,0.96167352215887647]
["2013-03-31T04:00:00","2013-03-31T04:00:00",null,12.127767232155385,12.431339433811285,12.734911635467185,13.038483837123085,13.342056038778985,13.645628240434885,13.949200442090785,14.252772643746685,14.556344845402585,null,0.36562092935296175,0.40024619451916743,0.4332521791400965,0.46479660534678258,0.49493204718290329,0.52375313792707867,0.55136502566666445,0.87895352183621012,1,null,0.55136502566666445,0.87895352183621012,1]
["2013-03-31T05:00:00","2013-03-31T05:00:00",null,12.252030044241101,12.555602245897001,12.859174447552901,13.162746649208801,13.466318850864701,13.769891052520601,14.073463254176501,14.377035455832401,14.6806076574883,null,0.40377917025431626,0.44114880050050359,0.47675194287911649,0.5107883787561307,0.54330016736648845,0.57439245679754525,0.60417039513665682,0.93384082343584374,1,null,0.60417039513665682,0.93384082343584374,1]
["2013-03-31T06:00:00","2013-03-31T06:00:00",null,12.311297739629042,12.614869941284942,12.918442142940842,13.222014344596742,13.525586546252642,13.829158747908542,14.132730949564442,14.436303151220342,14.739875352876242,null,0.43964518285131821,0.47979072260369393,0.5180435967836684,0.55461410156595314,0.58954429618549009,0.62293932872963498,0.6549358917119501,0.98671979656698505,1,null,0.6549358917119501,0.98671979656698505,1]
["2013-03-31T07:00:00","2013-03-31T07:00:00",null,12.365575299097664,12.669147500753564,12.972719702409464,13.276291904065364,13.579864105721263,13.883436307377163,14.187008509033063,14.490580710688963,14.794152912344863,null,0.47326102637890993,0.51622453487241626,0.55716920008869464,0.59630531820245647,0.63369597806611488,0.66943581295829013,0.70367203020128,1,1,null,0.70367203020128,1,1]
["2013-03-31T08:00:00","2013-03-31T08:00:00",null,11.936096884841472,12.239669086497372,12.543241288153272,12.846813489809172,13.150385691465072,13.453957893120972,13.757530094776872,14.061102296432772,14.364674498088672,null,0.4656377900456275,0.51138772285405776,0.55499263468043325,0.59665230689073001,0.63645085795483214,0.67449343596009548,0.71093776303755329,1,1,null,0.71093776303755329,1,1]
["2013-03-31T09:00:00","2013-03-31T09:00:00",null,11.984754166958806,12.288326368614706,12.591898570270606,12.895470771926506,13.199042973582406,13.502615175238306,13.806187376894206,14.109759578550106,14.413331780206006,null,0.42793168591990216,0.47642598380831414,0.52264908300984458,0.56680076489046949,0.60898617753754425,0.64929995422968889,0.6879208467154081,0.97905450099876046,0.98105231465851728,null,0.6879208467154081,0.97905450099876046,0.98105231465851728]
["2013-03-31T10:00:00","2013-03-31T10:00:00",null,11.845278988505838,12.148851190161738,12.452423391817637,12.755995593473537,13.059567795129437,13.363139996785337,13.666712198441237,13.970284400097137,14.273856601753037,null,0.3910667664930218,0.44235800350509324,0.49123083450798533,0.53791658529388064,0.58250988914139912,0.62512640894663185,0.66594489645808352,0.95918151248854833,0.96319816942553305,null,0.66594489645808352,0.95918151248854833,0.96319816942553305]
["2013-03-31T11:00:00","2013-03-31T11:00:00",null,12.16594075890149,12.46951296055739,12.77308516221329,13.07665736386919,13.38022956552509,13.68380176718099,13.98737396883689,14.29094617049279,14.59451837214869,null,0.35095277116685275,0.40506197692005486,0.45661608415051524,0.50586744826788765,0.55290018774205651,0.59785099508658401,0.64090913685871043,0.93628025906249435,0.94234730370291364,null,0.64090913685871043,0.93628025906249435,0.94234730370291364]
["2013-03-31T12:00:00","2013-03-31T12:00:00",null,12.057867991318144,12.361440192974044,12.665012394629944,12.968584596285844,13.272156797941744,13.575728999597644,13.879301201253543,14.182873402909443,14.486445604565343,null,0.30517129393221581,0.3620038351479285,0.41616561494480825,0.46789847392377326,0.51729704536344356,0.56450853658611688,0.60972221414903349,0.90716475367372318,0.9152190971651637,null,0.60972221414903349,0.90716475367372318,0.9152190971651637]
["2013-03-31T13:00:00","2013-03-31T13:00:00",null,12.269749917060093,12.573322118715993,12.876894320371893,13.180466522027793,13.484038723683692,13.787610925339592,14.091183126995492,14.394755328651392,14.698327530307292,null,0.25927415380148772,0.31900878222821549,0.37593595672254804,0.43029751788540355,0.48220912861287318,0.53182851103599016,0.57934493171199486,0.87898506626241701,0.88915288630970546,null,0.57934493171199486,0.87898506626241701,0.88915288630970546]
["2013-03-31T14:00:00","2013-03-31T14:00:00",null,12.429645173326033,12.733217374981933,13.036789576637833,13.340361778293733,13.643933979949633,13.947506181605533,14.251078383261433,14.554650584917333,14.858222786573233,null,0.2053226701793191,0.26807504871315319,0.32787276599229415,0.38497869223513131,0.43950849033775591,0.49163039723993662,0.54155470911638504,0.84348707197115969,0.85586300185291619,null,0.54155470911638504,0.84348707197115969,0.85586300185291619]
["2013-03-31T15:00:00","2013-03-31T15:00:00",null,12.46344328175681,12.76701548341271,13.07058768506861,13.37415988672451,13.677732088380409,13.981304290036309,14.284876491692209,14.588448693348109,14.892020895004009,null,0.14899483978291347,0.21478599804132498,0.27747528772274549,0.33734660866303545,0.39451562375828614,0.44917159956573727,0.50151431745136499,0.80575993822796321,0.82036500756165887,null,0.50151431745136499,0.80575993822796321,0.82036500756165887]
["2013-03-31T16:00:00","2013-03-31T16:00:00",null,12.525889056661226,12.829461258317126,13.133033459973026,13.436605661628926,13.740177863284826,14.043750064940726,14.347322266596626,14.650894468252526,14.954466669908426,null,9.0332721847213082E-2,0.15920471906514427,0.22482764038378655,0.28750641525647158,0.34735670657929058,0.40457829571821885,0.4593709640392325,0.76597190197259657,0.78283765518443804,null,0.4593709640392325,0.76597190197259657,0.78283765518443804]
["2013-03-31T17:00:00","2013-03-31T17:00:00",null,12.528317656347232,12.831889858003132,13.135462059659032,13.439034261314932,13.742606462970832,14.046178664626732,14.349750866282632,14.653323067938532,14.956895269594431,null,3.1544426206685953E-2,0.10349726238413681,0.17206433014873646,0.23755055895381652,0.30008212650420385,0.35986932897460921,0.41712246253974439,0.7260787176298743,0.74520515471986171,null,0.41712246253974439,0.7260787176298743,0.74520515471986171]
["2013-03-31T18:00:00","2013-03-31T18:00:00",null,12.368645483020565,12.672217684676465,12.975789886332365,13.279362087988265,13.582934289644164,13.886506491300064,14.190078692955964,14.493650894611864,14.797223096267764,null,0,4.8073705538989521E-2,0.11960594936701766,0.18793117653069946,0.25316504992612621,0.31553889534547985,0.37527352377220763,0.68660612563657453,0.70800376141344334,null,0.37527352377220763,0.68660612563657453,0.70800376141344334]
["2013-03-31T19:00:00","2013-03-31T19:00:00",null,12.219231355407464,12.522803557063364,12.826375758719264,13.129947960375164,13.433520162031064,13.737092363686964,14.040664565342864,14.344236766998764,14.647808968654664,null,0,0,6.9944507708958339E-2,0.14106667399629963,0.20898182361929468,0.27391076756138988,0.33608483161476804,0.6497622358271653,0.67341004067344434,null,0.33608483161476804,0.6497622358271653,0.67341004067344434]
["2013-03-31T20:00:00","2013-03-31T20:00:00",null,11.994837815294469,12.298410016950369,12.601982218606269,12.905554420262169,13.209126621918069,13.512698823573968,13.816271025229868,14.119843226885768,14.423415428541668,null,0,0,2.6192388560284864E-2,0.10002737550140114,0.17052916807334445,0.23792909206829671,0.30246898808717632,0.61840707617771939,0.64422093162352423,null,0.30246898808717632,0.61840707617771939,0.64422093162352423]
["2013-03-31T21:00:00","2013-03-31T21:00:00",null,11.804080000404099,12.107652202059999,12.411224403715899,12.714796605371799,13.018368807027699,13.321941008683599,13.625513210339498,13.929085411995398,14.232657613651298,null,0,0,0,6.3551503997736569E-2,0.13656633585747918,0.20637415105287515,0.27320627537610725,0.5913419584923828,0.61925877568530008,null,0.27320627537610725,0.5913419584923828,0.61925877568530008]
["2013-03-31T22:00:00","2013-03-31T22:00:00",null,11.582229119893057,11.885801321548957,12.189373523204857,12.492945724860757,12.796517926516657,13.100090128172557,13.403662329828457,13.707234531484357,14.010806733140257,null,0,0,0,3.3121647517020153E-2,0.10855488538594202,0.18066544369442608,0.24970567785212619,0.5699443227155141,0.59986946837692379,null,0.24970567785212619,0.5699443227155141,0.59986946837692379]
["2013-03-31T23:00:00","2013-03-31T23:00:00",null,11.432623067621179,11.736195269277079,12.039767470932979,12.343339672588879,12.646911874244779,12.950484075900679,13.254056277556579,13.557628479212479,13.861200680868379,null,0,0,0,5.9198373181212662E-3,8.3718907152544583E-2,0.15809014933917448,0.22928591928766479,0.55158546666322283,0.58347688155818267,null,0.22928591928766479,0.55158546666322283,0.58347688155818267]
["2013-04-01","2013-04-01",null,11.409557983243605,11.713130184899505,12.016702386555405,12.320274588211305,12.623846789867205,12.927418991523105,13.230991193179005,13.534563394834905,13.838135596490805,null,0,0,0,0,6.2752378533833961E-2,0.13930018612872519,0.21256737339812121,0.53684370481596488,0.57062778528332592,null,0.21256737339812121,0.53684370481596488,0.57062778528332592]
["2013-04-01T01:00:00","2013-04-01T01:00:00",null,11.264375442313483,11.567947643969383,11.871519845625283,12.175092047281183,12.478664248937083,12.782236450592983,13.085808652248883,13.389380853904782,13.692953055560682,null,0,0,0,0,4.491926291832081E-2,0.12359106187779556,0.19887709242441948,0.52508814864960662,0.56071232064569099,null,0.19887709242441948,0.52508814864960662,0.56071232064569099]
["2013-04-01T02:00:00","2013-04-01T02:00:00",null,11.15436342696503,11.45793562862093,11.76150783027683,12.06508003193273,12.36865223358863,12.67222443524453,12.97579663690043,13.27936883855633,13.58294104021223,null,0,0,0,0,2.8694913039348648E-2,0.1094696737459358,0.18676403276105205,0.51487826936737591,0.55233201808344812,null,0.18676403276105205,0.51487826936737591,0.55233201808344812]
["2013-04-01T03:00:00","2013-04-01T03:00:00",null,11.13122613142275,11.43479833307865,11.73837053473455,12.04194273639045,12.34551493804635,12.64908713970225,12.952659341358149,13.256231543014049,13.559803744669949,null,0,0,0,0,1.3532558842668248E-2,9.638925167889667E-2,0.17566039473629858,0.50566729691502355,0.54492959273361252,null,0.17566039473629858,0.50566729691502355,0.54492959273361252]
["2013-04-01T04:00:00","2013-04-01T04:00:00",null,10.938137015575551,11.241709217231451,11.545281418887351,11.848853620543251,12.152425822199151,12.455998023855051,12.75957022551095,13.06314242716685,13.36671462882275,null,0,0,0,0,0,8.2446615295541467E-2,0.16374711643890683,0.49568874342497521,0.53680164558102306,null,0.16374711643890683,0.49568874342497521,0.53680164558102306]
["2013-04-01T05:00:00","2013-04-01T05:00:00",null,11.104113286671325,11.407685488327225,11.711257689983125,12.014829891639025,12.318402093294925,12.621974294950824,12.925546496606724,13.229118698262624,13.532690899918524,null,0,0,0,0,0,6.7410438803687814E-2,0.15074029803301664,0.48461664982642844,0.52758015831993521,null,0.15074029803301664,0.48461664982642844,0.52758015831993521]
["2013-04-01T06:00:00","2013-04-01T06:00:00",null,11.095374307311525,11.398946508967425,11.702518710623325,12.006090912279225,12.309663113935125,12.613235315591025,12.916807517246925,13.220379718902825,13.523951920558725,null,0,0,0,0,0,4.9871737832770401E-2,0.13530455880921163,0.47116820945364463,0.51604541313702368,null,0.13530455880921163,0.47116820945364463,0.51604541313702368]
["2013-04-01T07:00:00","2013-04-01T07:00:00",null,11.031063919821543,11.334636121477443,11.638208323133343,11.941780524789243,12.245352726445143,12.548924928101043,12.852497129756943,13.156069331412843,13.459641533068742,null,0,0,0,0,0,3.1986048173579446E-2,0.11953234570586864,0.45741483962752955,0.50420573850078088,null,0.11953234570586864,0.45741483962752955,0.50420573850078088]
["2013-04-01T08:00:00","2013-04-01T08:00:00",null,11.495390100446514,11.798962302102414,12.102534503758314,12.406106705414214,12.709678907070113,13.013251108726013,13.316823310381913,13.620395512037813,13.923967713693713,null,0,0,0,0,0,1.2617770482674245E-2,0.10223548533586915,0.44209476329981573,0.4907783277454682,null,0.10223548533586915,0.44209476329981573,0.4907783277454682]
["2013-04-01T09:00:00","2013-04-01T09:00:00",null,11.76396401698431,12.06753621864021,12.37110842029611,12.67468062195201,12.97825282360791,13.28182502526381,13.58539722691971,13.88896942857561,14.19254163023151,null,0,0,0,0,0,0,8.0038724095097769E-2,0.42194838976247895,0.47259822344168151,null,8.0038724095097769E-2,0.42194838976247895,0.47259822344168151]
["2013-04-01T10:00:00","2013-04-01T10:00:00",null,11.98849685548727,12.29206905714317,12.59564125879907,12.89921346045497,13.20278566211087,13.50635786376677,13.80993006542267,14.113502267078569,14.417074468734469,null,0,0,0,0,0,0,4.9293423352314486E-2,0.39340068404542811,0.44615347947174311,null,4.9293423352314486E-2,0.39340068404542811,0.44615347947174311]
["2013-04-01T11:00:00","2013-04-01T11:00:00",null,12.065646266073813,12.369218467729713,12.672790669385613,12.976362871041513,13.279935072697413,13.583507274353313,13.887079476009212,14.190651677665112,14.494223879321012,null,0,0,0,0,0,0,1.5656550207251659E-2,0.36201397996977552,0.41691179637814518,null,1.5656550207251659E-2,0.36201397996977552,0.41691179637814518]
["2013-04-01T12:00:00","2013-04-01T12:00:00",null,12.143035361417247,12.446607563073147,12.750179764729047,13.053751966384947,13.357324168040847,13.660896369696747,13.964468571352647,14.268040773008547,14.571612974664447,null,0,0,0,0,0,0,0,0.33257251551020195,0.38966792694430402,null,-1.6087657365410013E-2,0.33257251551020195,0.38966792694430402]
["2013-04-01T13:00:00","2013-04-01T13:00:00",null,12.175263559987595,12.478835761643495,12.782407963299395,13.085980164955295,13.389552366611195,13.693124568267095,13.996696769922995,14.300268971578895,14.603841173234795,null,0,0,0,0,0,0,0,0.30299435853706602,0.3623083946143717,null,-3.1891414894959537E-2,0.30299435853706602,0.3623083946143717]
["2013-04-01T14:00:00","2013-04-01T14:00:00",null,12.390767709042615,12.694339910698515,12.997912112354415,13.301484314010315,13.605056515666215,13.908628717322115,14.212200918978015,14.515773120633915,14.819345322289815,null,0,0,0,0,0,0,0,0.27101882517222198,0.33257251551020239,null,-3.4309820904138796E-2,0.27101882517222198,0.33257251551020239]
["2013-04-01T15:00:00","2013-04-01T15:00:00",null,12.451398126972762,12.754970328628662,13.058542530284562,13.362114731940462,13.665686933596362,13.969259135252262,14.272831336908162,14.576403538564062,14.879975740219962,null,0,0,0,0,0,0,0,0.23698238929520779,0.30080727832006959,null,-3.6402267842515636E-2,0.23698238929520779,0.30080727832006959]
["2013-04-01T16:00:00","2013-04-01T16:00:00",null,12.535014787928683,12.838586989584583,13.142159191240482,13.445731392896382,13.749303594552282,14.052875796208182,14.356447997864082,14.660020199519982,14.963592401175882,null,0,0,0,0,0,0,0,0.20003335139844292,0.26617149834512838,null,-3.936744390594412E-2,0.20003335139844292,0.26617149834512838]
["2013-04-01T17:00:00","2013-04-01T17:00:00",null,12.495358279179738,12.798930480835638,13.102502682491538,13.406074884147438,13.709647085803338,14.013219287459238,14.316791489115138,14.620363690771038,14.923935892426938,null,0,0,0,0,0,0,0,0.1618225364534106,0.2303054857481264,null,-4.0660765380418247E-2,0.1618225364534106,0.2303054857481264]
["2013-04-01T18:00:00","2013-04-01T18:00:00",null,12.516253558550261,12.819825760206161,13.123397961862061,13.426970163517961,13.730542365173861,14.034114566829761,14.337686768485661,14.641258970141561,14.94483117179746,null,0,0,0,0,0,0,0,0.15647049880700956,0.22730876525849122,null,-7.8125028905225644E-3,0.15647049880700956,0.22730876525849122]
["2013-04-01T19:00:00","2013-04-01T19:00:00",null,12.479305936169299,12.782878137825199,13.086450339481098,13.390022541136998,13.693594742792898,13.997166944448798,14.300739146104698,14.604311347760598,14.907883549416498,null,1.3753369826115093E-2,1.7012960534139313E-2,2.0125343919865663E-2,2.3090519983294148E-2,2.5929518341895885E-2,2.8642338995670882E-2,3.1250011562090257E-2,0.19021252003942801,0.26343764807388226,null,3.1250011562090257E-2,0.19021252003942801,0.26343764807388226]
["2013-04-01T20:00:00","2013-04-01T20:00:00",null,12.231706848766681,12.535279050422581,12.838851252078481,13.142423453734381,13.445995655390281,13.749567857046181,14.05314005870208,14.35671226035798,14.66028446201388,null,3.4089009920691998E-2,4.0513558058120375E-2,4.664369155095302E-2,5.2489925207925489E-2,5.807328864650891E-2,6.3404296675438843E-2,6.8525008529657538E-2,0.22989540820743898,0.30543379416371685,null,6.8525008529657538E-2,0.22989540820743898,0.30543379416371685]
["2013-04-01T21:00:00","2013-04-01T21:00:00",null,12.208769365500221,12.51234156715612,12.81591376881202,13.11948597046792,13.42305817212382,13.72663037377972,14.03020257543562,14.33377477709152,14.63734697874742,null,5.8367703291104647E-2,6.786257557931713E-2,7.6926340709371571E-2,8.5569513490003524E-2,9.3813123538684137E-2,0.10169923009035564,0.10925937757122473,0.27296406478830093,0.35074210500525349,null,0.10925937757122473,0.27296406478830093,0.35074210500525349]
["2013-04-01T22:00:00","2013-04-01T22:00:00",null,11.995203873506339,12.298776075162239,12.602348276818139,12.905920478474039,13.209492680129939,13.513064881785839,13.816637083441739,14.120209285097639,14.423781486753539,null,8.8156156438951791E-2,0.10064774921679945,0.11255051270545562,0.12390650613986257,0.13473675913749145,0.14509384574202,0.15501982518839053,0.32098519628361255,0.4009292871000909,null,0.15501982518839053,0.32098519628361255,0.4009292871000909]
["2013-04-01T23:00:00","2013-04-01T23:00:00",null,11.945232631246663,12.248804832902563,12.552377034558463,12.855949236214363,13.159521437870263,13.463093639526162,13.766665841182062,14.070238042837962,14.373810244493862,null,0.12304429182354651,0.13840642738620257,0.15304304114610487,0.16700670714693119,0.18031845500615271,0.19305188838491827,0.20523855170943461,0.37338048821291797,0.45540651115903763,null,0.20523855170943461,0.37338048821291797,0.45540651115903763]
["2013-04-02","2013-04-02",null,11.786040149860819,12.089612351516719,12.393184553172619,12.696756754828519,13.000328956484418,13.303901158140318,13.607473359796218,13.911045561452118,14.214617763108018,null,0.1645462419028097,0.18265274254544744,0.19989702887176913,0.21634218973418809,0.23201976955891104,0.24701388681582243,0.26135608593112902,0.4315589249467825,0.51556173193518784,null,0.26135608593112902,0.4315589249467825,0.51556173193518784]
["2013-04-02T01:00:00","2013-04-02T01:00:00",null,11.740439598570052,12.044011800225952,12.347584001881852,12.651156203537752,12.954728405193652,13.258300606849552,13.561872808505452,13.865445010161352,14.169017211817252,null,0.21114787421882047,0.23188307704534872,0.25161937304199861,0.27043036586991898,0.2883686295727878,0.30552879742922495,0.32193189905670172,0.49410100730590523,0.57999647986671177,null,0.32193189905670172,0.49410100730590523,0.57999647986671177]
["2013-04-02T02:00:00","2013-04-02T02:00:00",null,11.77081671464339,12.07438891629929,12.37796111795519,12.68153331961109,12.985105521266989,13.288677722922889,13.592249924578789,13.895822126234689,14.199394327890589,null,0.25963165729849685,0.28293247345650219,0.30511871988853806,0.3262534854470176,0.34639985898435449,0.36568401820537516,0.38410596311007983,0.55819928135789121,0.64594536025615668,null,0.38410596311007983,0.55819928135789121,0.64594536025615668]
["2013-04-02T03:00:00","2013-04-02T03:00:00",null,11.780103907886666,12.083676109542566,12.387248311198466,12.690820512854366,12.994392714510266,13.297964916166165,13.601537117822065,13.905109319477965,14.208681521133865,null,0.30770536283748628,0.33358230713570436,0.35821850400312616,0.38168755710090047,0.40405255528144091,0.4254607058670451,0.44591200885771326,0.62194005191286805,0.71154725195732793,null,0.44591200885771326,0.62194005191286805,0.71154725195732793]
["2013-04-02T04:00:00","2013-04-02T04:00:00",null,11.77373733305755,12.07730953471345,12.38088173636935,12.68445393802525,12.98802613968115,13.29159834133705,13.59517054299295,13.89874274464885,14.20231494630475,null,0.35935410334656681,0.38772305731511308,0.41472508614803633,0.44045482312395645,0.46496484228655155,0.48842338057559032,0.51084095279980857,0.68874063180989342,0.78013534933939888,null,0.51084095279980857,0.68874063180989342,0.78013534933939888]
["2013-04-02T05:00:00","2013-04-02T05:00:00",null,12.061349024747512,12.364921226403412,12.668493428059312,12.972065629715212,13.275637831371112,13.579210033027012,13.882782234682912,14.186354436338812,14.489926637994712,null,0.4050724917287904,0.43602808864628489,0.46548006791459406,0.49355460723854455,0.52030428066181433,0.54589732512417222,0.57036528505182504,0.75021020367798885,0.84348707197115991,null,0.57036528505182504,0.75021020367798885,0.84348707197115991]
["2013-04-02T06:00:00","2013-04-02T06:00:00",null,12.282255493911531,12.585827695567431,12.889399897223331,13.192972098879231,13.496544300535131,13.800116502191031,14.103688703846931,14.407260905502831,14.710833107158731,null,0.43844649465546415,0.47223057512282485,0.50438486023617346,0.53503552770033669,0.56424566636772788,0.59218351317811613,0.61890164217517918,0.80090209659213318,0.89625038220621001,null,0.61890164217517918,0.80090209659213318,0.89625038220621001]
["2013-04-02T07:00:00","2013-04-02T07:00:00",null,12.548907406857916,12.852479608513816,13.156051810169716,13.459624011825616,13.763196213481516,14.066768415137416,14.370340616793316,14.673912818449216,14.977485020105116,null,0.46420777605759106,0.50094651777964461,0.53591877163412394,0.56926123013459096,0.60104749694219484,0.63144580899670466,0.66051925515053356,0.84478039344563338,0.942294729659236,null,0.66051925515053356,0.84478039344563338,0.942294729659236]
["2013-04-02T08:00:00","2013-04-02T08:00:00",null,12.436880577727202,12.740452779383102,13.044024981039001,13.347597182694901,13.651169384350801,13.954741586006701,14.258313787662601,14.561885989318501,14.865458190974401,null,0.48404922014159657,0.52365850464845853,0.56137512358291952,0.5973357694585415,0.63161404593647352,0.66440973438269157,0.69577540884087297,0.88222362735296966,0.98184092531368472,null,0.69577540884087297,0.88222362735296966,0.98184092531368472]
["2013-04-02T09:00:00","2013-04-02T09:00:00",null,12.351409976740129,12.654982178396029,12.958554380051929,13.262126581707829,13.565698783363729,13.869270985019629,14.172843186675529,14.476415388331429,14.779987589987329,null,0.44312558454278927,0.4855423229820463,0.52594021814407554,0.56445596254243913,0.60118418945575713,0.63631416544126995,0.66990897935139049,0.85850221884554179,0.96016990450969142,null,0.66990897935139049,0.85850221884554179,0.96016990450969142]
["2013-04-02T10:00:00","2013-04-02T10:00:00",null,12.366225527393375,12.669797729049275,12.973369930705175,13.276942132361075,13.580514334016975,13.884086535672875,14.187658737328775,14.491230938984675,14.794803140640575,null,0.3979329365973438,0.44317815858646703,0.48626784478480012,0.52734920251464079,0.56652737986334478,0.60400215819688796,0.63984714117641872,0.83058540165262473,0.93432450463768002,null,0.63984714117641872,0.83058540165262473,0.93432450463768002]
["2013-04-02T11:00:00","2013-04-02T11:00:00",null,12.627843487878081,12.931415689533981,13.234987891189881,13.538560092845781,13.842132294501681,14.145704496157581,14.449276697813481,14.752848899469381,15.056421101125281,null,0.3506268120960504,0.39881618053113099,0.44471332066185909,0.48846543981053253,0.53020923049071367,0.57013395925964272,0.60832374458720384,0.80131217413282019,0.90721732771740116,null,0.60832374458720384,0.80131217413282019,0.90721732771740116]
["2013-04-02T12:00:00","2013-04-02T12:00:00",null,12.605316296089192,12.908888497745092,13.212460699400992,13.516032901056892,13.819605102712792,14.123177304368692,14.426749506024592,14.730321707680492,15.033893909336392,null,0.30416187229360192,0.35527435755716874,0.40395792200282077,0.45038080257032698,0.49466917696451412,0.53702282655135802,0.57755741422694939,0.77277498322450489,0.88083567259987605,null,0.57755741422694939,0.77277498322450489,0.88083567259987605]
["2013-04-02T13:00:00","2013-04-02T13:00:00",null,12.125719933900438,12.429292135556338,12.732864337212238,13.036436538868138,13.340008740524038,13.643580942179938,13.947153143835838,14.250725345491738,14.554297547147637,null,0.26167153019319589,0.31571764709398453,0.36720866547203157,0.41629179264963501,0.46312475075782811,0.50791783597132245,0.55077619637747299,0.74822290482696763,0.85841810037565791,null,0.55077619637747299,0.74822290482696763,0.85841810037565791]
["2013-04-02T14:00:00","2013-04-02T14:00:00",null,12.182721860800168,12.486294062456068,12.789866264111968,13.093438465767868,13.397010667423768,13.700582869079668,14.004155070735568,14.307727272391467,14.611299474047367,null,0.2231032117511545,0.27998832701054488,0.33417113642489576,0.38583039174271189,0.43511330028629097,0.48225118784781562,0.52735971732337639,0.72695144675492573,0.83920754481578619,null,0.52735971732337639,0.72695144675492573,0.83920754481578619]
["2013-04-02T15:00:00","2013-04-02T15:00:00",null,12.131777622008194,12.435349823664094,12.738922025319994,13.042494226975894,13.346066428631794,13.649638630287694,13.953210831943593,14.256783033599493,14.560355235255393,null,0.18336774953946572,0.24312340758366452,0.30004006726926152,0.35429648034476147,0.40607139855866875,0.45558563289443038,0.50296536105687251,0.70472314108794765,0.81907168608718495,null,0.50296536105687251,0.70472314108794765,0.81907168608718495]
["2013-04-02T16:00:00","2013-04-02T16:00:00",null,12.243626175790965,12.547198377446865,12.850770579102765,13.154342780758665,13.457914982414565,13.761487184070464,14.065059385726364,14.368631587382264,14.672203789038164,null,0.14223381776594718,0.20487053340368996,0.26452104336053311,0.32139564381118796,0.37567308650415904,0.42757418242289325,0.47723562408095233,0.68118048432902434,0.79762147626663848,null,0.47723562408095233,0.68118048432902434,0.79762147626663848]
["2013-04-02T17:00:00","2013-04-02T17:00:00",null,12.352672746245831,12.656244947901731,12.959817149557631,13.263389351213531,13.566961552869431,13.870533754525331,14.174105956181231,14.477678157837131,14.781250359493031,null,9.973296085680558E-2,0.16525073408809235,0.22765612393365275,0.2871594265681981,0.34393939374023291,0.39823786605067529,0.45019153601308687,0.65633399128689129,0.77488845978035348,null,0.45019153601308687,0.65633399128689129,0.77488845978035348]
["2013-04-02T18:00:00","2013-04-02T18:00:00",null,12.130512707198688,12.434084908854588,12.737657110510488,13.041229312166388,13.344801513822288,13.648373715478188,13.951945917134088,14.255518118789988,14.559090320445888,null,5.7042837390423873E-2,0.125504757067668,0.19071760084562345,0.25289166489900156,0.31221621578504238,0.36895412372213515,0.4232315664151059,0.63161367594958506,0.75230265061636636,null,0.4232315664151059,0.63161367594958506,0.75230265061636636]
["2013-04-02T19:00:00","2013-04-02T19:00:00",null,11.890661873348023,12.194234075003923,12.497806276659823,12.801378478315723,13.104950679971623,13.408522881627523,13.712095083283423,14.015667284939322,14.319239486595222,null,2.1166309984686334E-2,9.2456713211796646E-2,0.16036134802605595,0.2251010254109112,0.28687552673233796,0.34594772220872549,0.40245430435363538,0.61297092006143361,0.735699767622914,null,0.40245430435363538,0.61297092006143361,0.735699767622914]
["2013-04-02T20:00:00","2013-04-02T20:00:00",null,11.471669472286752,11.775241673942652,12.078813875598552,12.382386077254452,12.685958278910352,12.989530480566252,13.293102682222152,13.596674883878052,13.900247085533952,null,0,6.4739677384855226E-2,0.13530455880921172,0.20256779029060185,0.26673966800373672,0.3281040917844768,0.38679775414638357,0.5993963019838231,0.7241229632050602,null,0.38679775414638357,0.5993963019838231,0.7241229632050602]
["2013-04-02T21:00:00","2013-04-02T21:00:00",null,11.022987186309589,11.326559387965487,11.630131589621387,11.933703791277287,12.237275992933187,12.540848194589087,12.844420396244987,13.147992597900886,13.451564799556786,null,0,4.7211491222673374E-2,0.1202578675086225,0.18988693095551407,0.25629846292932368,0.31979739288338282,0.38052041333125303,0.59506420078477151,0.72164146834346754,null,0.38052041333125303,0.59506420078477151,0.72164146834346754]
["2013-04-02T22:00:00","2013-04-02T22:00:00",null,10.744547179863275,11.048119381519177,11.351691583175077,11.655263784830977,11.958835986486877,12.262408188142777,12.565980389798677,12.869552591454577,13.173124793110476,null,0,3.6170942050333277E-2,0.11159366511051941,0.18347289762682126,0.2520294505826855,0.31755773862270814,0.38021548387792176,0.59659936286016357,0.72494311828643399,null,0.38021548387792176,0.59659936286016357,0.72494311828643399]
["2013-04-02T23:00:00","2013-04-02T23:00:00",null,10.545835353992242,10.849407555648142,11.152979757304044,11.456551958959944,11.760124160615844,12.063696362271743,12.367268563927643,12.670840765583543,12.974412967239443,null,0,2.7853728340503738E-2,0.1056212537487202,0.17971911090822562,0.25037862561120228,0.31790472731098168,0.38246565294733204,0.60065807903209045,0.73072626309099309,null,0.38246565294733204,0.60065807903209045,0.73072626309099309]
["2013-04-03","2013-04-03",null,10.537751809955882,10.841324011611782,11.144896213267682,11.448468414923582,11.752040616579482,12.055612818235382,12.359185019891282,12.662757221547182,12.966329423203081,null,0,2.3363905010418764E-2,0.10337108467930993,0.17958241839466332,0.25226077637486788,0.32170057326451956,0.38807004600338657,0.6079974155295127,0.73971642455989861,null,0.38807004600338657,0.6079974155295127,0.73971642455989861]
["2013-04-03T01:00:00","2013-04-03T01:00:00",null,10.555758821642472,10.859331023298372,11.162903224954272,11.466475426610172,11.770047628266072,12.073619829921972,12.377192031577872,12.680764233233772,12.984336434889672,null,0,2.1513298672959851E-2,0.1036865289413768,0.18194825036016476,0.25657184795644827,0.32786225118355888,0.39598769698126474,0.61759743590508076,0.7509041810545366,null,0.39598769698126474,0.61759743590508076,0.7509041810545366]
["2013-04-03T02:00:00","2013-04-03T02:00:00",null,10.507876871174043,10.811449072829943,11.115021274485843,11.418593476141742,11.722165677797642,12.025737879453542,12.329310081109442,12.632882282765342,12.936454484421242,null,0,2.1954920639853454E-2,0.10624162746411836,0.18650116254266311,0.26302794052008333,0.33611637604097505,0.40594522085384194,0.62918475513167005,0.76404769197398914,null,0.40594522085384194,0.62918475513167005,0.76404769197398914]
["2013-04-03T03:00:00","2013-04-03T03:00:00",null,10.468794729986257,10.772366931642157,11.075939133298057,11.379511334953957,11.683083536609857,11.986655738265757,12.290227939921657,12.593800141577557,12.897372343233457,null,2.2081098344680196E-4,2.4362811840297153E-2,0.11072093598546777,0.19293622548882705,0.27131360980370617,0.34615801838343674,0.41765871778525798,0.64249650299089156,0.77887357229113152,null,0.41765871778525798,0.64249650299089156,0.77887357229113152]
["2013-04-03T04:00:00","2013-04-03T04:00:00",null,10.488747464354319,10.792319666010219,11.095891867666118,11.399464069322018,11.703036270977918,12.006608472633818,12.310180674289718,12.613752875945618,12.917325077601518,null,0,2.5813855445804709E-2,0.11426442652935216,0.1984565000749971,0.27871603515354182,0.35533744640958237,0.42853103001782911,0.65497758096000369,0.79288981233563571,null,0.42853103001782911,0.65497758096000369,0.79288981233563571]
["2013-04-03T05:00:00","2013-04-03T05:00:00",null,10.457375947815256,10.760948149471156,11.064520351127056,11.368092552782956,11.671664754438856,11.975236956094756,12.278809157750656,12.582381359406556,12.885953561062456,null,0,2.5372233478911106E-2,0.11596782554451321,0.20219977198485717,0.28438351706200976,0.36283450503803805,0.43776303208765255,0.6658709228100459,0.80536037549601225,null,0.43776303208765255,0.6658709228100459,0.80536037549601225]
["2013-04-03T06:00:00","2013-04-03T06:00:00",null,10.479265107547658,10.782837309203558,11.086409510859458,11.389981712515358,11.693553914171257,11.997126115827157,12.300698317483057,12.604270519138957,12.907842720794857,null,0,2.3816041786047931E-2,0.11658819925991137,0.20488104821242548,0.28901003290565702,0.36931162721914423,0.44600664213633318,0.67578638744768083,0.81687409106145259,null,0.44600664213633318,0.67578638744768083,0.81687409106145259]
["2013-04-03T07:00:00","2013-04-03T07:00:00",null,10.369297116640329,10.672869318296229,10.976441519952129,11.280013721608029,11.583585923263929,11.887158124919829,12.190730326575729,12.494302528231628,12.797874729887528,null,0,2.0787776870206075E-2,0.11579958860474422,0.20620591411310629,0.2923432272748302,0.37454800196945409,0.45305156398915969,0.68454522312440402,0.82727323690092336,null,0.45305156398915969,0.68454522312440402,0.82727323690092336]
["2013-04-03T08:00:00","2013-04-03T08:00:00",null,10.257764531029897,10.561336732685797,10.864908934341697,11.168481135997597,11.472053337653497,11.775625539309397,12.079197740965297,12.382769942621197,12.686342144277097,null,0,1.9830929275269932E-2,0.11704033603554054,0.20952859367354387,0.29763217606881787,0.38170858671837182,0.4619891514143874,0.69517569475605723,0.83950195946038197,null,0.4619891514143874,0.69517569475605723,0.83950195946038197]
["2013-04-03T09:00:00","2013-04-03T09:00:00",null,10.239604341678888,10.543176543334788,10.846748744990689,11.150320946646589,11.453893148302489,11.757465349958389,12.061037551614289,12.364609753270189,12.668181954926089,null,0,1.9799384849063247E-2,0.11918535701759518,0.21373451716776867,0.30378333917912165,0.38971035616613448,0.47174689392098895,0.70660529185161314,0.8525192926750077,null,0.47174689392098895,0.70660529185161314,0.8525192926750077]
["2013-04-03T10:00:00","2013-04-03T10:00:00",null,10.243278926168976,10.546851127824876,10.850423329480778,11.153995531136678,11.457567732792578,11.761139934448478,12.064712136104378,12.368284337760278,12.671856539416178,null,0,1.955754424814532E-2,0.12113059663367415,0.2177406592960178,0.30974523573218532,0.39752285905665702,0.48132588467908594,0.71785613719866448,0.86535787414112886,null,0.48132588467908594,0.71785613719866448,0.86535787414112886]
["2013-04-03T11:00:00","2013-04-03T11:00:00",null,10.310559118724852,10.614131320380752,10.917703522036652,11.221275723692552,11.524847925348451,11.828420127004351,12.131992328660251,12.435564530316151,12.739136731972051,null,0,1.9441881352054137E-2,0.12318098433710874,0.22183091989415141,0.31578073594639788,0.40539845079959297,0.49094693467212519,0.72914904178065809,0.87822800003345669,null,0.49094693467212519,0.72914904178065809,0.87822800003345669]
["2013-04-03T12:00:00","2013-04-03T12:00:00",null,10.305777631035809,10.609349832691709,10.912922034347609,11.216494236003509,11.520066437659409,11.823638639315309,12.127210840971209,12.430783042627109,12.734355244283009,null,0,1.9631147909294253E-2,0.12552578668513906,0.22621559513688075,0.32210013599647064,0.41355794237838905,0.50085188450102458,0.7407153313897763,0.89137151095290923,null,0.50085188450102458,0.7407153313897763,0.89137151095290923]
["2013-04-03T13:00:00","2013-04-03T13:00:00",null,10.337016090240155,10.640588291896055,10.944160493551955,11.247732695207855,11.551304896863755,11.854877098519655,12.158449300175555,12.462021501831455,12.765593703487355,null,0,1.819061911252226E-2,0.12628285291409952,0.22905459349548249,0.32690540358862247,0.42023484592547095,0.5093057907244164,0.75085160701085807,0.90311655231053201,null,0.5093057907244164,0.75085160701085807,0.90311655231053201]
["2013-04-03T14:00:00","2013-04-03T14:00:00",null,10.348704673958698,10.652276875614598,10.955849077270498,11.259421278926398,11.562993480582298,11.866565682238198,12.170137883894098,12.473710085549998,12.777282287205898,null,0,1.6140231409087671E-2,0.12644057504513295,0.23130476256489277,0.33114287150905397,0.42634394980083246,0.51720241208482343,0.76045162738642613,0.91433585323137667,null,0.51720241208482343,0.76045162738642613,0.91433585323137667]
["2013-04-03T15:00:00","2013-04-03T15:00:00",null,10.334648699460775,10.638220901116675,10.941793102772575,11.245365304428475,11.548937506084375,11.852509707740275,12.156081909396175,12.459654111052075,12.763226312707975,null,0,1.4783821082200173E-2,0.1272817597439779,0.234227879393379,0.33603225757109029,0.43309445700906324,0.52572992196936419,0.77066150666865685,0.92615449825014839,null,0.52572992196936419,0.77066150666865685,0.92615449825014839]
["2013-04-03T16:00:00","2013-04-03T16:00:00",null,10.400302201393371,10.703874403049271,11.007446604705171,11.311018806361071,11.614591008016971,11.918163209672871,12.221735411328771,12.525307612984671,12.828879814640571,null,0,1.3700795782437287E-2,0.12837529985247634,0.2373823220140476,0.34113193980783785,0.44005526039200527,0.53444669841114512,0.78105013769939213,0.93814138020868909,null,0.53444669841114512,0.78105013769939213,0.93814138020868909]
["2013-04-03T17:00:00","2013-04-03T17:00:00",null,10.380106401361019,10.683678603016919,10.987250804672819,11.290823006328718,11.594395207984618,11.897967409640518,12.201539611296418,12.505111812952318,12.808684014608218,null,0,1.3564103268874981E-2,0.13039414312970424,0.24144103818597454,0.3471148659783726,0.44786776328252781,0.54400465955177102,0.7922589238115012,0.95092738763113249,null,0.54400465955177102,0.7922589238115012,0.95092738763113249]
["2013-04-03T18:00:00","2013-04-03T18:00:00",null,10.362673858903554,10.666246060559454,10.969818262215353,11.273390463871253,11.576962665527153,11.880534867183053,12.184107068838953,12.487679270494853,12.791251472150753,null,0,1.4352713924042131E-2,0.13331725995819046,0.24638299829168867,0.35396000646522346,0.45653196568063087,0.5543932905825063,0.80428786500498417,0.9645125205174786,null,0.5543932905825063,0.80428786500498417,0.9645125205174786]
["2013-04-03T19:00:00","2013-04-03T19:00:00",null,10.311197903810966,10.614770105466866,10.918342307122767,11.221914508778667,11.525486710434567,11.829058912090467,12.132631113746367,12.436203315402267,12.739775517058167,null,0,1.4216021410479824E-2,0.13534661804415393,0.25046274408108671,0.35997447706196495,0.46438652780609568,0.56400382576680996,0.81555973996950659,0.97737213160107095,null,0.56400382576680996,0.81555973996950659,0.97737213160107095]
["2013-04-03T20:00:00","2013-04-03T20:00:00",null,10.151285561755845,10.454857763411745,10.758429965067645,11.062002166723545,11.365574368379445,11.669146570035345,11.972718771691245,12.276290973347145,12.579863175003045,null,0,1.5172869005415967E-2,0.1384800310473514,0.25564654478771875,0.36709300257594041,0.47334514484879453,0.57470790105961211,0.82792515504252751,0.99131476798442619,null,0.57470790105961211,0.82792515504252751,0.99131476798442619]
["2013-04-03T21:00:00","2013-04-03T21:00:00",null,10.032112990844684,10.335685192500584,10.639257394156484,10.942829595812384,11.246401797468284,11.549973999124184,11.853546200780084,12.157118402435984,12.460690604091884,null,1.3038362832096877E-3,1.8716359549300361E-2,0.14414751295581932,0.26331184035594346,0.37665096371656626,0.48470113828320149,0.58776729350918011,0.8426038280373721,1,null,0.58776729350918011,0.8426038280373721,1]
["2013-04-03T22:00:00","2013-04-03T22:00:00",null,9.9265085149561667,10.230080716612067,10.533652918267967,10.837225119923868,11.140797321579768,11.444369523235668,11.747941724891568,12.051513926547468,12.355086128203368,null,4.5003381388205354E-3,2.4131486048114791E-2,0.15164457158427502,0.27277516821794928,0.38797541272476654,0.49779207515897617,0.60253008497390914,0.85895435562117106,1,null,0.60253008497390914,0.85895435562117106,1]
["2013-04-03T23:00:00","2013-04-03T23:00:00",null,9.9277811326848813,10.231353334340781,10.534925535996681,10.838497737652581,11.142069939308481,11.445642140964381,11.749214342620281,12.052786544276181,12.356358745932081,null,1.1440111904291454E-2,3.317422156069811E-2,0.16266409113914398,0.28566632372774831,0.40263305610213995,0.51412157312530393,0.62044731905930683,0.87838572216448962,1,null,0.62044731905930683,0.87838572216448962,1]
["2013-04-04","2013-04-04",null,9.8606052975584788,10.164177499214379,10.467749700870279,10.771321902526179,11.074894104182079,11.378466305837978,11.682038507493878,11.985610709149778,12.289182910805678,null,1.8295767199877876E-2,4.2153868220868057E-2,0.1736415514590707,0.29852593481134065,0.41726966986204228,0.5304405562828961,0.63836455314470453,0.89781708870780819,1,null,0.63836455314470453,0.89781708870780819,1]
["2013-04-04T01:00:00","2013-04-04T01:00:00",null,9.8132724564370086,10.116844658092909,10.420416859748808,10.723989061404708,11.027561263060608,11.331133464716508,11.634705666372408,11.938277868028308,12.241850069684208,null,2.7811669105561484E-2,5.3720157829986251E-2,0.1871425658755323,0.31384601113905447,0.43430366001365273,0.54910434178851864,0.65857401553445472,0.91948810951180149,1,null,0.65857401553445472,0.91948810951180149,1]
["2013-04-04T02:00:00","2013-04-04T02:00:00",null,9.788466764714153,10.092038966370053,10.395611168025953,10.699183369681855,11.002755571337755,11.306327772993654,11.609899974649554,11.913472176305454,12.217044377961354,null,3.8694496146868151E-2,6.6621828148520829E-2,0.20193690176646803,0.33042786451503575,0.4525783975960595,0.56897733029873077,0.67996113650258783,0.94230524446797104,1,null,0.67996113650258783,0.94230524446797104,1]
["2013-04-04T03:00:00","2013-04-04T03:00:00",null,9.705209964604963,10.008782166260863,10.312354367916763,10.615926569572663,10.919498771228563,11.223070972884463,11.526643174540363,11.830215376196263,12.133787577852162,null,5.0365933843341967E-2,8.0291079504751423E-2,0.21748830388636423,0.34775626931124193,0.47158917178995557,0.58957584061169677,0.7020632644647391,0.96583738641815875,1,null,0.7020632644647391,0.96583738641815875,1]
["2013-04-04T04:00:00","2013-04-04T04:00:00",null,9.7534792907241616,10.057051492380062,10.360623694035962,10.664195895691861,10.967768097347761,11.271340299003661,11.574912500659561,11.878484702315461,12.182056903971361,null,5.9019621432709488E-2,9.0900521518933478E-2,0.22993783742926963,0.36195126110425063,0.48742447374571196,0.60696733426031635,0.72092683133633728,0.98609942285158669,1,null,0.72092683133633728,0.98609942285158669,1]
["2013-04-04T05:00:00","2013-04-04T05:00:00",null,9.7312306945632621,10.034802896219162,10.338375097875062,10.641947299530962,10.945519501186862,11.249091702842762,11.552663904498662,11.856236106154562,12.159808307810462,null,6.3015248752223044E-2,9.6936021733146069E-2,0.23789754764209006,0.37171951841958772,0.49890664488494568,0.62006878594482662,0.73556344509623961,1,1,null,0.73556344509623961,1,1]
["2013-04-04T06:00:00","2013-04-04T06:00:00",null,9.6170610902451923,9.9206332919010922,10.224205493556992,10.527777695212892,10.831349896868792,11.134922098524692,11.438494300180592,11.742066501836492,12.045638703492392,null,7.7599288468447464E-3,4.3552337782697806E-2,0.18626983675048064,0.32174263249946156,0.45049646546641825,0.57313067974927789,0.69002380846252065,0.95578522926696174,0.95704700631522921,null,0.69002380846252065,0.95578522926696174,0.95704700631522921]
["2013-04-04T07:00:00","2013-04-04T07:00:00",null,9.7030643342063296,10.00663653586223,10.310208737518129,10.613780939174029,10.917353140829929,11.220925342485829,11.524497544141729,11.828069745797629,12.131641947453529,null,0,0,0.12422195040192929,0.26147174882722019,0.39189743638313124,0.51611938678506075,0.63451613314748889,0.90169705313123083,0.90431524050638579,null,0.63451613314748889,0.90169705313123083,0.90431524050638579]
["2013-04-04T08:00:00","2013-04-04T08:00:00",null,9.7942782479062789,10.097850449562179,10.401422651218079,10.70499485287398,11.00856705452988,11.31213925618578,11.61571145784168,11.91928365949758,12.22285586115348,null,0,0,6.0912287005110505E-2,0.19996011772418248,0.33208920429525457,0.45790940562498955,0.57783079925407421,0.84645224803458807,0.85044787535410171,null,0.57783079925407421,0.84645224803458807,0.85044787535410171]
["2013-04-04T09:00:00","2013-04-04T09:00:00",null,9.7679513422747846,10.071523543930684,10.375095745586584,10.678667947242483,10.982240148898383,11.285812350554282,11.589384552210182,11.892956753866082,12.196528955521982,null,0,0,0,0.13630346563909015,0.27018852526900111,0.39768058118769045,0.51917919612710939,0.78929374774807304,0.79471938905562312,null,0.51917919612710939,0.78929374774807304,0.79471938905562312]
["2013-04-04T10:00:00","2013-04-04T10:00:00",null,9.8276728298668026,10.131245031522703,10.434817233178602,10.738389434834502,11.041961636490402,11.345533838146302,11.649106039802202,11.952678241458102,12.256250443114002,null,0,0,0,6.956597459447815E-2,0.20529112575311248,0.33451812511316953,0.45766756502407169,0.72933830833789848,0.73624653767716286,null,0.45766756502407169,0.72933830833789848,0.73624653767716286]
["2013-04-04T11:00:00","2013-04-04T11:00:00",null,9.9213178301823639,10.224890031838264,10.528462233494164,10.832034435150064,11.135606636805964,11.439178838461864,11.742751040117763,12.046323241773663,12.349895443429563,null,0,0,0,1.5456768841275864E-3,0.13912143438022084,0.27010440679911674,0.39491518649023771,0.66817366592313432,0.67658551291158409,null,0.39491518649023771,0.66817366592313432,0.67658551291158409]
["2013-04-04T12:00:00","2013-04-04T12:00:00",null,9.9997287867673741,10.303300988423274,10.606873190079174,10.910445391735074,11.214017593390974,11.517589795046874,11.821161996702774,12.124734198358674,12.428306400014574,null,0,0,0,0,7.2447032188022217E-2,0.20518597766575697,0.3316686119458323,0.60650431268906324,0.61643029213543388,null,0.3316686119458323,0.60650431268906324,0.61643029213543388]
["2013-04-04T13:00:00","2013-04-04T13:00:00",null,10.151768340728955,10.455340542384855,10.758912744040755,11.062484945696655,11.366057147352555,11.669629349008455,11.973201550664355,12.276773752320254,12.580345953976154,null,0,0,0,0,5.0155637668631292E-3,0.13951048230343671,0.26765445636373086,0.54407789322603162,0.55550749032158764,null,0.26765445636373086,0.54407789322603162,0.55550749032158764]
["2013-04-04T14:00:00","2013-04-04T14:00:00",null,10.175980806863173,10.479553008519073,10.783125210174973,11.086697411830873,11.390269613486772,11.693841815142672,11.997414016798572,12.300986218454472,12.604558420110372,null,0,0,0,0,0,7.2699387597675774E-2,0.20252573105565985,0.48055793365450161,0.49352269282544964,null,0.20252573105565985,0.48055793365450161,0.49352269282544964]
["2013-04-04T15:00:00","2013-04-04T15:00:00",null,10.358338874403536,10.661911076059436,10.965483277715336,11.269055479371236,11.572627681027136,11.876199882683036,12.179772084338936,12.483344285994836,12.786916487650736,null,0,0,0,0,0,5.7978655367888973E-2,0.18976075325068759,0.46965407699572381,0.48438532403424628,null,0.18976075325068759,0.46965407699572381,0.48438532403424628]
["2013-04-04T16:00:00","2013-04-04T16:00:00",null,10.491013907223099,10.794586108878999,11.098158310534899,11.401730512190799,11.705302713846699,12.008874915502599,12.312447117158499,12.616019318814399,12.919591520470298,null,0,0,0,0,0,5.2921032366083656E-2,0.18670094390863903,0.46849744803481197,0.48504775698458669,null,0.18670094390863903,0.46849744803481197,0.48504775698458669]
["2013-04-04T17:00:00","2013-04-04T17:00:00",null,10.415222470061448,10.718794671717347,11.022366873373247,11.325939075029147,11.629511276685047,11.933083478340947,12.236655679996847,12.540227881652747,12.843800083308647,null,0,0,0,0,0,5.1165059307244805E-2,0.18687969565714357,0.47051629131203987,0.48881205851191789,null,0.18687969565714357,0.47051629131203987,0.48881205851191789]
["2013-04-04T18:00:00","2013-04-04T18:00:00",null,10.362529075196401,10.6661012768523,10.9696734785082,11.2732456801641,11.57681788182,11.8803900834759,12.1839622851318,12.4875344867877,12.7911066884436,null,0,0,0,0,0,5.1795947831378523E-2,0.18939273494494288,0.47481684808488472,0.49481601429992378,null,0.18939273494494288,0.47481684808488472,0.49481601429992378]
["2013-04-04T19:00:00","2013-04-04T19:00:00",null,10.305495490376302,10.609067692032202,10.912639893688102,11.216212095344002,11.519784296999902,11.823356498655802,12.126928700311701,12.430500901967601,12.734073103623501,null,0,0,0,0,1.1986881958540678E-3,5.4908331217104873E-2,0.19433469505065701,0.48149375163196662,0.50314374281848884,null,0.19433469505065701,0.48149375163196662,0.50314374281848884]
["2013-04-04T20:00:00","2013-04-04T20:00:00",null,10.247581491211015,10.551153692866915,10.854725894522815,11.158298096178715,11.461870297834615,11.765442499490515,12.069014701146415,12.372586902802315,12.676159104458215,null,0,0,2.1029617471123997E-5,2.0924469383768376E-3,5.2468895590454369E-3,6.0817653726490714E-2,0.20201050542761725,0.49085193140661681,0.51408965871220891,null,0.20201050542761725,0.49085193140661681,0.51408965871220891]
["2013-04-04T21:00:00","2013-04-04T21:00:00",null,10.229255933601618,10.532828135257517,10.836400336913417,11.139972538569317,11.443544740225217,11.747116941881117,12.050689143537017,12.354261345192917,12.657833546848817,null,0,0,9.253031687294558E-4,5.0365933843341971E-3,1.0136275621081766E-2,6.7547131317250389E-2,0.21048544126848023,0.50098820702769853,0.52580315564362501,null,0.21048544126848023,0.50098820702769853,0.52580315564362501]
["2013-04-04T22:00:00","2013-04-04T22:00:00",null,10.111270262073097,10.414842463728997,10.718414665384898,11.021986867040798,11.325559068696698,11.629131270352598,11.932703472008498,12.236275673664398,12.539847875320298,null,0,1.3143510919452497E-3,4.3531308165226665E-3,1.047274950061975E-2,1.7465097309768481E-2,7.6663470490982641E-2,0.22130517945737352,0.51342722576186839,0.53978785126192241,null,0.22130517945737352,0.51342722576186839,0.53978785126192241]
["2013-04-04T23:00:00","2013-04-04T23:00:00",null,10.006599511916148,10.310171713572048,10.613743915227948,10.917316116883846,11.220888318539746,11.524460520195646,11.828032721851546,12.131604923507446,12.435177125163346,null,9.3581797746501781E-4,4.4582789038782869E-3,9.5789907580969801E-3,1.7675393484479718E-2,2.6528862439822921E-2,8.7493723488611494E-2,0.23380728704395673,0.52751706946752142,0.55539182742549642,null,0.23380728704395673,0.52751706946752142,0.55539182742549642]
["2013-04-05","2013-04-05",null,9.9064046554242289,10.209976857080129,10.513549058736029,10.817121260391929,11.120693462047829,11.424265663703729,11.727837865359628,12.031410067015528,12.334982268671428,null,3.5540053526199556E-3,9.2635464960301207E-3,1.6445160862418963E-2,2.6486803204880671E-2,3.7169848880211659E-2,9.9880168179103529E-2,0.24783404189719643,0.54311053082235983,0.57247839162078462,null,0.24783404189719643,0.54311053082235983,0.57247839162078462]
["2013-04-05T01:00:00","2013-04-05T01:00:00",null,9.803673315888588,10.107245517544488,10.410817719200388,10.714389920856288,11.017962122512188,11.321534324168088,11.625106525823988,11.928678727479888,12.232250929135787,null,8.0964027263827378E-3,1.5961479660583113E-2,2.5172452112935423E-2,3.7117274836533848E-2,4.9608867614381505E-2,0.11402258592843442,0.26359574019180387,0.56040739119235927,0.59123681040502718,null,0.26359574019180387,0.56040739119235927,0.59123681040502718]
["2013-04-05T02:00:00","2013-04-05T02:00:00",null,9.7885308604406731,10.092103062096573,10.395675263752473,10.699247465408373,11.002819667064273,11.306391868720173,11.609964070376073,11.913536272031973,12.217108473687873,null,1.3637706930023911E-2,2.3626775228807809E-2,3.4846076149652461E-2,4.8673049636916481E-2,6.2952159899809679E-2,0.12905876242028808,0.28023016761146297,0.57856646587867488,0.61083641388811472,null,0.28023016761146297,0.57856646587867488,0.61083641388811472]
["2013-04-05T03:00:00","2013-04-05T03:00:00",null,9.7695394349202207,10.073111636576121,10.376683838232021,10.68025603988792,10.98382824154382,11.28740044319972,11.59097264485562,11.89454484651152,12.19811704816742,null,2.0125343919865663E-2,3.2217373965761964E-2,4.5413458928892272E-2,6.1101553562350766E-2,7.7147151692818383E-2,0.14491509399351557,0.29766372049502476,0.59750363641142201,0.6311930836001628,null,0.29766372049502476,0.59750363641142201,0.6311930836001628]
["2013-04-05T04:00:00","2013-04-05T04:00:00",null,9.716550757063434,10.020122958719334,10.323695160375234,10.627267362031134,10.930839563687034,11.234411765342934,11.537983966998834,11.841556168654733,12.145128370310633,null,2.5666648123506837E-2,3.9893184342722224E-2,5.5108112583080432E-2,7.2688872788940082E-2,9.05325032131888E-2,0.15999332972031147,0.31434020714962607,0.61570477033267978,0.6508452611269282,null,0.31434020714962607,0.61570477033267978,0.6508452611269282]
["2013-04-05T05:00:00","2013-04-05T05:00:00",null,9.7327140902423697,10.03628629189827,10.33985849355417,10.643430695210069,10.947002896865969,11.250575098521869,11.554147300177769,11.857719501833669,12.161291703489569,null,3.0324708393360801E-2,4.6706780403366399E-2,6.3961581538423629E-2,8.345603693415557E-2,0.10311872926965651,0.17429346960067579,0.33025962757526695,0.63316986764244831,0.66977191685093984,null,0.33025962757526695,0.63316986764244831,0.66977191685093984]
["2013-04-05T06:00:00","2013-04-05T06:00:00",null,9.5704839734588028,9.8740561751147027,10.177628376770603,10.481200578426503,10.784772780082402,11.088344981738302,11.391917183394202,11.695489385050102,11.999061586706002,null,3.2427670140473201E-2,5.1080940837360186E-2,7.0480762954472073E-2,9.1994061627431914E-2,0.11354941953533401,0.18652219216013441,0.34419174914988659,0.64872126976234445,0.68684796623749256,null,0.34419174914988659,0.64872126976234445,0.68684796623749256]
["2013-04-05T07:00:00","2013-04-05T07:00:00",null,9.8278235375195688,10.131395739175469,10.434967940831369,10.738540142487267,11.042112344143167,11.345684545799067,11.649256747454967,11.952828949110867,12.256401150766767,null,3.5603142378612923E-2,5.6443493292496802E-2,7.7893703113043278E-2,0.1013522414020821,0.12473717602997197,0.19945540690487568,0.35876527405737552,0.66486150117143217,0.70447078567829446,null,0.35876527405737552,0.66486150117143217,0.70447078567829446]
["2013-04-05T08:00:00","2013-04-05T08:00:00",null,10.052691247664313,10.356263449320213,10.659835650976113,10.963407852632013,11.266980054287913,11.570552255943813,11.874124457599713,12.177696659255613,12.481268860911513,null,3.7758678169403134E-2,6.0765079682812785E-2,8.4265677206793843E-2,0.10964842549444051,0.13486293684231818,0.21130559634985405,0.37225577366510154,0.67991870728075698,0.72101057981933347,null,0.37225577366510154,0.67991870728075698,0.72101057981933347]
["2013-04-05T09:00:00","2013-04-05T09:00:00",null,10.291933352035729,10.595505553691629,10.899077755347529,11.202649957003429,11.506222158659329,11.809794360315228,12.113366561971128,12.416938763627028,12.720510965282928,null,3.4583205931263412E-2,5.986080613155445E-2,8.5506424637590159E-2,0.11291853101120029,0.14005725235768579,0.21831897377647391,0.38099357972435355,0.69030733831149227,0.7329659173516675,null,0.38099357972435355,0.69030733831149227,0.7329659173516675]
["2013-04-05T10:00:00","2013-04-05T10:00:00",null,10.557818870804175,10.861391072460075,11.164963274115975,11.468535475771874,11.772107677427774,12.075679879083674,12.379252080739574,12.682824282395474,12.986396484051374,null,2.5109363260522051E-2,5.2773825043785666E-2,8.0680127427967208E-2,0.11023725478363199,0.13941584902481652,0.21960178044221249,0.38411647791881548,0.69517569475605745,0.73950612838518703,null,0.38411647791881548,0.69517569475605745,0.73950612838518703]
["2013-04-05T11:00:00","2013-04-05T11:00:00",null,10.876899817705993,11.180472019361893,11.484044221017793,11.787616422673693,12.091188624329593,12.394760825985493,12.698333027641393,13.001905229297293,13.305477430953193,null,6.9502885742064799E-3,3.7169848880211659E-2,6.7505072082308021E-2,9.9364942551060875E-2,0.13073061700924232,0.212987965747544,0.37948996207516822,0.69243132967607579,0.73855979559898643,null,0.37948996207516822,0.69243132967607579,0.73855979559898643]
["2013-04-05T12:00:00","2013-04-05T12:00:00",null,11.044664761812305,11.348236963468203,11.651809165124103,11.955381366780003,12.258953568435903,12.562525770091803,12.866097971747703,13.169670173403603,13.473242375059503,null,0,1.7086564195288242E-2,4.9934826685183925E-2,8.4171043928173789E-2,0.11779740226450107,0.20221028679359296,0.37076267082465175,0.68565979285037382,0.73365989472821458,null,0.37076267082465175,0.68565979285037382,0.73365989472821458]
["2013-04-05T13:00:00","2013-04-05T13:00:00",null,11.229678191613614,11.533250393269514,11.836822594925414,12.140394796581313,12.443966998237213,12.747539199893113,13.051111401549013,13.354683603204913,13.658255804860813,null,0,0,2.2207276049506938E-2,5.8903958536618312E-2,9.488563402971148E-2,0.1815276580107425,0.35221454821512038,0.66915154313554148,0.7190968846294612,null,0.35221454821512038,0.66915154313554148,0.7190968846294612]
["2013-04-05T14:00:00","2013-04-05T14:00:00",null,11.610074776398843,11.913646978054743,12.217219179710643,12.520791381366543,12.824363583022443,13.127935784678343,13.431507986334243,13.735080187990143,14.038652389646042,null,0,0,0,2.5372233478911099E-2,6.3866948259803588E-2,0.15290634863254274,0.3258749523325376,0.64499902746995552,0.69703681590225208,null,0.3258749523325376,0.64499902746995552,0.69703681590225208]
["2013-04-05T15:00:00","2013-04-05T15:00:00",null,11.697195714999019,12.000767916654919,12.304340118310819,12.607912319966719,12.911484521622619,13.215056723278519,13.518628924934418,13.822201126590318,14.125773328246218,null,0,0,0,0,3.3826139702302957E-2,0.1253260053191636,0.3006394113671888,0.622013655574017,0.67619646498836816,null,0.3006394113671888,0.622013655574017,0.67619646498836816]
["2013-04-05T16:00:00","2013-04-05T16:00:00",null,11.717503602600726,12.021075804256625,12.324648005912525,12.628220207568425,12.931792409224325,13.235364610880225,13.538936812536125,13.842509014192025,14.146081215847925,null,0,0,0,0,5.8462336569724827E-3,9.9753990474276827E-2,0.27737013963539009,0.60094197886795075,0.65722775002941436,null,0.27737013963539009,0.60094197886795075,0.65722775002941436]
["2013-04-05T17:00:00","2013-04-05T17:00:00",null,11.793319611937623,12.096891813593523,12.400464015249423,12.704036216905322,13.007608418561222,13.311180620217122,13.614752821873022,13.918325023528922,14.221897225184822,null,0,0,0,0,0,7.4055797924563307E-2,0.25396417539002908,0.57972309483958662,0.63810131293942707,null,0.25396417539002908,0.57972309483958662,0.63810131293942707]
["2013-04-05T18:00:00","2013-04-05T18:00:00",null,11.702796293050657,12.006368494706557,12.309940696362457,12.613512898018357,12.917085099674257,13.220657301330156,13.524229502986056,13.827801704641956,14.131373906297856,null,0,0,0,0,0,4.9051582751396879E-2,0.23125218852121515,0.55919818818776956,0.61966885322598686,null,0.23125218852121515,0.55919818818776956,0.61966885322598686]
["2013-04-05T19:00:00","2013-04-05T19:00:00",null,11.534811298580706,11.838383500236606,12.141955701892506,12.445527903548406,12.749100105204306,13.052672306860206,13.356244508516106,13.659816710172006,13.963388911827906,null,0,0,0,0,0,2.7832698723032769E-2,0.21226244394479019,0.54234294978466369,0.60485348771757996,null,0.21226244394479019,0.54234294978466369,0.60485348771757996]
["2013-04-05T20:00:00","2013-04-05T20:00:00",null,11.357939078026273,11.661511279682173,11.965083481338073,12.268655682993973,12.572227884649873,12.875800086305773,13.179372287961673,13.482944489617573,13.786516691273473,null,0,0,0,0,0,1.0714590101537837E-2,0.19731038592282102,0.52945179427486466,0.59393911625006657,null,0.19731038592282102,0.52945179427486466,0.59393911625006657]
["2013-04-05T21:00:00","2013-04-05T21:00:00",null,11.195906854719816,11.499479056375716,11.803051258031616,12.106623459687516,12.410195661343415,12.713767862999315,13.017340064655215,13.320912266311115,13.624484467967015,null,0,0,0,0,0,0,0.18600696653209187,0.52015670335262787,0.58655772051770205,null,0.18600696653209187,0.52015670335262787,0.58655772051770205]
["2013-04-05T22:00:00","2013-04-05T22:00:00",null,11.136152068672889,11.439724270328789,11.743296471984689,12.046868673640589,12.350440875296488,12.654013076952388,12.957585278608288,13.261157480264188,13.564729681920088,null,0,0,0,0,0,0,0.18011867364017714,0.51616107603311434,0.58437064030070518,null,0.18011867364017714,0.51616107603311434,0.58437064030070518]
["2013-04-05T23:00:00","2013-04-05T23:00:00",null,10.976262656617047,11.279834858272947,11.583407059928847,11.886979261584747,12.190551463240647,12.494123664896547,12.797695866552447,13.101268068208347,13.404840269864247,null,0,0,0,0,0,0,0.17786850457076686,0.51575099849242745,0.58570602101012159,null,0.17786850457076686,0.51575099849242745,0.58570602101012159]
["2013-04-06","2013-04-06",null,10.885213745328629,11.188785946984527,11.492358148640427,11.795930350296327,12.099502551952227,12.403074753608127,12.706646955264027,13.010219156919927,13.313791358575827,null,0,0,0,0,0,0,0.17652260905261494,0.51622416488552769,0.58792464565332514,null,0.17652260905261494,0.51622416488552769,0.58792464565332514]
["2013-04-06T01:00:00","2013-04-06T01:00:00",null,10.912847076460505,11.216419278116405,11.519991479772305,11.823563681428205,12.127135883084105,12.430708084740004,12.734280286395904,13.037852488051804,13.341424689707704,null,0,0,0,0,0,0,0.17696423101950853,0.51845330433746684,0.59184666931168972,null,0.17696423101950853,0.51845330433746684,0.59184666931168972]
["2013-04-06T02:00:00","2013-04-06T02:00:00",null,10.972158339551308,11.275730541207208,11.579302742863108,11.882874944519008,12.186447146174908,12.490019347830808,12.793591549486708,13.097163751142608,13.400735952798508,null,0,0,0,0,0,0,0.17775284167467567,0.52100840286020844,0.59608413723212117,null,0.17775284167467567,0.52100840286020844,0.59608413723212117]
["2013-04-06T03:00:00","2013-04-06T03:00:00",null,10.880142753561614,11.183714955217512,11.487287156873412,11.790859358529312,12.094431560185212,12.398003761841112,12.701575963497012,13.005148165152912,13.308720366808812,null,0,0,0,0,0,0,0.17951932954225008,0.52452034897788613,0.60126793793875322,null,0.17951932954225008,0.52452034897788613,0.60126793793875322]
["2013-04-06T04:00:00","2013-04-06T04:00:00",null,10.965218685180529,11.268790886836429,11.572363088492329,11.875935290148229,12.179507491804129,12.483079693460029,12.786651895115929,13.090224096771829,13.393796298427729,null,0,0,0,0,0,0,0.1806759585031619,0.52743295099763676,0.60585239454745821,null,0.1806759585031619,0.52743295099763676,0.60585239454745821]
["2013-04-06T05:00:00","2013-04-06T05:00:00",null,10.928658335404904,11.232230537060804,11.535802738716704,11.839374940372604,12.142947142028504,12.446519343684404,12.750091545340304,13.053663746996204,13.357235948652104,null,0,0,0,0,0,0,0.18044463271097955,0.5289891426904999,0.60912250006421798,null,0.18044463271097955,0.5289891426904999,0.60912250006421798]
["2013-04-06T06:00:00","2013-04-06T06:00:00",null,10.896684846235434,11.200257047891334,11.503829249547234,11.807401451203134,12.110973652859034,12.414545854514934,12.718118056170834,13.021690257826734,13.325262459482634,null,0,0,0,0,0,0,0.17856248194731394,0.52894708345555763,0.61082589907937901,null,0.17856248194731394,0.52894708345555763,0.61082589907937901]
["2013-04-06T07:00:00","2013-04-06T07:00:00",null,10.842832148777326,11.146404350433226,11.449976552089126,11.753548753745026,12.057120955400926,12.360693157056826,12.664265358712726,12.967837560368626,13.271409762024525,null,0,0,0,0,0,0,0.17603892785077907,0.52828465050521722,0.61194046880534858,null,0.17603892785077907,0.52828465050521722,0.61194046880534858]
["2013-04-06T08:00:00","2013-04-06T08:00:00",null,10.973853179436182,11.27742538109208,11.58099758274798,11.88456978440388,12.188141986059779,12.491714187715679,12.795286389371579,13.098858591027479,13.402430792683379,null,0,0,0,0,0,0,0.17096027523150262,0.52510917826707748,0.61057354366972549,null,0.17096027523150262,0.52510917826707748,0.61057354366972549]
["2013-04-06T09:00:00","2013-04-06T09:00:00",null,11.09005116586613,11.39362336752203,11.69719556917793,12.00076777083383,12.30433997248973,12.60791217414563,12.91148437580153,13.21505657745743,13.51862877911333,null,0,0,0,0,0,0,0.16400998665729613,0.52008309969147881,0.60738755662285016,null,0.16400998665729613,0.52008309969147881,0.60738755662285016]
["2013-04-06T10:00:00","2013-04-06T10:00:00",null,11.39077108791173,11.69434328956763,11.99791549122353,12.30148769287943,12.60505989453533,12.90863209619123,13.21220429784713,13.51577649950303,13.81934870115893,null,0,0,0,0,0,0,0.15344260387805633,0.51147147133705351,0.60065807903209045,null,0.15344260387805633,0.51147147133705351,0.60065807903209045]
["2013-04-06T11:00:00","2013-04-06T11:00:00",null,11.669103331991744,11.972675533647644,12.276247735303544,12.579819936959444,12.883392138615344,13.186964340271244,13.490536541927144,13.794108743583044,14.097680945238944,null,0,0,0,0,0,0,0.14026754853239715,0.50027320003368003,0.59136298810985366,null,0.14026754853239715,0.50027320003368003,0.59136298810985366]
["2013-04-06T12:00:00","2013-04-06T12:00:00",null,11.775965332969212,12.079537534625112,12.383109736281012,12.686681937936912,12.990254139592812,13.293826341248712,13.597398542904612,13.900970744560512,14.204542946216412,null,0,0,0,0,0,0,0.12297068816239766,0.4850372421758507,0.57809329948557442,null,0.12297068816239766,0.4850372421758507,0.57809329948557442]
["2013-04-06T13:00:00","2013-04-06T13:00:00",null,11.969870763377864,12.273442965033764,12.577015166689664,12.880587368345564,13.184159570001464,13.487731771657364,13.791303973313264,14.094876174969164,14.398448376625064,null,0,0,0,0,0,0,0.10377064741126145,0.46790861874562023,0.56294146009762958,null,0.10377064741126145,0.46790861874562023,0.56294146009762958]
["2013-04-06T14:00:00","2013-04-06T14:00:00",null,12.089712725498019,12.393284927153919,12.696857128809819,13.000429330465719,13.304001532121619,13.607573733777519,13.911145935433419,14.214718137089319,14.518290338745219,null,0,0,0,0,0,0,8.2877722453699759E-2,0.4491081407264354,0.54613879573820145,null,8.2877722453699759E-2,0.4491081407264354,0.54613879573820145]
["2013-04-06T15:00:00","2013-04-06T15:00:00",null,12.331258128038655,12.634830329694555,12.938402531350455,13.241974733006355,13.545546934662255,13.849119136318155,14.152691337974055,14.456263539629955,14.759835741285855,null,0,0,0,0,0,0,5.8283584821220244E-2,0.42663799445853939,0.52570852236500454,null,5.8283584821220244E-2,0.42663799445853939,0.52570852236500454]
["2013-04-06T16:00:00","2013-04-06T16:00:00",null,12.463045522958197,12.766617724614097,13.070189926269997,13.373762127925897,13.677334329581797,13.980906531237697,14.284478732893596,14.588050934549496,14.891623136205396,null,0,0,0,0,0,0,2.9083960962564576E-2,0.39965699524308729,0.50084099970540041,null,2.9083960962564576E-2,0.39965699524308729,0.50084099970540041]
["2013-04-06T17:00:00","2013-04-06T17:00:00",null,12.554800925475742,12.858373127131642,13.161945328787542,13.465517530443442,13.769089732099342,14.072661933755242,14.376234135411142,14.679806337067042,14.983378538722942,null,0,0,0,0,0,0,0,0.36956361264190885,0.47291366770374776,null,-3.2701055167596929E-3,0.36956361264190885,0.47291366770374776]
["2013-04-06T18:00:00","2013-04-06T18:00:00",null,12.5493336070752,12.8529058087311,13.156478010387,13.4600502120429,13.763622413698799,14.067194615354699,14.370766817010599,14.674339018666499,14.977911220322399,null,0,0,0,0,0,0,0,0.3371149128839645,0.44268359258900702,null,-3.4761957679767967E-2,0.3371149128839645,0.44268359258900702]
["2013-04-06T19:00:00","2013-04-06T19:00:00",null,12.51793372568161,12.82150592733751,13.12507812899341,13.42865033064931,13.73222253230521,14.03579473396111,14.33936693561701,14.64293913727291,14.94651133892881,null,0,0,0,0,0,0,0,0.30564409033842743,0.41342087987793796,null,-3.3763050849889571E-2,0.30564409033842743,0.41342087987793796]
["2013-04-06T20:00:00","2013-04-06T20:00:00",null,12.316031464508498,12.619603666164398,12.923175867820298,13.226748069476198,13.530320271132098,13.833892472787998,14.137464674443898,14.441036876099798,14.744609077755698,null,0,0,0,0,0,0,0,0.27871566516665314,0.38863747568821833,null,-2.9157564623713418E-2,0.27871566516665314,0.38863747568821833]
["2013-04-06T21:00:00","2013-04-06T21:00:00",null,12.2077289601575,12.5113011618134,12.8148733634693,13.118445565125199,13.422017766781099,13.725589968436999,14.029162170092899,14.332734371748799,14.636306573404699,null,0,0,0,0,0,0,0,0.25560411556588786,0.36759734340835876,null,-2.5277600200291041E-2,0.25560411556588786,0.36759734340835876]
["2013-04-06T22:00:00","2013-04-06T22:00:00",null,12.026814475057888,12.330386676713788,12.633958878369688,12.937531080025588,13.241103281681488,13.544675483337388,13.848247684993288,14.151819886649188,14.455392088305087,null,0,0,0,0,0,0,0,0.2363620155798094,0.3503740866995082,null,-2.1345061733190854E-2,0.2363620155798094,0.3503740866995082]
["2013-04-06T23:00:00","2013-04-06T23:00:00",null,11.937558735812315,12.241130937468215,12.544703139124115,12.848275340780015,13.151847542435915,13.455419744091815,13.758991945747715,14.062564147403615,14.366136349059515,null,0,0,2.6287021838904996E-4,2.7128206537749954E-3,5.0576230018053205E-3,7.297277262480026E-3,9.4422982445346738E-3,0.2478441867190431,0.36382252707229201,null,9.4422982445346738E-3,0.2478441867190431,0.36382252707229201]
["2013-04-07","2013-04-07",null,11.832649757543054,12.136221959198954,12.439794160854854,12.743366362510754,13.046938564166654,13.350510765822554,13.654082967478454,13.957655169134354,14.261227370790253,null,3.5571597952406241E-2,3.8189785327561176E-2,4.0955180025013978E-2,4.5781477234636943E-2,5.0386963460813089E-2,5.4792668321013573E-2,5.8998591815238366E-2,0.29937726433203243,0.41724827025768252,null,5.8998591815238366E-2,0.29937726433203243,0.41724827025768252]
["2013-04-07T01:00:00","2013-04-07T01:00:00",null,11.676216652010009,11.979788853665909,12.283361055321809,12.586933256977709,12.890505458633609,13.194077660289508,13.497649861945408,13.801222063601308,14.104794265257208,null,7.4781319727316928E-2,7.9965120433948988E-2,8.5159435949316617E-2,9.230950588949878E-2,9.9123101950142956E-2,0.10564228336619139,0.11185653532890852,0.35415941784431043,0.47388103010741944,null,0.11185653532890852,0.35415941784431043,0.47388103010741944]
["2013-04-07T02:00:00","2013-04-07T02:00:00",null,11.558351746372525,11.861923948028425,12.165496149684325,12.469068351340225,12.772640552996124,13.076212754652024,13.379784956307924,13.683357157963824,13.986929359619724,null,0.11594679592704216,0.12367518034768021,0.13127738706349154,0.14071968530802623,0.14972036158566729,0.158321475131357,0.16652302594509535,0.41072908884163395,0.53226976301599527,null,0.16652302594509535,0.41072908884163395,0.53226976301599527]
["2013-04-07T03:00:00","2013-04-07T03:00:00",null,11.586226289129142,11.889798490785042,12.193370692440942,12.496942894096842,12.800515095752742,13.104087297408642,13.407659499064541,13.711231700720441,14.014803902376341,null,0.15921523387387979,0.16942511315611047,0.17938263702868767,0.19106458953389707,0.20219977198485722,0.21284075842524597,0.22298754885506328,0.46905473289779637,0.59237240974846761,null,0.22298754885506328,0.46905473289779637,0.59237240974846761]
["2013-04-07T04:00:00","2013-04-07T04:00:00",null,11.652988596519155,11.956560798175055,12.260132999830955,12.563705201486854,12.867277403142754,13.170849604798654,13.474421806454554,13.777994008110454,14.081566209766354,null,0.19942386247866886,0.21217832547490556,0.22455425535666201,0.2385389509749595,0.25186121364291653,0.26459464702168212,0.27673925111125619,0.52470961553512607,0.64985686910578511,null,0.27673925111125619,0.52470961553512607,0.64985686910578511]
["2013-04-07T05:00:00","2013-04-07T05:00:00",null,11.800894724024346,12.104466925680246,12.408039127336146,12.711611328992046,13.015183530647946,13.318755732303845,13.622327933959745,13.925900135615645,14.229472337271545,null,0.23626775228807811,0.25161937304199861,0.26645576816787658,0.28279578094293994,0.29835769787157168,0.31322563742365633,0.32741011440792944,0.57733623325661387,0.70435512278220291,null,0.32741011440792944,0.57733623325661387,0.70435512278220291]
["2013-04-07T06:00:00","2013-04-07T06:00:00",null,11.868412653112129,12.171984854768029,12.475557056423929,12.779129258079829,13.082701459735729,13.386273661391629,13.689845863047529,13.993418064703429,14.296990266359328,null,0.2702726437388856,0.28828451110290332,0.30564446032531617,0.32438184949208765,0.34223599472507188,0.35929101449415346,0.37556793841680342,0.62749187092524461,0.75643497044944152,null,0.37556793841680342,0.62749187092524461,0.75643497044944152]
["2013-04-07T07:00:00","2013-04-07T07:00:00",null,11.902525815679963,12.206098017335863,12.509670218991763,12.813242420647663,13.116814622303563,13.420386823959463,13.723959025615363,14.027531227271263,14.331103428927163,null,0.30280546196671443,0.32349860555830046,0.34341365330345486,0.36457996328814118,0.38474736644294905,0.40402101085523418,0.42241141133373211,0.6763647019281368,0.80724252625967707,null,0.42241141133373211,0.6763647019281368,0.80724252625967707]
["2013-04-07T08:00:00","2013-04-07T08:00:00",null,11.963466967406115,12.267039169062015,12.570611370717915,12.874183572373814,13.177755774029714,13.481327975685614,13.784900177341514,14.088472378997414,14.392044580653314,null,0.33279369648053725,0.35622069034336939,0.37873289584620762,0.40238070069248655,0.42491393581279591,0.44644826410322686,0.46699420037251499,0.72300839347908985,0.85586300185291575,null,0.46699420037251499,0.72300839347908985,0.85586300185291575]
["2013-04-07T09:00:00","2013-04-07T09:00:00",null,12.05848358433691,12.36205578599281,12.66562798764871,12.96920018930461,13.27277239096051,13.57634459261641,13.87991679427231,14.18348899592821,14.48706119758411,null,0.35876527405737541,0.38499972185260256,0.41018268877427355,0.43638559214329403,0.46134774808151824,0.48520584910250836,0.50798092482373569,0.76611910929489402,0.90101359056341901,null,0.50798092482373569,0.76611910929489402,0.90101359056341901]
["2013-04-07T10:00:00","2013-04-07T10:00:00",null,12.190787358655692,12.494359560311592,12.797931761967492,13.101503963623392,13.405076165279292,13.708648366935192,14.012220568591092,14.315792770246992,14.619364971902892,null,0.38621943966592776,0.41528237101102111,0.44316764377773155,0.47195719009570025,0.49937981127804598,0.52558271464706641,0.55060795943770402,0.81090167969965254,0.9478675782890833,null,0.55060795943770402,0.81090167969965254,0.9478675782890833]
["2013-04-07T11:00:00","2013-04-07T11:00:00",null,12.325688325574687,12.629260527230587,12.932832728886487,13.236404930542387,13.539977132198286,13.843549333854186,14.147121535510086,14.450693737165986,14.754265938821886,null,0.41419934571125822,0.44613281984115999,0.476741428070381,0.50813864695476907,0.53805327780744305,0.5666325279507004,0.59393948623695503,0.85640977190716483,0.99546811743497243,null,0.59393948623695503,0.85640977190716483,0.99546811743497243]
["2013-04-07T12:00:00","2013-04-07T12:00:00",null,12.462296405727482,12.765868607383382,13.069440809039282,13.373013010695182,13.676585212351082,13.980157414006982,14.283729615662882,14.587301817318782,14.890874018974682,null,0.43978187536488056,0.47460692189706188,0.5079704100150001,0.54200684589201431,0.57443451603248752,0.60542165737618858,0.6350313587755313,0.89970975428020916,1,null,0.6350313587755313,0.89970975428020916,1]
["2013-04-07T13:00:00","2013-04-07T13:00:00",null,12.620041807986475,12.923614009642375,13.227186211298275,13.530758412954174,13.834330614610074,14.137902816265974,14.441475017921874,14.745047219577774,15.048619421233674,null,0.46251489185116562,0.50027357002056871,0.53643399726216645,0.57315170936674897,0.60813447802996368,0.64156105500031513,0.6735155587476882,0.94044412332177629,1,null,0.6735155587476882,0.94044412332177629,1]
["2013-04-07T14:00:00","2013-04-07T14:00:00",null,12.674733039958538,12.978305241614438,13.281877443270337,13.585449644926237,13.889021846582137,14.192594048238037,14.496166249893937,14.799738451549837,15.103310653205737,null,0.4848273159880282,0.52555117022085973,0.56455059582105926,0.60397061377068118,0.64155054019157975,0.67744809721478827,0.71177894773639827,0.98098922580610337,1,null,0.71177894773639827,0.98098922580610337,1]
["2013-04-07T15:00:00","2013-04-07T15:00:00",null,12.720584499268897,13.024156700924797,13.327728902580697,13.631301104236597,13.934873305892497,14.238445507548397,14.542017709204297,14.845589910860197,15.149162112516096,null,0.5054153114922586,0.54914640102346091,0.5910058545997332,0.63315972282060129,0.67335783661665483,0.71176843292766268,0.74849665984098079,1,1,null,0.74849665984098079,1,1]
["2013-04-07T16:00:00","2013-04-07T16:00:00",null,12.844805191368865,13.148377393024765,13.451949594680665,13.755521796336565,14.059093997992465,14.362666199648364,14.666238401304264,14.969810602960164,15.273382804616064,null,0.52309070497673837,0.56983954461504693,0.61456954097612759,0.65947828908571293,0.70230510506565702,0.74323925547319969,0.78238588839569712,1,1,null,0.78238588839569712,1,1]
["2013-04-07T17:00:00","2013-04-07T17:00:00",null,12.844827733859654,13.148399935515554,13.451972137171454,13.755544338827354,14.059116540483254,14.362688742139154,14.666260943795054,14.969833145450954,15.273405347106854,null,0.53842129611318779,0.5881878858586026,0.63578842500449173,0.68345205300279432,0.72890757116662885,0.77236527567070645,0.81393031460238308,1,1,null,0.81393031460238308,1,1]
["2013-04-07T18:00:00","2013-04-07T18:00:00",null,12.664115069922952,12.967687271578852,13.271259473234752,13.574831674890651,13.878403876546551,14.181976078202451,14.485548279858351,14.789120481514251,15.092692683170151,null,0.49232437461648398,0.54498253676417829,0.59534847060752027,0.6456513155984489,0.69363038785881836,0.73949598356333968,0.78337428041683987,0.97166259045766046,0.97379709663097946,null,0.78337428041683987,0.97166259045766046,0.97379709663097946]
["2013-04-07T19:00:00","2013-04-07T19:00:00",null,12.759622692515752,13.063194894171652,13.366767095827552,13.670339297483451,13.973911499139351,14.277483700795251,14.581055902451151,14.884628104107051,15.188200305762951,null,0.44282065508945812,0.49843347849184533,0.55162789588505345,0.60462253191228599,0.65518824712160373,0.7035248228789821,0.74976895169798374,0.94032846042568574,0.94465004681600162,null,0.74976895169798374,0.94032846042568574,0.94465004681600162]
["2013-04-07T20:00:00","2013-04-07T20:00:00",null,12.635905601904122,12.939477803560022,13.243050005215922,13.546622206871822,13.850194408527722,14.153766610183622,14.457338811839522,14.760911013495422,15.064483215151322,null,0.39515702709115558,0.45371399693950015,0.50971586826510329,0.56539178051990413,0.61852310906069907,0.66930963525346332,0.71790908122923092,0.91072927383507873,0.91721691082492041,null,0.71790908122923092,0.91072927383507873,0.91721691082492041]
["2013-04-07T21:00:00","2013-04-07T21:00:00",null,12.502305918025607,12.805878119681507,13.109450321337407,13.413022522993307,13.716594724649207,14.020166926305107,14.323739127961007,14.627311329616907,14.930883531272807,null,0.34977511258846999,0.4112551992653008,0.47004349490582786,0.52837965377072593,0.58404505121679129,0.63727101303620592,0.68819423174253269,0.88324356380031965,0.89187622177221604,null,0.68819423174253269,0.88324356380031965,0.89187622177221604]
["2013-04-07T22:00:00","2013-04-07T22:00:00",null,12.358193069742255,12.661765271398155,12.965337473054054,13.268909674709954,13.572481876365854,13.876054078021754,14.179626279677654,14.483198481333554,14.786770682989454,null,0.31009222442045903,0.37439027983842044,0.43585985170651581,0.49676162390289103,0.55486645697560677,0.61043722114305166,0.66360009411005316,0.86079444714989484,0.87148800763396128,null,0.66360009411005316,0.86079444714989484,0.87148800763396128]
["2013-04-07T23:00:00","2013-04-07T23:00:00",null,12.2758715469534,12.5794437486093,12.8830159502652,13.1865881519211,13.490160353577,13.7937325552329,14.0973047568888,14.4008769585447,14.7044491602006,null,0.27378458985656345,0.34083752516324212,0.40492528440649239,0.4683295810819314,0.52883179054635532,0.5866842682094171,0.64203422139341548,0.8413315361803696,0.85403342513292835,null,0.64203422139341548,0.8413315361803696,0.85403342513292835]
["2013-04-08","2013-04-08",null,12.166006601462753,12.469578803118653,12.773151004774553,13.076723206430453,13.380295408086353,13.683867609742252,13.987439811398152,14.291012013054052,14.594584214709952,null,0.23887542485449761,0.30867272524115796,0.3753681570508276,0.44126446339659481,0.50414301963525576,0.56427721079393445,0.62179321457745862,0.82317246149405399,0.83787216410636955,null,0.62179321457745862,0.82317246149405399,0.83787216410636955]
["2013-04-08T01:00:00","2013-04-08T01:00:00",null,12.069231434176352,12.372803635832252,12.676375837488152,12.979948039144052,13.283520240799952,13.587092442455852,13.890664644111752,14.194236845767652,14.497809047423551,null,0.20800394640688757,0.28046149340364512,0.34970150892732077,0.41801622128226723,0.48319752063401628,0.54553982162716297,0.60516930196653507,0.80856739216035833,0.82520181958001737,null,0.60516930196653507,0.80856739216035833,0.82520181958001737]
["2013-04-08T02:00:00","2013-04-08T02:00:00",null,11.934087526850762,12.237659728506662,12.541231930162562,12.844804131818462,13.148376333474362,13.451948535130262,13.755520736786162,14.059092938442062,14.362665140097961,null,0.17978219976063917,0.25486844894128724,0.32661098894402663,0.39731256288194566,0.46476506092057612,0.52927341251324855,0.5909848249822619,0.79637021402710639,0.81490782182790222,null,0.5909848249822619,0.79637021402710639,0.81490782182790222]
["2013-04-08T03:00:00","2013-04-08T03:00:00",null,11.916044775571615,12.219616977227515,12.523189178883415,12.826761380539315,13.130333582195215,13.433905783851115,13.737477985507015,14.041050187162915,14.344622388818815,null,0.15235957857829346,0.23005350032536093,0.30428804999842851,0.37735545590184899,0.44706863781862527,0.51374304001082349,0.57751535499200701,0.78486701327040154,0.80529728664359856,null,0.57751535499200701,0.78486701327040154,0.80529728664359856]
["2013-04-08T05:00:00","2013-04-08T05:00:00",null,12.244638681901908,12.548210883557807,12.851783085213707,13.155355286869607,13.458927488525507,13.762499690181407,14.066071891837307,14.369644093493207,14.673216295149107,null,0.11732423587140089,0.19775200788971448,0.27458371532046588,0.35013261608547896,0.42222214477649228,0.49115723084683632,0.55709559642754558,0.76652918683558147,0.78894675905979961,null,0.55709559642754558,0.76652918683558147,0.78894675905979961]
["2013-04-08T06:00:00","2013-04-08T06:00:00",null,12.32905261739349,12.63262481904939,12.93619702070529,13.23976922236119,13.54334142401709,13.84691362567299,14.15048582732889,14.45405802898479,14.757630230640689,null,7.8797976664301744E-2,0.16202268780627482,0.2415146418471234,0.31960812632614249,0.3941265758350706,0.46538543463597387,0.53354242485988668,0.74510000663250608,0.76955745175142332,null,0.53354242485988668,0.74510000663250608,0.76955745175142332]
["2013-04-08T07:00:00","2013-04-08T07:00:00",null,12.306447304755965,12.610019506411865,12.913591708067765,13.217163909723665,13.520736111379565,13.824308313035464,14.127880514691364,14.431452716347264,14.735024918003164,null,3.8179270518825748E-2,0.12425349482813614,0.20646878433149526,0.28714891175946261,0.36414885612998332,0.43777354689638809,0.50819122099844671,0.7219253681793274,0.74846474542788599,null,0.50819122099844671,0.7219253681793274,0.74846474542788599]
["2013-04-08T08:00:00","2013-04-08T08:00:00",null,12.419126604869437,12.722698806525337,13.026271008181237,13.329843209837136,13.633415411493036,13.936987613148936,14.240559814804836,14.544132016460736,14.847704218116636,null,0,8.5001713818283198E-2,0.16994033878415288,0.25322813877853961,0.33272009281938852,0.40872113036003027,0.48142051795770585,0.69733123054684787,0.72596305473378331,null,0.48142051795770585,0.69733123054684787,0.72596305473378331]
["2013-04-08T09:00:00","2013-04-08T09:00:00",null,12.638772676346797,12.942344878002697,13.245917079658597,13.549489281314496,13.853061482970396,14.156633684626296,14.460205886282196,14.763778087938096,15.067350289593996,null,0,4.012451013490459E-2,0.12787058903316934,0.21385018006385992,0.29590774743618597,0.37436925022094925,0.44942395497539067,0.66758483663394297,0.6983827114204042,null,0.44942395497539067,0.66758483663394297,0.6983827114204042]
["2013-04-08T10:00:00","2013-04-08T10:00:00",null,12.851520628041126,13.155092829697026,13.458665031352925,13.762237233008825,14.065809434664725,14.369381636320625,14.672953837976525,14.976526039632425,15.280098241288325,null,0,0,8.0785275515322719E-2,0.16951974643473053,0.25420601599094711,0.33520158768098079,0.41267469844460147,0.63315935283371294,0.66618636707211332,null,0.41267469844460147,0.63315935283371294,0.66618636707211332]
["2013-04-08T11:00:00","2013-04-08T11:00:00",null,12.993140552676167,13.296712754332066,13.600284955987966,13.903857157643866,14.207429359299766,14.511001560955666,14.814573762611566,15.118145964267466,15.421718165923366,null,0,0,3.1344644840710208E-2,0.12285502526630637,0.21020154143262015,0.29375221164539539,0.37366475803566646,0.59649421477280828,0.63178191288935448,null,0.37366475803566646,0.59649421477280828,0.63178191288935448]
["2013-04-08T12:00:00","2013-04-08T12:00:00",null,13.126993594972593,13.430565796628493,13.734137998284393,14.037710199940292,14.341282401596192,14.644854603252092,14.948426804907992,15.251999006563892,15.555571208219792,null,0,0,0,7.4181975629389885E-2,0.16419925321453641,0.25031553675878876,0.33269906320191689,0.55789435190456016,0.59545324870798777,null,0.33269906320191689,0.55789435190456016,0.59545324870798777]
["2013-04-08T13:00:00","2013-04-08T13:00:00",null,13.194056011374737,13.497628213030637,13.801200414686537,14.104772616342437,14.408344817998337,14.711917019654237,15.015489221310137,15.319061422966037,15.622633624621937,null,0,0,0,2.3069490365823016E-2,0.11579958860474453,0.20452354471541626,0.28939908082887256,0.51700226073195954,0.55686390064847524,null,0.28939908082887256,0.51700226073195954,0.55686390064847524]
["2013-04-08T14:00:00","2013-04-08T14:00:00",null,13.229583538168615,13.533155739824515,13.836727941480415,14.140300143136315,14.443872344792215,14.747444546448115,15.051016748104015,15.354588949759915,15.658161151415815,null,0,0,0,0,6.6211750607834144E-2,0.15755389409366083,0.24495298430365198,0.47496405540718267,0.51714946805425754,null,0.24495298430365198,0.47496405540718267,0.51714946805425754]
["2013-04-08T15:00:00","2013-04-08T15:00:00",null,13.260068197877214,13.563640399533114,13.867212601189014,14.170784802844913,14.474357004500813,14.777929206156713,15.081501407812613,15.385073609468513,15.688645811124413,null,0,0,0,0,1.5698609442194304E-2,0.10967996992064705,0.19961312903590864,0.43205312095735415,0.47657282114372379,null,0.19961312903590864,0.43205312095735415,0.47657282114372379]
["2013-04-08T16:00:00","2013-04-08T16:00:00",null,13.290408736229754,13.593980937885654,13.897553139541554,14.201125341197454,14.504697542853354,14.808269744509253,15.111841946165153,15.415414147821053,15.718986349476953,null,0,0,0,0,0,6.0701990830399261E-2,0.1531902484684024,0.38806967601649833,0.43494469335963382,null,0.1531902484684024,0.38806967601649833,0.43494469335963382]
["2013-04-08T17:00:00","2013-04-08T17:00:00",null,13.218510355186062,13.522082556841962,13.825654758497862,14.129226960153762,14.432799161809662,14.736371363465562,15.039943565121462,15.343515766777362,15.647087968433262,null,0,0,0,0,0,1.4110873323124051E-2,0.1091121702489265,0.34639948899746614,0.3955982790711608,null,0.1091121702489265,0.34639948899746614,0.3955982790711608]
["2013-04-08T18:00:00","2013-04-08T18:00:00",null,13.194028263659618,13.497600465315518,13.801172666971418,14.104744868627318,14.408317070283218,14.711889271939118,15.015461473595018,15.319033675250918,15.622605876906817,null,0,0,0,0,0,1.3532558842668142E-2,0.11103638024753434,0.35072107538778213,0.40222260857456488,null,0.11103638024753434,0.35072107538778213,0.40222260857456488]
["2013-04-08T19:00:00","2013-04-08T19:00:00",null,13.24588676485352,13.54945896650942,13.85303116816532,14.156603369821219,14.460175571477119,14.763747773133019,15.067319974788919,15.370892176444819,15.674464378100719,null,1.3196084963130307E-2,1.6318983157592219E-2,1.931570364722739E-2,2.2175731623300252E-2,2.4920096703281935E-2,4.1081357729840576E-2,0.14110873323124165,0.38321183438066869,0.4370476551067462,null,0.14110873323124165,0.38321183438066869,0.4370476551067462]
["2013-04-08T20:00:00","2013-04-08T20:00:00",null,13.167675752260948,13.471247953916848,13.774820155572748,14.078392357228648,14.381964558884548,14.685536760540447,14.989108962196347,15.292681163852247,15.596253365508147,null,2.9189109049920108E-2,3.5392846203901679E-2,4.1333713139494216E-2,4.7011709856697691E-2,5.2458380781718807E-2,7.1206284757225707E-2,0.17372566992895497,0.41821563266135459,0.47434368169178459,null,0.17372566992895497,0.41821563266135459,0.47434368169178459]
["2013-04-08T21:00:00","2013-04-08T21:00:00",null,13.040417121459502,13.343989323115402,13.647561524771302,13.951133726427202,14.254705928083101,14.558278129739001,14.861850331394901,15.165422533050801,15.468994734706701,null,4.6980165430491008E-2,5.6264741543992247E-2,6.5139240116806579E-2,7.3614175957669545E-2,8.1752637918994536E-2,0.10307667003471413,0.20806703525930045,0.45492282995720151,0.51333259248324847,null,0.20806703525930045,0.45492282995720151,0.51333259248324847]
["2013-04-08T22:00:00","2013-04-08T22:00:00",null,12.913707424475032,13.217279626130932,13.520851827786831,13.824424029442731,14.127996231098631,14.431568432754531,14.735140634410431,15.038712836066331,15.342285037722231,null,7.2489091422964419E-2,8.4696784364951885E-2,9.6368222061425715E-2,0.10751391932112142,0.11820747980518798,0.14198146235629353,0.24931662992891018,0.49843310850495703,0.55899840682179425,null,0.24931662992891018,0.49843310850495703,0.55899840682179425]
["2013-04-08T23:00:00","2013-04-08T23:00:00",null,12.746392158782211,13.049964360438111,13.353536562094011,13.65710876374991,13.96068096540581,14.26425316706171,14.56782536871761,14.87139757037351,15.17496977202941,null,0.10055311593817939,0.11570495532612421,0.13019436176372867,0.14403185005972824,0.15730153868400748,0.18353598647923453,0.29323698601735265,0.54461414847154532,0.60735601219664392,null,0.29323698601735265,0.54461414847154532,0.60735601219664392]
["2013-04-09","2013-04-09",null,12.610782957892351,12.914355159548251,13.217927361204151,13.521499562860051,13.82507176451595,14.12864396617185,14.43221616782775,14.73578836948365,15.03936057113955,null,0.13390608924738207,0.15191795661139973,0.16913069851151474,0.18556534456519813,0.20132704285980557,0.22994835223800519,0.34193106527174028,0.59549530794292982,0.66032961860640527,null,0.34193106527174028,0.59549530794292982,0.66032961860640527]
["2013-04-09T01:00:00","2013-04-09T01:00:00",null,12.465574107590497,12.769146309246397,13.072718510902297,13.376290712558196,13.679862914214096,13.983435115869996,14.287007317525896,14.590579519181796,14.894151720837696,null,0.16983519069679742,0.19066502680194569,0.21056955973836458,0.22958033393226066,0.24780249747098959,0.27876860919721957,0.39300149130036488,0.64872126976234468,0.71562699774672578,null,0.39300149130036488,0.64872126976234468,0.71562699774672578]
["2013-04-09T02:00:00","2013-04-09T02:00:00",null,12.472853869654886,12.776426071310786,13.079998272966685,13.383570474622585,13.687142676278485,13.990714877934385,14.294287079590285,14.597859281246185,14.901431482902085,null,0.20859277569607895,0.23217749168994445,0.25471072681025386,0.27623454029194922,0.2968540802223863,0.33011242025296883,0.44654289738184655,0.70436563759093873,0.77329020885254773,null,0.44654289738184655,0.70436563759093873,0.77329020885254773]
["2013-04-09T03:00:00","2013-04-09T03:00:00",null,12.496237601283431,12.799809802939331,13.103382004595231,13.406954206251131,13.710526407907031,14.014098609562931,14.31767081121883,14.62124301287473,14.92481521453063,null,0.2464881463790444,0.27284877187909828,0.29803173880076927,0.3220791063789995,0.34511705231861589,0.38067813546228646,0.49932723723436778,0.75926345399930795,0.83022789815561593,null,0.49932723723436778,0.75926345399930795,0.83022789815561593]
["2013-04-09T04:00:00","2013-04-09T04:00:00",null,12.542712503364516,12.846284705020416,13.149856906676316,13.453429108332216,13.757001309988116,14.060573511644016,14.364145713299916,14.667717914955816,14.971290116611716,null,0.28243827744593086,0.31160635687837979,0.33947060002761908,0.36607306612859092,0.39156096250359324,0.42945633318655857,0.55034508921931458,0.81242632696630945,0.8854516736347875,null,0.55034508921931458,0.81242632696630945,0.8854516736347875]
["2013-04-09T05:00:00","2013-04-09T05:00:00",null,12.778462975562574,13.082035177218474,13.385607378874374,13.689179580530274,13.992751782186174,14.296323983842074,14.599896185497974,14.903468387153874,15.207040588809773,null,0.30944030627885405,0.34158407658346707,0.37228731809130811,0.40159209003731933,0.42967714417000547,0.47005400971456346,0.59332962733029204,0.85769257857290382,0.93290500545837873,null,0.59332962733029204,0.85769257857290382,0.93290500545837873]
["2013-04-09T06:00:00","2013-04-09T06:00:00",null,12.872737754513686,13.176309956169586,13.479882157825486,13.783454359481386,14.087026561137286,14.390598762793186,14.694170964449086,14.997743166104986,15.301315367760886,null,0.33560115041293231,0.37071009678097377,0.40424182183868101,0.43625941443846722,0.46693111152010164,0.50978947192625224,0.63544143631621786,0.90208610105444653,0.97949612296565391,null,0.63544143631621786,0.90208610105444653,0.97949612296565391]
["2013-04-09T07:00:00","2013-04-09T07:00:00",null,12.963426021790298,13.266998223446198,13.570570425102098,13.874142626757997,14.177714828413897,14.481287030069797,14.784859231725697,15.088431433381597,15.392003635037497,null,0.35831313728174624,0.39645034856562955,0.43286313121688075,0.4676461185141198,0.50095703258838031,0.54634946189980127,0.67443034710768179,0.94340929938520524,1,null,0.67443034710768179,0.94340929938520524,1]
["2013-04-09T08:00:00","2013-04-09T08:00:00",null,12.981973363862554,13.285545565518454,13.589117767174354,13.892689968830254,14.196262170486154,14.499834372142054,14.803406573797954,15.106978775453854,15.410550977109754,null,0.38063607622734436,0.42181206723580511,0.46111642228933586,0.49867531909276325,0.53463596496838539,0.58257297799381236,0.71309329882834327,0.98441705345389707,1,null,0.71309329882834327,0.98441705345389707,1]
["2013-04-09T09:00:00","2013-04-09T09:00:00",null,13.041828739951846,13.345400941607746,13.648973143263646,13.952545344919546,14.256117546575446,14.559689748231346,14.863261949887246,15.166834151543146,15.470406353199046,null,0.4006352424423833,0.44488155760162812,0.48711954429238069,0.52748589502820309,0.56613833194012919,0.61665147310576884,0.74964277399315682,1,1,null,0.74964277399315682,1,1]
["2013-04-09T10:00:00","2013-04-09T10:00:00",null,13.226927330893989,13.530499532549889,13.834071734205789,14.137643935861689,14.441216137517589,14.744788339173489,15.048360540829389,15.351932742485289,15.655504944141189,null,0.41681753308641323,0.46418674644011992,0.50940042400303653,0.55261628790619621,0.59400257508936849,0.6471339036301631,0.78264875861408589,1,1,null,0.78264875861408589,1,1]
["2013-04-09T11:00:00","2013-04-09T11:00:00",null,13.382110404485427,13.685682606141327,13.989254807797227,14.292827009453127,14.596399211109027,14.899971412764927,15.203543614420827,15.507115816076727,15.810688017732627,null,0.43031854750287485,0.48082117385977902,0.52904208672106634,0.57513900821776998,0.61928017528965951,0.67506123563181575,0.81312067432974455,1,1,null,0.81312067432974455,1,1]
["2013-04-09T12:00:00","2013-04-09T12:00:00",null,13.412667719002226,13.716239920658126,14.019812122314026,14.323384323969925,14.626956525625825,14.930528727281725,15.234100928937625,15.537673130593525,15.841245332249425,null,0.43985547902602956,0.49357563685601574,0.54487738867682267,0.59392897142821921,0.64089862204997494,0.69939250304590617,0.84005961431025444,1,1,null,0.84005961431025444,1,1]
["2013-04-09T13:00:00","2013-04-09T13:00:00",null,13.519180746830443,13.822752948486343,14.126325150142243,14.429897351798143,14.733469553454043,15.037041755109943,15.340613956765843,15.644186158421743,15.947758360077643,null,0.45125353169537874,0.50812813214603358,0.56245814888268231,0.6144013040363584,0.66414686416430246,0.72530099177033092,0.8685232015574208,1,1,null,0.8685232015574208,1,1]
["2013-04-09T14:00:00","2013-04-09T14:00:00",null,13.722502667420066,14.026074869075966,14.329647070731866,14.633219272387766,14.936791474043666,15.240363675699566,15.543935877355466,15.847508079011366,16.151080280667266,null,0.45561717732063695,0.51575136847931602,0.57320428341042662,0.62814415905373788,0.68076026196649042,0.74466926946123613,0.89054121104968764,1,1,null,0.89054121104968764,1,1]
["2013-04-09T15:00:00","2013-04-09T15:00:00",null,13.632620743101736,13.936192944757636,14.239765146413536,14.543337348069436,14.846909549725336,15.150481751381236,15.454053953037135,15.757626154693035,16.061198356348935,null,0.4183316655443341,0.48174647702850854,0.54233280496281655,0.60027991590449858,0.65577707641079508,0.72246199341172923,0.87098366680154238,0.98299755427459623,0.98545801951871781,null,0.87098366680154238,0.98299755427459623,0.98545801951871781]
["2013-04-09T16:00:00","2013-04-09T16:00:00",null,13.531296108184076,13.834868309839976,14.138440511495876,14.442012713151776,14.745584914807676,15.049157116463576,15.352729318119476,15.656301519775376,15.959873721431276,null,0.34801913952963104,0.41466199729562297,0.47832916418945065,0.53923093638582564,0.59756709525072382,0.66697534771416855,0.81810469367040106,0.93263162043125425,0.93749997687581954,null,0.81810469367040106,0.93263162043125425,0.93749997687581954]
["2013-04-09T17:00:00","2013-04-09T17:00:00",null,13.706627398236481,14.010199599892381,14.313771801548281,14.617344003204181,14.920916204860081,15.224488406515981,15.528060608171881,15.831632809827781,16.135205011483681,null,0.27709675460826538,0.34693611422986814,0.41366309046574434,0.47749849429934116,0.5386421070966344,0.61075266540511852,0.76447916911903491,0.88150862035895183,0.88877435319522524,null,0.76447916911903491,0.88150862035895183,0.88877435319522524]
["2013-04-09T18:00:00","2013-04-09T18:00:00",null,13.583872605137767,13.887444806793667,14.191017008449567,14.494589210105467,14.798161411761367,15.101733613417267,15.405305815073167,15.708878016729066,16.012450218384966,null,0.20762541329240725,0.28066127476962088,0.35043754553881007,0.41720658100962865,0.48115764773931696,0.55595999708410493,0.71227314374696959,0.83178408984847918,0.84144719907646071,null,0.71227314374696959,0.83178408984847918,0.84144719907646071]
["2013-04-09T19:00:00","2013-04-09T19:00:00",null,13.67002594993863,13.97359815159453,14.27717035325043,14.58074255490633,14.88431475656223,15.18788695821813,15.491459159874029,15.795031361529929,16.098603563185829,null,0.13239195678946114,0.20872946820964125,0.28166018159949902,0.35144696717742391,0.41830012111812731,0.49588889477783926,0.65487280285953664,0.77695987710125891,0.7891044811908331,null,0.65487280285953664,0.77695987710125891,0.7891044811908331]
["2013-04-09T20:00:00","2013-04-09T20:00:00",null,13.476157439977488,13.779729641633388,14.083301843289288,14.386874044945188,14.690446246601088,14.994018448256988,15.297590649912888,15.601162851568787,15.904735053224687,null,6.6674402192198653E-2,0.14613481180684068,0.22207276049506919,0.2947300888578025,0.36432760787848756,0.44456611333956114,0.60608409032652899,0.73061060019490165,0.74510000663250608,null,0.60608409032652899,0.73061060019490165,0.74510000663250608]
["2013-04-09T21:00:00","2013-04-09T21:00:00",null,13.514044026263086,13.817616227918986,14.121188429574886,14.424760631230786,14.728332832886686,15.031905034542586,15.335477236198486,15.639049437854386,15.942621639510286,null,0,8.2236319120830417E-2,0.16119201791616522,0.23674091868117808,0.30911434720805153,0.39201309927922229,0.55608617478893174,0.68306263509269027,0.69991787349579615,null,0.55608617478893174,0.68306263509269027,0.69991787349579615]
["2013-04-09T22:00:00","2013-04-09T22:00:00",null,13.40681714189288,13.71038934354878,14.01396154520468,14.31753374686058,14.62110594851648,14.92467815017238,15.228250351828279,15.531822553484179,15.835394755140079,null,0,2.2081098344680229E-2,0.10399145839470796,0.18237935751832254,0.25746560669897101,0.34297203133656112,0.50954763132533432,0.63893198282953656,0.65810047915446612,null,0.50954763132533432,0.63893198282953656,0.65810047915446612]
["2013-04-09T23:00:00","2013-04-09T23:00:00",null,13.415804152876198,13.719376354532098,14.022948556187998,14.326520757843898,14.630092959499798,14.933665161155698,15.237237362811598,15.540809564467498,15.844381766123398,null,0,0,4.3804693192351078E-2,0.12508416471824521,0.20294632340508206,0.29111299465276935,0.46025420797301969,0.59208850991260786,0.61362283820303887,null,0.46025420797301969,0.59208850991260786,0.61362283820303887]
["2013-04-10","2013-04-10",null,13.346138060422813,13.649710262078713,13.953282463734613,14.256854665390513,14.560426867046413,14.863999068702313,15.167571270358213,15.471143472014113,15.774715673670013,null,0,0,0,7.2678357980204222E-2,0.15322179289460938,0.24396459228250936,0.41557678565561679,0.549787434369442,0.5736139909642255,null,0.41557678565561679,0.549787434369442,0.5736139909642255]
["2013-04-10T01:00:00","2013-04-10T01:00:00",null,13.280043547210632,13.583615748866531,13.887187950522431,14.190760152178331,14.494332353834231,14.797904555490131,15.101476757146031,15.405048958801931,15.708621160457831,null,0,0,0,1.9936077362625239E-2,0.10318181812206983,0.19652177526765363,0.37062597831108923,0.50722348860788702,0.53335278831575861,null,0.37062597831108923,0.50722348860788702,0.53335278831575861]
["2013-04-10T02:00:00","2013-04-10T02:00:00",null,11.536606461670564,11.840178663326464,12.143750864982364,12.447323066638264,12.750895268294164,13.054467469950064,13.358039671605964,13.661611873261863,13.965184074917763,null,0,0,0,0,6.7010876071736558E-2,0.16296902059247531,0.33956523330623911,0.47854960518600947,0.50696061838949802,null,0.33956523330623911,0.47854960518600947,0.50696061838949802]
["2013-04-10T03:00:00","2013-04-10T03:00:00",null,10.64420719230376,10.94777939395966,11.25135159561556,11.55492379727146,11.85849599892736,12.16206820058326,12.46564040223916,12.76921260389506,13.07278480555096,null,0,0,0,0,5.2700221382636678E-2,0.1509085349727857,0.32964976866860413,0.47067401344307352,0.50103026626264102,null,0.32964976866860413,0.47067401344307352,0.50103026626264102]
["2013-04-10T04:00:00","2013-04-10T04:00:00",null,10.343041549459848,10.646613751115748,10.950185952771648,11.253758154427548,11.557330356083447,11.860902557739347,12.164474759395247,12.468046961051147,12.771619162707047,null,0,0,0,0,4.5592210677396765E-2,0.1459245156321293,0.32668459260517563,0.4696330473782529,0.50181887691780813,null,0.32668459260517563,0.4696330473782529,0.50181887691780813]
["2013-04-10T05:00:00","2013-04-10T05:00:00",null,10.247729028578828,10.551301230234728,10.854873431890628,11.158445633546528,11.462017835202428,11.765590036858327,12.069162238514227,12.372734440170127,12.676306641826027,null,0,0,0,0,4.3163289859481944E-2,0.14551443809144238,0.32820923987183209,0.47298727136489715,0.50690804434582015,null,0.32820923987183209,0.47298727136489715,0.50690804434582015]
["2013-04-10T06:00:00","2013-04-10T06:00:00",null,10.119072637762823,10.422644839418723,10.726217041074623,11.029789242730523,11.333361444386423,11.636933646042323,11.940505847698223,12.244078049354123,12.547650251010023,null,0,0,0,0,4.3489248930284365E-2,0.14781718120453047,0.33238361893985019,0.47894916791796083,0.51456282510530926,null,0.33238361893985019,0.47894916791796083,0.51456282510530926]
["2013-04-10T07:00:00","2013-04-10T07:00:00",null,10.056376264753609,10.359948466409509,10.663520668065409,10.967092869721309,11.270665071377209,11.574237273033109,11.877809474689009,12.181381676344909,12.484953878000809,null,0,0,0,1.2512622395318778E-3,4.6759354447044148E-2,0.15300098191116254,0.33937596674899889,0.48765542955100616,0.52490939690110228,null,0.33937596674899889,0.48765542955100616,0.52490939690110228]
["2013-04-10T08:00:00","2013-04-10T08:00:00",null,9.9574482538464544,10.261020455502354,10.564592657158254,10.868164858814154,11.171737060470054,11.475309262125954,11.778881463781854,12.082453665437754,12.386025867093654,null,0,0,7.1500699401821585E-4,4.0692309806624931E-3,5.1575136847931545E-2,0.15969891507571554,0.34786141739859744,0.49784427921576574,0.5367175271111384,null,0.34786141739859744,0.49784427921576574,0.5367175271111384]
["2013-04-10T09:00:00","2013-04-10T09:00:00",null,9.9640781637478142,10.267650365403714,10.571222567059614,10.874794768715514,11.178366970371414,11.481939172027314,11.785511373683214,12.089083575339114,12.392655776995014,null,0,0,1.0619956822917618E-3,6.5296962247840002E-3,5.6043930560545394E-2,0.16606037436073054,0.35602090897739352,0.50770716980972286,0.54819969825037207,null,0.35602090897739352,0.50770716980972286,0.54819969825037207]
["2013-04-10T10:00:00","2013-04-10T10:00:00",null,9.9584675162540002,10.2620397179099,10.5656119195658,10.8691841212217,11.1727563228776,11.4763285245335,11.7799007261894,12.0834729278453,12.3870451295012,null,0,0,0,5.7621151870879744E-3,5.7358281652490642E-2,0.16935150949496144,0.36119419487529003,0.51465745838392929,0.55684287103100405,null,0.36119419487529003,0.51465745838392929,0.55684287103100405]
["2013-04-10T11:00:00","2013-04-10T11:00:00",null,9.8784316768880096,10.18200387854391,10.485576080199809,10.789148281855709,11.092720483511609,11.396292685167509,11.699864886823409,12.003437088479309,12.307009290135209,null,0,0,0,5.5097597774344861E-3,5.9198373181213994E-2,0.17316838506597046,0.36688270640122905,0.52212297258617835,0.56600126943967854,null,0.36688270640122905,0.52212297258617835,0.56600126943967854]
["2013-04-10T12:00:00","2013-04-10T12:00:00",null,9.8892484991538687,10.192820700809769,10.496392902465669,10.799965104121569,11.103537305777468,11.407109507433368,11.710681709089268,12.014253910745168,12.317826112401068,null,0,0,7.3603661148933987E-4,8.3697877535073503E-3,6.4066729625779195E-2,0.17992940708293681,0.37545227552071209,0.53239594072082241,0.5779040329283347,null,0.37545227552071209,0.53239594072082241,0.5779040329283347]
["2013-04-10T13:00:00","2013-04-10T13:00:00",null,9.7471247171244322,10.050696918780332,10.354269120436232,10.657841322092132,10.961413523748032,11.264985725403932,11.568557927059832,11.872130128715732,12.175702330371632,null,0,0,1.6403101627476715E-3,1.141908228682033E-2,6.9145382245055634E-2,0.18692175489208554,0.38426368524111304,0.54293177907385548,0.59008018144411545,null,0.38426368524111304,0.54293177907385548,0.59008018144411545]
["2013-04-10T14:00:00","2013-04-10T14:00:00",null,9.8823562561210121,10.185928457776912,10.489500659432812,10.793072861088712,11.096645062744612,11.400217264400512,11.703789466056412,12.007361667712312,12.310933869368212,null,0,0,2.5866429489482512E-3,1.4478891628868871E-2,7.4203005246860951E-2,0.19387204346629203,0.39301200610910064,0.55337298414826852,0.60214066706380509,null,0.39301200610910064,0.55337298414826852,0.60214066706380509]
["2013-04-10T15:00:00","2013-04-10T15:00:00",null,9.8458884782089431,10.149460679864843,10.453032881520741,10.756605083176641,11.060177284832541,11.363749486488441,11.667321688144341,11.970893889800241,12.274466091456141,null,0,0,1.8821507636655973E-3,1.5940450043111988E-2,7.7714951364538654E-2,0.19931871439131313,0.40029876856284513,0.56240520485211631,0.61283422754787165,null,0.40029876856284513,0.56240520485211631,0.61283422754787165]
["2013-04-10T16:00:00","2013-04-10T16:00:00",null,9.9200724731539207,10.223644674809821,10.527216876465719,10.830789078121619,11.134361279777519,11.437933481433419,11.741505683089319,12.045077884745218,12.348650086401118,null,0,0,9.1478835999389357E-4,1.7139138238966057E-2,8.0953512455091747E-2,0.20449200028920964,0.40730163118072943,0.57115352572010392,0.62323337338734242,null,0.40730163118072943,0.57115352572010392,0.62323337338734242]
["2013-04-10T17:00:00","2013-04-10T17:00:00",null,10.051824495937019,10.355396697592919,10.658968899248819,10.962541100904719,11.266113302560619,11.569685504216519,11.873257705872419,12.176829907528319,12.480402109184219,null,0,0,2.3132579218236376E-4,1.8579667035738049E-2,8.4402369720356085E-2,0.20984403793561068,0.41446221592964716,0.58002802429291822,0.63373766731416881,null,0.41446221592964716,0.58002802429291822,0.63373766731416881]
["2013-04-10T18:00:00","2013-04-10T18:00:00",null,10.153026358530818,10.456598560186718,10.76017076184262,11.06374296349852,11.36731516515442,11.670887366810319,11.974459568466219,12.278031770122119,12.581603971778019,null,0,0,0,1.8537607800795802E-2,8.6400183380112863E-2,0.21376606159397532,0.42021381630799959,0.58751456811263836,0.64288555091410771,null,0.42021381630799959,0.58751456811263836,0.64288555091410771]
["2013-04-10T19:00:00","2013-04-10T19:00:00",null,10.128082146832494,10.431654348488394,10.735226550144294,11.038798751800194,11.342370953456093,11.645943155111993,11.949515356767893,12.253087558423793,12.556659760079693,null,0,0,0,1.6192805452765476E-2,8.6147827970459376E-2,0.21550100503534306,0.4238309105130329,0.59292969461145284,0.65000407642808322,null,0.4238309105130329,0.59292969461145284,0.65000407642808322]
["2013-04-10T20:00:00","2013-04-10T20:00:00",null,10.037431337491565,10.341003539147465,10.644575740803365,10.948147942459265,11.251720144115165,11.555292345771065,11.858864547426965,12.162436749082865,12.466008950738765,null,0,0,0,1.495205802196916E-2,8.6989012669304339E-2,0.21831897377647366,0.42852051520909357,0.59940681679255903,0.65817408281561485,null,0.42852051520909357,0.59940681679255903,0.65817408281561485]
["2013-04-10T21:00:00","2013-04-10T21:00:00",null,9.9997559132829554,10.303328114938855,10.606900316594755,10.910472518250655,11.214044719906555,11.517616921562455,11.821189123218355,12.124761324874255,12.428333526530155,null,0,0,0,1.5551402119896194E-2,8.9628229661930403E-2,0.22289291557644314,0.43492403372905081,0.60755579356261957,0.66798439936589415,null,0.43492403372905081,0.60755579356261957,0.66798439936589415]
["2013-04-10T22:00:00","2013-04-10T22:00:00",null,9.809795518190576,10.113367719846476,10.416939921502376,10.720512123158276,11.024084324814176,11.327656526470076,11.631228728125976,11.934800929781876,12.238373131437775,null,0,0,1.2197178133251916E-3,1.8895111297804908E-2,9.4980267308331465E-2,0.23013761879524536,0.44396676924163414,0.61831244289909948,0.68036032924765066,null,0.44396676924163414,0.61831244289909948,0.68036032924765066]
["2013-04-10T23:00:00","2013-04-10T23:00:00",null,9.6645876079456521,9.968159809601552,10.271732011257452,10.575304212913354,10.878876414569254,11.182448616225154,11.486020817881053,11.789593019536953,12.093165221192853,null,5.5728486298478586E-4,2.8495131673373013E-3,6.2352815801882643E-3,2.5940033150631446E-2,0.10394939915976585,0.24092581255793197,0.45647939163695289,0.63245486064843037,0.6960589386898447,null,0.45647939163695289,0.63245486064843037,0.6960589386898447]
["2013-04-11","2013-04-11",null,9.5548314165179598,9.8584036181738597,10.16197581982976,10.465548021485661,10.769120223141561,11.072692424797461,11.376264626453361,11.679836828109261,11.983409029765161,null,3.4383424565287732E-3,7.9807398302915566E-3,1.3479984798990482E-2,3.5182550029190442E-2,0.11507406680199045,0.25382748287646656,0.47106343135317741,0.64863715129246025,0.71375536179179555,null,0.47106343135317741,0.64863715129246025,0.71375536179179555]
["2013-04-11T01:00:00","2013-04-11T01:00:00",null,9.5138740002112243,9.8174462018671242,10.121018403523024,10.424590605178926,10.728162806834826,11.031735008490726,11.335307210146626,11.638879411802526,11.942451613458426,null,8.6431727806319612E-3,1.5372650371391641E-2,2.2922283043525157E-2,4.6570087889804088E-2,0.12828066657385631,0.26876902608970016,0.48763476992042309,0.66675416674383359,0.7333444504661476,null,0.48763476992042309,0.66675416674383359,0.7333444504661476]
["2013-04-11T02:00:00","2013-04-11T02:00:00",null,9.5302140238790152,9.8337862255349151,10.137358427190815,10.440930628846715,10.744502830502615,11.048075032158515,11.351647233814415,11.655219435470315,11.958791637126215,null,1.2870125892327885E-2,2.1807713317555585E-2,3.1439278119330373E-2,5.7042837390423838E-2,0.14060402241193498,0.2828378401778821,0.5033649237888238,0.68405102711383303,0.75212389886786135,null,0.5033649237888238,0.68405102711383303,0.75212389886786135]
["2013-04-11T03:00:00","2013-04-11T03:00:00",null,9.4777757603835013,9.7813479620394013,10.084920163695301,10.388492365351201,10.692064567007101,10.995636768663001,11.299208970318901,11.602781171974801,11.906353373630701,null,2.0114829111130102E-2,3.1186922709676886E-2,4.2826815979944019E-2,7.0312526014703086E-2,0.1556507137125242,0.29956690087616122,0.52168172060617279,0.703881956389103,0.77338484213116776,null,0.52168172060617279,0.703881956389103,0.77338484213116776]
["2013-04-11T04:00:00","2013-04-11T04:00:00",null,9.5059108095598983,9.8094830112157982,10.113055212871698,10.416627414527598,10.720199616183498,11.023771817839398,11.327344019495298,11.630916221151198,11.934488422807098,null,2.5771796210862459E-2,3.9020455217670572E-2,5.2700221382636733E-2,8.2110141416003646E-2,0.16926739102507699,0.31489749201261064,0.53864210709663429,0.72237750495495656,0.79334194911126443,null,0.53864210709663429,0.72237750495495656,0.79334194911126443]
["2013-04-11T05:00:00","2013-04-11T05:00:00",null,9.4958305871062798,9.7994027887621797,10.10297499041808,10.40654719207398,10.71011939372988,11.013691595385779,11.317263797041679,11.620835998697579,11.924408200353479,null,2.8106083750157222E-2,4.3636456252582292E-2,5.9461243399603098E-2,9.0900521518933478E-2,0.17996095150914354,0.32738908479045831,0.55283709888964294,0.73819177729324181,0.81068086871620615,null,0.55283709888964294,0.73819177729324181,0.81068086871620615]
["2013-04-11T06:00:00","2013-04-11T06:00:00",null,9.5148703020218903,9.8184425036777903,10.12201470533369,10.42558690698959,10.72915910864549,11.03273131030139,11.33630351195729,11.63987571361319,11.94344791526909,null,2.9473008885780281E-2,4.7316639310028989E-2,6.5317991865311134E-2,9.8797142879340535E-2,0.18979229767689401,0.339039492869461,0.5662224504100134,0.75320692416762436,0.82725220728345183,null,0.5662224504100134,0.75320692416762436,0.82725220728345183]
["2013-04-11T07:00:00","2013-04-11T07:00:00",null,9.5348198298614619,9.8383920315173619,10.141964233173262,10.44553643482916,10.74910863648506,11.05268083814096,11.35625303979686,11.65982524145276,11.96339744310866,null,2.9609701399342585E-2,4.9798134171621621E-2,6.999708175263622E-2,0.1055581648963069,0.19850907411867491,0.3496068756487008,0.57853529143935645,0.76718110497718628,0.84280360940334798,null,0.57853529143935645,0.76718110497718628,0.84280360940334798]
["2013-04-11T08:00:00","2013-04-11T08:00:00",null,9.597755516160511,9.901327717816411,10.204899919472311,10.508472121128209,10.812044322784109,11.115616524440009,11.419188726095909,11.722760927751809,12.026333129407709,null,3.0166986262327371E-2,5.2668676956430044E-2,7.5044189945705983E-2,0.11265566079281125,0.20755180963125822,0.36047918788127192,0.59114254711329528,0.78142867081387279,0.85860736693289763,null,0.59114254711329528,0.78142867081387279,0.85860736693289763]
["2013-04-11T09:00:00","2013-04-11T09:00:00",null,9.7403730332446177,10.043945234900518,10.347517436556418,10.651089638212317,10.954661839868217,11.258234041524117,11.561806243180017,11.865378444835917,12.168950646491817,null,2.6623495718442979E-2,5.153307761298935E-2,7.6179789289146677E-2,0.11592576630957104,0.21284075842524591,0.36767131705639633,0.6001432233909364,0.79214326091541043,0.87095175238844746,null,0.6001432233909364,0.79214326091541043,0.87095175238844746]
["2013-04-11T10:00:00","2013-04-11T10:00:00",null,9.8499579535570536,10.153530155212954,10.457102356868853,10.760674558524753,11.064246760180653,11.367818961836553,11.671391163492453,11.974963365148353,12.278535566804253,null,2.0913954575032815E-2,4.8273486904965128E-2,7.5222941694210538E-2,0.11714548412289623,0.21611086394200568,0.37288666218923511,0.60719866005249845,0.80094415582707579,0.88142450188906718,null,0.60719866005249845,0.80094415582707579,0.88142450188906718]
["2013-04-11T11:00:00","2013-04-11T11:00:00",null,9.9811415879172163,10.284713789573116,10.588285991229016,10.891858192884916,11.195430394540816,11.499002596196716,11.802574797852616,12.106146999508516,12.409719201164416,null,1.1860704253713935E-2,4.1722761062710001E-2,7.1038047817456859E-2,0.11520024450681726,0.21627910088177468,0.3750527127887609,0.61126789103316093,0.80681141910151943,0.88900567898740734,null,0.61126789103316093,0.80681141910151943,0.88900567898740734]
["2013-04-11T12:00:00","2013-04-11T12:00:00",null,10.042212874021114,10.345785075677014,10.649357277332914,10.952929478988814,11.256501680644714,11.560073882300614,11.863646083956514,12.167218285612414,12.470790487268314,null,3.4067980303220894E-3,3.5750349700910788E-2,6.7399923994952413E-2,0.11377023051878082,0.21694153383211509,0.37770244459012253,0.61578925878945256,0.81312030434285665,0.89701796324390559,null,0.61578925878945256,0.81312030434285665,0.89701796324390559]
["2013-04-11T13:00:00","2013-04-11T13:00:00",null,10.320624590272409,10.624196791928309,10.927768993584209,11.231341195240109,11.534913396896009,11.838485598551909,12.142057800207809,12.445630001863709,12.749202203519609,null,0,2.623444779522718E-2,6.0260368863505817E-2,0.10888084445674449,0.2141761391346623,0.37695589316989764,0.61695640255909989,0.81611702483249182,0.90174962717490847,null,0.61695640255909989,0.81611702483249182,0.90174962717490847]
["2013-04-11T14:00:00","2013-04-11T14:00:00",null,10.683427227527737,10.986999429183637,11.290571630839537,11.594143832495437,11.897716034151337,12.201288235807237,12.504860437463137,12.808432639119037,13.112004840774937,null,0,2.7864243149239264E-3,3.9493621610770871E-2,9.064816610927999E-2,0.19835135198764148,0.36342333432722934,0.60560040912469293,0.80683244871899062,0.89444183510369291,null,0.60560040912469293,0.80683244871899062,0.89444183510369291]
["2013-04-11T15:00:00","2013-04-11T15:00:00",null,10.873541016017816,11.177113217673716,11.480685419329616,11.784257620985516,12.087829822641416,12.391402024297316,12.694974225953215,12.998546427609115,13.302118629265015,null,0,0,1.3585132886346107E-2,6.7368379568745723E-2,0.17757408992617096,0.3450329338487314,0.58947069252434081,0.7928687827181643,0.88253907161503675,null,0.58947069252434081,0.7928687827181643,0.88253907161503675]
["2013-04-11T16:00:00","2013-04-11T16:00:00",null,11.006625329646864,11.310197531302764,11.613769732958664,11.917341934614564,12.220914136270464,12.524486337926364,12.828058539582264,13.131630741238164,13.435202942894064,null,0,0,0,4.4687937126138493E-2,0.15735411272768524,0.32715775899827598,0.57382465712582453,0.77934673868423154,0.87104638566706749,null,0.57382465712582453,0.77934673868423154,0.87104638566706749]
["2013-04-11T17:00:00","2013-04-11T17:00:00",null,10.940858043887289,11.244430245543189,11.548002447199089,11.851574648854989,12.155146850510889,12.458719052166789,12.762291253822688,13.065863455478588,13.369435657134488,null,0,0,0,2.1723594847671088E-2,0.13687126531081045,0.30904074354690264,0.55795781074386153,0.76562491328432314,0.85936443316185807,null,0.55795781074386153,0.76562491328432314,0.85936443316185807]
["2013-04-11T18:00:00","2013-04-11T18:00:00",null,11.065298405899235,11.368870607555134,11.672442809211034,11.976015010866934,12.279587212522834,12.583159414178734,12.886731615834634,13.190303817490534,13.493876019146434,null,0,0,0,0,0.11415927844199654,0.28871561826106129,0.53991439895363713,0.74975806690236013,0.84556900410080071,null,0.53991439895363713,0.74975806690236013,0.84556900410080071]
["2013-04-11T19:00:00","2013-04-11T19:00:00",null,10.848059164184347,11.151631365840247,11.455203567496147,11.758775769152047,12.062347970807947,12.365920172463847,12.669492374119747,12.973064575775647,13.276636777431547,null,0,0,0,0,9.1541924851802681E-2,0.26853770029751783,0.5220497389119173,0.73410151669510837,0.83201541564066128,null,0.5220497389119173,0.73410151669510837,0.83201541564066128]
["2013-04-11T20:00:00","2013-04-11T20:00:00",null,10.715087056163817,11.018659257819717,11.322231459475617,11.625803661131517,11.929375862787417,12.232948064443317,12.536520266099217,12.840092467755117,13.143664669411017,null,0,0,0,0,7.4539479126398939E-2,0.25385902730267329,0.50956866094280517,0.72372340047310868,0.8236456278871539,null,0.50956866094280517,0.72372340047310868,0.8236456278871539]
["2013-04-11T21:00:00","2013-04-11T21:00:00",null,10.618643727414954,10.922215929070854,11.225788130726754,11.529360332382653,11.832932534038553,12.136504735694453,12.440076937350353,12.743649139006253,13.047221340662153,null,0,0,0,0,6.1795530938897794E-2,0.2433442185671113,0.50117784357182671,0.71735142637935811,0.8191978637920112,null,0.50117784357182671,0.71735142637935811,0.8191978637920112]
["2013-04-11T22:00:00","2013-04-11T22:00:00",null,10.545948011427765,10.849520213083665,11.153092414739564,11.456664616395464,11.760236818051364,12.063809019707264,12.367381221363164,12.670953423019064,12.974525624674964,null,0,0,0,0,5.2363747503098683E-2,0.23606797092210241,0.49596249843898793,0.71409183567133394,0.81779939423018144,null,0.49596249843898793,0.71409183567133394,0.81779939423018144]
["2013-04-11T23:00:00","2013-04-11T23:00:00",null,10.405007080965987,10.708579282621887,11.012151484277787,11.315723685933687,11.619295887589587,11.922868089245487,12.226440290901387,12.530012492557287,12.833584694213187,null,0,0,0,0,4.6191554775323787E-2,0.23199873994143991,0.49390159592681776,0.71392359873156497,0.81945021920166472,null,0.49390159592681776,0.71392359873156497,0.81945021920166472]
["2013-04-12","2013-04-12",null,10.338799813470846,10.642372015126746,10.945944216782646,11.249516418438546,11.553088620094446,11.856660821750346,12.160233023406246,12.463805225062146,12.767377426718046,null,0,0,0,0,4.3047626963390748E-2,0.2308946850242059,0.49473226581692714,0.71659436015039768,0.82387695367933633,null,0.49473226581692714,0.71659436015039768,0.82387695367933633]
["2013-04-12T01:00:00","2013-04-12T01:00:00",null,10.076914277008584,10.380486478664483,10.684058680320383,10.987630881976283,11.291203083632183,11.594775285288083,11.898347486943983,12.201919688599883,12.505491890255783,null,0,0,0,5.5728486298478586E-4,4.5644784721074562E-2,0.23541605278049757,0.50109372510194217,0.72469076287678047,0.83363469618593788,null,0.50109372510194217,0.72469076287678047,0.83363469618593788]
["2013-04-12T02:00:00","2013-04-12T02:00:00",null,10.084917142829243,10.388489344485142,10.692061546141041,10.995633747796941,11.299205949452841,11.60277815110874,11.90635035276464,12.20992255442054,12.51349475607644,null,0,0,1.5982509278054237E-3,4.2164383029603611E-3,5.1259692585864672E-2,0.2428815669827466,0.51032572717176561,0.73559461953555827,0.8461262889637855,null,0.51032572717176561,0.73559461953555827,0.8461262889637855]
["2013-04-12T03:00:00","2013-04-12T03:00:00",null,9.9728662849941045,10.276438486650004,10.580010688305904,10.883582889961804,11.187155091617704,11.490727293273604,11.794299494929504,12.097871696585404,12.401443898241304,null,0,1.4615584142431176E-3,5.215345132838751E-3,9.8523757852215926E-3,5.8819840066733749E-2,0.25225026156613234,0.52141885038778346,0.74831753810558832,0.86040539922667869,null,0.52141885038778346,0.74831753810558832,0.86040539922667869]
["2013-04-12T04:00:00","2013-04-12T04:00:00",null,9.9745443942384391,10.278116595894339,10.581688797550239,10.885260999206139,11.188833200862039,11.492405402517939,11.795977604173839,12.099549805829739,12.403122007485639,null,0,2.9862056808996071E-3,8.8850133815498878E-3,1.5551402119896196E-2,6.6432561591280637E-2,0.26168204500193143,0.53257506245621478,0.76111406033676732,0.87475811315072083,null,0.53257506245621478,0.76111406033676732,0.87475811315072083]
["2013-04-12T05:00:00","2013-04-12T05:00:00",null,10.004583637857069,10.308155839512969,10.611728041168867,10.915300242824767,11.218872444480667,11.522444646136567,11.826016847792467,12.129589049448366,12.433161251104266,null,0,2.8179687411306153E-3,1.0903856658777791E-2,1.9631147909294253E-2,7.2468061805493228E-2,0.26956815155360292,0.54221714206672511,0.77242799453623201,0.88764926866051985,null,0.54221714206672511,0.77242799453623201,0.88764926866051985]
["2013-04-12T06:00:00","2013-04-12T06:00:00",null,9.9978827422541734,10.301454943910073,10.605027145565973,10.908599347221873,11.212171548877773,11.515743750533673,11.819315952189573,12.122888153845473,12.426460355501373,null,0,0,9.7998017415437816E-3,2.0682628782850453E-2,7.5559415573748456E-2,0.27459423012920153,0.54907279736231152,0.78102910808192172,0.89790120717769284,null,0.54907279736231152,0.78102910808192172,0.89790120717769284]
["2013-04-12T07:00:00","2013-04-12T07:00:00",null,10.265177801156748,10.568750002812648,10.872322204468549,11.175894406124449,11.479466607780349,11.783038809436249,12.086611011092149,12.390183212748049,12.693755414403949,null,0,0,9.2109724523523097E-3,2.2186246432035817E-2,7.9039817265219484E-2,0.27994626777560261,0.55621235249375811,0.78986154741979375,0.90835292706084148,null,0.55621235249375811,0.78986154741979375,0.90835292706084148]
["2013-04-12T08:00:00","2013-04-12T08:00:00",null,10.577368812999453,10.880941014655352,11.184513216311254,11.488085417967154,11.791657619623054,12.095229821278954,12.398802022934854,12.702374224590754,13.005946426246654,null,0,0,7.0659514702976628E-3,2.2123157579622445E-2,8.0942997646356207E-2,0.28372108411166935,0.56176417150613489,0.79710625063859597,0.91721691082492018,null,0.56176417150613489,0.79710625063859597,0.91721691082492018]
["2013-04-12T09:00:00","2013-04-12T09:00:00",null,10.867771571058071,11.171343772713971,11.474915974369871,11.778488176025771,12.082060377681671,12.385632579337571,12.689204780993471,12.992776982649371,13.296349184305271,null,0,0,0,1.1934307914862869E-2,7.293071338985796E-2,0.27778021717607682,0.55778957380409244,0.79501380370021912,0.91691198137158891,null,0.55778957380409244,0.79501380370021912,0.91691198137158891]
["2013-04-12T10:00:00","2013-04-12T10:00:00",null,11.086313868478372,11.389886070134272,11.693458271790172,11.997030473446072,12.300602675101972,12.604174876757872,12.907747078413772,13.211319280069672,13.514891481725572,null,0,0,0,0,6.1595749572922125E-2,0.26855872991498897,0.5505869298202325,0.78972485490623145,0.91346312410632458,null,0.5505869298202325,0.78972485490623145,0.91346312410632458]
["2013-04-12T11:00:00","2013-04-12T11:00:00",null,11.404510058299156,11.708082259955056,12.011654461610956,12.315226663266856,12.618798864922756,12.922371066578656,13.225943268234555,13.529515469890455,13.833087671546355,null,0,0,0,0,4.5834051278314691E-2,0.25496308221990732,0.53906269944605656,0.78017740857434115,0.90579782853809987,null,0.53906269944605656,0.78017740857434115,0.90579782853809987]
["2013-04-12T12:00:00","2013-04-12T12:00:00",null,11.531122836991425,11.834695038647325,12.138267240303225,12.441839441959125,12.745411643615025,13.048983845270925,13.352556046926825,13.656128248582725,13.959700450238625,null,0,0,0,0,2.4762374572248447E-2,0.23616260420072246,0.52242827202639752,0.76561439847558777,0.89321160248163212,null,0.52242827202639752,0.76561439847558777,0.89321160248163212]
["2013-04-12T13:00:00","2013-04-12T13:00:00",null,11.689442125293048,11.993014326948948,12.296586528604848,12.600158730260748,12.903730931916648,13.207303133572548,13.510875335228448,13.814447536884348,14.118019738540248,null,0,0,0,0,2.7338502712455359E-4,0.21398687257742222,0.50247116504630085,0.74778128286007461,0.87739733014334687,null,0.50247116504630085,0.74778128286007461,0.87739733014334687]
["2013-04-12T14:00:00","2013-04-12T14:00:00",null,11.800323414733722,12.103895616389622,12.407467818045522,12.711040019701421,13.014612221357321,13.318184423013221,13.621756624669121,13.925328826325021,14.228901027980921,null,0,0,0,0,0,0.18763676188610384,0.47841328265933503,0.72592099549884126,0.85764000452922584,null,0.47841328265933503,0.72592099549884126,0.85764000452922584]
["2013-04-12T15:00:00","2013-04-12T15:00:00",null,11.923284248042155,12.226856449698055,12.530428651353954,12.834000853009854,13.137573054665754,13.441145256321654,13.744717457977554,14.048289659633454,14.351861861289354,null,0,0,0,0,0,0.15667065015987375,0.44982351770734197,0.69960242923372962,0.83349800367237548,null,0.44982351770734197,0.69960242923372962,0.83349800367237548]
["2013-04-12T16:00:00","2013-04-12T16:00:00",null,11.992359118749008,12.295931320404907,12.599503522060807,12.903075723716707,13.206647925372607,13.510220127028507,13.813792328684407,14.117364530340307,14.420936731996207,null,0,0,0,0,0,0.12293914373619086,0.41851041729283833,0.67061310154978515,0.80672730063163467,null,0.41851041729283833,0.67061310154978515,0.80672730063163467]
["2013-04-12T17:00:00","2013-04-12T17:00:00",null,12.107662884326329,12.411235085982229,12.714807287638129,13.018379489294029,13.321951690949929,13.625523892605829,13.929096094261729,14.232668295917628,14.536240497573528,null,0,0,0,0,0,8.6946953434362151E-2,0.38494714780892442,0.63938411960516606,0.77772745813895472,null,0.38494714780892442,0.63938411960516606,0.77772745813895472]
["2013-04-12T18:00:00","2013-04-12T18:00:00",null,12.144859465497007,12.448431667152906,12.752003868808806,13.055576070464706,13.359148272120606,13.662720473776506,13.966292675432406,14.269864877088306,14.573437078744206,null,0,0,0,0,0,4.9440630674612504E-2,0.34990129029329631,0.60669357924630385,0.74728708684950274,null,0.34990129029329631,0.60669357924630385,0.74728708684950274]
["2013-04-12T19:00:00","2013-04-12T19:00:00",null,11.986280598509794,12.289852800165693,12.593425001821593,12.896997203477493,13.200569405133393,13.504141606789293,13.807713808445193,14.111286010101093,14.414858211756993,null,0,0,0,0,0,1.2428503925434271E-2,0.31537065840571071,0.57453929413295524,0.71740400042303554,null,0.31537065840571071,0.57453929413295524,0.71740400042303554]
["2013-04-12T20:00:00","2013-04-12T20:00:00",null,11.889306136971641,12.192878338627541,12.49645054028344,12.80002274193934,13.10359494359524,13.40716714525114,13.71073934690704,14.01431154856294,14.31788375021884,null,0,0,0,0,0,0,0.28434145782706727,0.54582335147613548,0.69090668240941933,null,0.28434145782706727,0.54582335147613548,0.69090668240941933]
["2013-04-12T21:00:00","2013-04-12T21:00:00",null,11.710986509398726,12.014558711054626,12.318130912710526,12.621703114366426,12.925275316022326,13.228847517678226,13.532419719334126,13.835991920990026,14.139564122645925,null,0,0,0,0,0,0,0.25733942899414408,0.52107149171262257,0.66831035843669662,null,0.25733942899414408,0.52107149171262257,0.66831035843669662]
["2013-04-12T22:00:00","2013-04-12T22:00:00",null,11.435181132245837,11.738753333901737,12.042325535557637,12.345897737213537,12.649469938869437,12.953042140525337,13.256614342181237,13.560186543837137,13.863758745493037,null,0,0,0,0,0,0,0.23831813999151244,0.50417419407457442,0.65344241888461196,null,0.23831813999151244,0.50417419407457442,0.65344241888461196]
["2013-04-12T23:00:00","2013-04-12T23:00:00",null,11.223403922438235,11.526976124094135,11.830548325750035,12.134120527405935,12.437692729061835,12.741264930717735,13.044837132373635,13.348409334029535,13.651981535685435,null,0,0,0,0,0,0,0.22182040508541567,0.48976890610685447,0.64103494457664878,null,0.22182040508541567,0.48976890610685447,0.64103494457664878]
["2013-04-13","2013-04-13",null,11.213674512986252,11.517246714642152,11.820818916298052,12.124391117953952,12.427963319609852,12.731535521265751,13.035107722921651,13.338679924577551,13.642252126233451,null,0,0,0,0,0,0,0.20890821995814554,0.47887556425681227,0.63207632753394993,null,0.20890821995814554,0.47887556425681227,0.63207632753394993]
["2013-04-13T01:00:00","2013-04-13T01:00:00",null,11.026591089342418,11.330163290998318,11.633735492654218,11.937307694310118,12.240879895966017,12.544452097621917,12.848024299277817,13.151596500933717,13.455168702589617,null,0,0,0,0,0,0,0.19822517428281455,0.47020084704997361,0.62531530551698356,null,0.19822517428281455,0.47020084704997361,0.62531530551698356]
["2013-04-13T02:00:00","2013-04-13T02:00:00",null,10.976686655708734,11.280258857364634,11.583831059020534,11.887403260676434,12.190975462332334,12.494547663988234,12.798119865644134,13.101692067300034,13.405264268955934,null,0,0,0,0,0,0,0.18951891264976922,0.46346085465047837,0.62045746388115386,null,0.18951891264976922,0.46346085465047837,0.62045746388115386]
["2013-04-13T03:00:00","2013-04-13T03:00:00",null,10.990883110285468,11.294455311941368,11.598027513597268,11.901599715253168,12.205171916909068,12.508744118564968,12.812316320220868,13.115888521876768,13.419460723532668,null,0,0,0,0,0,0,0.18333620511325877,0.45919184230384019,0.61800751344576788,null,0.18333620511325877,0.45919184230384019,0.61800751344576788]
["2013-04-13T04:00:00","2013-04-13T04:00:00",null,10.964155071388442,11.267727273044342,11.571299474700242,11.874871676356141,12.178443878012041,12.482016079667941,12.785588281323841,13.089160482979741,13.392732684635641,null,0,0,0,0,0,0,0.17519774315193379,0.45300913476732974,0.61369644186418748,null,0.17519774315193379,0.45300913476732974,0.61369644186418748]
["2013-04-13T05:00:00","2013-04-13T05:00:00",null,11.010680299060539,11.314252500716441,11.61782470237234,11.92139690402824,12.22496910568414,12.52854130734004,12.83211350899594,13.13568571065184,13.43925791230774,null,0,0,0,0,0,0,0.1651245563832654,0.44493376165841814,0.60752424913641256,null,0.1651245563832654,0.44493376165841814,0.60752424913641256]
["2013-04-13T06:00:00","2013-04-13T06:00:00",null,11.033698294683498,11.337270496339398,11.640842697995298,11.944414899651198,12.247987101307098,12.551559302962998,12.855131504618898,13.158703706274798,13.462275907930698,null,0,0,0,0,0,0,0.15401040354977635,0.43582793729342145,0.6003426347700237,null,0.15401040354977635,0.43582793729342145,0.6003426347700237]
["2013-04-13T07:00:00","2013-04-13T07:00:00",null,11.051312920928424,11.354885122584324,11.658457324240224,11.962029525896124,12.265601727552024,12.569173929207924,12.872746130863824,13.176318332519724,13.479890534175624,null,0,0,0,0,0,0,0.14222330295721136,0.4260701947868199,0.59251961707076561,null,0.14222330295721136,0.4260701947868199,0.59251961707076561]
["2013-04-13T08:00:00","2013-04-13T08:00:00",null,11.340275611948403,11.643847813604303,11.947420015260203,12.250992216916103,12.554564418572003,12.858136620227903,13.161708821883803,13.465281023539703,13.768853225195603,null,0,0,0,0,0,0,0.13043620236464637,0.41627039304527613,0.58462299571035858,null,0.13043620236464637,0.41627039304527613,0.58462299571035858]
["2013-04-13T09:00:00","2013-04-13T09:00:00",null,11.561511203895758,11.865083405551658,12.168655607207558,12.472227808863458,12.775800010519358,13.079372212175258,13.382944413831158,13.686516615487058,13.990088817142958,null,0,0,0,0,0,0,0.1126661756015466,0.40059281322055318,0.57094322954539245,null,0.1126661756015466,0.40059281322055318,0.57094322954539245]
["2013-04-13T10:00:00","2013-04-13T10:00:00",null,11.793565486298956,12.097137687954856,12.400709889610756,12.704282091266656,13.007854292922556,13.311426494578456,13.614998696234355,13.918570897890255,14.222143099546155,null,0,0,0,0,0,0,9.1415747146975798E-2,0.38147689093930148,0.55386718015883973,null,9.1415747146975798E-2,0.38147689093930148,0.55386718015883973]
["2013-04-13T11:00:00","2013-04-13T11:00:00",null,11.958100549754336,12.261672751410236,12.565244953066136,12.868817154722036,13.172389356377936,13.475961558033836,13.779533759689736,14.083105961345636,14.386678163001536,null,0,0,0,0,0,0,6.6884698366909662E-2,0.35912240756749669,0.53359462891667619,null,6.6884698366909662E-2,0.35912240756749669,0.53359462891667619]
["2013-04-13T12:00:00","2013-04-13T12:00:00",null,12.046472737138926,12.350044938794825,12.653617140450725,12.957189342106625,13.260761543762525,13.564333745418425,13.867905947074325,14.171478148730225,14.475050350386125,null,0,0,0,0,0,0,3.8946851556521431E-2,0.33342421501778319,0.51004145734901729,null,3.8946851556521431E-2,0.33342421501778319,0.51004145734901729]
["2013-04-13T13:00:00","2013-04-13T13:00:00",null,12.139944045932967,12.443516247588867,12.747088449244767,13.050660650900667,13.354232852556567,13.657805054212467,13.961377255868367,14.264949457524267,14.568521659180167,null,0,0,0,0,0,0,1.0230908899701616E-2,0.30694792662163806,0.48571018993492682,null,1.0230908899701616E-2,0.30694792662163806,0.48571018993492682]
["2013-04-13T14:00:00","2013-04-13T14:00:00",null,12.195679548417358,12.499251750073258,12.802823951729158,13.106396153385058,13.409968355040958,13.713540556696858,14.017112758352757,14.320684960008657,14.624257161664557,null,0,0,0,0,0,0,0,0.2784948541832073,0.45943368290475739,null,-2.0493362225610542E-2,0.2784948541832073,0.45943368290475739]
["2013-04-13T15:00:00","2013-04-13T15:00:00",null,12.251097809282188,12.554670010938088,12.858242212593987,13.161814414249887,13.465386615905787,13.768958817561687,14.072531019217587,14.376103220873487,14.679675422529387,null,0,0,0,0,0,0,0,0.25078833316500143,0.43388269767734172,null,-2.9956690087616131E-2,0.25078833316500143,0.43388269767734172]
["2013-04-13T16:00:00","2013-04-13T16:00:00",null,12.248676007754218,12.552248209410118,12.855820411066018,13.159392612721918,13.462964814377818,13.766537016033718,14.070109217689618,14.373681419345518,14.677253621001418,null,0,0,0,0,0,0,0,0.21788749663142792,0.40324254502191403,null,-3.5256153690339381E-2,0.21788749663142792,0.40324254502191403]
["2013-04-13T17:00:00","2013-04-13T17:00:00",null,12.319214497868579,12.622786699524479,12.926358901180379,13.229931102836279,13.533503304492179,13.837075506148079,14.140647707803979,14.444219909459878,14.747792111115778,null,0,0,0,0,0,0,0,0.18517592665509455,0.37278114411499091,null,-3.5056372324363698E-2,0.18517592665509455,0.37278114411499091]
["2013-04-13T18:00:00","2013-04-13T18:00:00",null,12.357326326954507,12.660898528610407,12.964470730266306,13.268042931922206,13.571615133578106,13.875187335234006,14.178759536889906,14.482331738545806,14.785903940201706,null,0,0,0,0,0,0,0,0.1512972129091138,0.34117362905589155,null,-3.6244545711482203E-2,0.1512972129091138,0.34117362905589155]
["2013-04-13T19:00:00","2013-04-13T19:00:00",null,12.195311837478272,12.498884039134172,12.802456240790072,13.106028442445972,13.409600644101872,13.713172845757772,14.016745047413671,14.320317249069571,14.623889450725471,null,0,0,0,0,0,0,0,0.11778651746887772,0.30995516192000799,null,-3.58870422144731E-2,0.11778651746887772,0.30995516192000799]
["2013-04-13T20:00:00","2013-04-13T20:00:00",null,12.02062354914278,12.32419575079868,12.62776795245458,12.93134015411048,13.234912355766379,13.538484557422279,13.842056759078179,14.145628960734079,14.449201162389979,null,0,0,0,0,0,0,0,8.777725333758378E-2,0.28218555204938878,null,-3.2343551670588708E-2,8.777725333758378E-2,0.28218555204938878]
["2013-04-13T21:00:00","2013-04-13T21:00:00",null,11.847044243293553,12.150616444949453,12.454188646605353,12.757760848261253,13.061333049917152,13.364905251573052,13.668477453228952,13.972049654884852,14.275621856540752,null,0,0,0,0,0,1.1671437696473817E-3,3.4909165002065833E-3,9.3486794480993951E-2,0.29002959936611805,null,3.4909165002065833E-3,9.3486794480993951E-2,0.29002959936611805]
["2013-04-13T22:00:00","2013-04-13T22:00:00",null,11.739748254821876,12.043320456477776,12.346892658133676,12.650464859789576,12.954037061445476,13.257609263101376,13.561181464757276,13.864753666413176,14.168325868069076,null,3.8389566693536853E-2,4.1249594669609715E-2,4.3972930132120273E-2,4.6559573081068527E-2,4.9030553133925597E-2,5.2553014060338868E-2,5.7137470669043892E-2,0.1492783696318859,0.34788207702918017,null,5.7137470669043892E-2,0.1492783696318859,0.34788207702918017]
["2013-04-13T23:00:00","2013-04-13T23:00:00",null,11.583800880950051,11.887373082605951,12.190945284261851,12.494517485917751,12.798089687573651,13.10166188922955,13.40523409088545,13.70880629254135,14.01237849419725,null,8.4160529119438221E-2,8.9754407366757216E-2,9.5064385778216021E-2,0.10012200878002134,0.10493779118090873,0.11069990636799672,0.11741886915002082,0.21161015581629741,0.41215910282967066,null,0.11741886915002082,0.21161015581629741,0.41215910282967066]
["2013-04-14","2013-04-14",null,11.529529497354343,11.833101699010243,12.136673900666143,12.440246102322043,12.743818303977942,13.047390505633842,13.350962707289742,13.654534908945642,13.958107110601542,null,0.13227629389336992,0.14055144836825723,0.14840601049372204,0.15588203950470661,0.1630005650186821,0.17096027523150253,0.17977168495190349,0.27597130008667237,0.47843394228991792,null,0.17977168495190349,0.27597130008667237,0.47843394228991792]
["2013-04-14T01:00:00","2013-04-14T01:00:00",null,11.399085180812946,11.702657382468846,12.006229584124746,12.309801785780646,12.613373987436546,12.916946189092446,13.220518390748346,13.524090592404246,13.827662794060146,null,0.18294715719004317,0.19387204346629211,0.20422913007082069,0.21409202066477784,0.22348174486563471,0.23359699086924535,0.24446930310181647,0.34264570227887098,0.54699049524578214,null,0.24446930310181647,0.34264570227887098,0.54699049524578214]
["2013-04-14T02:00:00","2013-04-14T02:00:00",null,11.311426203169333,11.614998404825233,11.918570606481133,12.222142808137033,12.525715009792933,12.829287211448833,13.132859413104732,13.436431614760632,13.740003816416532,null,0.23417530534970121,0.24773940861857624,0.26060953451090413,0.27285928668783382,0.28450969476683652,0.29679099136997295,0.30972420611471424,0.40986687452531884,0.6160938182558956,null,0.30972420611471424,0.40986687452531884,0.6160938182558956]
["2013-04-14T03:00:00","2013-04-14T03:00:00",null,11.260472862323056,11.564045063978956,11.867617265634856,12.171189467290755,12.474761668946655,12.778333870602555,13.081906072258455,13.385478273914355,13.689050475570255,null,0.28768516700497621,0.30384642803153505,0.31917701916798447,0.33376105888420893,0.34764060641515077,0.36203537957413512,0.37698743759610431,0.47906483081405232,0.68713186607335242,null,0.37698743759610431,0.47906483081405232,0.68713186607335242]
["2013-04-14T04:00:00","2013-04-14T04:00:00",null,11.1313992448534,11.434971446509298,11.738543648165198,12.042115849821098,12.345688051476998,12.649260253132898,12.952832454788798,13.256404656444698,13.559976858100597,null,0.34051156609243971,0.3593120441116246,0.37715567453587334,0.39411606102633479,0.41025629243542244,0.42680660138519699,0.44380904711060082,0.54784219475336338,0.75778086596759353,null,0.44380904711060082,0.54784219475336338,0.75778086596759353]
["2013-04-14T05:00:00","2013-04-14T05:00:00",null,11.229250352412397,11.532822554068296,11.836394755724196,12.139966957380096,12.443539159035996,12.747111360691896,13.050683562347796,13.354255764003696,13.657827965659596,null,0.38875350857119817,0.41028783686162917,0.43072862504356174,0.45015999158688025,0.46864502534399821,0.48743498855444745,0.50657194045317033,0.61263444618189644,0.82451835701220555,null,0.50657194045317033,0.61263444618189644,0.82451835701220555]
["2013-04-14T06:00:00","2013-04-14T06:00:00",null,11.377856236437058,11.681428438092958,11.985000639748858,12.288572841404758,12.592145043060658,12.895717244716558,13.199289446372457,13.502861648028357,13.806433849684257,null,0.43692184738880768,0.46116899633301367,0.48417539784642338,0.50604620001639222,0.52685500650406947,0.54786359435772225,0.56911402281229306,0.67719537181824707,0.89101400745589965,null,0.56911402281229306,0.67719537181824707,0.89101400745589965]
["2013-04-14T07:00:00","2013-04-14T07:00:00",null,11.548738876042485,11.852311077698385,12.155883279354285,12.459455481010185,12.763027682666085,13.066599884321985,13.370172085977885,13.673744287633784,13.977316489289684,null,0.48401767571538989,0.51095661569589979,0.53652863054078659,0.56082835352867022,0.58396093274690664,0.60717763043502748,0.63054153544544622,0.74064172772862813,0.95639508817362417,null,0.63054153544544622,0.74064172772862813,0.95639508817362417]
["2013-04-14T08:00:00","2013-04-14T08:00:00",null,11.863246659455463,12.166818861111363,12.470391062767263,12.773963264423163,13.077535466079063,13.381107667734963,13.684679869390862,13.988252071046762,14.291824272702662,null,0.5272230248098142,0.55688530025283456,0.58505447285540524,0.61182517589614593,0.6373130722711482,0.66277993902867938,0.68829937982988831,0.8004499598165048,1,null,0.68829937982988831,0.8004499598165048,1]
["2013-04-14T09:00:00","2013-04-14T09:00:00",null,12.106953975087619,12.410526176743518,12.714098378399418,13.017670580055318,13.321242781711218,13.624814983367118,13.928387185023018,14.231959386678918,14.535531588334818,null,0.56333087800773407,0.59583215180935623,0.62671414506570189,0.65607149105539087,0.68403036748325019,0.71185255139754722,0.73963267607690197,0.85393879185430865,1,null,0.73963267607690197,0.85393879185430865,1]
["2013-04-14T10:00:00","2013-04-14T10:00:00",null,12.266823463426043,12.570395665081943,12.873967866737843,13.177540068393743,13.481112270049643,13.784684471705543,14.088256673361442,14.391828875017342,14.695401076673242,null,0.59566391486958725,0.63106727588222444,0.66470414902728736,0.69669019720086689,0.72716211291652555,0.75739218803126618,0.78746454101497354,0.90397876662684817,1,null,0.78746454101497354,0.90397876662684817,1]
["2013-04-14T11:00:00","2013-04-14T11:00:00",null,12.512103516572672,12.815675718228572,13.119247919884472,13.422820121540372,13.726392323196272,14.029964524852172,14.333536726508072,14.637108928163972,14.940681129819872,null,0.54786359435772236,0.58620058700758138,0.62262388446756822,0.65728069405998046,0.69029719348964513,0.72296670423103615,0.75537334475403828,0.87412722462658765,0.97229347898179408,null,0.75537334475403828,0.87412722462658765,0.97229347898179408]
["2013-04-14T12:00:00","2013-04-14T12:00:00",null,12.783864843670516,13.087437045326416,13.391009246982316,13.694581448638216,13.998153650294116,14.301725851950016,14.605298053605916,14.908870255261816,15.212442456917715,null,0.49380696264819812,0.53519324983137007,0.57451863450237206,0.61195135360097264,0.64762809964073453,0.68284219409613156,0.71767775543704848,0.83877643765762822,0.93918234627350938,null,0.71767775543704848,0.83877643765762822,0.93918234627350938]
["2013-04-14T13:00:00","2013-04-14T13:00:00",null,13.019807015409349,13.323379217065249,13.626951418721148,13.930523620377048,14.234095822032948,14.537668023688848,14.841240225344748,15.144812427000648,15.448384628656548,null,0.4369008177713366,0.48134691429655707,0.5235849009873097,0.5638145592095698,0.6021725814769,0.63994177445503864,0.67723780104007703,0.8007023152261582,0.90336890772018519,null,0.67723780104007703,0.8007023152261582,0.90336890772018519]
["2013-04-14T14:00:00","2013-04-14T14:00:00",null,13.279236933349658,13.582809135005558,13.886381336661458,14.189953538317358,14.493525739973258,14.797097941629158,15.100670143285058,15.404242344940958,15.707814546596857,null,0.37616728251473053,0.42369421799947066,0.46887635113618065,0.51193449290830695,0.55299482102067654,0.59336117175649894,0.63314920801186558,0.75900058378091928,0.86396991938803436,null,0.63314920801186558,0.75900058378091928,0.86396991938803436]
["2013-04-14T15:00:00","2013-04-14T15:00:00",null,13.445996096502615,13.749568298158515,14.053140499814415,14.356712701470315,14.660284903126215,14.963857104782115,15.267429306438014,15.571001508093914,15.874573709749814,null,0.30951390994000305,0.36021631766288287,0.40844774533290584,0.45441848912478283,0.49826524155207635,0.54131286851546701,0.58366651810231085,0.71198887392422161,0.81933455630557372,null,0.58366651810231085,0.71198887392422161,0.81933455630557372]
["2013-04-14T16:00:00","2013-04-14T16:00:00",null,13.673392314034956,13.976964515690856,14.280536717346756,14.584108919002656,14.887681120658556,15.191253322314456,15.494825523970356,15.798397725626256,16.101969927282155,null,0.23780291436347023,0.29174388317690314,0.34307717942391691,0.3920130992792224,0.4387093648738532,0.48449084210848997,0.52947319387922431,0.66032961860640549,0.7701042218056724,null,0.52947319387922431,0.66032961860640549,0.7701042218056724]
["2013-04-14T17:00:00","2013-04-14T17:00:00",null,13.8350894249036,14.1386616265595,14.4422338282154,14.7458060298713,15.0493782315272,15.3529504331831,15.656522634839,15.9600948364949,16.2636670381508,null,0.16076091075800747,0.21801404432314242,0.27253332761703147,0.32450802719691441,0.37413792442876698,0.42272685559579881,0.470400998402837,0.60385458088770205,0.7161317085660327,null,0.470400998402837,0.60385458088770205,0.7161317085660327]
["2013-04-14T18:00:00","2013-04-14T18:00:00",null,13.894471859970906,14.198044061626806,14.501616263282706,14.805188464938606,15.108760666594506,15.412332868250406,15.715905069906306,16.019477271562206,16.323049473218106,null,8.172109349278793E-2,0.14231793623583161,0.20004423619406708,0.25508925992473408,0.30767381841127961,0.35910174793691318,0.4094992262064619,0.54557099606648185,0.66037167784134743,null,0.4094992262064619,0.54557099606648185,0.66037167784134743]
["2013-04-14T19:00:00","2013-04-14T19:00:00",null,13.749037290628355,14.052609492284255,14.356181693940155,14.659753895596054,14.963326097251954,15.266898298907854,15.570470500563754,15.874042702219654,16.177614903875554,null,2.0503877034346724E-3,6.6043513668064879E-2,0.12701888952558901,0.18518681145071791,0.24075757561816305,0.29505604792860507,0.34820840608687104,0.48692990774825257,0.60428568804585969,null,0.34820840608687104,0.48692990774825257,0.60428568804585969]
["2013-04-14T20:00:00","2013-04-14T20:00:00",null,13.575111275674086,13.878683477329986,14.182255678985886,14.485827880641786,14.789400082297686,15.092972283953586,15.396544485609486,15.700116687265385,16.003688888921285,null,0,0,5.9587421104429925E-2,0.12078360794540068,0.17926697413259648,0.23635187075796243,0.29218550514379671,0.43348313494539092,0.55332041010459065,null,0.29218550514379671,0.43348313494539092,0.55332041010459065]
["2013-04-14T21:00:00","2013-04-14T21:00:00",null,13.373104451643176,13.676676653299076,13.980248854954976,14.283821056610876,14.587393258266776,14.890965459922676,15.194537661578575,15.498109863234475,15.801682064890375,null,0,0,0,6.3088852413372004E-2,0.12437967253296286,0.18415636019463266,0.24257663752941522,0.38635576219260204,0.50859041374350988,null,0.24257663752941522,0.38635576219260204,0.50859041374350988]
["2013-04-14T22:00:00","2013-04-14T22:00:00",null,13.109922854616784,13.413495056272684,13.717067257928584,14.020639459584483,14.324211661240383,14.627783862896283,14.931356064552183,15.234928266208083,15.538500467863983,null,0,0,0,1.4373743541513266E-2,7.8335325079936874E-2,0.14066711126434825,0.20153733903451673,0.34768229566320502,0.47217763109225869,null,0.20153733903451673,0.34768229566320502,0.47217763109225869]
["2013-04-14T23:00:00","2013-04-14T23:00:00",null,12.994740122834582,13.298312324490482,13.601884526146382,13.905456727802282,14.209028929458182,14.512601131114081,14.816173332769981,15.119745534425881,15.423317736081781,null,0,0,0,0,3.6255060520217756E-2,0.10108937118369289,0.16434646053683394,0.31279416027861029,0.43948709073339642,null,0.16434646053683394,0.31279416027861029,0.43948709073339642]
["2013-04-15","2013-04-15",null,12.919075341070762,13.222647542726662,13.526219744382562,13.829791946038462,14.133364147694362,14.436936349350262,14.740508551006162,15.044080752662062,15.347652954317962,null,0,0,0,0,0,6.4182392521870274E-2,0.12978428422304167,0.28049266784296384,0.40935164889727571,null,0.12978428422304167,0.28049266784296384,0.40935164889727571]
["2013-04-15T01:00:00","2013-04-15T01:00:00",null,12.884239994235308,13.187812195891208,13.491384397547108,13.794956599203008,14.098528800858908,14.402101002514808,14.705673204170708,15.009245405826608,15.312817607482508,null,0,0,0,0,0,2.8547705717050662E-2,9.6473370148781268E-2,0.24942140802937812,0.38042541006574465,null,9.6473370148781268E-2,0.24942140802937812,0.38042541006574465]
["2013-04-15T02:00:00","2013-04-15T02:00:00",null,12.943199539865713,13.246771741521613,13.550343943177513,13.853916144833413,14.157488346489313,14.461060548145213,14.764632749801113,15.068204951457012,15.371777153112912,null,0,0,0,0,0,0,6.1038464709937339E-2,0.21624718646868002,0.34943826872204342,null,6.1038464709937339E-2,0.21624718646868002,0.34943826872204342]
["2013-04-15T03:00:00","2013-04-15T03:00:00",null,12.896201217245792,13.199773418901692,13.503345620557592,13.806917822213492,14.110490023869392,14.414062225525292,14.717634427181192,15.021206628837092,15.324778830492992,null,0,0,0,0,0,0,6.1185672032235204E-2,0.21864456286038816,0.35399118090454179,null,6.1185672032235204E-2,0.21864456286038816,0.35399118090454179]
["2013-04-15T04:00:00","2013-04-15T04:00:00",null,12.955737375808674,13.259309577464574,13.562881779120474,13.866453980776374,14.170026182432274,14.473598384088174,14.777170585744074,15.080742787399974,15.384314989055873,null,2.3395449436625446E-2,2.6413199543731739E-2,2.9294257137275726E-2,3.204913702599297E-2,3.4688354018619028E-2,3.722242292388947E-2,0.10082650096530393,0.26060916452401611,0.39819543682884445,null,0.10082650096530393,0.26060916452401611,0.39819543682884445]
["2013-04-15T05:00:00","2013-04-15T05:00:00",null,13.12378391855658,13.42735612021248,13.73092832186838,14.034500523524279,14.338072725180179,14.641644926836079,14.945217128491979,15.248789330147879,15.552361531803779,null,4.0513558058120375E-2,4.664369155095302E-2,5.2510954825396618E-2,5.8125862690186728E-2,6.3498929954058897E-2,6.8651186234484282E-2,0.13476830356369807,0.29695885832285396,0.43686890335824147,null,0.13476830356369807,0.29695885832285396,0.43686890335824147]
["2013-04-15T06:00:00","2013-04-15T06:00:00",null,13.243643769472953,13.547215971128853,13.850788172784753,14.154360374440653,14.457932576096553,14.761504777752453,15.065076979408353,15.368649181064253,15.672221382720153,null,5.3331109906770452E-2,6.2657745255213948E-2,7.1574303062970523E-2,8.0112327756246868E-2,8.8282334143778521E-2,9.6115866651772214E-2,0.1648091121211987,0.32947064693321165,0.4717570387428362,null,0.1648091121211987,0.32947064693321165,0.4717570387428362]
["2013-04-15T07:00:00","2013-04-15T07:00:00",null,13.33891804378182,13.64249024543772,13.94606244709362,14.24963464874952,14.55320685040542,14.85677905206132,15.16035125371722,15.46392345537312,15.76749565702902,null,6.5465199187608999E-2,7.7967306774192224E-2,8.9922644306526217E-2,0.10137327101955323,0.11234021653074437,0.1228445104575708,0.19411388406720997,0.36124639893207999,0.50590913751594158,null,0.19411388406720997,0.36124639893207999,0.50590913751594158]
["2013-04-15T08:00:00","2013-04-15T08:00:00",null,13.381000304718789,13.684572506374689,13.988144708030589,14.291716909686489,14.595289111342389,14.898861312998289,15.202433514654189,15.506005716310089,15.809577917965989,null,7.6211333715353366E-2,9.1920457966282995E-2,0.10694611964940109,0.12133037799964991,0.1351047774432361,0.14831137721510196,0.22216739377368938,0.3917919183088876,0.5388520332844573,null,0.22216739377368938,0.3917919183088876,0.5388520332844573]
["2013-04-15T09:00:00","2013-04-15T09:00:00",null,13.604739264118056,13.908311465773956,14.211883667429856,14.515455869085756,14.819028070741656,15.122600272397555,15.426172474053455,15.729744675709355,16.033316877365255,null,8.4644210321274088E-2,0.10356035123655012,0.12164582226171677,0.13896371224918738,0.15555608043390418,0.17146498605080948,0.24791816036708073,0.42004520938134271,0.56950270074862053,null,0.24791816036708073,0.42004520938134271,0.56950270074862053]
["2013-04-15T10:00:00","2013-04-15T10:00:00",null,13.731508452552124,14.035080654208024,14.338652855863923,14.642225057519823,14.945797259175723,15.249369460831623,15.552941662487523,15.856513864143423,16.160086065799323,null,8.8839619006763321E-2,0.11102586543879914,0.13223423465842771,0.15254884513553349,0.17202227091379427,0.19069657122815237,0.26979947734578524,0.44448162488278881,0.59639958149418815,null,0.26979947734578524,0.44448162488278881,0.59639958149418815]
["2013-04-15T11:00:00","2013-04-15T11:00:00",null,13.923271084214008,14.226843285869908,14.530415487525808,14.833987689181708,15.137559890837608,15.441132092493508,15.744704294149408,16.048276495805307,16.351848697461207,null,8.9281240973656931E-2,0.11476913734865921,0.13914246399769195,0.16249585419937515,0.18488188199738659,0.20635312143540419,0.28814781858934091,0.46541660907529275,0.61982657535702024,null,0.28814781858934091,0.46541660907529275,0.61982657535702024]
["2013-04-15T12:00:00","2013-04-15T12:00:00",null,14.091620808561606,14.395193010217506,14.698765211873406,15.002337413529306,15.305909615185206,15.609481816841106,15.913054018497006,16.216626220152904,16.520198421808807,null,8.7136219991602287E-2,0.11594679592704216,0.14350610962295018,0.16990879435794637,0.19523896860191514,0.21952817678106337,0.30403569458877511,0.48392267244988185,0.64084567801940873,null,0.30403569458877511,0.48392267244988185,0.64084567801940873]
["2013-04-15T13:00:00","2013-04-15T13:00:00",null,14.296369226134564,14.599941427790464,14.903513629446364,15.207085831102264,15.510658032758164,15.814230234414064,16.117802436069965,16.421374637725862,16.724946839381765,null,8.1058660542447453E-2,0.11322346046453161,0.14401082044225716,0.17350485894550857,0.20181072406164138,0.22895996021686249,0.31621184310455591,0.49874855276702429,0.65822665685929271,null,0.31621184310455591,0.49874855276702429,0.65822665685929271]
["2013-04-15T14:00:00","2013-04-15T14:00:00",null,14.340770458796758,14.644342660452658,14.947914862108558,15.251487063764458,15.555059265420358,15.858631467076258,16.162203668732158,16.465775870388057,16.769348072043957,null,7.084878126021675E-2,0.10645192363882967,0.14053041875078615,0.17318941468344171,0.20453405952415193,0.2346064125078593,0.32466574932794778,0.50991527964419114,0.67200105630287899,null,0.32466574932794778,0.50991527964419114,0.67200105630287899]
["2013-04-15T15:00:00","2013-04-15T15:00:00",null,14.417554654945077,14.721126856600977,15.024699058256877,15.328271259912777,15.631843461568677,15.935415663224576,16.238987864880478,16.542560066536375,16.846132268192278,null,5.5434071653882866E-2,9.4507100915231249E-2,0.1319082755876253,0.16775325856715614,0.20216822755865049,0.23519524179705076,0.32809357697574099,0.51607695756323047,0.68080195121454434,null,0.32809357697574099,0.51607695756323047,0.68080195121454434]
["2013-04-15T16:00:00","2013-04-15T16:00:00",null,14.485522281081421,14.789094482737321,15.092666684393221,15.396238886049121,15.699811087705021,16.003383289360919,16.306955491016822,16.610527692672719,16.914099894328622,null,3.6843889809409253E-2,7.9407835570964216E-2,0.12016323423000255,0.15922574868261535,0.1967425862511005,0.2327452913616648,0.32850365451642788,0.51925242980137021,0.6866376700627812,null,0.32850365451642788,0.51925242980137021,0.6866376700627812]
["2013-04-15T17:00:00","2013-04-15T17:00:00",null,14.546249677130783,14.849821878786683,15.153394080442583,15.456966282098483,15.760538483754383,16.064110685410284,16.367682887066181,16.671255088722084,16.974827290377981,null,1.6297953540121108E-2,6.2373845419353785E-2,0.10650449768250751,0.14880557322567342,0.18944530898862047,0.22844473458881995,0.32709467014586258,0.52061935493699329,0.69069638623470808,null,0.32709467014586258,0.52061935493699329,0.69069638623470808]
["2013-04-15T18:00:00","2013-04-15T18:00:00",null,14.50185188859458,14.805424090250479,15.108996291906379,15.412568493562279,15.716140695218179,16.019712896874079,16.323285098529979,16.626857300185879,16.930429501841779,null,0,4.4078078219475909E-2,9.1615528512951724E-2,0.1371867095728774,0.18098088795649306,0.22300857847253439,0.3245711160493277,0.52090325477285349,0.69369310672434326,null,0.3245711160493277,0.52090325477285349,0.69369310672434326]
["2013-04-15T19:00:00","2013-04-15T19:00:00",null,14.369829851039292,14.673402052695192,14.976974254351092,15.280546456006991,15.584118657662891,15.887690859318791,16.191263060974691,16.494835262630591,16.798407464286491,null,0,2.9798967956582718E-2,8.0701157045438371E-2,0.12948986957844602,0.17638591653905247,0.22138929792725784,0.32582237828885957,0.52491991170983821,0.70037001027142509,null,0.32582237828885957,0.52491991170983821,0.70037001027142509]
["2013-04-15T20:00:00","2013-04-15T20:00:00",null,14.136521920663249,14.440094122319149,14.743666323975049,15.047238525630949,15.350810727286849,15.654382928942749,15.957955130598648,16.261527332254548,16.565099533910448,null,0,2.0272551242163546E-2,7.4486905082721225E-2,0.12646160466260417,0.17640694615652361,0.22434395918195077,0.33160552309341867,0.53341587716817229,0.71148416310491414,null,0.33160552309341867,0.53341587716817229,0.71148416310491414]
["2013-04-15T21:00:00","2013-04-15T21:00:00",null,14.018090189374963,14.321662391030863,14.625234592686763,14.928806794342663,15.232378995998562,15.535951197654462,15.839523399310362,16.143095600966262,16.446667802622162,null,0,1.4457862011397761E-2,7.1931806559979661E-2,0.12703991914306009,0.17998198112661468,0.23081056655432139,0.34084803997197766,0.54532915546556404,0.72597356954251857,null,0.34084803997197766,0.54532915546556404,0.72597356954251857]
["2013-04-15T22:00:00","2013-04-15T22:00:00",null,13.788387502586964,14.091959704242864,14.395531905898764,14.699104107554664,15.002676309210564,15.306248510866464,15.609820712522364,15.913392914178264,16.216965115834164,null,0,1.62453794964433E-2,7.6873766665693802E-2,0.13499962935588053,0.19085429335918577,0.24446930310181642,0.35718805274704102,0.56424529638084009,0.74737120531938728,null,0.35718805274704102,0.56424529638084009,0.74737120531938728]
["2013-04-15T23:00:00","2013-04-15T23:00:00",null,13.670016837035877,13.973589038691777,14.277161240347677,14.580733442003577,14.884305643659477,15.187877845315377,15.491450046971277,15.795022248627177,16.098594450283077,null,2.5340689052704415E-3,2.2007494683531276E-2,8.5737750429772566E-2,0.14682878918338776,0.20553296635403032,0.26188182636790708,0.37722927819702218,0.58681007592735612,0.7723649056838181,null,0.37722927819702218,0.58681007592735612,0.7723649056838181]
["2013-04-16","2013-04-16",null,13.485649221164191,13.789221422820091,14.092793624475991,14.396365826131891,14.699938027787791,15.003510229443691,15.307082431099591,15.610654632755491,15.914226834411391,null,8.611628354425277E-3,3.1292070797032522E-2,9.8082135885322358E-2,0.16210680627615934,0.22361843737919695,0.28266960323811313,0.40060369801617651,0.6126765054168386,0.80062871156500881,null,0.40060369801617651,0.6126765054168386,0.80062871156500881]
["2013-04-16T01:00:00","2013-04-16T01:00:00",null,13.381176145406627,13.684748347062527,13.988320548718427,14.291892750374327,14.595464952030227,14.899037153686127,15.202609355342027,15.506181556997927,15.809753758653827,null,1.8421944904704619E-2,4.4246315159244903E-2,0.11404361554590547,0.18094934353028644,0.24521585452204131,0.30691675218231912,0.42738491586565291,0.64190767370170099,0.83220468219790145,null,0.42738491586565291,0.64190767370170099,0.83220468219790145]
["2013-04-16T02:00:00","2013-04-16T02:00:00",null,13.345468753054568,13.649040954710468,13.952613156366368,14.256185358022268,14.559757559678168,14.863329761334068,15.166901962989968,15.470474164645868,15.774046366301768,null,2.9367860798424659E-2,5.8315129247426857E-2,0.13109863531498703,0.2008538764667053,0.26786475253844183,0.33219435238261014,0.45518607016247886,0.67212723400770613,0.86475853004320136,null,0.45518607016247886,0.67212723400770613,0.86475853004320136]
["2013-04-16T03:00:00","2013-04-16T03:00:00",null,13.327811723211962,13.631383924867862,13.934956126523762,14.238528328179662,14.542100529835562,14.845672731491462,15.149244933147362,15.452817134803261,15.756389336459161,null,4.0913120790071734E-2,7.2972772624800286E-2,0.1487319695645245,0.22133672388358008,0.29108145022656273,0.35802923744588594,0.483533994513554,0.70289356436796058,0.89783811832527938,null,0.483533994513554,0.70289356436796058,0.89783811832527938]
["2013-04-16T04:00:00","2013-04-16T04:00:00",null,13.217553363122704,13.521125564778604,13.824697766434504,14.128269968090404,14.431842169746304,14.735414371402204,15.038986573058104,15.342558774714004,15.646130976369903,null,5.1101970454831308E-2,8.6337094527699582E-2,0.16513507119200121,0.24064191272207192,0.31317306337997847,0.3827810972093989,0.51085146760854405,0.73267150270707215,0.92998188862989239,null,0.51085146760854405,0.73267150270707215,0.92998188862989239]
["2013-04-16T05:00:00","2013-04-16T05:00:00",null,13.292851109278086,13.596423310933986,13.899995512589886,14.203567714245786,14.507139915901686,14.810712117557586,15.114284319213485,15.417856520869385,15.721428722525285,null,5.9671539574314335E-2,9.8124195120264573E-2,0.18000301074408587,0.25845399872011393,0.33380311811915109,0.40612397260234656,0.53679150075917548,0.76110354552803183,0.96081130784256019,null,0.53679150075917548,0.76110354552803183,0.96081130784256019]
["2013-04-16T06:00:00","2013-04-16T06:00:00",null,13.24959776923353,13.55316997088943,13.85674217254533,14.16031437420123,14.46388657585713,14.767458777513029,15.071030979168929,15.374603180824829,15.678175382480729,null,6.6937272410587681E-2,0.10864951866456213,0.19364071767410979,0.27506739652230189,0.35327654389741192,0.42833124865185351,0.56162747899257293,0.7884630778579641,0.99059976099040736,null,0.56162747899257293,0.7884630778579641,0.99059976099040736]
["2013-04-16T07:00:00","2013-04-16T07:00:00",null,13.283580687301502,13.587152888957402,13.890725090613302,14.194297292269201,14.497869493925101,14.801441695581001,15.105013897236901,15.408586098892801,15.712158300548701,null,7.5790741365930878E-2,0.12071000428425174,0.20877152744458349,0.29314235273873296,0.3741694688549736,0.45192647945445463,0.58781986755285787,0.81714747608857718,1,null,0.58781986755285787,0.81714747608857718,1]
["2013-04-16T08:00:00","2013-04-16T08:00:00",null,13.310180087006366,13.613752288662265,13.917324490318165,14.220896691974065,14.524468893629965,14.828041095285865,15.131613296941765,15.435185498597665,15.738757700253565,null,8.3676847917602382E-2,0.13181364230900522,0.2229665192375922,0.31029200578643457,0.39414760545254141,0.47462795151453296,0.61312901217935556,0.84495914519413862,1,null,0.61312901217935556,0.84495914519413862,1]
["2013-04-16T09:00:00","2013-04-16T09:00:00",null,13.411510026100483,13.715082227756383,14.018654429412283,14.322226631068183,14.625798832724083,14.929371034379983,15.232943236035883,15.536515437691783,15.840087639347683,null,9.0847947475255666E-2,0.14221278814847604,0.23644650403658268,0.32671613703138241,0.4134002202473554,0.496593386963122,0.6377021201943639,0.8720347776882108,1,null,0.6377021201943639,0.8720347776882108,1]
["2013-04-16T10:00:00","2013-04-16T10:00:00",null,13.538367708456075,13.841939910111975,14.145512111767875,14.449084313423775,14.752656515079675,15.056228716735575,15.359800918391475,15.663373120047375,15.966945321703275,null,9.6694181132228135E-2,0.15128706808726605,0.24861213774362792,0.34183643199312058,0.43135951356769531,0.51727601574597248,0.66100293635236929,0.89784863313401553,1,null,0.66100293635236929,0.89784863313401553,1]
["2013-04-16T11:00:00","2013-04-16T11:00:00",null,13.773872502737479,14.077444704393379,14.381016906049279,14.684589107705179,14.988161309361079,15.291733511016979,15.595305712672879,15.898877914328779,16.202450115984679,null,0.10041642342461708,0.15823735666147254,0.25865378008608964,0.35484325039901077,0.44721584514092277,0.53586619759044607,0.68221130557199783,0.921580556450179,1,null,0.68221130557199783,0.921580556450179,1]
["2013-04-16T12:00:00","2013-04-16T12:00:00",null,13.956728401548339,14.260300603204239,14.563872804860139,14.867445006516039,15.171017208171939,15.474589409827839,15.778161611483739,16.081733813139639,16.385306014795539,null,9.8197798781413506E-2,0.15933089676997098,0.26293330724146335,0.36217207208769747,0.45746778365809571,0.54893610484874966,0.69798351867534081,0.93994992731120586,1,null,0.69798351867534081,0.93994992731120586,1]
["2013-04-16T13:00:00","2013-04-16T13:00:00",null,14.144517923347147,14.448090125003047,14.751662326658947,15.055234528314847,15.358806729970746,15.662378931626646,15.965951133282546,16.269523334938448,16.573095536594344,null,9.2404139168118848E-2,0.15688094633458502,0.26369037347042384,0.36600997727617762,0.4642708649100043,0.55857818445926,0.71035944855709732,0.9549650741855884,1,null,0.71035944855709732,0.9549650741855884,1]
["2013-04-16T14:00:00","2013-04-16T14:00:00",null,14.329140570648086,14.632712772303986,14.936284973959886,15.239857175615786,15.543429377271686,15.847001578927586,16.150573780583485,16.454145982239385,16.757718183895285,null,8.3361403655535529E-2,0.15121346442611711,0.26125093784377346,0.36668292503525357,0.46793001834997988,0.56510788068404405,0.71965453947933411,0.96692041171792242,1,null,0.71965453947933411,0.96692041171792242,1]
["2013-04-16T15:00:00","2013-04-16T15:00:00",null,14.425073361555368,14.728645563211268,15.032217764867168,15.335789966523068,15.639362168178968,15.942934369834868,16.246506571490769,16.550078773146666,16.853650974802569,null,6.8598612190806485E-2,0.13992055984412352,0.25328071282221748,0.36190920186930842,0.46622661933481885,0.56635914292357592,0.72375531488620326,0.97375503739603775,1,null,0.72375531488620326,0.97375503739603775,1]
["2013-04-16T16:00:00","2013-04-16T16:00:00",null,14.589013640426657,14.892585842082557,15.196158043738457,15.499730245394357,15.803302447050257,16.106874648706157,16.410446850362057,16.714019052017957,17.017591253673856,null,5.1564622039196054E-2,0.12635645657524855,0.24306031873125122,0.35489582444268858,0.46230459567645421,0.56540229532863973,0.72565849526733994,0.97842361247462728,1,null,0.72565849526733994,0.97842361247462728,1]
["2013-04-16T17:00:00","2013-04-16T17:00:00",null,14.616216541963675,14.919788743619575,15.223360945275475,15.526933146931375,15.830505348587275,16.134077550243177,16.437649751899073,16.741221953554977,17.044794155210873,null,3.0934567300023415E-2,0.10926989237996031,0.22937003775754949,0.34447564898574662,0.45502834803144532,0.56114379779073709,0.72431259974918805,0.97988517088887039,1,null,0.72431259974918805,0.97988517088887039,1]
["2013-04-16T18:00:00","2013-04-16T18:00:00",null,14.61903687517899,14.92260907683489,15.22618127849079,15.52975348014669,15.83332568180259,16.136897883458488,16.440470085114391,16.744042286770288,17.047614488426191,null,1.0230908899701841E-2,9.2109724523523132E-2,0.21561666793143441,0.33399238467639131,0.44768901153402302,0.5568222114004211,0.72290361537862269,0.98129415525943575,1,null,0.72290361537862269,0.98129415525943575,1]
["2013-04-16T19:00:00","2013-04-16T19:00:00",null,14.440068305786419,14.743640507442318,15.047212709098218,15.350784910754118,15.654357112410018,15.957929314065918,16.261501515721818,16.565073717377718,16.868645919033618,null,0,7.7809584643158819E-2,0.20470229646392107,0.3263270891081666,0.44314661416026024,0.55528704932502904,0.72426002570551018,0.98543698990124717,1,null,0.72426002570551018,0.98543698990124717,1]
["2013-04-16T20:00:00","2013-04-16T20:00:00",null,14.321642976444881,14.625215178100781,14.928787379756681,15.232359581412581,15.535931783068481,15.839503984724381,16.143076186380281,16.446648388036181,16.750220589692081,null,0,6.7137053776563399E-2,0.19737347477523437,0.32219476927509072,0.44209513328670402,0.55720074451490131,0.72902323406271974,0.99294456333843839,1,null,0.72902323406271974,0.99294456333843839,1]
["2013-04-16T21:00:00","2013-04-16T21:00:00",null,14.360907661136268,14.664479862792168,14.968052064448068,15.271624266103968,15.575196467759868,15.878768669415768,16.182340871071666,16.48591307272757,16.789485274383466,null,0,5.7831448045591032E-2,0.19136951898722848,0.31935577091648898,0.44230542946141527,0.56034467232683438,0.73498513061578341,1,1,null,0.73498513061578341,1,1]
["2013-04-16T22:00:00","2013-04-16T22:00:00",null,14.191218616896396,14.494790818552296,14.798363020208196,15.101935221864096,15.405507423519996,15.709079625175896,16.012651826831796,16.316224028487696,16.619796230143596,null,0,5.1217633350922533E-2,0.18803632461805533,0.31916650435924887,0.44514442782001701,0.56609627270518681,0.74353367011779536,1,1,null,0.74353367011779536,1,1]
["2013-04-16T23:00:00","2013-04-16T23:00:00",null,13.985872103846116,14.289444305502016,14.593016507157916,14.896588708813816,15.200160910469716,15.503733112125616,15.807305313781516,16.110877515437416,16.414449717093316,null,0,4.8504812697147535E-2,0.18857257986356898,0.32281514299048886,0.45178978694089217,0.57561217461087044,0.75581496672093174,1,1,null,0.75581496672093174,1,1]
["2013-04-17","2013-04-17",null,13.837353202389053,14.140925404044953,14.444497605700853,14.748069807356753,15.051642009012653,15.355214210668553,15.658786412324453,15.962358613980353,16.265930815636253,null,0,5.070240772287999E-2,0.19395616193617674,0.33124801959640959,0.46314578037529913,0.58977562197767242,0.77268071993277321,1,1,null,0.77268071993277321,1,1]
["2013-04-17T01:00:00","2013-04-17T01:00:00",null,13.675917850325934,13.979490051981834,14.283062253637734,14.586634455293634,14.890206656949534,15.193778858605434,15.497351060261334,15.800923261917234,16.104495463573134,null,4.3846752427293533E-3,5.8325644056162439E-2,0.20468126684644997,0.34494881537884686,0.47969608932507374,0.60905978119869308,0.79459358133768443,1,1,null,0.79459358133768443,1,1]
["2013-04-17T02:00:00","2013-04-17T02:00:00",null,13.596597136364053,13.900169338019953,14.203741539675853,14.507313741331753,14.810885942987653,15.114458144643553,15.418030346299453,15.721602547955353,16.025174749611253,null,1.1440111904291454E-2,6.8577582573335391E-2,0.21799301470567145,0.36119419487529014,0.49874892275391208,0.63081492047257082,0.81894587836924604,1,1,null,0.81894587836924604,1,1]
["2013-04-17T03:00:00","2013-04-17T03:00:00",null,13.723886250708034,14.027458452363934,14.331030654019834,14.634602855675734,14.938175057331634,15.241747258987534,15.545319460643434,15.848891662299334,16.152463863955234,null,1.652927933230346E-2,7.6873766665693802E-2,0.22934900814007841,0.37549433475565447,0.51586703137540701,0.65064584974784079,0.84138448021093537,1,1,null,0.84138448021093537,1,1]
["2013-04-17T04:00:00","2013-04-17T04:00:00",null,13.851747623145954,14.155319824801854,14.458892026457754,14.762464228113654,15.066036429769554,15.369608631425454,15.673180833081354,15.976753034737254,16.280325236393153,null,1.6508249714832335E-2,8.0122842564982463E-2,0.23573149704256455,0.38487354414777575,0.52812729836107231,0.66567151143095893,0.85907038850415063,1,1,null,0.85907038850415063,1,1]
["2013-04-17T05:00:00","2013-04-17T05:00:00",null,14.007686599180891,14.311258800836791,14.614831002492691,14.918403204148591,15.221975405804491,15.525547607460391,15.829119809116291,16.132692010772189,16.436264212428092,null,0,2.7433135991081291E-2,0.18619623308933198,0.33835603030164946,0.48451187172596116,0.62484250911077166,0.82092266241153167,0.96442840204759372,0.96690989690918638,null,0.82092266241153167,0.96442840204759372,0.96690989690918638]
["2013-04-17T06:00:00","2013-04-17T06:00:00",null,14.086069877602352,14.389642079258252,14.693214280914152,14.996786482570052,15.300358684225952,15.603930885881852,15.907503087537751,16.211075289193651,16.514647490849551,null,0,0,0.11055269904569896,0.2658248796437428,0.41496692674895408,0.55815759210983751,0.75700314010805025,0.90315861154547394,0.90819520492980821,null,0.75700314010805025,0.90315861154547394,0.90819520492980821]
["2013-04-17T07:00:00","2013-04-17T07:00:00",null,14.183033025743789,14.486605227399689,14.790177429055589,15.093749630711489,15.397321832367389,15.700894034023289,16.004466235679189,16.308038437335089,16.611610638990989,null,0,0,3.1817811233810722E-2,0.19023391964378761,0.34240423166484074,0.48849698423673926,0.69013947135861153,0.83898673383233913,0.84662048497435716,null,0.69013947135861153,0.83898673383233913,0.84662048497435716]
["2013-04-17T08:00:00","2013-04-17T08:00:00",null,14.158115944050394,14.461688145706294,14.765260347362194,15.068832549018094,15.372404750673994,15.675976952329894,15.979549153985793,16.283121355641693,16.586693557297593,null,0,0,0,0.1154736295339418,0.27066169166210124,0.41964601663627932,0.62407492807307552,0.77560346677437142,0.78582386086533773,null,0.62407492807307552,0.77560346677437142,0.78582386086533773]
["2013-04-17T09:00:00","2013-04-17T09:00:00",null,14.086797139462615,14.390369341118515,14.693941542774414,14.997513744430314,15.301085946086214,15.604658147742114,15.908230349398014,16.211802551053914,16.515374752709814,null,0,0,0,4.0418924779500265E-2,0.19864576663223713,0.35054269362616586,0.55777905899535707,0.71200990354169247,0.72482745539034255,null,0.55777905899535707,0.71200990354169247,0.72482745539034255]
["2013-04-17T10:00:00","2013-04-17T10:00:00",null,14.17647247842741,14.48004468008331,14.78361688173921,15.08718908339511,15.39076128505101,15.69433348670691,15.99790568836281,16.30147789001871,16.60505009167461,null,0,0,0,0,0.1263038825315706,0.28110289673651445,0.49113620122936513,0.64805883681200438,0.66346303160960274,null,0.49113620122936513,0.64805883681200438,0.66346303160960274]
["2013-04-17T11:00:00","2013-04-17T11:00:00",null,14.313742244678897,14.617314446334797,14.920886647990697,15.224458849646597,15.528031051302497,15.831603252958397,16.135175454614298,16.438747656270195,16.742319857926098,null,0,0,0,0,5.2279629033214134E-2,0.20999124525790866,0.42282148887441884,0.58244643030209753,0.60044778285737965,null,0.42282148887441884,0.58244643030209753,0.60044778285737965]
["2013-04-17T12:00:00","2013-04-17T12:00:00",null,14.455420733992728,14.758992935648628,15.062565137304528,15.366137338960428,15.669709540616328,15.973281742272228,16.276853943928128,16.580426145584028,16.883998347239928,null,0,0,0,0,0,0.13468418509381364,0.35036394187766112,0.51274376319405701,0.53339484755070077,null,0.35036394187766112,0.51274376319405701,0.53339484755070077]
["2013-04-17T13:00:00","2013-04-17T13:00:00",null,14.566771446372055,14.870343648027955,15.173915849683855,15.477488051339755,15.781060252995655,16.084632454651555,16.388204656307455,16.691776857963355,16.995349059619254,null,0,0,0,0,0,5.8567484657080338E-2,0.27709675460826511,0.44222094100464271,0.4655217571626481,null,0.27709675460826511,0.44222094100464271,0.4655217571626481]
["2013-04-17T14:00:00","2013-04-17T14:00:00",null,14.678171943626447,14.981744145282347,15.285316346938247,15.588888548594147,15.892460750250047,16.196032951905948,16.499605153561845,16.803177355217748,17.106749556873645,null,0,0,0,0,0,0,0.2006225506745227,0.36853316138582426,0.3945257685801335,null,0.2006225506745227,0.36853316138582426,0.3945257685801335]
["2013-04-17T15:00:00","2013-04-17T15:00:00",null,14.821113283244189,15.124685484900089,15.428257686555989,15.731829888211889,16.035402089867787,16.338974291523691,16.642546493179587,16.946118694835491,17.249690896491387,null,0,0,0,0,0,0,0.11738732472381393,0.28813693379371724,0.3168633912592726,null,0.11738732472381393,0.28813693379371724,0.3168633912592726]
["2013-04-17T16:00:00","2013-04-17T16:00:00",null,14.462641345438794,14.766213547094694,15.069785748750594,15.373357950406493,15.676930152062393,15.980502353718293,16.284074555374193,16.587646757030093,16.891218958685993,null,0,0,0,0,0,0,6.8482949294715073E-2,0.24198743825333563,0.27336362752025262,null,6.8482949294715073E-2,0.24198743825333563,0.27336362752025262]
["2013-04-17T17:00:00","2013-04-17T17:00:00",null,14.889199358358601,15.192771560014501,15.496343761670401,15.799915963326301,16.103488164982203,16.407060366638099,16.710632568294002,17.014204769949899,17.317776971605802,null,0,0,0,0,0,0,4.6990680239226354E-2,0.22338674160012645,0.25755986999070291,null,4.6990680239226354E-2,0.22338674160012645,0.25755986999070291]
["2013-04-17T18:00:00","2013-04-17T18:00:00",null,14.605507647943,14.9090798495989,15.2126520512548,15.5162242529107,15.8197964545666,16.1233686562225,16.4269408578784,16.730513059534299,17.034085261190199,null,0,0,0,0,0,0,3.634969379883761E-2,0.21558475351833944,0.25250224698889756,null,3.634969379883761E-2,0.21558475351833944,0.25250224698889756]
["2013-04-17T19:00:00","2013-04-17T19:00:00",null,14.538888664610113,14.842460866266013,15.146033067921913,15.449605269577813,15.753177471233712,16.056749672889612,16.360321874545512,16.663894076201412,16.967466277857312,null,0,0,0,0,0,0,2.8989327683944209E-2,0.21104235614457667,0.25068318507764531,null,2.8989327683944209E-2,0.21104235614457667,0.25068318507764531]
["2013-04-17T20:00:00","2013-04-17T20:00:00",null,14.372628580284289,14.676200781940189,14.979772983596089,15.283345185251989,15.586917386907889,15.890489588563788,16.194061790219688,16.497633991875588,16.801206193531488,null,0,0,0,0,0,0,2.8085054132685878E-2,0.21289296248203557,0.25520455283393695,null,2.8085054132685878E-2,0.21289296248203557,0.25520455283393695]
["2013-04-17T21:00:00","2013-04-17T21:00:00",null,14.308605092457499,14.612177294113399,14.915749495769299,15.219321697425199,15.522893899081099,15.826466100736999,16.130038302392897,16.433610504048801,16.737182705704697,null,0,0,0,0,0,4.9419601057141388E-4,3.1376189266916786E-2,0.21887588865257035,0.26379515157089112,null,3.1376189266916786E-2,0.21887588865257035,0.26379515157089112]
["2013-04-17T22:00:00","2013-04-17T22:00:00",null,14.33496037288579,14.63853257454169,14.94210477619759,15.24567697785349,15.54924917950939,15.85282138116529,16.156393582821188,16.459965784477092,16.763537986132988,null,0,0,0,0,0,2.6076725664193751E-3,3.6255060520217555E-2,0.2264150065159683,0.27391039757450175,null,3.6255060520217555E-2,0.2264150065159683,0.27391039757450175]
["2013-04-17T23:00:00","2013-04-17T23:00:00",null,14.275500638299782,14.579072839955682,14.882645041611582,15.186217243267482,15.489789444923382,15.793361646579282,16.096933848235182,16.400506049891082,16.704078251546981,null,0,0,0,0,9.9890682987838967E-4,6.4560925636350658E-3,4.2847845597414926E-2,0.23564700858579174,0.2856869833583312,null,4.2847845597414926E-2,0.23564700858579174,0.2856869833583312]
["2013-04-18","2013-04-18",null,14.166417955322958,14.469990156978858,14.773562358634758,15.077134560290657,15.380706761946557,15.684278963602457,15.987851165258357,16.291423366914259,16.594995568570155,null,0,0,0,1.3458955181519358E-3,5.2574043677809986E-3,1.3522044033932729E-2,5.2616102912752025E-2,0.24801242365881265,0.30055492291041586,null,5.2616102912752025E-2,0.24801242365881265,0.30055492291041586]
["2013-04-18T01:00:00","2013-04-18T01:00:00",null,14.042977083746466,14.346549285402366,14.650121487058266,14.953693688714166,15.257265890370066,15.560838092025966,15.864410293681866,16.167982495337768,16.471554696993664,null,0,0,0,4.1533494505469892E-3,1.0987975128662286E-2,2.2049553918473509E-2,6.3835403833596677E-2,0.26182888233734114,0.31686339125927254,null,6.3835403833596677E-2,0.26182888233734114,0.31686339125927254]
["2013-04-18T02:00:00","2013-04-18T02:00:00",null,14.005792674170811,14.309364875826711,14.612937077482611,14.916509279138511,15.220081480794411,15.523653682450311,15.827225884106211,16.130798085762109,16.434370287418012,null,0,0,9.7787721240726586E-4,8.1594915787961096E-3,1.7885689659190955E-2,3.1733692763926111E-2,7.620081890661759E-2,0.27677042555057474,0.3342864293340988,null,7.620081890661759E-2,0.27677042555057474,0.3342864293340988]
["2013-04-18T03:00:00","2013-04-18T03:00:00",null,13.867412003620395,14.170984205276294,14.474556406932194,14.778128608588094,15.081700810243994,15.385273011899894,15.688845213555794,15.992417415211694,16.295989616867594,null,0,0,3.7748163360667572E-3,1.3963666000826332E-2,2.6581436483500726E-2,4.320534909442425E-2,9.0332721847212916E-2,0.29346794182264718,0.35345492565902831,null,9.0332721847212916E-2,0.29346794182264718,0.35345492565902831]
["2013-04-18T04:00:00","2013-04-18T04:00:00",null,12.136000764559851,12.439572966215751,12.743145167871651,13.046717369527551,13.350289571183451,13.653861772839351,13.957433974495251,14.261006176151151,14.564578377807051,null,3.869449614686815E-3,7.4234549673067706E-3,1.4584039716224489E-2,2.7990420854066035E-2,4.3689030296260097E-2,6.3246574544405409E-2,0.11319191603832469,0.31901892705006285,0.38158203902665666,null,0.11319191603832469,0.31901892705006285,0.38158203902665666]
["2013-04-18T05:00:00","2013-04-18T05:00:00",null,11.167554958779814,11.471127160435714,11.774699362091614,12.078271563747514,12.381843765403413,12.685415967059313,12.988988168715213,13.292560370371113,13.596132572027013,null,1.9610118291823127E-2,2.610827009040044E-2,3.6065793962977655E-2,5.2121906902180819E-2,7.0344070440909762E-2,9.2298991080763212E-2,0.14453656087903499,0.35255065210777004,0.41720621102274069,null,0.14453656087903499,0.35255065210777004,0.41720621102274069]
["2013-04-18T06:00:00","2013-04-18T06:00:00",null,10.955007431797403,11.258579633453303,11.562151835109203,11.865724036765103,12.169296238421003,12.472868440076903,12.776440641732803,13.080012843388703,13.383585045044603,null,6.4298055417961616E-2,7.3719324045025167E-2,8.6442242615055176E-2,0.10512705773814884,0.12584123094720598,0.15017249836129645,0.20467075203771407,0.41484037905723931,0.48155684048438013,null,0.20467075203771407,0.41484037905723931,0.48155684048438013]
["2013-04-18T07:00:00","2013-04-18T07:00:00",null,10.733494148316069,11.037066349971969,11.340638551627869,11.644210753283769,11.947782954939669,12.251355156595569,12.554927358251469,12.858499559907369,13.162071761563269,null,0.11238227576568663,0.12468460198629416,0.14014137082757031,0.16141282889961223,0.18457695254405529,0.21124250749744053,0.26795938581706175,0.48025300420117051,0.54898830890553918,null,0.26795938581706175,0.48025300420117051,0.54898830890553918]
["2013-04-18T08:00:00","2013-04-18T08:00:00",null,10.638242758234655,10.941814959890555,11.245387161546455,11.548959363202355,11.852531564858255,12.156103766514155,12.459675968170055,12.763248169825955,13.066820371481855,null,0.16854186922232325,0.18353598647923466,0.20152682422578125,0.22520617349826688,0.25065201063832687,0.2794836161912379,0.33826139702302926,0.55252128464068817,0.62312822529998679,null,0.33826139702302926,0.55252128464068817,0.62312822529998679]
["2013-04-18T09:00:00","2013-04-18T09:00:00",null,10.571226850326656,10.874799051982558,11.178371253638458,11.481943455294358,11.785515656950258,12.089087858606158,12.392660060262058,12.696232261917958,12.999804463573858,null,0.22438601841689304,0.24208244151884387,0.26263889259686757,0.28874716268726802,0.31648522813168056,0.34750391390158847,0.40836362686302108,0.62460029852296572,0.69708938994592984,null,0.40836362686302108,0.62460029852296572,0.69708938994592984]
["2013-04-18T10:00:00","2013-04-18T10:00:00",null,10.433977276931955,10.737549478587855,11.041121680243755,11.344693881899655,11.648266083555555,11.951838285211455,12.255410486867355,12.558982688523255,12.862554890179155,null,0.28350027312822257,0.30384642803153505,0.32690540358862252,0.35537950564452442,0.38536774015834718,0.41852093210157421,0.48141000314897026,0.69957088480752283,0.77390006775921028,null,0.48141000314897026,0.69957088480752283,0.77390006775921028]
["2013-04-18T11:00:00","2013-04-18T11:00:00",null,10.327403320045864,10.630975521701764,10.934547723357664,11.238119925013564,11.541692126669464,11.845264328325364,12.148836529981264,12.452408731637163,12.755980933293063,null,0.34434947128091986,0.36732432836812284,0.39286479878680292,0.42368370319073517,0.45589056234776149,0.49115723084683649,0.55605463036272484,0.77611869240241416,0.85226693726535385,null,0.55605463036272484,0.77611869240241416,0.85226693726535385]
["2013-04-18T12:00:00","2013-04-18T12:00:00",null,10.247246782098092,10.550818983753992,10.854391185409892,11.157963387065791,11.461535588721691,11.765107790377591,12.068679992033491,12.372252193689391,12.675824395345291,null,0.36643056962560006,0.39182383272198229,0.41965653144501491,0.45263097163973737,0.48688821850019826,0.52410012661535221,0.5908376176599639,0.81265765275849211,0.89047775221038616,null,0.5908376176599639,0.81265765275849211,0.89047775221038616]
["2013-04-18T13:00:00","2013-04-18T13:00:00",null,10.235708022612398,10.539280224268298,10.842852425924198,11.146424627580098,11.449996829235998,11.753569030891898,12.057141232547798,12.360713434203698,12.664285635859597,null,0.3643486374959588,0.39204464370542907,0.42204339302798749,0.45707873573488011,0.49328122221141996,0.5323332218552973,0.60082668595874777,0.82431857564623034,0.90371589640845873,null,0.60082668595874777,0.82431857564623034,0.90371589640845873]
["2013-04-18T14:00:00","2013-04-18T14:00:00",null,10.410670358808453,10.714242560464353,11.017814762120254,11.321386963776154,11.624959165432054,11.928531367087954,12.232103568743854,12.535675770399754,12.839247972055654,null,0.3543280247709682,0.38444243698961778,0.41672289980779315,0.45392429311421151,0.49217716729418592,0.53317440655414228,0.60351847699505168,0.82876633974137304,0.90983551509255578,null,0.60351847699505168,0.82876633974137304,0.90983551509255578]
["2013-04-18T15:00:00","2013-04-18T15:00:00",null,10.601532798407208,10.905105000063109,11.208677201719009,11.512249403374909,11.815821605030809,12.119393806686709,12.422966008342609,12.726538209998509,13.030110411654409,null,0.33656851281660399,0.36922750874925958,0.40391586276787861,0.44339896956991393,0.48380737954067859,0.52685500650406947,0.59915483136979342,0.8262638152623093,0.90910999328980202,null,0.59915483136979342,0.8262638152623093,0.90910999328980202]
["2013-04-18T16:00:00","2013-04-18T16:00:00",null,10.714097652701215,11.017669854357115,11.321242056013014,11.624814257668914,11.928386459324814,12.231958660980714,12.535530862636614,12.839103064292514,13.142675265948414,null,0.31323615223239193,0.34856590958388023,0.38577781769903419,0.42765830089277762,0.47033790955042365,0.51555158711334037,0.5899017996824989,0.81896653799982932,0.90368435198225205,null,0.5899017996824989,0.81896653799982932,0.90368435198225205]
["2013-04-18T17:00:00","2013-04-18T17:00:00",null,10.734654022629169,11.038226224285069,11.341798425940969,11.645370627596868,11.948942829252768,12.252515030908668,12.556087232564568,12.859659434220468,13.163231635876368,null,0.28545602755303712,0.32357220921944935,0.3634233343272294,0.40780634200003657,0.45286229743191964,0.50033665887298218,0.5768318924241953,0.80793650363622482,0.8946100720434621,null,0.5768318924241953,0.80793650363622482,0.8946100720434621]
["2013-04-18T18:00:00","2013-04-18T18:00:00",null,10.651661058910676,10.955233260566578,11.258805462222478,11.562377663878378,11.865949865534278,12.169522067190178,12.473094268846078,12.776666470501977,13.080238672157877,null,0.25817009888425374,0.29908321967432544,0.34158407658346712,0.38846960873533803,0.43591242575019368,0.4856369562606665,0.56428772560266982,0.79744272451813392,0.88606153254145015,null,0.56428772560266982,0.79744272451813392,0.88606153254145015]
["2013-04-18T19:00:00","2013-04-18T19:00:00",null,10.557177524997567,10.860749726653466,11.164321928309366,11.467894129965266,11.771466331621166,12.075038533277066,12.378610734932966,12.682182936588866,12.985755138244766,null,0.23186204742787761,0.27557210734160881,0.32071218124337658,0.37008972306557564,0.41990888685466832,0.47188358643455142,0.55266886194987386,0.78786373376003693,0.87842778139943212,null,0.55266886194987386,0.78786373376003693,0.87842778139943212]
["2013-04-18T20:00:00","2013-04-18T20:00:00",null,10.397502444378169,10.701074646034069,11.004646847689969,11.308219049345869,11.611791251001769,11.915363452657669,12.218935654313569,12.522507855969469,12.826080057625369,null,0.20998073044917309,0.2564036110166793,0.30409878344118862,0.35590524608130253,0.4080166381747477,0.46216790316289214,0.54502459599912023,0.78218573704283345,0.87463193544589424,null,0.54502459599912023,0.78218573704283345,0.87463193544589424]
["2013-04-18T21:00:00","2013-04-18T21:00:00",null,10.242850194217201,10.546422395873101,10.849994597529001,11.153566799184901,11.457139000840801,11.760711202496701,12.064283404152601,12.367855605808501,12.671427807464401,null,0.19230533696469337,0.24134640490735451,0.29152307219345647,0.34568485199033627,0.400014868726985,0.45626909546224187,0.54112360195822673,0.78018792338307663,0.87445318369738967,null,0.54112360195822673,0.78018792338307663,0.87445318369738967]
["2013-04-18T22:00:00","2013-04-18T22:00:00",null,10.106788703888698,10.410360905544598,10.713933107200498,11.017505308856398,11.321077510512298,11.624649712168198,11.928221913824098,12.231794115479998,12.535366317135898,null,0.17804725631927132,0.22964342278467401,0.28223849607995521,0.33869250418118757,0.39518857151736203,0.45349318595605348,0.54029293206811735,0.78120785983042618,0.877229093203578,null,0.54029293206811735,0.78120785983042618,0.877229093203578]
["2013-04-18T23:00:00","2013-04-18T23:00:00",null,9.9767751178179385,10.280347319473838,10.583919521129738,10.887491722785638,11.191063924441538,11.494636126097438,11.798208327753338,12.101780529409238,12.405352731065138,null,0.16682795539842665,0.22092664634289311,0.27587703679494019,0.33456018434811169,0.39316972824013413,0.45347215633858234,0.54216456802304736,0.78487752807913735,0.8826126752761857,null,0.54216456802304736,0.78487752807913735,0.8826126752761857]
["2013-04-19","2013-04-19",null,9.9267844173983857,10.230356619054286,10.533928820710186,10.837501022366085,11.141073224021985,11.444645425677885,11.748217627333785,12.051789828989685,12.355362030645585,null,0.15825838627894362,0.21479651285006046,0.27203913160646004,0.33288832975915733,0.39354826135461435,0.45579592906914157,0.54632843228232986,0.79078685058852316,0.89018333756579038,null,0.54632843228232986,0.79078685058852316,0.89018333756579038]
["2013-04-19T01:00:00","2013-04-19T01:00:00",null,9.7521261542974074,10.055698355953307,10.359270557609209,10.662842759265109,10.966414960921009,11.269987162576909,11.573559364232809,11.877131565888709,12.180703767544609,null,0.15159199754059732,0.21054853012089342,0.27007286237290995,0.33307759631639744,0.39576688599781795,0.45993876371095299,0.55229032883539353,0.79847317577421895,0.89952048772296944,null,0.55229032883539353,0.79847317577421895,0.89952048772296944]
["2013-04-19T02:00:00","2013-04-19T02:00:00",null,9.7114076094580337,10.014979811113934,10.318552012769834,10.622124214425734,10.925696416081633,11.229268617737533,11.532840819393433,11.836413021049333,12.139985222705233,null,0.14723886672407466,0.20856123126987219,0.27030418816509233,0.33541188385569221,0.40007795757939835,0.46613198605619899,0.56025003904821391,0.80812577019346488,0.91077133307002078,null,0.56025003904821391,0.80812577019346488,0.91077133307002078]
["2013-04-19T03:00:00","2013-04-19T03:00:00",null,9.7226331298533921,10.026205331509292,10.329777533165192,10.633349734821092,10.936921936476992,11.240494138132892,11.544066339788792,11.847638541444692,12.151210743100592,null,0.14614532661557622,0.20984403793561077,0.27382664909150561,0.34104782133795342,0.40771170872141638,0.47564788796188262,0.57155345843894301,0.82113258859935512,0.92538691721245192,null,0.57155345843894301,0.82113258859935512,0.92538691721245192]
["2013-04-19T04:00:00","2013-04-19T04:00:00",null,9.6714308305067558,9.9750030321626557,10.278575233818556,10.582147435474456,10.885719637130356,11.189291838786255,11.492864040442155,11.796436242098055,12.100008443753955,null,0.14427369066064619,0.21039080798985998,0.27665513264137181,0.34603184067860981,0.41472508614803621,0.48458547538711033,0.58229959296668732,0.83361366656846725,0.93949779053557614,null,0.58229959296668732,0.83361366656846725,0.93949779053557614]
["2013-04-19T05:00:00","2013-04-19T05:00:00",null,9.6751519848543062,9.9787241865102061,10.282296388166104,10.585868589822004,10.889440791477904,11.193012993133804,11.496585194789704,11.800157396445604,12.103729598101504,null,0.14222330295721158,0.21076934110434023,0.27932589406020458,0.35085813788823278,0.42158074144362262,0.49336534068130461,0.59290903498086933,0.84594753721528149,0.95347197134513806,null,0.59290903498086933,0.84594753721528149,0.95347197134513806]
["2013-04-19T06:00:00","2013-04-19T06:00:00",null,9.616647609644378,9.920219811300278,10.223792012956178,10.527364214612078,10.830936416267978,11.134508617923878,11.438080819579778,11.741653021235678,12.045225222891577,null,0.13954202672964328,0.21054853012089342,0.28142885580731697,0.3551376650436065,0.42793168591990205,0.50166152477366299,0.6030453106019511,0.85783978589520216,0.96702555980527749,null,0.6030453106019511,0.85783978589520216,0.96702555980527749]
["2013-04-19T07:00:00","2013-04-19T07:00:00",null,9.660612564718388,9.964184766374288,10.267756968030188,10.571329169686088,10.874901371341988,11.178473572997888,11.482045774653788,11.785617976309688,12.089190177965587,null,0.13831179410758251,0.21172618869927637,0.28486719826384577,0.36071051367345436,0.43552337782697781,0.51115639706187543,0.6143487299926802,0.87085711910982788,0.9816726883739153,null,0.6143487299926802,0.87085711910982788,0.9816726883739153]
["2013-04-19T08:00:00","2013-04-19T08:00:00",null,9.740266644203956,10.043838845859856,10.347411047515756,10.650983249171656,10.954555450827556,11.258127652483456,11.561699854139356,11.865272055795256,12.168844257451155,null,0.13651376181380143,0.2123255327972034,0.28773774104865418,0.36571556263158189,0.44254727006233324,0.5200834696783676,0.62508434971168902,0.88330665265273334,0.99575201727083285,null,0.62508434971168902,0.88330665265273334,0.99575201727083285]
["2013-04-19T09:00:00","2013-04-19T09:00:00",null,9.8568820631039635,10.160454264759863,10.464026466415763,10.767598668071663,11.071170869727563,11.374743071383463,11.678315273039363,11.981887474695263,12.285459676351163,null,0.13219217542348544,0.21046441165100893,0.28818987782428335,0.36834426481547239,0.44723687475839391,0.52672882879924277,0.63358031517002311,0.89355859116990632,1,null,0.63358031517002311,0.89355859116990632,1]
["2013-04-19T10:00:00","2013-04-19T10:00:00",null,9.9629979441321428,10.266570145788043,10.570142347443943,10.873714549099843,11.177286750755743,11.480858952411642,11.784431154067542,12.088003355723442,12.391575557379342,null,0.12598843826950384,0.20674216935862,0.28681243787992472,0.36917493470558177,0.45015999158688014,0.53163924447875022,0.64037288161319617,0.90212816028938936,1,null,0.64037288161319617,0.90212816028938936,1]
["2013-04-19T11:00:00","2013-04-19T11:00:00",null,10.121080678378725,10.424652880034625,10.728225081690525,11.031797283346425,11.335369485002325,11.638941686658224,11.942513888314124,12.246086089970024,12.549658291625924,null,0.11513715565440386,0.1984670148837327,0.2809767190316878,0.36564195897043295,0.44880358125999265,0.53235425147276838,0.64304364303202888,0.90666004285441659,1,null,0.64304364303202888,0.90666004285441659,1]
["2013-04-19T12:00:00","2013-04-19T12:00:00",null,10.330685544923877,10.634257746579777,10.937829948235677,11.241402149891577,11.544974351547477,11.848546553203377,12.152118754859277,12.455690956515177,12.759263158171077,null,0.10081598615656842,0.18677454756978776,0.27177626138807104,0.35878630367484654,0.44417706541634538,0.52984121218496905,0.64253893221272185,0.90805851241624636,1,null,0.64253893221272185,0.90805851241624636,1]
["2013-04-19T13:00:00","2013-04-19T13:00:00",null,10.516225974220671,10.819798175876571,11.123370377532471,11.426942579188371,11.73051478084427,12.03408698250017,12.33765918415607,12.64123138581197,12.94480358746787,null,8.0869393985207316E-2,0.16957232047840834,0.25717119205437544,0.34664169958527241,0.43435623405733048,0.52223900546915769,0.63703968724402293,0.90455708110730426,0.99841226388093018,null,0.63703968724402293,0.90455708110730426,0.99841226388093018]
["2013-04-19T14:00:00","2013-04-19T14:00:00",null,10.69574864698053,10.99932084863643,11.302893050292329,11.606465251948229,11.910037453604129,12.213609655260029,12.517181856915929,12.820754058571829,13.124326260227729,null,5.5644367828594082E-2,0.14719680748913241,0.23747695529266782,0.32950256134630634,0.41963550182754367,0.50982101635245902,0.62680877834432114,0.89640810433724372,0.99225058596189086,null,0.62680877834432114,0.89640810433724372,0.99225058596189086]
["2013-04-19T15:00:00","2013-04-19T15:00:00",null,10.870006472098364,11.173578673754264,11.477150875410164,11.780723077066064,12.084295278721964,12.387867480377864,12.691439682033764,12.995011883689664,13.298584085345563,null,2.219676124077137E-2,0.11677746581715155,0.20991764159675982,0.30465606830417336,0.39736513692562336,0.49001111669466024,0.60933316622581712,0.88115111686194325,0.97912810465990952,null,0.60933316622581712,0.88115111686194325,0.97912810465990952]
["2013-04-19T16:00:00","2013-04-19T16:00:00",null,10.976378850566197,11.279951052222097,11.583523253877997,11.887095455533897,12.190667657189797,12.494239858845697,12.797812060501597,13.101384262157497,13.404956463813397,null,0,8.4843991687249765E-2,0.18086522506040204,0.27832698723032612,0.37363321360945995,0.46875017343135389,0.59041702531054108,0.86447463020734194,0.96459663898736281,null,0.59041702531054108,0.86447463020734194,0.96459663898736281]
["2013-04-19T17:00:00","2013-04-19T17:00:00",null,10.97782306940457,11.28139527106047,11.58496747271637,11.88853967437227,12.19211187602817,12.49568407768407,12.79925627933997,13.102828480995869,13.406400682651769,null,0,5.2910517557347977E-2,0.15181280852404425,0.25200842096521442,0.34990129029329653,0.44748923016804754,0.57150088439526503,0.84780865836147612,0.9500651733148161,null,0.57150088439526503,0.84780865836147612,0.9500651733148161]
["2013-04-19T18:00:00","2013-04-19T18:00:00",null,11.068558775933608,11.372130977589508,11.675703179245408,11.979275380901308,12.282847582557208,12.586419784213108,12.889991985869008,13.193564187524908,13.497136389180808,null,0,2.0230492007221289E-2,0.12200332575872598,0.22493278847114229,0.32541230074817262,0.42547122067578069,0.55183819205976414,0.83038562028664986,0.93478715622204456,null,0.55183819205976414,0.83038562028664986,0.93478715622204456]
["2013-04-19T19:00:00","2013-04-19T19:00:00",null,10.928309555808172,11.231881757464071,11.535453959119971,11.839026160775871,12.142598362431771,12.446170564087671,12.749742765743571,13.053314967399471,13.356887169055371,null,0,0,9.1857369113869741E-2,0.19755222652373886,0.30066044098465966,0.40322188539133152,0.5319757183582875,0.81279434527205463,0.91936193180697512,null,0.5319757183582875,0.81279434527205463,0.91936193180697512]
["2013-04-19T20:00:00","2013-04-19T20:00:00",null,10.763492311798522,11.067064513454422,11.370636715110322,11.674208916766222,11.977781118422122,12.281353320078022,12.584925521733922,12.888497723389822,13.192069925045722,null,0,0,6.5717554597262612E-2,0.17411471785217117,0.27978854564456912,0.38478942567789132,0.51585651656667098,0.79889376812364166,0.90756431640567459,null,0.51585651656667098,0.79889376812364166,0.90756431640567459]
["2013-04-19T21:00:00","2013-04-19T21:00:00",null,10.677985500297421,10.981557701953321,11.285129903609221,11.588702105265121,11.892274306921021,12.195846508576921,12.49941871023282,12.80299091188872,13.10656311354462,null,0,0,4.3583882208904606E-2,0.15460974764770366,0.26276507030169427,0.37013178230051791,0.50343852744997231,0.78862079998899759,0.8993312211657295,null,0.50343852744997231,0.78862079998899759,0.8993312211657295]
["2013-04-19T22:00:00","2013-04-19T22:00:00",null,10.49229040391416,10.795862605570058,11.099434807225958,11.403007008881858,11.706579210537758,12.010151412193657,12.313723613849557,12.617295815505457,12.920868017161357,null,0,0,2.6686584570856476E-2,0.14023600410619042,0.25078870315188917,0.36042661383759417,0.49588889477783882,0.78312155502029868,0.89578773062184514,null,0.49588889477783882,0.78312155502029868,0.89578773062184514]
["2013-04-19T23:00:00","2013-04-19T23:00:00",null,10.388158238339336,10.691730439995236,10.995302641651136,11.298874843307036,11.602447044962936,11.906019246618836,12.209591448274736,12.513163649930636,12.816735851586536,null,0,0,1.4657643377373551E-2,0.13061495411315119,0.2434493666544669,0.3552638427484332,0.49278702620084802,0.78197544086812243,0.89651325242459889,null,0.49278702620084802,0.78197544086812243,0.89651325242459889]
["2013-04-20","2013-04-20",null,10.164062279958499,10.467634481614398,10.771206683270298,11.074778884926198,11.378351086582098,11.681923288237998,11.985495489893898,12.289067691549798,12.592639893205698,null,0,0,6.6243295034041846E-3,0.12493695739594771,0.24000050938920256,0.35391794723028125,0.49344945915118843,0.78454105419959952,0.90089792766732824,null,0.49344945915118843,0.78454105419959952,0.90089792766732824]
["2013-04-20T01:00:00","2013-04-20T01:00:00",null,10.045229708256977,10.348801909912877,10.652374111568777,10.955946313224677,11.259518514880577,11.563090716536477,11.866662918192377,12.170235119848277,12.473807321504177,null,0,0,1.1355993434408219E-3,0.12176148515780798,0.23900160255932418,0.35499045772130855,0.49648823887576587,0.78945146987910697,0.90758534602314567,null,0.49648823887576587,0.78945146987910697,0.90758534602314567]
["2013-04-20T02:00:00","2013-04-20T02:00:00",null,10.012852306474683,10.316424508130583,10.619996709786482,10.923568911442382,11.227141113098282,11.530713314754182,11.834285516410082,12.137857718065982,12.441429919721882,null,0,0,0,0.12003705652517581,0.23942219490874667,0.35745092296543007,0.50088342892723081,0.79567623665055964,0.91555557104470164,null,0.50088342892723081,0.79567623665055964,0.91555557104470164]
["2013-04-20T03:00:00","2013-04-20T03:00:00",null,9.9799249701753041,10.283497171831204,10.587069373487104,10.890641575143004,11.194213776798904,11.497785978454804,11.801358180110704,12.104930381766604,12.408502583422504,null,0,0,0,0.1200686009513825,0.24156721589080132,0.36159375760724149,0.50691892914144343,0.80352028396728892,0.92511353218532755,null,0.50691892914144343,0.80352028396728892,0.92511353218532755]
["2013-04-20T04:00:00","2013-04-20T04:00:00",null,9.9813780473343385,10.284950248990238,10.588522450646138,10.892094652302038,11.195666853957938,11.499239055613838,11.802811257269738,12.106383458925638,12.409955660581538,null,0,0,0,0.11994242324655575,0.24355451474182255,0.36557887011801948,0.51280722203335816,0.8112066091529847,0.93451377119491996,null,0.51280722203335816,0.8112066091529847,0.93451377119491996]
["2013-04-20T05:00:00","2013-04-20T05:00:00",null,9.9159172216285079,10.219489423284408,10.523061624940308,10.826633826596208,11.130206028252108,11.433778229908008,11.737350431563907,12.040922633219807,12.344494834875707,null,0,0,0,0.1195428605146044,0.24527894337445472,0.36932214202787955,0.51846418913309056,0.81868263816396925,0.94371422883853673,null,0.51846418913309056,0.81868263816396925,0.94371422883853673]
["2013-04-20T06:00:00","2013-04-20T06:00:00",null,9.8876552365953696,10.19122743825127,10.494799639907169,10.798371841563069,11.101944043218969,11.405516244874869,11.709088446530769,12.012660648186669,12.316232849842569,null,0,0,0,0.11709291007921846,0.24501607315606566,0.3711412039391318,0.52224952027789284,0.82433960526370165,0.95114819861457911,null,0.52224952027789284,0.82433960526370165,0.95114819861457911]
["2013-04-20T07:00:00","2013-04-20T07:00:00",null,10.057421819089676,10.360994020745576,10.664566222401476,10.968138424057376,11.271710625713276,11.575282827369175,11.878855029025075,12.182427230680975,12.485999432336875,null,0,0,0,0.11668283253853154,0.24670895736249115,0.37483190180531406,0.5278328837164763,0.83173151580480176,0.96025402297957585,null,0.5278328837164763,0.83173151580480176,0.96025402297957585]
["2013-04-20T08:00:00","2013-04-20T08:00:00",null,10.219191537145022,10.522763738800922,10.826335940456822,11.129908142112722,11.433480343768622,11.737052545424522,12.040624747080422,12.344196948736322,12.647769150392222,null,0,0,0,0.11517921488934617,0.24730830146041818,0.37742905956299788,0.53232270704656126,0.83802988623740338,0.9682663072360741,null,0.53232270704656126,0.83802988623740338,0.9682663072360741]
["2013-04-20T09:00:00","2013-04-20T09:00:00",null,10.529446000767916,10.833018202423816,11.136590404079715,11.440162605735615,11.743734807391515,12.047307009047415,12.350879210703315,12.654451412359215,12.958023614015115,null,0,0,0,0.10567382779239812,0.2400530834328804,0.37231886251751473,0.52925238289577714,0.83690480170269821,0.96899182903882786,null,0.52925238289577714,0.83690480170269821,0.96899182903882786]
["2013-04-20T10:00:00","2013-04-20T10:00:00",null,10.902066940377324,11.205639142033224,11.509211343689124,11.812783545345024,12.116355747000924,12.419927948656824,12.723500150312724,13.027072351968624,13.330644553624523,null,0,0,0,8.9007855946532349E-2,0.22575294355251607,0.36026889170656068,0.5193474330668777,0.82905023957723345,0.96308250652944205,null,0.5193474330668777,0.82905023957723345,0.96308250652944205]
["2013-04-20T11:00:00","2013-04-20T11:00:00",null,11.148634614575572,11.452206816231472,11.755779017887372,12.059351219543272,12.362923421199172,12.666495622855072,12.970067824510972,13.273640026166872,13.577212227822772,null,0,0,0,6.7810001535639361E-2,0.20698400995953792,0.34381321603540616,0.50509986723019118,0.81690563548765938,0.95295674571709588,null,0.50509986723019118,0.81690563548765938,0.95295674571709588]
["2013-04-20T12:00:00","2013-04-20T12:00:00",null,11.280855960153845,11.584428161809745,11.888000363465645,12.191572565121545,12.495144766777445,12.798716968433345,13.102289170089245,13.405861371745145,13.709433573401045,null,0,0,0,4.4099107836947052E-2,0.18574409631370267,0.32491810473760124,0.48845492500179655,0.80239519943258386,0.94048618255671934,null,0.48845492500179655,0.80239519943258386,0.94048618255671934]
["2013-04-20T13:00:00","2013-04-20T13:00:00",null,11.461599422838328,11.765171624494227,12.068743826150127,12.372316027806027,12.675888229461927,12.979460431117827,13.283032632773727,13.586604834429627,13.890177036085527,null,0,0,0,1.8947685341482754E-2,0.16305313906235988,0.30458246464302435,0.47035893916789434,0.78644423458073631,0.92658560540830637,null,0.47035893916789434,0.78644423458073631,0.92658560540830637]
["2013-04-20T14:00:00","2013-04-20T14:00:00",null,11.414711980595211,11.718284182251111,12.021856383907011,12.325428585562911,12.629000787218811,12.932572988874711,13.23614519053061,13.53971739218651,13.84328959384241,null,0,0,0,0,0.1393107009374609,0.28322688810109792,0.45127456131284932,0.76953642213395257,0.91175972509116399,null,0.45127456131284932,0.76953642213395257,0.91175972509116399]
["2013-04-20T15:00:00","2013-04-20T15:00:00",null,11.399920482814531,11.703492684470431,12.007064886126331,12.310637087782231,12.614209289438131,12.917781491094031,13.221353692749931,13.524925894405831,13.828498096061731,null,0,0,0,0,0.11316037161211821,0.25952650921114118,0.42989795515345181,0.7503889554264942,0.89473624974828914,null,0.42989795515345181,0.7503889554264942,0.89473624974828914]
["2013-04-20T16:00:00","2013-04-20T16:00:00",null,11.409911168305984,11.713483369961883,12.017055571617783,12.320627773273683,12.624199974929583,12.927772176585483,13.231344378241383,13.534916579897283,13.838488781553183,null,0,0,0,0,8.6578935128617487E-2,0.23539502316302641,0.4081007566446318,0.73083141117834893,0.87731321167346288,null,0.4081007566446318,0.73083141117834893,0.87731321167346288]
["2013-04-20T17:00:00","2013-04-20T17:00:00",null,11.431359068295944,11.734931269951844,12.038503471607743,12.342075673263643,12.645647874919543,12.949220076575443,13.252792278231343,13.556364479887243,13.859936681543143,null,0,0,0,0,5.920888798994961E-2,0.21049595607721561,0.3855570067155869,0.71053783031871431,0.85916465179588286,null,0.3855570067155869,0.71053783031871431,0.85916465179588286]
["2013-04-20T18:00:00","2013-04-20T18:00:00",null,11.327629086532303,11.631201288188203,11.934773489844103,12.238345691500003,12.541917893155903,12.845490094811803,13.149062296467703,13.452634498123603,13.756206699779503,null,0,0,0,0,2.9967204896351695E-2,0.18378834188888812,0.3612572837277031,0.68854085044391866,0.83936526694681957,null,0.3612572837277031,0.68854085044391866,0.83936526694681957]
["2013-04-20T19:00:00","2013-04-20T19:00:00",null,11.181252956979149,11.484825158635049,11.788397360290949,12.091969561946849,12.395541763602749,12.699113965258649,13.002686166914549,13.306258368570449,13.609830570226348,null,0,0,0,0,8.096402726382769E-4,0.15718587578791626,0.33709425325338166,0.66670159270015639,0.81975514865499644,null,0.33709425325338166,0.66670159270015639,0.81975514865499644]
["2013-04-20T20:00:00","2013-04-20T20:00:00",null,11.029316190886252,11.332888392542152,11.636460594198052,11.940032795853952,12.243604997509852,12.547177199165752,12.850749400821652,13.154321602477552,13.457893804133452,null,0,0,0,0,0,0.13371682269014187,0.31602257654731541,0.64791162948970715,0.80314175085280848,null,0.31602257654731541,0.64791162948970715,0.80314175085280848]
["2013-04-20T21:00:00","2013-04-20T21:00:00",null,10.971106561333732,11.274678762989632,11.578250964645532,11.881823166301432,12.185395367957332,12.488967569613232,12.792539771269132,13.096111972925032,13.399684174580932,null,0,0,0,0,0,0.11572598494359529,0.30030293748765025,0.63436855583830332,0.7916700945223103,null,0.30030293748765025,0.63436855583830332,0.7916700945223103]
["2013-04-20T22:00:00","2013-04-20T22:00:00",null,10.843163693581854,11.146735895237756,11.450308096893655,11.753880298549555,12.057452500205455,12.361024701861355,12.664596903517255,12.968169105173155,13.271741306829055,null,0,0,0,0,0,0.10307667003471421,0.28983018798703047,0.62595670884985377,0.78523503157614638,null,0.28983018798703047,0.62595670884985377,0.78523503157614638]
["2013-04-20T23:00:00","2013-04-20T23:00:00",null,10.744196082683208,11.047768284339108,11.351340485995008,11.654912687650908,11.958484889306808,12.262057090962708,12.565629292618608,12.869201494274508,13.172773695930408,null,0,0,0,0,0,9.4727911898677991E-2,0.28356336198063553,0.62167718169448005,0.78284816999317386,null,0.28356336198063553,0.62167718169448005,0.78284816999317386]
["2013-04-21","2013-04-21",null,10.626167690090313,10.929739891746213,11.233312093402112,11.536884295058012,11.840456496713912,12.144028698369812,12.447600900025712,12.751173101681612,13.054745303337512,null,0,0,0,0,0,8.8429541466076358E-2,0.27931537925146849,0.61938495339012756,0.78241706283501578,null,0.27931537925146849,0.61938495339012756,0.78241706283501578]
["2013-04-21T01:00:00","2013-04-21T01:00:00",null,10.639302972673265,10.942875174329165,11.246447375985065,11.550019577640965,11.853591779296865,12.157163980952765,12.460736182608665,12.764308384264565,13.067880585920465,null,0,0,0,0,0,8.46547251300096E-2,0.27752786176642297,0.61949010147748318,0.78432024321615246,null,0.27752786176642297,0.61949010147748318,0.78432024321615246]
["2013-04-21T02:00:00","2013-04-21T02:00:00",null,10.574685407621214,10.878257609277114,11.181829810933014,11.485402012588914,11.788974214244814,12.092546415900713,12.396118617556613,12.699690819212513,13.003263020868413,null,0,0,0,0,0,8.3687362726337894E-2,0.27849522417009465,0.6222870406011427,0.78887315539865077,null,0.27849522417009465,0.6222870406011427,0.78887315539865077]
["2013-04-21T03:00:00","2013-04-21T03:00:00",null,10.560485181588948,10.864057383244848,11.167629584900748,11.471201786556648,11.774773988212548,12.078346189868448,12.381918391524348,12.685490593180248,12.989062794836148,null,0,0,0,0,0,8.3371918464271028E-2,0.28010398990663565,0.62571486824893596,0.79403592648781174,null,0.28010398990663565,0.62571486824893596,0.79403592648781174]
["2013-04-21T04:00:00","2013-04-21T04:00:00",null,10.433002384220437,10.736574585876337,11.040146787532237,11.343718989188137,11.647291190844037,11.950863392499937,12.254435594155836,12.558007795811736,12.861579997467636,null,0,0,0,0,0,8.2583307809103876E-2,0.2812606188675475,0.62872210354730673,0.79880964965375689,null,0.2812606188675475,0.62872210354730673,0.79880964965375689]
["2013-04-21T05:00:00","2013-04-21T05:00:00",null,10.465075863516661,10.768648065172561,11.072220266828461,11.375792468484361,11.679364670140261,11.982936871796161,12.286509073452061,12.590081275107961,12.893653476763861,null,9.9680386813127738E-3,1.2554681630261025E-2,1.5004632065646971E-2,1.7317889987470612E-2,1.9504970204467505E-2,0.10417021014321265,0.30482430524394194,0.65417845549610232,0.82605351908759805,null,0.30482430524394194,0.65417845549610232,0.82605351908759805]
["2013-04-21T06:00:00","2013-04-21T06:00:00",null,10.660588927357699,10.964161129013599,11.267733330669499,11.571305532325399,11.874877733981299,12.178449935637198,12.482022137293098,12.785594338948998,13.089166540604898,null,6.4613499680028469E-2,6.9902448474016166E-2,7.4918012240879239E-2,7.966019098061769E-2,8.4150014310702667E-2,0.17100233446644469,0.37373836169681529,0.72507981079999684,0.89884753996389377,null,0.37373836169681529,0.72507981079999684,0.89884753996389377]
["2013-04-21T07:00:00","2013-04-21T07:00:00",null,10.608290807310205,10.911863008966105,11.215435210622005,11.519007412277904,11.822579613933804,12.126151815589704,12.429724017245604,12.733296218901504,13.036868420557404,null,0.12149861493941888,0.12943729553476818,0.13695538378069502,0.14407390929467048,0.15081390169416575,0.23981124283196242,0.44457662814829646,0.79786331686755696,0.97347113756017722,null,0.44457662814829646,0.79786331686755696,0.97347113756017722]
["2013-04-21T08:00:00","2013-04-21T08:00:00",null,10.840864249854956,11.144436451510856,11.448008653166756,11.751580854822656,12.055153056478556,12.358725258134456,12.662297459790356,12.965869661446256,13.269441863102156,null,0.17738482336893091,0.18794169133943514,0.19794127444695461,0.20740460230896041,0.21637373416039479,0.30749506666277499,0.51427929525633698,0.86949019397420524,1,null,0.51427929525633698,0.86949019397420524,1]
["2013-04-21T09:00:00","2013-04-21T09:00:00",null,11.1182409770408,11.421813178696699,11.725385380352598,12.028957582008498,12.332529783664398,12.636101985320298,12.939674186976198,13.243246388632098,13.546818590287998,null,0.2304320334398412,0.24361760359423593,0.25610919637208357,0.26794887100832637,0.27916817192917104,0.37242401060487029,0.58125862690186691,0.93841476523581413,1,null,0.58125862690186691,0.93841476523581413,1]
["2013-04-21T10:00:00","2013-04-21T10:00:00",null,11.467012314811804,11.770584516467704,12.074156718123604,12.377728919779504,12.681301121435403,12.984873323091303,13.288445524747203,13.592017726403103,13.895589928059003,null,0.27783279121975468,0.29372066721918882,0.30877787332851359,0.32306749840014237,0.33661057205154621,0.43208503537044907,0.64303312822329362,1,1,null,0.64303312822329362,1,1]
["2013-04-21T11:00:00","2013-04-21T11:00:00",null,11.660534060274262,11.964106261930162,12.267678463586062,12.571250665241962,12.874822866897862,13.178395068553762,13.481967270209662,13.785539471865562,14.089111673521462,null,0.32029158889395404,0.33897640401704765,0.35669385673646958,0.3735070359046333,0.38945800075648079,0.48723520718847174,0.7003808950670487,1,1,null,0.7003808950670487,1,1]
["2013-04-21T12:00:00","2013-04-21T12:00:00",null,11.674387991742595,11.977960193398495,12.281532395054395,12.585104596710295,12.888676798366195,13.192249000022095,13.495821201677995,13.799393403333895,14.102965604989794,null,0.35935410334656687,0.38093049087194003,0.40139230867134362,0.4208236752146623,0.43925613492810239,0.53940968813433032,0.75482657469978875,1,1,null,0.75482657469978875,1,1]
["2013-04-21T13:00:00","2013-04-21T13:00:00",null,11.830268344719061,12.133840546374961,12.43741274803086,12.74098494968676,13.04455715134266,13.34812935299856,13.65170155465446,13.95527375631036,14.25884595796626,null,0.39830095490308848,0.42272685559579898,0.44591200885771309,0.46793001834998005,0.48883345811627721,0.59134232847927104,0.8090093841141397,1,1,null,0.8090093841141397,1,1]
["2013-04-21T14:00:00","2013-04-21T14:00:00",null,11.860511655678433,12.164083857334333,12.467656058990233,12.771228260646133,13.074800462302033,13.378372663957933,13.681944865613833,13.985517067269733,14.289089268925633,null,0.43592294055892933,0.46322989884518379,0.48915941718707956,0.51378509924576587,0.53718054868239129,0.64206576581962216,0.86200402014137212,1,1,null,0.86200402014137212,1,1]
["2013-04-21T15:00:00","2013-04-21T15:00:00",null,11.992293852908368,12.295866054564268,12.599438256220168,12.903010457876068,13.206582659531968,13.510154861187868,13.813727062843768,14.117299264499668,14.420871466155567,null,0.47105291654444198,0.50126196204171158,0.52996738988979564,0.5572322889411081,0.58314077766553274,0.69043388600320732,0.91267488343804537,1,1,null,0.91267488343804537,1,1]
["2013-04-21T16:00:00","2013-04-21T16:00:00",null,12.053284803833193,12.356857005489093,12.660429207144993,12.964001408800893,13.267573610456793,13.571145812112693,13.874718013768593,14.178290215424493,14.481862417080393,null,0.50362779400721303,0.53679150075917559,0.56831489734839025,0.59826107262727102,0.62673517468317275,0.73647823345623331,0.96105351843036613,1,1,null,0.96105351843036613,1,1]
["2013-04-21T17:00:00","2013-04-21T17:00:00",null,12.031599431544201,12.335171633200101,12.638743834856001,12.942316036511901,13.245888238167801,13.549460439823701,13.853032641479601,14.156604843135501,14.460177044791401,null,0.53393147278310271,0.57011292964217153,0.60450686901619466,0.63718689456632149,0.66827918399737818,0.780514252440767,1,1,1,null,1,1,1]
["2013-04-21T18:00:00","2013-04-21T18:00:00",null,12.082521810018223,12.386094011674123,12.689666213330023,12.993238414985923,13.296810616641823,13.600382818297723,13.903955019953623,14.207527221609523,14.511099423265422,null,0.56536023609369757,0.60451738382493037,0.64175032155755529,0.67713265295272151,0.71081158533272648,0.82551763382897236,1,1,1,null,1,1,1]
["2013-04-21T19:00:00","2013-04-21T19:00:00",null,11.8459076782629,12.1494798799188,12.4530520815747,12.7566242832306,13.0601964848865,13.3637686865424,13.6673408881983,13.9709130898542,14.2744852915101,null,0.55311048391676787,0.59522229290269357,0.63526268456771351,0.67331577738171255,0.70953929347572353,0.82668477759861969,1,1,1,null,1,1,1]
["2013-04-21T20:00:00","2013-04-21T20:00:00",null,11.661397659015925,11.964969860671825,12.268542062327725,12.572114263983625,12.875686465639525,13.179258667295425,13.482830868951325,13.786403070607225,14.089975272263125,null,0.5132278143827812,0.5583047994321354,0.60115264502955035,0.6418870140711177,0.68065511387913469,0.80024003362868124,0.97586851395188523,0.97809765340382437,0.9802216447684079,null,0.97586851395188523,0.97809765340382437,0.9802216447684079]
["2013-04-21T21:00:00","2013-04-21T21:00:00",null,11.558414858789725,11.861987060445625,12.165559262101524,12.469131463757424,12.772703665413324,13.076275867069224,13.379848068725124,13.683420270381024,13.986992472036924,null,0.47774033490025947,0.52568786273442214,0.57125904379434755,0.61459057059359878,0.65582965045447283,0.77776988736078523,0.95564853675339956,0.9600226971873933,0.964207591064147,null,0.95564853675339956,0.9600226971873933,0.964207591064147]
["2013-04-21T22:00:00","2013-04-21T22:00:00",null,11.361270991738275,11.664843193394175,11.968415395050075,12.271987596705975,12.575559798361875,12.879132000017774,13.182704201673674,13.486276403329574,13.789848604985474,null,0.44775210038643665,0.49848605253552325,0.54668593577933922,0.59253050186638967,0.63614592850150076,0.76035736409469457,0.94041257889557017,0.94684764184173409,0.95301983456950901,null,0.94041257889557017,0.94684764184173409,0.95301983456950901]
["2013-04-21T23:00:00","2013-04-21T23:00:00",null,11.265963576891213,11.569535778547113,11.873107980203013,12.176680181858913,12.480252383514813,12.783824585170713,13.087396786826613,13.390968988482513,13.694541190138413,null,0.42211699668913649,0.475542739874527,0.52628720683234897,0.57455017892857863,0.6204683486767778,0.74687737929570408,0.92902504103495653,0.93745791764087727,0.94554380555852446,null,0.92902504103495653,0.93745791764087727,0.94554380555852446]
["2013-04-22","2013-04-22",null,11.184620408002559,11.488192609658459,11.791764811314358,12.095337012970258,12.398909214626158,12.702481416282058,13.006053617937958,13.309625819593858,13.613198021249758,null,0.40013053162307638,0.45616394737488625,0.50937939438556523,0.55998716882982524,0.60814499283869916,0.73667801482220896,0.92085503464742491,0.931222636060689,0.94115913031579512,null,0.92085503464742491,0.931222636060689,0.94115913031579512]
["2013-04-22T01:00:00","2013-04-22T01:00:00",null,11.037655739397895,11.341227941053795,11.644800142709695,11.948372344365595,12.251944546021495,12.555516747677395,12.859088949333294,13.162661150989194,13.466233352645094,null,0.37833333311425638,0.43700596585869228,0.492723937348435,0.54569754375819646,0.59611605164521619,0.72679409461078071,0.91302150213943123,0.92533434316877428,0.93713195857007492,null,0.91302150213943123,0.92533434316877428,0.93713195857007492]
["2013-04-22T02:00:00","2013-04-22T02:00:00",null,10.941084541197014,11.244656742852914,11.548228944508814,11.851801146164714,12.155373347820614,12.458945549476514,12.762517751132414,13.066089952788314,13.369662154444214,null,0.35772430799255484,0.41902564292088129,0.47723562408095216,0.53257506245621511,0.58524373941264507,0.7180562885515287,0.90631305416614272,0.92057113481156472,0.93421935655032429,null,0.90631305416614272,0.92057113481156472,0.93421935655032429]
["2013-04-22T03:00:00","2013-04-22T03:00:00",null,10.853853891162057,11.157426092817957,11.460998294473857,11.764570496129757,12.068142697785657,12.371714899441557,12.675287101097457,12.978859302753357,13.282431504409256,null,0.3377882306299293,0.40172878255088179,0.46242025857254532,0.52012552891330965,0.57504437493914995,0.7099809154426171,0.9002775539519301,0.91647035940469557,0.93196918748091406,null,0.9002775539519301,0.91647035940469557,0.93196918748091406]
["2013-04-22T04:00:00","2013-04-22T04:00:00",null,10.924492135772972,11.228064337428872,11.531636539084772,11.835208740740672,12.138780942396572,12.442353144052472,12.745925345708372,13.049497547364272,13.353069749020172,null,0.3178731828847749,0.38442140737214675,0.44759437825540288,0.50764445094419752,0.56479243642197696,0.70185296829002763,0.89416845007656853,0.91228546552794187,0.9296243851328837,null,0.89416845007656853,0.91228546552794187,0.9296243851328837]
["2013-04-22T05:00:00","2013-04-22T05:00:00",null,10.931239695909554,11.234811897565454,11.538384099221354,11.841956300877253,12.145528502533153,12.449100704189053,12.752672905844953,13.056245107500853,13.359817309156753,null,0.29425692246470264,0.36351796760584948,0.42925655182058275,0.49174606013602778,0.55121781834436645,0.69047594523814959,0.88489438877180282,0.90500921788293298,0.92425131786901149,null,0.88489438877180282,0.90500921788293298,0.92425131786901149]
["2013-04-22T06:00:00","2013-04-22T06:00:00",null,11.063222822294801,11.366795023950701,11.670367225606601,11.973939427262501,12.277511628918401,12.5810838305743,12.8846560322302,13.1882282338861,13.491800435542,null,0.26794887100832654,0.33996479603819063,0.40831105281934327,0.4732820559963809,0.53510913136148552,0.67660691251594329,0.87315986222291564,0.89531456422874478,0.91650190383090235,null,0.87315986222291564,0.89531456422874478,0.91650190383090235]
["2013-04-22T07:00:00","2013-04-22T07:00:00",null,11.314441150645806,11.618013352301706,11.921585553957605,12.225157755613505,12.528729957269405,12.832302158925305,13.135874360581205,13.439446562237105,13.743018763893005,null,0.24343885184573152,0.31810450867695722,0.38896380474590919,0.4563216695059194,0.52041994355790544,0.66407326050315341,0.86269762753103141,0.88681859877041069,0.90988808913623387,null,0.86269762753103141,0.88681859877041069,0.90988808913623387]
["2013-04-22T08:00:00","2013-04-22T08:00:00",null,11.555328183884463,11.858900385540363,12.162472587196262,12.466044788852162,12.769616990508062,13.073189192163962,13.376761393819862,13.680333595475762,13.983905797131662,null,0.21463879071902722,0.29200675339529236,0.36543166279572142,0.43522896318238202,0.50165100996492729,0.6475229515533788,0.84826079513710484,0.87441112446244751,0.89941533963561415,null,0.84826079513710484,0.87441112446244751,0.89941533963561415]
["2013-04-22T09:00:00","2013-04-22T09:00:00",null,11.875236546671598,12.178808748327498,12.482380949983398,12.785953151639298,13.089525353295198,13.393097554951098,13.696669756606997,14.000241958262897,14.303814159918797,null,0.1782890969201894,0.25847502833758518,0.33458121396558255,0.4069336128749847,0.47578458047544475,0.62398029479445549,0.82693676302138508,0.85521108371131127,0.88225517177917701,null,0.82693676302138508,0.85521108371131127,0.88225517177917701]
["2013-04-22T10:00:00","2013-04-22T10:00:00",null,12.029401761140454,12.332973962796354,12.636546164452254,12.940118366108154,13.243690567764054,13.547262769419953,13.850834971075853,14.154407172731753,14.457979374387653,null,0.13548331055771651,0.21860287361233408,0.29751651317272648,0.37252915869222586,0.44392471000669187,0.59455985995235305,0.79984010090984181,0.83033304624297155,0.8595116404841564,null,0.79984010090984181,0.83033304624297155,0.8595116404841564]
["2013-04-22T11:00:00","2013-04-22T11:00:00",null,12.295919789431181,12.599491991087081,12.903064192742981,13.206636394398881,13.510208596054781,13.813780797710681,14.117352999366581,14.420925201022481,14.724497402678381,null,9.1205450972264929E-2,0.17723761604663318,0.25892716511321395,0.3366000572428105,0.41051916265381139,0.56358323341738736,0.77117673229669981,0.8038883022730331,0.83520140268753706,null,0.77117673229669981,0.8038883022730331,0.83520140268753706]
["2013-04-22T12:00:00","2013-04-22T12:00:00",null,12.482669655518066,12.786241857173966,13.089814058829866,13.393386260485766,13.696958462141666,14.000530663797566,14.304102865453466,14.607675067109366,14.911247268765266,null,4.5539636633719176E-2,0.1344844037278381,0.21894986230060723,0.29926197142282984,0.3757151457391012,0.53119762251185643,0.74110437931299245,0.77604508874126488,0.80948218052035237,null,0.74110437931299245,0.77604508874126488,0.80948218052035237]
["2013-04-22T13:00:00","2013-04-22T13:00:00",null,12.645393269412573,12.948965471068473,13.252537672724372,13.556109874380272,13.859682076036172,14.163254277692072,14.466826479347972,14.770398681003872,15.073970882659772,null,0,8.5527454255061447E-2,0.17287397042137456,0.25594095943231443,0.33502283593247628,0.49302886680176639,0.70534351480334612,0.74259748215344212,0.77826371338446876,null,0.70534351480334612,0.74259748215344212,0.77826371338446876]
["2013-04-22T14:00:00","2013-04-22T14:00:00",null,12.733034715772066,13.036606917427966,13.340179119083865,13.643751320739765,13.947323522395665,14.250895724051565,14.554467925707465,14.858040127363365,15.161612329019265,null,0,3.3321428882996128E-2,0.12360157668653105,0.20947601962986595,0.29123917235759611,0.4518213313670989,0.6665964446128001,0.70621624392839766,0.74414315903757011,null,0.6665964446128001,0.70621624392839766,0.74414315903757011]
["2013-04-22T15:00:00","2013-04-22T15:00:00",null,12.940659692561495,13.244231894217394,13.547804095873294,13.851376297529194,14.154948499185094,14.458520700840994,14.762092902496894,15.065665104152794,15.369237305808694,null,0,0,7.2289310056988493E-2,0.16097120693271846,0.2454261506967525,0.40858443784646797,0.6258200163362907,0.66781616242612529,0.70801427622217905,null,0.6258200163362907,0.66781616242612529,0.70801427622217905]
["2013-04-22T16:00:00","2013-04-22T16:00:00",null,13.06774717650117,13.37131937815707,13.67489157981297,13.97846378146887,14.28203598312477,14.58560818478067,14.889180386436569,15.192752588092469,15.496324789748369,null,0,0,1.6529279332303221E-2,0.10809223380157718,0.19530205745432846,0.36111007640540554,0.58087972380049868,0.62531530551698367,0.66784770685233219,null,0.58087972380049868,0.62531530551698367,0.66784770685233219]
["2013-04-22T17:00:00","2013-04-22T17:00:00",null,13.088710156103891,13.392282357759791,13.695854559415691,13.999426761071591,14.302998962727491,14.606571164383391,14.910143366039291,15.213715567695191,15.517287769351091,null,0,0,0,5.1943155153676111E-2,0.14198146235629358,0.31050230196114564,0.53286910711392266,0.57979669850073579,0.62472647622779243,null,0.53286910711392266,0.57979669850073579,0.62472647622779243]
["2013-04-22T18:00:00","2013-04-22T18:00:00",null,13.136183709416967,13.439755911072867,13.743328112728767,14.046900314384667,14.350472516040567,14.654044717696467,14.957616919352366,15.261189121008266,15.564761322664166,null,0,0,0,0,8.6873349773213149E-2,0.2581280396493113,0.48311303217724327,0.53256417766059128,0.57991236139682723,null,0.48311303217724327,0.53256417766059128,0.57991236139682723]
["2013-04-22T19:00:00","2013-04-22T19:00:00",null,12.966167255524555,13.269739457180455,13.573311658836355,13.876883860492255,14.180456062148155,14.484028263804055,14.787600465459954,15.091172667115854,15.394744868771754,null,0,0,0,0,3.5140490794248122E-2,0.20909748651538571,0.43666912199226593,0.48861227714594213,0.5383473224651506,null,0.43666912199226593,0.48861227714594213,0.5383473224651506]
["2013-04-22T20:00:00","2013-04-22T20:00:00",null,12.701966532081681,13.005538733737581,13.30911093539348,13.61268313704938,13.91625533870528,14.21982754036118,14.52339974201708,14.82697194367298,15.13054414532888,null,0,0,0,0,0,0.16633375938785505,0.39640791934379904,0.45074845088918336,0.50278623932147992,null,0.39640791934379904,0.45074845088918336,0.50278623932147992]
["2013-04-22T21:00:00","2013-04-22T21:00:00",null,12.526813708023402,12.830385909679302,13.133958111335202,13.437530312991102,13.741102514647002,14.044674716302902,14.348246917958802,14.651819119614702,14.955391321270602,null,0,0,0,0,0,0.12976325460557042,0.36223479095322253,0.41887806561169494,0.47312396387845951,null,0.36223479095322253,0.41887806561169494,0.47312396387845951]
["2013-04-22T22:00:00","2013-04-22T22:00:00",null,12.290956319814912,12.594528521470812,12.898100723126712,13.201672924782612,13.505245126438512,13.808817328094412,14.112389529750311,14.415961731406211,14.719533933062111,null,0,0,0,0,0,0.10170974489909101,0.33644196512488894,0.39524077557415155,0.45155809116182183,null,0.33644196512488894,0.39524077557415155,0.45155809116182183]
["2013-04-22T23:00:00","2013-04-22T23:00:00",null,12.13496687482831,12.43853907648421,12.74211127814011,13.04568347979601,13.349255681451909,13.652827883107809,13.956400084763709,14.259972286419609,14.563544488075509,null,0,0,0,0,0,7.6747588960866836E-2,0.31369843382986834,0.37461072083497893,0.43296790931734819,null,0.31369843382986834,0.37461072083497893,0.43296790931734819]
["2013-04-23","2013-04-23",null,12.071709361454927,12.375281563110827,12.678853764766727,12.982425966422626,13.285998168078526,13.589570369734426,13.893142571390326,14.196714773046226,14.500286974702126,null,0,0,0,0,0,5.4172294605615227E-2,0.29329970488287804,0.35628340920889434,0.41663841135102042,null,0.29329970488287804,0.35628340920889434,0.41663841135102042]
["2013-04-23T01:00:00","2013-04-23T01:00:00",null,12.014058601059491,12.31763080271539,12.62120300437129,12.92477520602719,13.22834740768309,13.53191960933899,13.83549181099489,14.13906401265079,14.44263621430669,null,0,0,0,0,0,3.3857684128509452E-2,0.27511960057909135,0.34014317779980668,0.40245393436674731,null,0.27511960057909135,0.34014317779980668,0.40245393436674731]
["2013-04-23T02:00:00","2013-04-23T02:00:00",null,11.976191069732595,12.279763271388495,12.583335473044395,12.886907674700295,13.190479876356195,13.494052078012094,13.797624279667994,14.101196481323894,14.404768682979794,null,0,0,0,0,0,1.8947685341482539E-2,0.26232307834791241,0.32935498403712005,0.39360046541140409,null,0.26232307834791241,0.32935498403712005,0.39360046541140409]
["2013-04-23T03:00:00","2013-04-23T03:00:00",null,12.14192983866797,12.44550204032387,12.74907424197977,13.05264644363567,13.35621864529157,13.65979084694747,13.96336304860337,14.266935250259269,14.570507451915169,null,3.8326477841123481E-2,4.1133931773518533E-2,4.3794178383615719E-2,4.6338762097621722E-2,4.8767682915536542E-2,7.0028626178842729E-2,0.31562264382847616,0.38477854088226732,0.45106389515125039,null,0.31562264382847616,0.38477854088226732,0.45106389515125039]
["2013-04-23T04:00:00","2013-04-23T04:00:00",null,12.188145294143641,12.491717495799541,12.795289697455441,13.098861899111341,13.402434100767241,13.706006302423141,14.009578504079041,14.313150705734941,14.616722907390841,null,7.4823378962259185E-2,8.0459316444520396E-2,8.5821868899657025E-2,9.0942580753875707E-2,9.5831966815912051E-2,0.11944822723598411,0.36729241395502782,0.43859333199087364,0.50695010358076242,null,0.36729241395502782,0.43859333199087364,0.50695010358076242]
["2013-04-23T05:00:00","2013-04-23T05:00:00",null,12.302845558108629,12.606417759764529,12.909989961420429,13.213562163076329,13.517134364732229,13.820706566388129,14.124278768044029,14.427850969699929,14.731423171355829,null,0.10667273462227647,0.11523178893302392,0.12337025089434892,0.13115120935866478,0.13857466432597157,0.16461984556395845,0.41478780501356138,0.48830734769261075,0.5587986254558186,null,0.41478780501356138,0.48830734769261075,0.5587986254558186]
["2013-04-23T06:00:00","2013-04-23T06:00:00",null,12.338220908077453,12.641793109733353,12.945365311389253,13.248937513045153,13.552509714701053,13.856081916356953,14.159654118012853,14.463226319668752,14.766798521324652,null,0.13720773919034851,0.14871093994705331,0.15965685584077338,0.17011909053265756,0.18010815883144146,0.2086032905048143,0.46111605230244757,0.53687524924217156,0.60952206279616972,null,0.46111605230244757,0.53687524924217156,0.60952206279616972]
["2013-04-23T07:00:00","2013-04-23T07:00:00",null,12.421869398844716,12.725441600500616,13.029013802156516,13.332586003812416,13.636158205468316,13.939730407124216,14.243302608780116,14.546874810436016,14.850447012091916,null,0.16740626987888257,0.18184310227280917,0.19558595729018874,0.20871895340090565,0.22126312022243111,0.25219768752245436,0.50704473685938234,0.58505410286851667,0.65984593740456943,null,0.50704473685938234,0.58505410286851667,0.65984593740456943]
["2013-04-23T08:00:00","2013-04-23T08:00:00",null,12.533863870748482,12.837436072404381,13.141008274060281,13.444580475716181,13.748152677372081,14.051724879027981,14.355297080683881,14.658869282339781,14.962441483995681,null,0.19294674029756267,0.21039080798985998,0.22701472060078354,0.24289208179148214,0.25805443598816252,0.29150204257598511,0.54875698311335674,0.62906909223557916,0.70607955141483558,null,0.54875698311335674,0.62906909223557916,0.70607955141483558]
["2013-04-23T09:00:00","2013-04-23T09:00:00",null,11.502212988640141,11.80578519029604,12.10935739195194,12.41292959360784,12.71650179526374,13.02007399691964,13.32364619857554,13.62721840023144,13.93079060188734,null,0.22297703404632774,0.24357554435929366,0.26320669226858795,0.28193356662662383,0.2998087414770792,0.33584299101385007,0.59556891160407877,0.67824685269180263,0.75750748094046927,null,0.59556891160407877,0.67824685269180263,0.75750748094046927]
["2013-04-23T10:00:00","2013-04-23T10:00:00",null,11.023733491067262,11.327305692723161,11.630877894379061,11.934450096034961,12.238022297690861,12.541594499346761,12.845166701002661,13.148738902658561,13.452311104314461,null,0.26755982308511062,0.29106042060909165,0.31343593359836763,0.33477048052282288,0.35512715023487085,0.39351671692840762,0.65548229177931105,0.74030525384908952,0.82161626980119074,null,0.65548229177931105,0.74030525384908952,0.82161626980119074]
["2013-04-23T11:00:00","2013-04-23T11:00:00",null,10.756700551360506,11.060272753016406,11.363844954672306,11.667417156328206,11.970989357984106,12.274561559640006,12.578133761295906,12.881705962951806,13.185278164607706,null,0.31763134228385687,0.34393939374023297,0.36897515333960612,0.39283325436059624,0.41558730046435233,0.45625858065350605,0.72039020610393523,0.80727407068588386,0.89056187068027071,null,0.72039020610393523,0.80727407068588386,0.89056187068027071]
["2013-04-23T12:00:00","2013-04-23T12:00:00",null,10.48231362392985,10.785885825585749,11.089458027241649,11.393030228897549,11.696602430553449,12.000174632209349,12.303746833865249,12.607319035521149,12.910891237177049,null,0.36854404618144804,0.39745977020424356,0.42495599504773818,0.45114838360802306,0.47611053954624716,0.51888478148251327,0.78501422059269932,0.87379075074704904,0.95888709784395254,null,0.78501422059269932,0.87379075074704904,0.95888709784395254]
["2013-04-23T13:00:00","2013-04-23T13:00:00",null,10.554520503417983,10.858092705073883,11.161664906729783,11.465237108385683,11.768809310041583,12.072381511697483,12.375953713353383,12.679525915009282,12.983098116665182,null,0.34941760909146075,0.38102512415056017,0.4110554178993252,0.4396556976600538,0.46689956709389485,0.5118503744384223,0.78004071606077852,0.87077300063994278,0.95774098369177629,null,0.78004071606077852,0.87077300063994278,0.95774098369177629]
["2013-04-23T14:00:00","2013-04-23T14:00:00",null,10.487448106461638,10.791020308117538,11.094592509773438,11.398164711429338,11.701736913085238,12.005309114741138,12.308881316397038,12.612453518052938,12.916025719708838,null,0.33000727216561332,0.36432760787848772,0.39692351495872991,0.42794220072863776,0.45748881327556684,0.50462670083709116,0.77489897458908874,0.86760804321053864,0.95645817702603775,null,0.77489897458908874,0.86760804321053864,0.95645817702603775]
["2013-04-23T15:00:00","2013-04-23T15:00:00",null,10.309896812341851,10.613469013997751,10.917041215653651,11.220613417309551,11.524185618965451,11.827757820621351,12.13133002227725,12.43490222393315,12.73847442558905,null,0.31957658189993582,0.35638892728313842,0.39135066632888205,0.42460900635946458,0.45626909546224165,0.50541531149225827,0.77759076562539264,0.87211889615809468,0.96269345860622602,null,0.77759076562539264,0.87211889615809468,0.96269345860622602]
["2013-04-23T16:00:00","2013-04-23T16:00:00",null,10.100001581458518,10.403573783114417,10.707145984770317,11.010718186426217,11.314290388082117,11.617862589738017,11.921434791393917,12.225006993049817,12.528579194705717,null,0.3165693466015651,0.35571597952406248,0.39288582840427411,0.42822610056449789,0.46186297370956064,0.51288082569450733,0.78683328250395168,0.88304378243434356,0.97521659581028031,null,0.78683328250395168,0.88304378243434356,0.97521659581028031]
["2013-04-23T17:00:00","2013-04-23T17:00:00",null,10.155181145281912,10.458753346937812,10.762325548593711,11.065897750249611,11.369469951905511,11.673042153561411,11.976614355217311,12.280186556873211,12.583758758529111,null,0.31060745004850143,0.35217248898017806,0.3916135365472711,0.42910934449828508,0.46477557572931133,0.51772815252160143,0.79351018605103352,0.89145562942279311,0.98528978257894873,null,0.79351018605103352,0.89145562942279311,0.98528978257894873]
["2013-04-23T18:00:00","2013-04-23T18:00:00",null,10.122450297847067,10.426022499502967,10.729594701158867,11.033166902814767,11.336739104470666,11.640311306126566,11.943883507782466,12.247455709438366,12.551027911094266,null,0.30272134349682994,0.34675736248136363,0.38853269758775144,0.42823661537323343,0.46599529354263652,0.52092465437721225,0.79858883867030994,0.89832179952711511,0.99385935169843176,null,0.79858883867030994,0.89832179952711511,0.99385935169843176]
["2013-04-23T19:00:00","2013-04-23T19:00:00",null,10.131015341276235,10.434587542932135,10.738159744588035,11.041731946243935,11.345304147899835,11.648876349555735,11.952448551211635,12.256020752867535,12.559592954523435,null,0.29435155574332261,0.3408795843981845,0.38499972185260262,0.42692226428128816,0.46678390419780369,0.52370056388340058,0.80324689894016388,0.90477789209075021,1,null,0.80324689894016388,0.90477789209075021,1]
["2013-04-23T20:00:00","2013-04-23T20:00:00",null,10.011975989244508,10.315548190900408,10.619120392556308,10.922692594212208,11.226264795868108,11.529836997524008,11.833409199179908,12.136981400835808,12.440553602491708,null,0.28854738132129237,0.33751484560280465,0.38393772617031086,0.42803683400725773,0.46994886162720784,0.52881076092888368,0.8102077023231059,0.91349466853253114,1,null,0.8102077023231059,0.91349466853253114,1]
["2013-04-23T21:00:00","2013-04-23T21:00:00",null,9.9607744682696495,10.264346669925549,10.567918871581449,10.871491073237349,11.175063274893249,11.478635476549149,11.782207678205049,12.085779879860949,12.389352081516849,null,0.28547705717050825,0.33681035341752197,0.38547288824570292,0.43167495782976217,0.47558479910946905,0.53633936398354609,0.81952382286281389,0.92451418808740016,1,null,0.81952382286281389,0.92451418808740016,1]
["2013-04-23T22:00:00","2013-04-23T22:00:00",null,9.8302578918219101,10.13383009347781,10.43740229513371,10.74097449678961,11.04454669844551,11.34811890010141,11.65169110175731,11.95526330341321,12.25883550506911,null,0.28580301624131066,0.33943905560141246,0.39026764102911921,0.43852009831661304,0.48436466440366333,0.5469488059977281,0.83186820831836372,0.93850939851443316,1,null,0.83186820831836372,0.93850939851443316,1]
["2013-04-23T23:00:00","2013-04-23T23:00:00",null,9.6966688955189646,10.000241097174865,10.303813298830764,10.607385500486663,10.910957702142563,11.214529903798462,11.518102105454362,11.821674307110262,12.125246508766162,null,0.28951474372496405,0.345379922537005,0.39830095490308859,0.44853019623286805,0.4962358834661128,0.56058651292775197,0.84717776983734194,0.95539618134374571,1,null,0.84717776983734194,0.95539618134374571,1]
["2013-04-24","2013-04-24",null,9.6511705286486968,9.9547427303045968,10.258314931960497,10.561887133616397,10.865459335272297,11.169031536928197,11.472603738584096,11.776175940239996,12.079748141895896,null,0.29583414377503681,0.35385485837786795,0.40880524882991504,0.46094818534956677,0.51046241968532824,0.57651644816212844,0.8647269856169949,0.97448055919879073,1,null,0.8647269856169949,0.97448055919879073,1]
["2013-04-24T01:00:00","2013-04-24T01:00:00",null,9.5435750049128956,9.8471472065687955,10.150719408224695,10.454291609880594,10.757863811536494,11.061436013192393,11.365008214848293,11.668580416504193,11.972152618160093,null,0.30445628693819765,0.36459047809687678,0.42152816739994503,0.47554273987452683,0.52682346207786268,0.59453883033488175,0.88433710390881803,0.99558378033106365,1,null,0.88433710390881803,0.99558378033106365,1]
["2013-04-24T02:00:00","2013-04-24T02:00:00",null,9.5281477990161925,9.8317200006720924,10.135292202327992,10.438864403983892,10.742436605639792,11.046008807295692,11.349581008951592,11.653153210607492,11.956725412263392,null,0.31388807037399674,0.37610419366231718,0.43500815219893552,0.49087333101097624,0.5438995114644154,0.61325518988418215,0.90462016995971717,1,1,null,0.90462016995971717,1,1]
["2013-04-24T03:00:00","2013-04-24T03:00:00",null,9.4470306801151747,9.7506028817710746,10.054175083426975,10.357747285082874,10.661319486738774,10.964891688394674,11.268463890050574,11.572036091706474,11.875608293362374,null,0.32408743484749186,0.3883854902654536,0.44924520322688644,0.50695047356765055,0.56172211227119295,0.63271810085370739,0.92562875781337006,1,1,null,0.92562875781337006,1,1]
["2013-04-24T04:00:00","2013-04-24T04:00:00",null,9.4037846328624219,9.7073568345183219,10.010929036174222,10.314501237830122,10.618073439486022,10.921645641141922,11.225217842797822,11.528790044453721,11.832362246109621,null,0.33283575571547946,0.39926831730676027,0.46213635873668546,0.52173429464985077,0.57828293602970304,0.65096129400990743,0.94545968708864003,1,1,null,0.94545968708864003,1,1]
["2013-04-24T05:00:00","2013-04-24T05:00:00",null,9.6091111853520967,9.9126833870079967,10.216255588663897,10.519827790319797,10.823399991975696,11.126972193631596,11.430544395287496,11.734116596943396,12.037688798599296,null,0.3297549167559598,0.39863742878262654,0.46381872813437536,0.52558271464706652,0.58419225853908885,0.65880534132663671,0.95514382593409264,1,1,null,0.95514382593409264,1,1]
["2013-04-24T06:00:00","2013-04-24T06:00:00",null,9.459226321910478,9.7627985235663779,10.066370725222278,10.369942926878178,10.673515128534078,10.977087330189978,11.280659531845878,11.584231733501777,11.887803935157677,null,0.32715775899827598,0.39851125107779978,0.46601632316010783,0.52996738988979586,0.59063783629398836,0.66719615869761517,0.96538524964253003,1,1,null,0.96538524964253003,1,1]
["2013-04-24T07:00:00","2013-04-24T07:00:00",null,9.4835240706480288,9.7870962723039288,10.090668473959829,10.394240675615729,10.697812877271629,11.001385078927528,11.304957280583428,11.608529482239328,11.912101683895228,null,0.32722084785068933,0.40096120151318571,0.47070592785616849,0.53677047114170451,0.59943873120565372,0.67787920437294613,0.97784529799417097,1,1,null,0.97784529799417097,1,1]
["2013-04-24T08:00:00","2013-04-24T08:00:00",null,9.6056248925262757,9.9091970941821756,10.212769295838076,10.516341497493976,10.819913699149875,11.123485900805775,11.427058102461675,11.730630304117575,12.034202505773475,null,0.32816718063688993,0.40423130702994547,0.47616311358992519,0.54429907419636692,0.60891257387639508,0.68919313857241082,0.99090469044373897,1,1,null,0.99090469044373897,1,1]
["2013-04-24T09:00:00","2013-04-24T09:00:00",null,9.8041255011962658,10.107697702852166,10.411269904508066,10.714842106163966,11.018414307819866,11.321986509475765,11.625558711131665,11.929130912787565,12.232703114443465,null,0.32595907080242192,0.40439954396971445,0.47858151959910444,0.54883095676139415,0.61544227010117913,0.69761550036959596,1,1,1,null,1,1,1]
["2013-04-24T10:00:00","2013-04-24T10:00:00",null,10.032770155804791,10.336342357460691,10.63991455911659,10.94348676077249,11.24705896242839,11.55063116408429,11.85420336574019,12.15777556739609,12.46134776905199,null,0.31890363414085982,0.3998150873610094,0.47632083572095862,0.5487783827177164,0.61746111337840703,0.70161112768910949,1,1,1,null,1,1,1]
["2013-04-24T11:00:00","2013-04-24T11:00:00",null,10.056332462107584,10.359904663763484,10.663476865419383,10.967049067075283,11.270621268731183,11.574193470387083,11.877765672042983,12.181337873698883,12.484910075354783,null,0.27808514662940814,0.36127831334517468,0.43992908268717856,0.51441598776989983,0.58502292842919823,0.67099200465115294,0.97111582040341116,0.97275613056615884,0.97432283706775757,null,0.97111582040341116,0.97275613056615884,0.97432283706775757]
["2013-04-24T12:00:00","2013-04-24T12:00:00",null,10.224507384142189,10.528079585798089,10.831651787453989,11.135223989109889,11.438796190765789,11.742368392421689,12.045940594077589,12.349512795733489,12.653084997389389,null,0.19140106341343505,0.27708623979952979,0.35810284110703511,0.43481888564169552,0.5075393028568419,0.59550619273855332,0.89753318887194833,0.90098204613721267,0.90427318127144352,null,0.89753318887194833,0.90098204613721267,0.90427318127144352]
["2013-04-24T13:00:00","2013-04-24T13:00:00",null,10.455442691423086,10.759014893078986,11.062587094734885,11.366159296390785,11.669731498046685,11.973303699702585,12.276875901358485,12.580448103014385,12.884020304670285,null,0.10018509763243472,0.1884358873500066,0.27189192428416231,0.35091071193191076,0.42580769455531847,0.5158460017579356,0.81984978193361635,0.8251702751538107,0.83024892777308701,null,0.81984978193361635,0.8251702751538107,0.83024892777308701]
["2013-04-24T14:00:00","2013-04-24T14:00:00",null,10.616952216845471,10.920524418501373,11.224096620157272,11.527668821813172,11.831241023469072,12.134813225124972,12.438385426780872,12.741957628436772,13.045529830092672,null,4.500338138820531E-3,9.5411374466489604E-2,0.1813909654971802,0.26278609991916568,0.33994376642071922,0.43213760941412654,0.73818126248450633,0.74544699532077963,0.75237625427751487,null,0.73818126248450633,0.74544699532077963,0.75237625427751487]
["2013-04-24T15:00:00","2013-04-24T15:00:00",null,10.855443983445449,11.159016185101349,11.462588386757249,11.766160588413149,12.069732790069049,12.373304991724948,12.676877193380848,12.980449395036748,13.284021596692648,null,0,0,8.3203681524502263E-2,0.1671328848517582,0.24669844255375542,0.34118451385151527,0.64940473233015639,0.65874188248733545,0.6676584402950918,null,0.64940473233015639,0.65874188248733545,0.6676584402950918]
["2013-04-24T16:00:00","2013-04-24T16:00:00",null,10.852049999133435,11.155622200789335,11.459194402445235,11.762766604101135,12.066338805757034,12.369911007412934,12.673483209068834,12.977055410724734,13.280627612380634,null,0,0,0,7.1637391915384138E-2,0.15360032600908949,0.25036811080246629,0.56076489468936874,0.57217346216745346,0.58307731882623104,null,0.56076489468936874,0.57217346216745346,0.58307731882623104]
["2013-04-24T17:00:00","2013-04-24T17:00:00",null,10.890731969608334,11.194304171264234,11.497876372920134,11.801448574576034,12.105020776231934,12.408592977887833,12.712165179543733,13.015737381199633,13.319309582855533,null,0,0,0,0,5.8830354875469199E-2,0.15791139759066963,0.47051629131204009,0.48402782053723725,0.49695052047324273,null,0.47051629131204009,0.48402782053723725,0.49695052047324273]
["2013-04-24T18:00:00","2013-04-24T18:00:00",null,10.90253825839422,11.20611046005012,11.50968266170602,11.813254863361919,12.116827065017819,12.420399266673719,12.723971468329619,13.027543669985519,13.331115871641419,null,0,0,0,0,0,6.496048836830158E-2,0.3797840067328756,0.39540901251392074,0.41035055572715412,null,0.3797840067328756,0.39540901251392074,0.41035055572715412]
["2013-04-24T19:00:00","2013-04-24T19:00:00",null,10.663318999263868,10.966891200919768,11.270463402575668,11.574035604231568,11.877607805887468,12.181180007543368,12.484752209199268,12.788324410855168,13.091896612511068,null,0,0,0,0,0,0,0.29612818843274435,0.31374049306481072,0.33057470185044524,null,0.29612818843274435,0.31374049306481072,0.33057470185044524]
["2013-04-24T20:00:00","2013-04-24T20:00:00",null,10.44557430222687,10.74914650388277,11.05271870553867,11.35629090719457,11.65986310885047,11.96343531050637,12.267007512162269,12.570579713818169,12.874151915474069,null,0,0,0,0,0,0,0.29652775116469571,0.31593808809054319,0.33447569589133874,null,0.29652775116469571,0.31593808809054319,0.33447569589133874]
["2013-04-24T21:00:00","2013-04-24T21:00:00",null,10.416300392532412,10.719872594188312,11.023444795844211,11.327016997500111,11.630589199156011,11.934161400811911,12.237733602467811,12.541305804123711,12.844878005779611,null,0,0,0,0,0,0,0.29628591056377779,0.3175363390183486,0.337829919877983,null,0.29628591056377779,0.3175363390183486,0.337829919877983]
["2013-04-24T22:00:00","2013-04-24T22:00:00",null,10.417886664235525,10.721458865891424,11.025031067547324,11.328603269203224,11.632175470859124,11.935747672515024,12.239319874170924,12.542892075826824,12.846464277482724,null,0,0,0,0,0,8.7272912505164584E-4,0.29901976083502391,0.32202616234843356,0.34400211260575791,null,0.29901976083502391,0.32202616234843356,0.34400211260575791]
["2013-04-24T23:00:00","2013-04-24T23:00:00",null,10.497639458383352,10.801211660039252,11.104783861695152,11.408356063351052,11.711928265006952,12.015500466662852,12.319072668318752,12.622644869974652,12.926217071630552,null,4.2931964067299634E-2,4.5455518163834516E-2,4.7831864938071525E-2,5.0092548816217358E-2,5.2237569798272002E-2,5.5139657009287114E-2,0.3552214135266028,0.38006790656873579,0.40379982988489899,null,0.3552214135266028,0.38006790656873579,0.40379982988489899]
["2013-04-25","2013-04-25",null,10.463362915867227,10.766935117523127,11.070507319179027,11.374079520834927,11.677651722490827,11.981223924146727,12.284796125802627,12.588368327458527,12.891940529114427,null,9.8029561841644505E-2,0.10312924407839208,0.10794502647927946,0.11251896827924894,0.11686158428703604,0.12183508881895685,0.42390414418729377,0.45062227318435677,0.47615222879430108,null,0.42390414418729377,0.45062227318435677,0.47615222879430108]
["2013-04-25T01:00:00","2013-04-25T01:00:00",null,10.379281075802625,10.682853277458525,10.986425479114425,11.289997680770325,11.593569882426225,11.897142084082125,12.200714285738025,12.504286487393925,12.807858689049825,null,0.15857383054101049,0.1661550076393507,0.17331559238826841,0.18011867364017703,0.18656425139507654,0.19352505477801857,0.4974972905274922,0.52601345181833625,0.55326783606091279,null,0.4974972905274922,0.52601345181833625,0.55326783606091279]
["2013-04-25T02:00:00","2013-04-25T02:00:00",null,10.364639552077232,10.668211753733132,10.971783955389032,11.275356157044932,11.578928358700832,11.882500560356732,12.186072762012632,12.489644963668532,12.793217165324432,null,0.21816125164544031,0.2284131901626133,0.23809732900806588,0.24728727184294708,0.25599353347599241,0.26509935784098909,0.57111146648516176,0.60157286739208482,0.63067785797212017,null,0.57111146648516176,0.60157286739208482,0.63067785797212017]
["2013-04-25T03:00:00","2013-04-25T03:00:00",null,10.258507772759163,10.562079974415063,10.865652176070963,11.169224377726863,11.472796579382763,11.776368781038663,12.079940982694563,12.383513184350463,12.687085386006363,null,0.28321637329236238,0.29600238071480584,0.3080944107607021,0.31955555228246468,0.33040683489756467,0.34155253215726039,0.64949936560877641,0.68180085804442281,0.71266182168329706,null,0.64949936560877641,0.68180085804442281,0.71266182168329706]
["2013-04-25T04:00:00","2013-04-25T04:00:00",null,10.235032884850733,10.538605086506633,10.842177288162535,11.145749489818435,11.449321691474335,11.752893893130235,12.056466094786135,12.360038296442035,12.663610498097935,null,0.34939657947398961,0.36469562618423235,0.37916400300436565,0.39286479878680292,0.40584007276648643,0.4190046133034101,0.72886514194479834,0.76298569629169699,0.79557108856320347,null,0.72886514194479834,0.76298569629169699,0.79557108856320347]
["2013-04-25T05:00:00","2013-04-25T05:00:00",null,10.311664309948892,10.615236511604792,10.918808713260692,11.222380914916592,11.525953116572492,11.829525318228391,12.133097519884291,12.436669721540191,12.740241923196091,null,0.41519825254113663,0.4329998237304431,0.44983403251607784,0.46576396775045426,0.48086323309472129,0.49603610210013727,0.80781032593139779,0.84373942738081309,0.87805976309368738,null,0.80781032593139779,0.84373942738081309,0.87805976309368738]
["2013-04-25T06:00:00","2013-04-25T06:00:00",null,10.29640919022555,10.59998139188145,10.90355359353735,11.207125795193249,11.510697996849149,11.814270198505049,12.117842400160949,12.421414601816849,12.724986803472749,null,0.47818195686715298,0.49857017100540774,0.51785433022642846,0.5360975233826285,0.55338386894389235,0.57062815527021404,0.88437916314376031,0.92219041535684121,0.95829826855476097,null,0.88437916314376031,0.92219041535684121,0.95829826855476097]
["2013-04-25T07:00:00","2013-04-25T07:00:00",null,10.469920378396083,10.773492580051983,11.077064781707882,11.380636983363782,11.684209185019682,11.987781386675582,12.291353588331482,12.594925789987382,12.898497991643282,null,0.53964101392651287,0.56262638582245139,0.58436049547885816,0.60491694655688177,0.62440088714387809,0.64373762040857663,0.95946541232440852,0.99916933010989062,1,null,0.95946541232440852,0.99916933010989062,1]
["2013-04-25T08:00:00","2013-04-25T08:00:00",null,10.67602079807725,10.97959299973315,11.28316520138905,11.58673740304495,11.89030960470085,12.19388180635675,12.497454008012649,12.801026209668549,13.104598411324449,null,0.59447574148246873,0.62019496364965332,0.64450520144627277,0.66750108815094678,0.68930880146850226,0.71084312975893327,1,1,1,null,1,1,1]
["2013-04-25T09:00:00","2013-04-25T09:00:00",null,10.937845353916902,11.241417555572802,11.544989757228702,11.848561958884602,12.152134160540502,12.455706362196402,12.759278563852302,13.062850765508202,13.366422967164102,null,0.6436535019386922,0.67218017803827179,0.69916117725372406,0.72468061805493289,0.7488857077641965,0.77271226435898011,1,1,1,null,1,1,1]
["2013-04-25T10:00:00","2013-04-25T10:00:00",null,11.139696873425521,11.443269075081421,11.746841276737321,12.050413478393221,12.353985680049121,12.657557881705021,12.961130083360921,13.264702285016821,13.568274486672721,null,0.6902130750197607,0.7215682346692065,0.75123051011222708,0.77929453462744191,0.80592854515462031,0.83205784486249201,1,1,1,null,1,1,1]
["2013-04-25T11:00:00","2013-04-25T11:00:00",null,11.37444561266371,11.67801781431961,11.98159001597551,12.285162217631409,12.588734419287309,12.892306620943209,13.195878822599109,13.499451024255009,13.803023225910909,null,0.7296541225868538,0.7639639434909925,0.79644418767514369,0.82717897360919124,0.85634705304164005,0.88490527356742665,1,1,1,null,1,1,1]
["2013-04-25T12:00:00","2013-04-25T12:00:00",null,11.487086947525439,11.790659149181339,12.094231350837239,12.397803552493139,12.701375754149039,13.004947955804939,13.308520157460839,13.612092359116739,13.915664560772639,null,0.70696316533551107,0.74424867711181375,0.77955740484583114,0.81298398181618259,0.8447071597713729,0.87570481592380989,0.9931233150869424,0.99535245453888155,0.99747644590346507,null,0.9931233150869424,0.99535245453888155,0.99747644590346507]
["2013-04-25T13:00:00","2013-04-25T13:00:00",null,11.689335364668008,11.992907566323908,12.296479767979807,12.600051969635707,12.903624171291607,13.207196372947507,13.510768574603407,13.814340776259307,14.117912977915207,null,0.66699637733163986,0.70725757998010663,0.74540530607272582,0.78152367407938106,0.81582298017478405,0.84927058676260703,0.96903388827376991,0.97350268198638368,0.97777169433302191,null,0.96903388827376991,0.97350268198638368,0.97777169433302191]
["2013-04-25T14:00:00","2013-04-25T14:00:00",null,11.806488523671391,12.11006072532729,12.41363292698319,12.71720512863909,13.02077733029499,13.32434953195089,13.62792173360679,13.93149393526269,14.23506613691859,null,0.62524207184272318,0.66849999498082513,0.70949723424078159,0.74832842290121182,0.78521437194556309,0.82113295858624313,0.94326209206290745,0.94998105484493145,0.95641611779109548,null,0.94326209206290745,0.94998105484493145,0.95641611779109548]
["2013-04-25T15:00:00","2013-04-25T15:00:00",null,11.80460501731806,12.10817721897396,12.41174942062986,12.71532162228576,13.01889382394166,13.32246602559756,13.62603822725346,13.92961042890936,14.23318263056526,null,0.58351931078001318,0.6297739544077503,0.67362070683504405,0.71516471614924926,0.75463730814254881,0.79302687483608592,0.91751132546951608,0.9264909721296859,0.93508157086664023,null,0.91751132546951608,0.9264909721296859,0.93508157086664023]
["2013-04-25T16:00:00","2013-04-25T16:00:00",null,11.774199852102978,12.077772053758878,12.381344255414778,12.684916457070678,12.988488658726578,13.292060860382477,13.595633062038377,13.899205263694277,14.202777465350177,null,0.54627585823865255,0.59542207426866922,0.64201319177594462,0.68617538846530479,0.7281505049376682,0.76891641840544223,0.8956825825344894,0.90683879460292049,0.91751132546951608,null,0.8956825825344894,0.90683879460292049,0.91751132546951608]
["2013-04-25T17:00:00","2013-04-25T17:00:00",null,11.843480647502993,12.147052849158893,12.450625050814793,12.754197252470693,13.057769454126593,13.361341655782493,13.664913857438393,13.968486059094293,14.272058260750192,null,0.5029969054830794,0.55517138642893793,0.60464356152975729,0.65153960849036352,0.69613291233788188,0.73939083547598417,0.86854386118800386,0.88198178675205197,0.89484139783564443,null,0.86854386118800386,0.88198178675205197,0.89484139783564443]
["2013-04-25T18:00:00","2013-04-25T18:00:00",null,11.92934284618407,12.23291504783997,12.53648724949587,12.84005945115177,13.14363165280767,13.44720385446357,13.75077605611947,14.05434825777537,14.35792045943127,null,0.45918169748199256,0.51437392853495734,0.56671664642058517,0.61634654365243746,0.6635475200663753,0.70929745287480572,0.84083734016979794,0.85654646442072746,0.87159315572131679,null,0.84083734016979794,0.85654646442072746,0.87159315572131679]
["2013-04-25T19:00:00","2013-04-25T19:00:00",null,11.796846667165472,12.100418868821372,12.403991070477272,12.707563272133171,13.011135473789071,13.314707675444971,13.618279877100871,13.921852078756771,14.225424280412671,null,0.41466199729562303,0.47292455249937193,0.52819038721348599,0.58059619395152662,0.63044690216682608,0.67873090388052704,0.81268919718469845,0.83071157935745166,0.84796638049250894,null,0.81268919718469845,0.83071157935745166,0.84796638049250894]
["2013-04-25T20:00:00","2013-04-25T20:00:00",null,11.655333967807838,11.958906169463738,12.262478371119638,12.566050572775538,12.869622774431438,13.173194976087338,13.476767177743238,13.780339379399138,14.083911581055037,null,0.37615676770599499,0.43737398416443685,0.49544727281094592,0.55052384096781926,0.60291913289712473,0.65363205542874059,0.78990360665473558,0.81014461347069244,0.82952340597033325,null,0.78990360665473558,0.81014461347069244,0.82952340597033325]
["2013-04-25T21:00:00","2013-04-25T21:00:00",null,11.544893759335729,11.848465960991629,12.152038162647528,12.455610364303428,12.759182565959328,13.062754767615228,13.366326969271128,13.669899170927028,13.973471372582928,null,0.34243577609104764,0.40650250571682683,0.46729912982584643,0.52495182612293245,0.57980758329635951,0.63286530817600561,0.77137651366267534,0.79376254146068681,0.8151917216637623,null,0.77137651366267534,0.79376254146068681,0.8151917216637623]
["2013-04-25T22:00:00","2013-04-25T22:00:00",null,11.316137825554275,11.619710027210175,11.923282228866075,12.226854430521975,12.530426632177875,12.833998833833775,13.137571035489675,13.441143237145575,13.744715438801475,null,0.31557043977168675,0.38237101966871206,0.44575428672667988,0.50587796307662303,0.56307852259808033,0.61837590173840118,0.75902161339839003,0.78343699928236488,0.80681141910151943,null,0.75902161339839003,0.78343699928236488,0.80681141910151943]
["2013-04-25T23:00:00","2013-04-25T23:00:00",null,11.184526927093998,11.488099128749898,11.791671330405798,12.095243532061698,12.398815733717598,12.702387935373498,13.005960137029398,13.309532338685298,13.613104540341197,null,0.2914810129585142,0.36097338389184341,0.42691174947255278,0.48946434664041077,0.54897816408369171,0.60647313824974503,0.74921129684811072,0.77563501120057787,0.80091261140086911,null,0.74921129684811072,0.77563501120057787,0.80091261140086911]
["2013-04-26","2013-04-26",null,11.100745397730559,11.404317599386459,11.707889801042359,12.011462002698259,12.315034204354159,12.618606406010059,12.922178607665959,13.225750809321859,13.529323010977759,null,0.26317514784238127,0.33527519134212991,0.40369505178443188,0.46859245130032023,0.53034592300427585,0.58996488853491269,0.73473240521924188,0.76309084437905239,0.79021905091680256,null,0.73473240521924188,0.76309084437905239,0.79021905091680256]
["2013-04-26T01:00:00","2013-04-26T01:00:00",null,11.224917301153555,11.528489502809455,11.832061704465355,12.135633906121255,12.439206107777155,12.742778309433055,13.046350511088955,13.349922712744855,13.653494914400754,null,0.23717202583933644,0.31200591961033119,0.38301242300158145,0.45038080257032687,0.51447907662231285,0.57632718160488883,0.72321868965380154,0.75361700170831103,0.78267993305340455,null,0.72321868965380154,0.75361700170831103,0.78267993305340455]
["2013-04-26T02:00:00","2013-04-26T02:00:00",null,11.184564275878355,11.488136477534255,11.791708679190155,12.095280880846055,12.398853082501955,12.702425284157854,13.005997485813754,13.309569687469654,13.613141889125554,null,0.21622652683809696,0.29366809317551107,0.36714557661961839,0.43685875853639411,0.50318617204031924,0.56716878319621433,0.71607913452235494,0.74841217138420779,0.77932570906676024,null,0.71607913452235494,0.74841217138420779,0.77932570906676024]
["2013-04-26T03:00:00","2013-04-26T03:00:00",null,11.082268072897898,11.385840274553798,11.689412476209698,11.992984677865598,12.296556879521498,12.600129081177398,12.903701282833298,13.207273484489198,13.510845686145098,null,0.1968161899122495,0.27685491400734741,0.35279286269557625,0.42484033215164674,0.49338637029877547,0.55947194320178295,0.71040113780515146,0.74464786985687659,0.77740149906815237,null,0.71040113780515146,0.74464786985687659,0.77740149906815237]
["2013-04-26T04:00:00","2013-04-26T04:00:00",null,11.144589493590663,11.448161695246563,11.751733896902463,12.055306098558363,12.358878300214263,12.662450501870163,12.966022703526063,13.269594905181963,13.573167106837863,null,0.17433552883561795,0.25702398473207749,0.33548548751684121,0.40991981855588427,0.48073705538989436,0.54898867889242764,0.70198929081670192,0.73820229210197708,0.77283807207691846,null,0.70198929081670192,0.73820229210197708,0.77283807207691846]
["2013-04-26T05:00:00","2013-04-26T05:00:00",null,11.216770884126351,11.520343085782251,11.823915287438151,12.127487489094051,12.431059690749951,12.734631892405851,13.038204094061751,13.341776295717651,13.645348497373551,null,0.14874248437326004,0.23415427573223013,0.31520242146594213,0.39209721774910666,0.46524874212241152,0.53572950507688399,0.6908435935570062,0.72908595292824485,0.76565645771052959,null,0.6908435935570062,0.72908595292824485,0.76565645771052959]
["2013-04-26T06:00:00","2013-04-26T06:00:00",null,11.248293139878905,11.551865341534805,11.855437543190705,12.159009744846605,12.462581946502505,12.766154148158405,13.069726349814305,13.373298551470205,13.676870753126105,null,0.1216668518791879,0.20983352312687523,0.29349985623574215,0.37287614738049935,0.44839350371930564,0.52112443574318834,0.67839406001410074,0.71868680708877408,0.75721306629587326,null,0.67839406001410074,0.71868680708877408,0.75721306629587326]
["2013-04-26T07:00:00","2013-04-26T07:00:00",null,11.394056882027559,11.697629083683459,12.001201285339359,12.304773486995259,12.608345688651159,12.911917890307059,13.215490091962959,13.519062293618859,13.822634495274759,null,9.4580704576380181E-2,0.18546019647784251,0.27171317253565769,0.35354992892453641,0.43140157280263747,0.50636164427845931,0.66575525991395523,0.70807736507459207,0.7485488638977702,null,0.66575525991395523,0.70807736507459207,0.7485488638977702]
["2013-04-26T08:00:00","2013-04-26T08:00:00",null,11.455765790601831,11.759337992257731,12.062910193913631,12.36648239556953,12.67005459722543,12.97362679888133,13.27719900053723,13.58077120219313,13.88434340384903,null,6.8020297710350577E-2,0.16159158064811677,0.25039965522867352,0.33466533243546703,0.41484074904412732,0.49200893035441717,0.65350550773702554,0.69783594136615468,0.74024216499667617,null,0.65350550773702554,0.69783594136615468,0.74024216499667617]
["2013-04-26T09:00:00","2013-04-26T09:00:00",null,11.558240049747013,11.861812251402913,12.165384453058813,12.468956654714713,12.772528856370613,13.076101058026513,13.379673259682413,13.683245461338313,13.986817662994213,null,3.361584352759172E-2,0.13005766925016632,0.22158907929323365,0.30845191425771096,0.39109831091922831,0.47062180938628406,0.63436855583830265,0.6808545252582221,0.72531113659217816,null,0.63436855583830265,0.6808545252582221,0.72531113659217816]
["2013-04-26T10:00:00","2013-04-26T10:00:00",null,11.64753675012566,11.95110895178156,12.25468115343746,12.55825335509336,12.86182555674926,13.16539775840516,13.46896996006106,13.772542161716959,14.076114363372859,null,1.882150763665609E-3,0.10109988599242858,0.19528102783685752,0.28465690208913413,0.36970067514235966,0.45151640191376791,0.61745022858278342,0.66602864494107972,0.71248306993479249,null,0.61745022858278342,0.66602864494107972,0.71248306993479249]
["2013-04-26T11:00:00","2013-04-26T11:00:00",null,11.767649909047035,12.071222110702935,12.374794312358835,12.678366514014735,12.981938715670635,13.285510917326535,13.589083118982435,13.892655320638335,14.196227522294235,null,0,7.0123259457462936E-2,0.16696464791198906,0.25888510587827168,0.34634728494067646,0.43047626963390834,0.59861820613739192,0.64931009905153614,0.69778336732247681,null,0.59861820613739192,0.64931009905153614,0.69778336732247681]
["2013-04-26T12:00:00","2013-04-26T12:00:00",null,12.220557208147019,12.524129409802919,12.827701611458819,13.131273813114719,13.434846014770619,13.738418216426519,14.041990418082419,14.345562619738319,14.649134821394219,null,0,3.5760864509646328E-2,0.13525198476553407,0.22970651163708714,0.31958709670867119,0.40601882451499111,0.57637938566167835,0.62918475513167049,0.67968738148857466,null,0.57637938566167835,0.62918475513167049,0.67968738148857466]
["2013-04-26T13:00:00","2013-04-26T13:00:00",null,12.568087388626839,12.871659590282739,13.175231791938639,13.478803993594539,13.782376195250439,14.085948396906339,14.389520598562239,14.693092800218139,14.996665001874039,null,0,0,9.869199479198501E-2,0.19571213499501519,0.28806370011945631,0.37685074508254213,0.54946147529863965,0.60443289536815759,0.65700693904596741,null,0.54946147529863965,0.60443289536815759,0.65700693904596741]
["2013-04-26T14:00:00","2013-04-26T14:00:00",null,12.722670519616244,13.026242721272144,13.329814922928044,13.633387124583944,13.936959326239844,14.240531527895744,14.544103729551644,14.847675931207544,15.151248132863444,null,0,0,5.7084896625366185E-2,0.15672322420355131,0.25157731380705617,0.34275122035311456,0.51765417887356457,0.57482319396881498,0.62951071420247273,null,0.51765417887356457,0.57482319396881498,0.62951071420247273]
["2013-04-26T15:00:00","2013-04-26T15:00:00",null,13.069883848154042,13.373456049809942,13.677028251465842,13.980600453121742,14.284172654777642,14.587744856433542,14.891317058089442,15.194889259745342,15.498461461401241,null,0,0,7.6442659507536745E-3,0.10998489937397823,0.20742563192643135,0.30108103333408237,0.47837085343750496,0.53782158202837227,0.59470669728776249,null,0.47837085343750496,0.53782158202837227,0.59470669728776249]
["2013-04-26T16:00:00","2013-04-26T16:00:00",null,13.384680136625814,13.688252338281714,13.991824539937614,14.295396741593514,14.598968943249414,14.902541144905314,15.206113346561214,15.509685548217114,15.813257749873014,null,0,0,0,5.342574318539025E-2,0.15357929639161835,0.2498318555569532,0.42961368533070399,0.49145127550454387,0.55063913387702212,null,0.42961368533070399,0.49145127550454387,0.55063913387702212]
["2013-04-26T17:00:00","2013-04-26T17:00:00",null,13.49269511824042,13.796267319896319,14.099839521552219,14.403411723208119,14.706983924864019,15.010556126519919,15.314128328175819,15.617700529831719,15.921272731487619,null,0,0,0,0,9.6147411077978723E-2,0.1950497020446752,0.377376115532432,0.44166365614165781,0.50319631686216637,null,0.377376115532432,0.44166365614165781,0.50319631686216637]
["2013-04-26T18:00:00","2013-04-26T18:00:00",null,13.477048075080134,13.780620276736034,14.084192478391934,14.387764680047834,14.691336881703734,14.994909083359634,15.298481285015534,15.602053486671434,15.905625688327333,null,0,0,0,0,3.6707197295846747E-2,0.13831179410758265,0.32321433573555214,0.38999388601510615,0.45391340831858729,null,0.32321433573555214,0.38999388601510615,0.45391340831858729]
["2013-04-26T19:00:00","2013-04-26T19:00:00",null,13.501289507838099,13.804861709493998,14.108433911149898,14.412006112805798,14.715578314461698,15.019150516117598,15.322722717773498,15.626294919429398,15.929867121085298,null,0,0,1.4405287967719936E-3,4.3846752427293533E-3,4.3909841279706714E-2,0.14821674393648204,0.33571644332213535,0.40498800327201756,0.47131541677594241,null,0.33571644332213535,0.40498800327201756,0.47131541677594241]
["2013-04-26T20:00:00","2013-04-26T20:00:00",null,13.472423161908512,13.775995363564412,14.079567565220312,14.383139766876212,14.686711968532112,14.990284170188012,15.293856371843912,15.597428573499812,15.901000775155712,null,0,1.1145697259695717E-3,5.6674819084679166E-3,1.1597834035324883E-2,5.3972513239639544E-2,0.16102378097639655,0.35116269735467592,0.4229683262098286,0.49172466053166825,null,0.35116269735467592,0.4229683262098286,0.49172466053166825]
["2013-04-26T21:00:00","2013-04-26T21:00:00",null,13.294192226797733,13.597764428453633,13.901336630109533,14.204908831765433,14.508481033421333,14.812053235077233,15.115625436733133,15.419197638389033,15.722769840044933,null,5.3730672638721807E-3,9.6420796105103519E-3,1.721274190011499E-2,2.6034666429251507E-2,7.1174740331018976E-2,0.1808757398691376,0.37356975477015852,0.44782533406069719,0.51892647073056708,null,0.37356975477015852,0.44782533406069719,0.51892647073056708]
["2013-04-26T22:00:00","2013-04-26T22:00:00",null,13.024138178653047,13.327710380308947,13.631282581964847,13.934854783620747,14.238426985276647,14.541999186932546,14.845571388588446,15.149143590244346,15.452715791900246,null,2.7233354625105573E-2,3.4499087461378919E-2,4.4929777727056419E-2,5.6496067336174613E-2,0.10425432861309702,0.21646836743901496,0.41157027354047959,0.48813911075284189,0.56145887206591538,null,0.41157027354047959,0.48813911075284189,0.56145887206591538]
["2013-04-26T23:00:00","2013-04-26T23:00:00",null,12.89720251339072,13.20077471504662,13.50434691670252,13.80791911835842,14.11149132001432,14.41506352167022,14.71863572332612,15.02220792498202,15.32578012663792,null,5.2647647338958922E-2,6.2889071047396314E-2,7.6169274480411109E-2,9.0458899552039868E-2,0.14081431858664609,0.25553088189162776,0.453019649576065,0.53188071509277979,0.60740858624032135,null,0.453019649576065,0.53188071509277979,0.60740858624032135]
["2013-04-27","2013-04-27",null,12.996163787680125,13.299735989336025,13.603308190991925,13.906880392647825,14.210452594303725,14.514024795959624,14.817596997615524,15.121169199271424,15.424741400927324,null,8.0175416608660233E-2,9.3329442336848298E-2,0.10938555527605145,0.12633542695777741,0.17923542970638962,0.29640194344675724,0.49622499867048925,0.57733623325661432,0.65501964019494607,null,0.49622499867048925,0.57733623325661432,0.65501964019494607]
["2013-04-27T01:00:00","2013-04-27T01:00:00",null,12.877725103923744,13.181297305579644,13.484869507235544,13.788441708891444,14.092013910547344,14.395586112203244,14.699158313859144,15.002730515515044,15.306302717170944,null,0.10903856658777791,0.12509467952698108,0.14391618716363705,0.16351579064672464,0.21894986230060728,0.33854529685888973,0.54069212481318096,0.62404301365998072,0.70387144158036707,null,0.54069212481318096,0.62404301365998072,0.70387144158036707]
["2013-04-27T02:00:00","2013-04-27T02:00:00",null,12.876103619346626,13.179675821002526,13.483248022658426,13.786820224314326,14.090392425970226,14.393964627626126,14.697536829282026,15.001109030937926,15.304681232593826,null,0.13788068694942446,0.15683888709964275,0.17842578943375154,0.20067512471820073,0.25864326527735382,0.38066762065355109,0.58513822133840154,0.67071824963714044,0.7526916985395814,null,0.58513822133840154,0.67071824963714044,0.7526916985395814]
["2013-04-27T03:00:00","2013-04-27T03:00:00",null,12.892036061024729,13.195608262680629,13.499180464336529,13.802752665992429,14.106324867648329,14.409897069304229,14.713469270960129,15.017041472616029,15.320613674271929,null,0.1662286113004996,0.18809941347046857,0.21246222531076572,0.23737180720531209,0.29788453147847122,0.42233780767258328,0.62915321070546404,0.71697289326487768,0.80109136314937324,null,0.62915321070546404,0.71697289326487768,0.80109136314937324]
["2013-04-27T04:00:00","2013-04-27T04:00:00",null,12.83437420363104,13.137946405286939,13.441518606942839,13.745090808598739,14.048663010254639,14.352235211910539,14.655807413566439,14.959379615222339,15.262951816878239,null,0.19377741018767203,0.2185818439948628,0.24575210976755502,0.27335348269840526,0.33643182030304153,0.46334556174127506,0.67251628193092172,0.76259664836848118,0.84888116885250253,null,0.67251628193092172,0.76259664836848118,0.84888116885250253]
["2013-04-27T05:00:00","2013-04-27T05:00:00",null,12.988249781301406,13.291821982957305,13.595394184613205,13.898966386269105,14.202538587925005,14.506110789580905,14.809682991236805,15.113255192892705,15.416827394548605,null,0.21277766957283256,0.24068397195701413,0.27081941379313479,0.30125978508258677,0.36705094334099808,0.49656184253691543,0.70823508720562578,0.80070231522615787,0.88928957882326731,null,0.70823508720562578,0.80070231522615787,0.88928957882326731]
["2013-04-27T06:00:00","2013-04-27T06:00:00",null,12.857527986386954,13.161100188042854,13.464672389698753,13.768244591354653,14.071816793010553,14.375388994666453,14.678961196322353,14.982533397978253,15.286105599634153,null,0.23073696289317244,0.26180822270675819,0.29495089984124956,0.32827232872424555,0.39682888168010966,0.5289789978686531,0.74318631144263381,0.8380824602810808,0.92900401141748501,null,0.74318631144263381,0.8380824602810808,0.92900401141748501]
["2013-04-27T07:00:00","2013-04-27T07:00:00",null,12.445041420016581,12.748613621672481,13.052185823328381,13.355758024984281,13.659330226640181,13.962902428296081,14.266474629951981,14.570046831607881,14.873619033263781,null,0.255593970744041,0.28975658432588197,0.32585392271506625,0.3619933203391929,0.43324166433136085,0.56796790866011704,0.78464620228695481,0.88189766828216765,0.97509041810545327,null,0.78464620228695481,0.88189766828216765,0.97509041810545327]
["2013-04-27T08:00:00","2013-04-27T08:00:00",null,12.235881998217309,12.539454199873209,12.843026401529109,13.146598603185009,13.450170804840909,13.753743006496808,14.057315208152708,14.360887409808608,14.664459611464508,null,0.28847377766014337,0.32558053768794171,0.36448533000952105,0.40330600386121601,0.47710944637612551,0.61427512633153203,0.83328770749766456,0.93277882775355214,1,null,0.83328770749766456,0.93277882775355214,1]
["2013-04-27T09:00:00","2013-04-27T09:00:00",null,12.24247671010527,12.54604891176117,12.84962111341707,13.15319331507297,13.45676551672887,13.76033771838477,14.06390992004067,14.36748212169657,14.67105432335247,null,0.3211432884015345,0.3611941948752902,0.40291695593800014,0.44441890601726342,0.52077744705491447,0.66039307744570697,0.88175046095986986,0.98348123547643207,1,null,0.88175046095986986,0.98348123547643207,1]
["2013-04-27T10:00:00","2013-04-27T10:00:00",null,12.26143985621658,12.56501205787248,12.868584259528379,13.172156461184279,13.475728662840179,13.779300864496079,14.082873066151979,14.386445267807879,14.690017469463779,null,0.35267719979948492,0.39569328233666912,0.44024452694924521,0.48443826806481238,0.56337293724267612,0.70544903287759009,0.92916173354851894,1,1,null,0.92916173354851894,1,1]
["2013-04-27T11:00:00","2013-04-27T11:00:00",null,12.107044988724509,12.410617190380409,12.714189392036308,13.017761593692208,13.321333795348108,13.624905997004008,13.928478198659908,14.232050400315808,14.535622601971708,null,0.3841900815799642,0.43020288460678358,0.47761415719543254,0.5245312337735103,0.6060630607090578,0.75062065120556443,0.97670969865073032,1,1,null,0.97670969865073032,1,1]
["2013-04-27T12:00:00","2013-04-27T12:00:00",null,12.078601136044055,12.382173337699955,12.685745539355855,12.989317741011755,13.292889942667655,13.596462144323555,13.900034345979455,14.203606547635355,14.507178749291255,null,0.37350703590463319,0.42242192614246771,0.47259859342856947,0.52214437219053778,0.6061892384138845,0.75315472011083484,0.98153599586035323,1,1,null,0.98153599586035323,1,1]
["2013-04-27T13:00:00","2013-04-27T13:00:00",null,12.159432433537049,12.463004635192949,12.766576836848849,13.070149038504749,13.373721240160648,13.677293441816548,13.980865643472448,14.284437845128348,14.588010046784248,null,0.32875600992608134,0.3806360762273443,0.43363071225457672,0.48586828205284888,0.57247876160767275,0.72190470854874456,0.9526307866462933,0.9733449598553503,0.9755004956461405,null,0.9526307866462933,0.9733449598553503,0.9755004956461405]
["2013-04-27T14:00:00","2013-04-27T14:00:00",null,12.377733586164776,12.681305787820676,12.984877989476576,13.288450191132476,13.592022392788376,13.895594594444276,14.199166796100176,14.502738997756076,14.806311199411976,null,0.28130267810249004,0.33615843527591704,0.39199206966175121,0.44694246011379835,0.53613958261757044,0.68803650961149931,0.9211284196745495,0.94411379157048791,0.9484458927695395,null,0.9211284196745495,0.94411379157048791,0.9484458927695395]
["2013-04-27T15:00:00","2013-04-27T15:00:00",null,12.530532706640734,12.834104908296634,13.137677109952534,13.441249311608434,13.744821513264334,14.048393714920234,14.351965916576134,14.655538118232034,14.959110319887934,null,0.23089468502420582,0.2887681923047391,0.34747236947538174,0.40516712500741053,0.49698243488633759,0.65139240116806574,0.88689220243155964,0.91218031744058614,0.91872052847410568,null,0.88689220243155964,0.91218031744058614,0.91872052847410568]
["2013-04-27T16:00:00","2013-04-27T16:00:00",null,12.565055378727607,12.868627580383507,13.172199782039407,13.475771983695306,13.779344185351206,14.082916387007106,14.386488588663006,14.690060790318906,14.993632991974806,null,0.17613356112939893,0.23711945179565858,0.29878880502972971,0.35931204411162465,0.45382965983559115,0.61082626906626758,0.84880756519135403,0.87647202697461757,0.88529395150375412,null,0.84880756519135403,0.87647202697461757,0.88529395150375412]
["2013-04-27T17:00:00","2013-04-27T17:00:00",null,12.663391271159616,12.966963472815516,13.270535674471416,13.574107876127316,13.877680077783216,14.181252279439116,14.484824481095016,14.788396682750916,15.091968884406816,null,0.12057331177068933,0.18466107101393978,0.24928508550270384,0.31263680813446493,0.40986724451220646,0.56945049669183112,0.80990277286977463,0.83995409623601081,0.85105773426076425,null,0.80990277286977463,0.83995409623601081,0.85105773426076425]
["2013-04-27T18:00:00","2013-04-27T18:00:00",null,12.743255260934813,13.046827462590713,13.350399664246613,13.653971865902513,13.957544067558413,14.261116269214313,14.564688470870212,14.868260672526112,15.171832874182012,null,6.2068915966022382E-2,0.12931111782994142,0.19695288242581177,0.26317514784238127,0.36316046410884006,0.52537241847235527,0.76834824874683361,0.80081797812224909,0.8142559036862973,null,0.76834824874683361,0.80081797812224909,0.8142559036862973]
["2013-04-27T19:00:00","2013-04-27T19:00:00",null,12.606223776090772,12.909795977746672,13.213368179402572,13.516940381058472,13.820512582714372,14.124084784370272,14.427656986026172,14.731229187682072,15.034801389337972,null,2.8284835498660899E-3,7.3277702078131529E-2,0.14397927601605043,0.21311414345237062,0.31589639884248888,0.48077911462483686,0.72631004342205674,0.7612297232328582,0.77702296595367226,null,0.72631004342205674,0.7612297232328582,0.77702296595367226]
["2013-04-27T20:00:00","2013-04-27T20:00:00",null,12.383432356816845,12.687004558472745,12.990576760128645,13.294148961784545,13.597721163440445,13.901293365096345,14.204865566752245,14.508437768408145,14.812009970064045,null,0,2.2743531295020568E-2,9.643131091383908E-2,0.16840517670876101,0.27390025275265428,0.44138012629268608,0.68940306476023416,0.72670960615400815,0.74478456237043922,null,0.68940306476023416,0.72670960615400815,0.74478456237043922]
["2013-04-27T21:00:00","2013-04-27T21:00:00",null,12.110685287299161,12.414257488955061,12.71782969061096,13.02140189226686,13.32497409392276,13.62854629557866,13.93211849723456,14.23569069889046,14.53926290054636,null,0,0,5.6454008101232363E-2,0.13116172416740041,0.2392539579689775,0.40921532637060193,0.65961461161238699,0.69920286650177799,0.71945438812647033,null,0.65961461161238699,0.69920286650177799,0.71945438812647033]
["2013-04-27T22:00:00","2013-04-27T22:00:00",null,12.007152049722079,12.310724251377978,12.614296453033878,12.917868654689778,13.221440856345678,13.525013058001578,13.828585259657478,14.132157461313378,14.435729662969278,null,0,0,2.0472332608139208E-2,9.782978047566887E-2,0.20845608318251641,0.38083585759332012,0.63353788594819327,0.67534476548078781,0.69770976366132809,null,0.63353788594819327,0.67534476548078781,0.69770976366132809]
["2013-04-27T23:00:00","2013-04-27T23:00:00",null,11.885865664642257,12.189437866298157,12.493010067954057,12.796582269609956,13.100154471265856,13.403726672921756,13.707298874577656,14.010871076233556,14.314443277889456,null,0,0,0,6.6337928312660693E-2,0.17947727030730753,0.35425442110981936,0.60924867776904501,0.65324263751863654,0.67770008263755366,null,0.60924867776904501,0.65324263751863654,0.67770008263755366]
["2013-04-28","2013-04-28",null,11.699360407213284,12.002932608869184,12.306504810525084,12.610077012180984,12.913649213836884,13.217221415492784,13.520793617148684,13.824365818804583,14.127938020460483,null,0,0,0,3.9483106802035352E-2,0.15506188442333257,0.33216280795640363,0.58938620406756836,0.63550415518174341,0.66199095838662403,null,0.58938620406756836,0.63550415518174341,0.66199095838662403]
["2013-04-28T01:00:00","2013-04-28T01:00:00",null,11.532597660042974,11.836169861698874,12.139742063354774,12.443314265010674,12.746886466666574,13.050458668322474,13.354030869978374,13.657603071634274,13.961175273290173,null,0,0,0,1.642413124494789E-2,0.13437925564048211,0.31374086305169901,0.57313030976238954,0.62131967819747025,0.6497832654446366,null,0.57313030976238954,0.62131967819747025,0.6497832654446366]
["2013-04-28T02:00:00","2013-04-28T02:00:00",null,11.390059293490214,11.693631495146114,11.997203696802014,12.300775898457914,12.604348100113814,12.907920301769714,13.211492503425614,13.515064705081514,13.818636906737414,null,0,0,0,0,0.11654614002496896,0.29812637207938947,0.55963981015466346,0.60985853667570766,0.64026736353895297,null,0.55963981015466346,0.60985853667570766,0.64026736353895297]
["2013-04-28T03:00:00","2013-04-28T03:00:00",null,11.341604099936049,11.645176301591949,11.948748503247849,12.252320704903749,12.555892906559649,12.859465108215549,13.163037309871449,13.466609511527349,13.770181713183248,null,0,0,0,0,0.1006792936430059,0.28444660591442333,0.54804197611933858,0.600248001491404,0.63256000873578599,null,0.54804197611933858,0.600248001491404,0.63256000873578599]
["2013-04-28T04:00:00","2013-04-28T04:00:00",null,11.250777356309179,11.554349557965079,11.857921759620979,12.161493961276879,12.465066162932779,12.768638364588679,13.072210566244578,13.375782767900478,13.679354969556378,null,0,0,0,0,8.2720000322666007E-2,0.2687374816634937,0.53447787285046355,0.58873428592596366,0.62301256240389569,null,0.53447787285046355,0.58873428592596366,0.62301256240389569]
["2013-04-28T05:00:00","2013-04-28T05:00:00",null,11.27338180986877,11.57695401152467,11.88052621318057,12.18409841483647,12.48767061649237,12.79124281814827,13.09481501980417,13.398387221460069,13.701959423115969,null,0,0,0,0,6.3814374216125541E-2,0.25210305424383461,0.5200094960303302,0.57633732642673607,0.61259238694695373,null,0.5200094960303302,0.57633732642673607,0.61259238694695373]
["2013-04-28T06:00:00","2013-04-28T06:00:00",null,11.288197980245217,11.591770181901117,11.895342383557017,12.198914585212917,12.502486786868817,12.806058988524716,13.109631190180616,13.413203391836516,13.716775593492416,null,0,0,0,0,4.42358003505091E-2,0.23481670868257068,0.50489971587732763,0.56330947840337475,0.60155183777461363,null,0.50489971587732763,0.56330947840337475,0.60155183777461363]
["2013-04-28T07:00:00","2013-04-28T07:00:00",null,11.556087261239981,11.85965946289588,12.16323166455178,12.46680386620768,12.77037606786358,13.07394826951948,13.37752047117538,13.68109267283128,13.98466487448718,null,0,0,0,0,2.544583714005981E-2,0.21824537011532497,0.49044185386592987,0.55088097447794049,0.59105805865652272,null,0.49044185386592987,0.55088097447794049,0.59105805865652272]
["2013-04-28T08:00:00","2013-04-28T08:00:00",null,11.731934293116986,12.035506494772886,12.339078696428786,12.642650898084685,12.946223099740585,13.249795301396485,13.553367503052385,13.856939704708285,14.160511906364185,null,0,0,0,0,2.4499504353857199E-3,0.1975417117150034,0.47191476087386963,0.5344358136155215,0.57661071145386056,null,0.47191476087386963,0.5344358136155215,0.57661071145386056]
["2013-04-28T09:00:00","2013-04-28T09:00:00",null,11.890022485109293,12.193594686765193,12.497166888421093,12.800739090076993,13.104311291732893,13.407883493388793,13.711455695044693,14.015027896700593,14.318600098356493,null,0,0,0,0,0,0.17355743298918647,0.45015962159999184,0.51481518051496278,0.55904046605673641,null,0.45015962159999184,0.51481518051496278,0.55904046605673641]
["2013-04-28T10:00:00","2013-04-28T10:00:00",null,12.179999255982024,12.483571457637924,12.787143659293823,13.090715860949723,13.394288062605623,13.697860264261523,14.001432465917423,14.305004667573323,14.608576869229223,null,0,0,0,0,0,0.1442736906606463,0.42317862238453974,0.49004229113397874,0.53638105323160035,null,0.42317862238453974,0.49004229113397874,0.53638105323160035]
["2013-04-28T11:00:00","2013-04-28T11:00:00",null,12.419168642999628,12.722740844655528,13.026313046311428,13.329885247967328,13.633457449623227,13.937029651279127,14.240601852935027,14.544174054590927,14.847746256246827,null,0,0,0,0,0,0.11168829838913967,0.39292751765232786,0.4620308406624416,0.51051462374211787,null,0.39292751765232786,0.4620308406624416,0.51051462374211787]
["2013-04-28T12:00:00","2013-04-28T12:00:00",null,12.694912927001436,12.998485128657336,13.302057330313236,13.605629531969136,13.909201733625036,14.212773935280936,14.516346136936836,14.819918338592736,15.123490540248635,null,0,0,0,0,0,7.7105092457876251E-2,0.36067859926035922,0.43202157653114764,0.48265038059287857,null,0.36067859926035922,0.43202157653114764,0.48265038059287857]
["2013-04-28T13:00:00","2013-04-28T13:00:00",null,13.08206792316598,13.385640124821879,13.689212326477779,13.992784528133679,14.296356729789579,14.599928931445479,14.903501133101379,15.207073334757279,15.510645536413179,null,0,0,0,0,0,3.3079588282078166E-2,0.31909253071121152,0.39278031033003025,0.44565928346117145,null,0.31909253071121152,0.39278031033003025,0.44565928346117145]
["2013-04-28T14:00:00","2013-04-28T14:00:00",null,13.250977471735833,13.554549673391733,13.858121875047633,14.161694076703533,14.465266278359433,14.768838480015333,15.072410681671233,15.375982883327133,15.679555084983033,null,0,0,0,0,0,0,0.27439407877633748,0.35045820516939319,0.40562940660488694,null,0.27439407877633748,0.35045820516939319,0.40562940660488694]
["2013-04-28T15:00:00","2013-04-28T15:00:00",null,13.384305587762739,13.687877789418639,13.991449991074539,14.295022192730439,14.598594394386339,14.902166596042239,15.205738797698139,15.509310999354039,15.812883201009939,null,0,0,0,0,0,0,0.2242279262989712,0.3027314883186773,0.3602580069109369,null,0.2242279262989712,0.3027314883186773,0.3602580069109369]
["2013-04-28T16:00:00","2013-04-28T16:00:00",null,13.537338469294319,13.840910670950219,14.144482872606119,14.448055074262019,14.751627275917919,15.055199477573819,15.358771679229719,15.662343880885619,15.965916082541519,null,0,0,0,0,0,0,0.16812090688601239,0.24913750819351779,0.30908243279495667,null,0.16812090688601239,0.24913750819351779,0.30908243279495667]
["2013-04-28T17:00:00","2013-04-28T17:00:00",null,13.633999414048859,13.937571615704758,14.241143817360658,14.544716019016558,14.848288220672458,15.151860422328358,15.455432623984258,15.759004825640158,16.062577027296058,null,0,0,0,0,0,0,0.10899613736594728,0.19256783719619425,0.25497322704175462,null,0.10899613736594728,0.19256783719619425,0.25497322704175462]
["2013-04-28T18:00:00","2013-04-28T18:00:00",null,13.691038762270832,13.994610963926732,14.298183165582632,14.601755367238532,14.905327568894432,15.208899770550332,15.512471972206232,15.816044173862132,16.119616375518032,null,0,0,0,0,0,0,4.8125909595778872E-2,0.13427373756623853,0.19917113708212711,null,4.8125909595778872E-2,0.13427373756623853,0.19917113708212711]
["2013-04-28T19:00:00","2013-04-28T19:00:00",null,13.65391092612029,13.957483127776189,14.261055329432089,14.564627531087989,14.868199732743889,15.171771934399789,15.475344136055689,15.778916337711589,16.082488539367489,null,0,0,0,0,0,0,0,7.2667473184580791E-2,0.14007791198826869,null,-1.6088027352298244E-2,7.2667473184580791E-2,0.14007791198826869]
["2013-04-28T20:00:00","2013-04-28T20:00:00",null,13.490087007124007,13.793659208779907,14.097231410435807,14.400803612091707,14.704375813747607,15.007948015403507,15.311520217059407,15.615092418715307,15.918664620371207,null,0,0,0,0,0,0,0,1.3668881369342425E-2,8.3571329843358522E-2,null,-6.1585234764186619E-2,1.3668881369342425E-2,8.3571329843358522E-2]
["2013-04-28T21:00:00","2013-04-28T21:00:00",null,13.316263681064648,13.619835882720547,13.923408084376447,14.226980286032347,14.530552487688247,14.834124689344147,15.137696891000047,15.441269092655947,15.744841294311847,null,0,0,0,2.2606838781458294E-3,5.0996822367475689E-3,7.8230176992581269E-3,1.0430690265677502E-2,2.6602096114083682E-2,9.8912435788543474E-2,null,1.0430690265677502E-2,2.6602096114083682E-2,9.8912435788543474E-2]
["2013-04-28T22:00:00","2013-04-28T22:00:00",null,13.065918597720238,13.369490799376138,13.673063001032038,13.976635202687937,14.280207404343837,14.583779605999737,14.887351807655637,15.190924009311537,15.494496210967437,null,1.3679766164966158E-2,1.6823693976899198E-2,1.984144408400549E-2,2.4983185555695307E-2,3.0577063803014289E-2,3.5950131066886472E-2,4.1091872538576289E-2,5.9692199204897295E-2,0.1343473412273874,null,4.1091872538576289E-2,5.9692199204897295E-2,0.1343473412273874]
["2013-04-28T23:00:00","2013-04-28T23:00:00",null,12.823330677183574,13.126902878839473,13.430475080495373,13.734047282151273,14.037619483807173,14.341191685463073,14.644763887118973,14.948336088774873,15.251908290430773,null,3.6149912432862148E-2,4.2364164395579287E-2,4.8305031331171817E-2,5.6254226735256686E-2,6.4518866401408415E-2,7.245754699675773E-2,8.0059753712569043E-2,0.10102591234439151,0.17794173824502743,null,8.0059753712569043E-2,0.10102591234439151,0.17794173824502743]
["2013-04-29","2013-04-29",null,12.728650540981956,13.032222742637856,13.335794944293756,13.639367145949656,13.942939347605556,14.246511549261456,14.550083750917356,14.853655952573256,15.157228154229156,null,6.2142519627171405E-2,7.1364006888259279E-2,8.0175416608660233E-2,9.0868977092726788E-2,0.10175180413403345,0.11220352401718209,0.1222136219334371,0.14548252367834763,0.22461697422218713,null,0.1222136219334371,0.14548252367834763,0.22461697422218713]
["2013-04-29T01:00:00","2013-04-29T01:00:00",null,12.564300466322294,12.867872667978194,13.171444869634094,13.475017071289994,13.778589272945894,14.082161474601794,14.385733676257694,14.689305877913593,14.992878079569493,null,9.1552439660538318E-2,0.10373910298505468,0.1153789962553218,0.12877486258442777,0.14223381776594715,0.15515651770195285,0.1675324475837093,0.19307254801550122,0.27438356396760205,null,0.1675324475837093,0.19307254801550122,0.27438356396760205]
["2013-04-29T02:00:00","2013-04-29T02:00:00",null,12.429486753905328,12.733058955561228,13.036631157217128,13.340203358873028,13.643775560528928,13.947347762184828,14.250919963840728,14.554492165496628,14.858064367152528,null,0.12318098433710881,0.13830127929884695,0.15274862650150914,0.16882576905818342,0.18483982276244437,0.200212473133836,0.21492269055488722,0.24271296005608942,0.32616899699024487,null,0.21492269055488722,0.24271296005608942,0.32616899699024487]
["2013-04-29T03:00:00","2013-04-29T03:00:00",null,12.209237875222376,12.512810076878276,12.816382278534176,13.119954480190076,13.423526681845976,13.727098883501876,14.030671085157776,14.334243286813676,14.637815488469576,null,0.1575749237111321,0.17561833550135647,0.19285210701894259,0.21158949618571407,0.23013761879524547,0.24793918998455192,0.26497318013616233,0.29498207428056811,0.38057261738804266,null,0.26497318013616233,0.29498207428056811,0.38057261738804266]
["2013-04-29T04:00:00","2013-04-29T04:00:00",null,12.19278230200919,12.49635450366509,12.79992670532099,13.10349890697689,13.40707110863279,13.71064331028869,14.01421551194459,14.31778771360049,14.62135991525639,null,0.19266284046170248,0.21361885427167754,0.23362853529545202,0.25501565626358513,0.27609784777838697,0.29630731016813711,0.31565455824157118,0.34787156222044496,0.43558609669250303,null,0.31565455824157118,0.34787156222044496,0.43558609669250303]
["2013-04-29T05:00:00","2013-04-29T05:00:00",null,12.262464556807831,12.566036758463731,12.869608960119631,13.173181161775531,13.476753363431431,13.780325565087331,14.083897766743231,14.387469968399131,14.691042170055031,null,0.22486969961872888,0.24880140430086797,0.27162905406577309,0.29571848087894564,0.31937680053396017,0.34204672816783177,0.36374929339803175,0.39821646644631581,0.48809705151789967,null,0.36374929339803175,0.39821646644631581,0.48809705151789967]
["2013-04-29T06:00:00","2013-04-29T06:00:00",null,12.231987315171722,12.535559516827622,12.839131718483522,13.142703920139422,13.446276121795322,13.749848323451221,14.053420525107121,14.356992726763021,14.660564928418921,null,0.25518389320335411,0.28213334799259948,0.30784205535104858,0.33467584724420285,0.36095235427437233,0.38612480638730767,0.41021423320048023,0.44697363455311678,0.53906232945916865,null,0.41021423320048023,0.44697363455311678,0.53906232945916865]
["2013-04-29T07:00:00","2013-04-29T07:00:00",null,12.535196272888685,12.838768474544585,13.142340676200485,13.445912877856385,13.749485079512285,14.053057281168185,14.356629482824085,14.660201684479985,14.963773886135884,null,0.28551911640545047,0.31541271764065321,0.34392887893149737,0.37345446186095549,0.40228606741386652,0.42991898477092338,0.45635321393212624,0.49536278435417308,0.58961752985975069,null,0.45635321393212624,0.49536278435417308,0.58961752985975069]
["2013-04-29T08:00:00","2013-04-29T08:00:00",null,12.802721393823761,13.106293595479661,13.409865797135561,13.713437998791461,14.017010200447361,14.320582402103261,14.624154603759161,14.927726805415061,15.231299007070961,null,0.31163790130458646,0.34451770822068883,0.37588338267887028,0.40813230107083898,0.43957157919016937,0.46970702102628997,0.49852811177046541,0.53984042530560028,0.63629276583691041,null,0.49852811177046541,0.53984042530560028,0.63629276583691041]
["2013-04-29T09:00:00","2013-04-29T09:00:00",null,13.227982506096385,13.531554707752285,13.835126909408185,14.138699111064085,14.442271312719985,14.745843514375885,15.049415716031785,15.352987917687685,15.656560119343585,null,0.33068021992468921,0.36661983618284016,0.4008981126607723,0.43594397017640046,0.47006452452329917,0.50276557969089686,0.53404713567919382,0.57772528117983013,0.67644882039802168,null,0.53404713567919382,0.57772528117983013,0.67644882039802168]
["2013-04-29T10:00:00","2013-04-29T10:00:00",null,13.118339422485416,13.421911624141316,13.725483825797216,14.029056027453116,14.332628229109016,14.636200430764916,14.939772632420816,15.243344834076716,15.546917035732616,null,0.33954420368876798,0.37840693677540516,0.41548215237699682,0.45319877131145769,0.48987442418109794,0.52503594459281722,0.55867281773788002,0.60461164711666215,0.70550123693437949,null,0.55867281773788002,0.60461164711666215,0.70550123693437949]
["2013-04-29T11:00:00","2013-04-29T11:00:00",null,13.73452904869346,14.03810125034936,14.34167345200526,14.64524565366116,14.94881785531706,15.25239005697296,15.55596225862886,15.85953446028476,16.16310666194066,null,0.34131069155634242,0.38350661901215272,0.42376782166061966,0.46453373512839352,0.50414301963525554,0.54212250878810542,0.57846168777820772,0.62699767491467362,0.7303897892114547,null,0.57846168777820772,0.62699767491467362,0.7303897892114547]
["2013-04-29T12:00:00","2013-04-29T12:00:00",null,13.72440253595795,14.027974737613849,14.331546939269749,14.635119140925649,14.938691342581549,15.242263544237449,15.545835745893349,15.849407947549249,16.152980149205149,null,0.34608441472228757,0.3915399328861221,0.43493454853778651,0.47869718249519555,0.52117700978686599,0.56191137882843312,0.60090028961989705,0.65199137527910445,0.75783344001127151,null,0.60090028961989705,0.65199137527910445,0.75783344001127151]
["2013-04-29T13:00:00","2013-04-29T13:00:00",null,13.642096278997553,13.945668480653453,14.249240682309352,14.552812883965252,14.856385085621152,15.159957287277052,15.463529488932952,15.767101690588852,16.070673892244752,null,0.34809274319077993,0.39688145572378758,0.44348308803979841,0.49030553133925597,0.53572950507688377,0.57928184285958151,0.62098357430482043,0.67468233253044718,0.78303743655041358,null,0.62098357430482043,0.67468233253044718,0.78303743655041358]
["2013-04-29T14:00:00","2013-04-29T14:00:00",null,13.723826443858911,14.027398645514811,14.330970847170711,14.634543048826611,14.938115250482511,15.241687452138411,15.545259653794311,15.848831855450211,16.152404057106111,null,0.35022724936409899,0.40233864145754428,0.45212626082043039,0.50199799865320094,0.55034508921931491,0.59670488093440777,0.64110891822468608,0.6974048342079967,0.80825194789829125,null,0.64110891822468608,0.6974048342079967,0.80825194789829125]
["2013-04-29T15:00:00","2013-04-29T15:00:00",null,13.679682484916526,13.983254686572426,14.286826888228326,14.590399089884226,14.893971291540126,15.197543493196026,15.501115694851926,15.804687896507826,16.108260098163726,null,0.35107894887167951,0.40655507976050465,0.45956023059647272,0.51251280738876293,0.5638145592095698,0.61301334928326445,0.66015123684478882,0.71906534020325441,0.83243600799008388,null,0.66015123684478882,0.71906534020325441,0.83243600799008388]
["2013-04-29T16:00:00","2013-04-29T16:00:00",null,13.525124227289723,13.828696428945623,14.132268630601523,14.435840832257423,14.739413033913323,15.042985235569223,15.346557437225123,15.650129638881022,15.953701840536922,null,0.34256195379587429,0.40138179386260814,0.45758344655418709,0.51359583268852582,0.56784173095529,0.61985848977011526,0.66969868317667913,0.73122045910156408,0.84709365136745729,null,0.66969868317667913,0.73122045910156408,0.84709365136745729]
["2013-04-29T17:00:00","2013-04-29T17:00:00",null,13.902699868798813,14.206272070454713,14.509844272110612,14.813416473766512,15.116988675422412,15.420560877078312,15.724133078734212,16.027705280390112,16.331277482046012,null,0.31618029867834924,0.37847002562781856,0.4379838430710995,0.49718221625231357,0.55448792386112622,0.6094383143131733,0.66210699126960337,0.7263415878482633,0.84483296748931147,null,0.66210699126960337,0.7263415878482633,0.84483296748931147]
["2013-04-29T18:00:00","2013-04-29T18:00:00",null,13.633533212459593,13.937105414115493,14.240677615771393,14.544249817427293,14.847822019083193,15.151394220739093,15.454966422394993,15.758538624050892,16.062110825706792,null,0.2548474193238161,0.32053342949487196,0.38329632283744153,0.44560707940438199,0.50590950750282981,0.56373044073968526,0.61915399758483258,0.68603832596485415,0.80707428931990832,null,0.61915399758483258,0.68603832596485415,0.80707428931990832]
["2013-04-29T19:00:00","2013-04-29T19:00:00",null,13.560225210965591,13.863797412621491,14.167369614277391,14.470941815933291,14.77451401758919,15.07808621924509,15.38165842090099,15.68523062255689,15.98880282421279,null,0.17632282768663909,0.24542615069675261,0.31145914955608195,0.37691383393495548,0.44022349733177402,0.50092548816217342,0.55912495451350919,0.62868004431236346,0.75228162099889473,null,0.55912495451350919,0.62868004431236346,0.75228162099889473]
["2013-04-29T20:00:00","2013-04-29T20:00:00",null,13.263455437781085,13.567027639436985,13.870599841092885,14.174172042748785,14.477744244404684,14.781316446060584,15.084888647716484,15.388460849372384,15.692033051028284,null,0.10234063342322487,0.1748402396549249,0.24411179960480733,0.31267886736940725,0.37896422163838983,0.44251572563612651,0.50344904225870846,0.57563283424145317,0.70175796502451937,null,0.50344904225870846,0.57563283424145317,0.70175796502451937]
["2013-04-29T21:00:00","2013-04-29T21:00:00",null,13.108889771331235,13.412461972987135,13.716034174643035,14.019606376298935,14.323178577954835,14.626750779610735,14.930322981266634,15.233895182922534,15.537467384578434,null,3.3742021232418401E-2,0.10955379221582046,0.1819797947863715,0.25357512746681327,0.32275205413807539,0.38907946764200041,0.45267303087467958,0.52741192138016579,0.65599751740735357,null,0.45267303087467958,0.52741192138016579,0.65599751740735357]
["2013-04-29T22:00:00","2013-04-29T22:00:00",null,12.833541017440689,13.137113219096589,13.440685420752489,13.744257622408389,14.047829824064289,14.351402025720189,14.654974227376089,14.958546429031989,15.262118630687889,null,0,5.1375355481955924E-2,0.12687168220329106,0.20139013171221906,0.27337451231587628,0.34238320204736961,0.40855289342026146,0.48576276397860474,0.61671419197129396,null,0.40855289342026146,0.48576276397860474,0.61671419197129396]
["2013-04-29T23:00:00","2013-04-29T23:00:00",null,12.652060703636105,12.955632905292005,13.259205106947904,13.562777308603804,13.866349510259704,14.169921711915604,14.473493913571504,14.777066115227404,15.080638316883304,null,0,0,7.811451409649009E-2,0.15545093234654869,0.23012710398650979,0.30172243666695137,0.37036310809270029,0.44994932542528054,0.58317195210485118,null,0.37036310809270029,0.44994932542528054,0.58317195210485118]
["2013-04-30","2013-04-30",null,12.466275718131559,12.769847919787459,13.073420121443359,13.376992323099259,13.680564524755159,13.984136726411059,14.287708928066959,14.591281129722859,14.894853331378759,null,0,0,2.868439823061314E-2,0.10872312232571117,0.18597542210588497,0.26004173483918358,0.331048238230434,0.41289513944116008,0.54829433152899199,null,0.331048238230434,0.41289513944116008,0.54829433152899199]
["2013-04-30T01:00:00","2013-04-30T01:00:00",null,12.213395091012439,12.516967292668339,12.820539494324239,13.124111695980138,13.427683897636038,13.731256099291938,14.034828300947838,14.338400502603738,14.641972704259638,null,0,0,0,7.3109465138362695E-2,0.15283274497139354,0.22926488967019362,0.30254259174832543,0.38655554355857724,0.5240366677760504,null,0.30254259174832543,0.38655554355857724,0.5240366677760504]
["2013-04-30T02:00:00","2013-04-30T02:00:00",null,12.326388974853135,12.629961176509035,12.933533378164935,13.237105579820835,13.540677781476735,13.844249983132634,14.147822184788534,14.451394386444434,14.754966588100334,null,0,0,0,3.356326948391402E-2,0.11584164783968642,0.19471322816513689,0.27032521778256347,0.35657782385348996,0.49620396905301778,null,0.27032521778256347,0.35657782385348996,0.49620396905301778]
["2013-04-30T03:00:00","2013-04-30T03:00:00",null,12.165355762233409,12.468927963889309,12.772500165545209,13.076072367201109,13.379644568857008,13.683216770512908,13.986788972168808,14.290361173824708,14.593933375480608,null,0,0,0,0,8.2089111798532413E-2,0.16335806851569101,0.24126228643747011,0.32971248753412907,0.47144159448076928,null,0.24126228643747011,0.32971248753412907,0.47144159448076928]
["2013-04-30T04:00:00","2013-04-30T04:00:00",null,12.065008746509434,12.368580948165334,12.672153149821234,12.975725351477134,13.279297553133034,13.582869754788934,13.886441956444834,14.190014158100734,14.493586359756634,null,0,0,0,0,4.6496484228655051E-2,0.13022590618993515,0.21047492645974458,0.30117529662581383,0.44504942455450869,null,0.21047492645974458,0.30117529662581383,0.44504942455450869]
["2013-04-30T05:00:00","2013-04-30T05:00:00",null,12.113361276413496,12.416933478069396,12.720505679725296,13.024077881381196,13.327650083037096,13.631222284692996,13.934794486348896,14.238366688004795,14.541938889660695,null,0,0,0,0,9.0847947475254653E-3,9.5295711570398206E-2,0.17793159342318021,0.27090316227613082,0.41696437042182261,null,0.17793159342318021,0.27090316227613082,0.41696437042182261]
["2013-04-30T06:00:00","2013-04-30T06:00:00",null,12.138775587134699,12.442347788790599,12.745919990446499,13.049492192102399,13.353064393758299,13.656636595414199,13.960208797070099,14.263780998725998,14.567353200381898,null,0,0,0,0,0,5.9440213782131796E-2,0.14447347202662192,0.23973726918392504,0.38799607235534928,null,0.14447347202662192,0.23973726918392504,0.38799607235534928]
["2013-04-30T07:00:00","2013-04-30T07:00:00",null,12.458491371771528,12.762063573427428,13.065635775083328,13.369207976739228,13.672780178395127,13.976352380051027,14.279924581706927,14.583496783362827,14.887068985018727,null,0,0,0,0,0,2.2796105338698233E-2,0.11019519554868981,0.20771967658413876,0.35814453035508875,null,0.11019519554868981,0.20771967658413876,0.35814453035508875]
["2013-04-30T08:00:00","2013-04-30T08:00:00",null,12.771102512927504,13.074674714583404,13.378246916239304,13.681819117895204,13.985391319551104,14.288963521207004,14.592535722862904,14.896107924518804,15.199680126174703,null,0,0,0,0,0,0,7.0270466779760898E-2,0.17012923535450461,0.32279374338612932,null,7.0270466779760898E-2,0.17012923535450461,0.32279374338612932]
["2013-04-30T09:00:00","2013-04-30T09:00:00",null,12.980050097094724,13.283622298750624,13.587194500406524,13.890766702062423,14.194338903718323,14.497911105374223,14.801483307030123,15.105055508686023,15.408627710341923,null,0,0,0,0,0,0,2.3206182879385397E-2,0.12550438708077949,0.28051369746043453,null,2.3206182879385397E-2,0.12550438708077949,0.28051369746043453]
["2013-04-30T10:00:00","2013-04-30T10:00:00",null,13.116097637674946,13.419669839330846,13.723242040986745,14.026814242642645,14.330386444298545,14.633958645954445,14.937530847610345,15.241103049266245,15.544675250922145,null,0,0,0,0,0,0,0,7.8986873234653213E-2,0.23636201557980971,null,-2.577179621086239E-2,7.8986873234653213E-2,0.23636201557980971]
["2013-04-30T11:00:00","2013-04-30T11:00:00",null,13.247243007357255,13.550815209013155,13.854387410669055,14.157959612324955,14.461531813980855,14.765104015636755,15.068676217292655,15.372248418948555,15.675820620604455,null,0,0,0,0,0,0,0,3.0808019608308139E-2,0.19055950872770164,null,-5.0660348487937705E-2,3.0808019608308139E-2,0.19055950872770164]
["2013-04-30T12:00:00","2013-04-30T12:00:00",null,13.460586789868881,13.764158991524781,14.067731193180681,14.37130339483658,14.67487559649248,14.97844779814838,15.28201999980428,15.58559220146018,15.88916440311608,null,0,0,0,0,0,0,0,0,0.14047747472021985,null,-5.5034508921931499E-2,-2.1702935217088479E-2,0.14047747472021985]
["2013-04-30T13:00:00","2013-04-30T13:00:00",null,13.305764308360146,13.609336510016046,13.912908711671946,14.216480913327846,14.520053114983746,14.823625316639646,15.127197518295546,15.430769719951446,15.734341921607346,null,0,0,0,0,0,0,0,1.8295767199877876E-3,0.14466236859697351,null,-6.2037371539815783E-4,1.8295767199877876E-3,0.14466236859697351]
["2013-04-30T14:00:00","2013-04-30T14:00:00",null,13.814339246153466,14.117911447809366,14.421483649465266,14.725055851121166,15.028628052777066,15.332200254432966,15.635772456088866,15.939344657744765,16.242916859400665,null,0,0,2.7969391236594915E-3,5.888292891914719E-3,8.8534689553432019E-3,1.1702982122680504E-2,1.4436832393926622E-2,1.8905626106540473E-2,0.16427248688879664,null,1.4436832393926622E-2,1.8905626106540473E-2,0.16427248688879664]
["2013-04-30T15:00:00","2013-04-30T15:00:00",null,13.784010532096026,14.087582733751926,14.391154935407826,14.694727137063726,14.998299338719626,15.301871540375526,15.605443742031426,15.909015943687326,16.212588145343226,null,0,5.1522562804253791E-4,6.5191814160484385E-3,1.2691374143823332E-2,1.8611211461944735E-2,2.4299722987883778E-2,2.9756908721640454E-2,3.6843889809409239E-2,0.18473430468820029,null,2.9756908721640454E-2,3.6843889809409239E-2,0.18473430468820029]
["2013-04-30T16:00:00","2013-04-30T16:00:00",null,13.83389750076017,14.13746970241607,14.44104190407197,14.744614105727869,15.048186307383769,15.351758509039669,15.655330710695569,15.958902912351469,16.262475114007369,null,0,0,8.6221431631608378E-3,1.7885689659190959E-2,2.6781217849476409E-2,3.5329757351488314E-2,4.353130816522667E-2,5.326802105435708E-2,0.20370301964715415,null,4.353130816522667E-2,5.326802105435708E-2,0.20370301964715415]
["2013-04-30T17:00:00","2013-04-30T17:00:00",null,13.881639437515911,14.185211639171811,14.488783840827711,14.792356042483611,15.095928244139511,15.399500445795411,15.703072647451311,16.006644849107211,16.310217050763111,null,0,0,9.2320020698234331E-3,2.1618446760315466E-2,3.3510695440236091E-2,4.4929777727056419E-2,5.5907238046983138E-2,6.830419754621074E-2,0.22130480947048492,null,5.5907238046983138E-2,6.830419754621074E-2,0.22130480947048492]
["2013-04-30T18:00:00","2013-04-30T18:00:00",null,13.819635240713854,14.123207442369754,14.426779644025654,14.730351845681554,15.033924047337454,15.337496248993354,15.641068450649254,15.944640652305154,16.248212853961054,null,0,0,9.3581797746501768E-3,2.489906708581081E-2,3.980906587283773E-2,5.4130235370673165E-2,6.789412000552382E-2,8.297235573231973E-2,0.23854909579680661,null,6.789412000552382E-2,8.297235573231973E-2,0.23854909579680661]
["2013-04-30T19:00:00","2013-04-30T19:00:00",null,13.684487634913957,13.988059836569857,14.291632038225757,14.595204239881657,14.898776441537557,15.202348643193456,15.505920844849356,15.809493046505256,16.113065248161156,null,0,5.7831448045590989E-4,1.3206599771865868E-2,3.1891414894959537E-2,4.9808648980357188E-2,6.7021390880472181E-2,8.357169983024676E-2,0.10132069697587542,0.25946305037183942,null,8.357169983024676E-2,0.10132069697587542,0.25946305037183942]
["2013-04-30T20:00:00","2013-04-30T20:00:00",null,13.48078494291132,13.78435714456722,14.08792934622312,14.39150154787902,14.69507374953492,14.99864595119082,15.30221815284672,15.60579035450262,15.90936255615852,null,1.3038362832096877E-3,5.2679191765165612E-3,2.1134765558479613E-2,4.2910934449828513E-2,6.3803859407390209E-2,8.3866114474842504E-2,0.1031502736958632,0.12352797302538236,0.28420439532661679,null,0.1031502736958632,0.12352797302538236,0.28420439532661679]
["2013-04-30T21:00:00","2013-04-30T21:00:00",null,13.419802571435536,13.723374773091436,14.026946974747336,14.330519176403236,14.634091378059136,14.937663579715036,15.241235781370936,15.544807983026836,15.848380184682735,null,7.2341884100666541E-3,1.4478891628868871E-2,3.3500180631500523E-2,5.8283584821220154E-2,8.2068082181061403E-2,0.10489573194596649,0.12684013777708439,0.1497729356293451,0.31290982317470106,null,0.12684013777708439,0.1497729356293451,0.31290982317470106]
["2013-04-30T22:00:00","2013-04-30T22:00:00",null,13.330010416271442,13.633582617927342,13.937154819583242,14.240727021239142,14.544299222895042,14.847871424550942,15.151443626206841,15.455015827862741,15.758588029518641,null,1.5456768841276135E-2,2.5940033150631446E-2,4.805267592151833E-2,7.5801256174666445E-2,0.102435266701845,0.12798625192926064,0.15254884513553346,0.17799468227559351,0.34353946102139316,null,0.15254884513553346,0.17799468227559351,0.34353946102139316]
["2013-04-30T23:00:00","2013-04-30T23:00:00",null,13.055715985534043,13.359288187189943,13.662860388845843,13.966432590501743,14.270004792157643,14.573576993813543,14.877149195469443,15.180721397125343,15.484293598781242,null,3.0524489759336478E-2,4.4162196689360389E-2,6.9271559949882433E-2,9.990119779657454E-2,0.12929008821247034,0.15746977562377648,0.18456643773531975,0.21244119569329462,0.38032026197838903,null,0.18456643773531975,0.21244119569329462,0.38032026197838903]
["2013-05-01T01:00:00","2013-05-01T01:00:00",null,12.774344330399833,13.077916532055733,13.381488733711633,13.685060935367533,13.988633137023433,14.292205338679333,14.595777540335233,14.899349741991132,15.202921943647032,null,5.3015665644703586E-2,6.9692152299304921E-2,9.7693087962106517E-2,0.131098635314987,0.16313725753224442,0.193851013848821,0.22337659677827909,0.25358564227554869,0.42370436282131785,null,0.22337659677827909,0.25358564227554869,0.42370436282131785]
["2013-05-01T02:00:00","2013-05-01T02:00:00",null,12.606077537324364,12.909649738980264,13.213221940636164,13.516794142292063,13.820366343947963,14.123938545603863,14.427510747259763,14.731082948915663,15.034655150571563,null,7.9050332073955093E-2,9.8723539218191603E-2,0.12957398804833048,0.16571338567245708,0.20035968045613389,0.23356544644303867,0.2654884057642049,0.297989679565827,0.47030599513732863,null,0.2654884057642049,0.297989679565827,0.47030599513732863]
["2013-05-01T03:00:00","2013-05-01T03:00:00",null,12.577659353506856,12.881231555162756,13.184803756818656,13.488375958474556,13.791948160130456,14.095520361786356,14.399092563442256,14.702664765098156,15.006236966754056,null,0.10909114063145572,0.13167694979544289,0.16529279332303459,0.20408192274852283,0.24125177162873451,0.27687594362481854,0.31112267567654395,0.34584257412136965,0.52029339586619039,null,0.31112267567654395,0.34584257412136965,0.52029339586619039]
["2013-05-01T04:00:00","2013-05-01T04:00:00",null,12.525717197092963,12.829289398748863,13.132861600404762,13.436433802060662,13.740006003716562,14.043578205372462,14.347150407028362,14.650722608684262,14.954294810340162,null,0.13821716082896246,0.16373660163017142,0.20015989909015819,0.24161978993447916,0.28134473733743243,0.31941885976890239,0.3560103941686581,0.39298046168289408,0.56958681921850507,null,0.3560103941686581,0.39298046168289408,0.56958681921850507]
["2013-05-01T05:00:00","2013-05-01T05:00:00",null,12.764038910775264,13.067611112431164,13.371183314087064,13.674755515742964,13.978327717398864,14.281899919054764,14.585472120710664,14.889044322366564,15.192616524022464,null,0.16104481059386755,0.18959251631091839,0.22890738617318468,0.27313267171495847,0.3154968361105378,0.35610502744727818,0.39512548266494874,0.43441932290974389,0.61325481989729402,null,0.39512548266494874,0.43441932290974389,0.61325481989729402]
["2013-05-01T06:00:00","2013-05-01T06:00:00",null,12.936743272705318,13.240315474361218,13.543887676017118,13.847459877673018,14.151032079328917,14.454604280984817,14.758176482640717,15.061748684296617,15.365320885952517,null,0.18043411790224387,0.21206266257881437,0.25431116407830245,0.30134390355247131,0.34638934417561895,0.38957366365257201,0.43106509892309963,0.47272477113339623,0.65383146680782778,null,0.43106509892309963,0.47272477113339623,0.65383146680782778]
["2013-05-01T07:00:00","2013-05-01T07:00:00",null,13.011175012105138,13.314747213761038,13.618319415416938,13.921891617072838,14.225463818728738,14.529036020384638,14.832608222040538,15.136180423696437,15.439752625352337,null,0.19706854532190296,0.2318094733841998,0.27704418056458752,0.32692643320609366,0.37469520929175187,0.42049771614385983,0.46449167589345119,0.50855923930419156,0.69197919290044674,null,0.46449167589345119,0.50855923930419156,0.69197919290044674]
["2013-05-01T08:00:00","2013-05-01T08:00:00",null,13.102304321426324,13.405876523082224,13.709448724738124,14.013020926394024,14.316593128049924,14.620165329705824,14.923737531361724,15.227309733017623,15.530881934673523,null,0.21025411547629771,0.24817051577673427,0.29643348787296386,0.3492178277254851,0.3997625133173317,0.44823578158827238,0.49478483986060529,0.54130235370673163,0.72707762445975266,null,0.49478483986060529,0.54130235370673163,0.72707762445975266]
["2013-05-01T09:00:00","2013-05-01T09:00:00",null,13.210400574726794,13.513972776382694,13.817544978038594,14.121117179694494,14.424689381350394,14.728261583006294,15.031833784662194,15.335405986318094,15.638978187973994,null,0.22256695650564082,0.26365882904421711,0.31495006605628856,0.37063649311982488,0.42396760302659542,0.47510111790763326,0.52420527470270772,0.57318325379295565,0.76131384170274252,null,0.52420527470270772,0.57318325379295565,0.76131384170274252]
["2013-05-01T10:00:00","2013-05-01T10:00:00",null,13.285296081850944,13.588868283506844,13.892440485162744,14.196012686818644,14.499584888474544,14.803157090130444,15.106729291786344,15.410301493442244,15.713873695098144,null,0.23220903611615118,0.27651844012780946,0.33088000129066497,0.38951057480015866,0.4456596534480598,0.49949547417413709,0.55119678872689537,0.60266677748747144,0.79319474178896654,null,0.55119678872689537,0.60266677748747144,0.79319474178896654]
["2013-05-01T11:00:00","2013-05-01T11:00:00",null,13.450979903673051,13.754552105328951,14.058124306984851,14.361696508640751,14.665268710296651,14.968840911952551,15.272413113608451,15.575985315264351,15.879557516920251,null,0.24184060091792597,0.289325477167724,0.34673633286389244,0.40827950839313681,0.46721501135596188,0.52373210830960748,0.57800955100257845,0.63195051981601158,0.82486534570047931,null,0.57800955100257845,0.63195051981601158,0.82486534570047931]
["2013-05-01T12:00:00","2013-05-01T12:00:00",null,13.453858523830096,13.757430725485996,14.061002927141896,14.364575128797796,14.668147330453696,14.971719532109596,15.275291733765496,15.578863935421396,15.882436137077296,null,0.24855956369995008,0.2992830010403012,0.35979572531346043,0.42431459171486885,0.48609960784503126,0.54535055506992292,0.60225669994678444,0.65872122285675239,0.85405445475039943,null,0.60225669994678444,0.65872122285675239,0.85405445475039943]
["2013-05-01T13:00:00","2013-05-01T13:00:00",null,13.641557384745113,13.945129586401013,14.248701788056913,14.552273989712813,14.855846191368713,15.159418393024612,15.462990594680512,15.766562796336412,16.070134997992312,null,0.2543847677394514,0.30833625136162007,0.37192981459429897,0.43940334225040034,0.50402735673916443,0.56599112461783108,0.62551545686984755,0.68449301906761484,0.88224465697044119,null,0.62551545686984755,0.68449301906761484,0.88224465697044119]
["2013-05-01T14:00:00","2013-05-01T14:00:00",null,13.721223584696443,14.024795786352342,14.328367988008242,14.631940189664142,14.935512391320042,15.239084592975942,15.542656794631842,15.846228996287742,16.149801197943642,null,0.21304053979122162,0.27018852526900117,0.33685241265246413,0.40725957194578732,0.47471206998441756,0.53937814370812365,0.60151014852655948,0.66299023520339051,0.86314976430666057,null,0.60151014852655948,0.66299023520339051,0.86314976430666057]
["2013-05-01T15:00:00","2013-05-01T15:00:00",null,13.910470586732696,14.214042788388596,14.517614990044496,14.821187191700396,15.124759393356296,15.428331595012196,15.731903796668096,16.035475998323996,16.339048199979896,null,0.13649273219633029,0.19693185280834075,0.26675018281247231,0.3401961218303729,0.41055070708001828,0.47801371992738384,0.54282700097338799,0.60689373059916729,0.8095347545640299,null,0.54282700097338799,0.60689373059916729,0.8095347545640299]
["2013-05-01T16:00:00","2013-05-01T16:00:00",null,13.93774883048513,14.24132103214103,14.54489323379693,14.84846543545283,15.15203763710873,15.45560983876463,15.75918204042053,16.06275424207643,16.36632644373233,null,5.6411948866290113E-2,0.12021580827368041,0.19326218455962951,0.26979947734578535,0.34312975346759478,0.41344227948229761,0.48099992560828342,0.54770587222668876,0.75289147990555738,null,0.48099992560828342,0.54770587222668876,0.75289147990555738]
["2013-05-01T17:00:00","2013-05-01T17:00:00",null,14.03395516370146,14.33752736535736,14.64109956701326,14.94467176866916,15.24824397032506,15.55181617198096,15.85538837363686,16.15896057529276,16.46253277694866,null,0,4.0387380353293714E-2,0.11670386215600261,0.1963850827540915,0.27272259417427164,0.34592669259125403,0.41627076303216376,0.48565798587813741,0.69341972169721877,null,0.41627076303216376,0.48565798587813741,0.69341972169721877]
["2013-05-01T18:00:00","2013-05-01T18:00:00",null,14.050124215849859,14.353696417505759,14.657268619161659,14.960840820817559,15.264413022473459,15.567985224129359,15.871557425785259,16.175129627441159,16.478701829097059,null,0,0,3.9588254889390911E-2,0.12241340329941285,0.20176866482669928,0.27787485045469679,0.35100534521053045,0.42307384428407241,0.63342222305210205,null,0.35100534521053045,0.42307384428407241,0.63342222305210205]
["2013-05-01T19:00:00","2013-05-01T19:00:00",null,14.03129150672865,14.33486370838455,14.63843591004045,14.942008111696349,15.245580313352249,15.549152515008149,15.852724716664049,16.156296918319949,16.459869119975849,null,0,0,0,4.9041067942661221E-2,0.13140356476831838,0.21041183760733101,0.28631824186935306,0.36106801717046333,0.5739925240787056,null,0.28631824186935306,0.36106801717046333,0.5739925240787056]
["2013-05-01T20:00:00","2013-05-01T20:00:00",null,13.688003739519601,13.991575941175501,14.295148142831401,14.598720344487301,14.902292546143201,15.205864747799101,15.509436949455001,15.813009151110901,16.116581352766801,null,0,0,0,0,6.6811094705761034E-2,0.14866888071211096,0.22729862043664356,0.30467709792164432,0.52013567373515701,null,0.22729862043664356,0.30467709792164432,0.52013567373515701]
["2013-05-01T21:00:00","2013-05-01T21:00:00",null,13.541651702953011,13.845223904608911,14.148796106264811,14.452368307920711,14.755940509576611,15.059512711232511,15.363084912888411,15.666657114544311,15.970229316200211,null,0,0,0,0,4.395190051465013E-3,8.9081459607681115E-2,0.17042401998598872,0.25041017003740884,0.46838178513872086,null,0.17042401998598872,0.25041017003740884,0.46838178513872086]
["2013-05-01T22:00:00","2013-05-01T22:00:00",null,13.185085110654441,13.488657312310341,13.792229513966241,14.095801715622141,14.399373917278041,14.702946118933941,15.006518320589841,15.310090522245741,15.613662723901641,null,0,0,0,0,0,3.8536774015834593E-2,0.12247649215182602,0.20495465187357431,0.42532364336659451,null,0.12247649215182602,0.20495465187357431,0.42532364336659451]
["2013-05-01T23:00:00","2013-05-01T23:00:00",null,12.849145226114695,13.152717427770595,13.456289629426495,13.759861831082395,14.063434032738295,14.367006234394195,14.670578436050095,14.974150637705995,15.277722839361894,null,0,0,0,0,0,0,8.3193166715766403E-2,0.16803715840301614,0.39068786339165329,null,8.3193166715766403E-2,0.16803715840301614,0.39068786339165329]
["2013-05-02","2013-05-02",null,12.605394686520109,12.908966888176009,13.212539089831909,13.516111291487809,13.819683493143708,14.123255694799608,14.426827896455508,14.730400098111408,15.033972299767308,null,0,0,0,0,0,0,4.9861223024034868E-2,0.13699744301563713,0.36184574303000672,null,4.9861223024034868E-2,0.13699744301563713,0.36184574303000672]
["2013-05-02T01:00:00","2013-05-02T01:00:00",null,12.470245023587109,12.773817225243009,13.077389426898909,13.380961628554809,13.684533830210709,13.988106031866609,14.291678233522509,14.595250435178409,14.898822636834309,null,0,0,0,0,0,0,2.1292487689512921E-2,0.11064733232431875,0.33761962370327187,null,2.1292487689512921E-2,0.11064733232431875,0.33761962370327187]
["2013-05-02T02:00:00","2013-05-02T02:00:00",null,12.377156559915225,12.680728761571125,12.984300963227025,13.287873164882924,13.591445366538824,13.895017568194724,14.198589769850624,14.502161971506524,14.805734173162424,null,0,0,0,0,0,0,0,8.5012228627018599E-2,0.31410851137055523,null,-6.5612406509908093E-3,8.5012228627018599E-2,0.31410851137055523]
["2013-05-02T03:00:00","2013-05-02T03:00:00",null,12.298769667709479,12.602341869365379,12.905914071021279,13.209486272677179,13.513058474333079,13.816630675988979,14.120202877644878,14.423775079300778,14.727347280956678,null,0,0,0,0,0,0,0,6.2142519627171253E-2,0.29332073450034918,null,-2.5035759599373115E-2,6.2142519627171253E-2,0.29332073450034918]
["2013-05-02T04:00:00","2013-05-02T04:00:00",null,11.449675484262203,11.753247685918103,12.056819887574003,12.360392089229903,12.663964290885803,12.967536492541702,13.271108694197602,13.574680895853502,13.878253097509402,null,0,0,0,0,0,0,0,4.6654206359688428E-2,0.27987229412756537,null,-1.7622819440801907E-2,4.6654206359688428E-2,0.27987229412756537]
["2013-05-02T05:00:00","2013-05-02T05:00:00",null,11.065125168918486,11.368697370574386,11.672269572230286,11.975841773886186,12.279413975542086,12.582986177197986,12.886558378853886,13.190130580509786,13.493702782165686,null,0,0,0,0,0,0,0,3.7821767021816347E-2,0.27298509440577223,null,-1.0872312232571105E-2,3.7821767021816347E-2,0.27298509440577223]
["2013-05-02T06:00:00","2013-05-02T06:00:00",null,10.800075794063879,11.103647995719779,11.407220197375679,11.710792399031579,12.014364600687479,12.317936802343379,12.621509003999279,12.925081205655179,13.228653407311079,null,0,0,0,0,0,0,0,3.4089009920691839E-2,0.27112397325957777,null,-5.6885115259390408E-3,3.4089009920691839E-2,0.27112397325957777]
["2013-05-02T07:00:00","2013-05-02T07:00:00",null,10.645273918486456,10.948846120142356,11.252418321798256,11.555990523454156,11.859562725110056,12.163134926765956,12.466707128421856,12.770279330077756,13.073851531733656,null,0,0,0,0,0,0,0,3.3962832215865095E-2,0.27280634265726766,null,-2.0188432772279036E-3,3.3962832215865095E-2,0.27280634265726766]
["2013-05-02T08:00:00","2013-05-02T08:00:00",null,10.56458727080579,10.86815947246169,11.17173167411759,11.47530387577349,11.778876077429389,12.082448279085289,12.386020480741189,12.689592682397089,12.993164884052989,null,0,0,0,0,0,0,0,3.4246732051725272E-2,0.27489878959564451,null,-1.6192805452765477E-3,3.4246732051725272E-2,0.27489878959564451]
["2013-05-02T09:00:00","2013-05-02T09:00:00",null,10.557721248157815,10.861293449813715,11.164865651469615,11.468437853125515,11.772010054781415,12.075582256437315,12.379154458093215,12.682726659749115,12.986298861405015,null,0,0,0,0,0,0,0,3.4782987297238936E-2,0.27724359194367482,null,-1.3564103268874977E-3,3.4782987297238936E-2,0.27724359194367482]
["2013-05-02T10:00:00","2013-05-02T10:00:00",null,10.269700470392381,10.573272672048281,10.876844873704181,11.180417075360081,11.483989277015981,11.787561478671881,12.091133680327781,12.394705881983681,12.698278083639581,null,0,0,6.0985890666259582E-4,2.7023058450394333E-3,4.689604696060651E-3,6.5717554597262487E-3,8.3592729447717878E-3,4.4835144448436205E-2,0.28891502964014865,null,8.3592729447717878E-3,4.4835144448436205E-2,0.28891502964014865]
["2013-05-02T11:00:00","2013-05-02T11:00:00",null,10.359905397608223,10.663477599264123,10.967049800920023,11.270622002575923,11.574194204231823,11.877766405887723,12.181338607543623,12.484910809199523,12.788483010855423,null,0,0,2.8389983586017388E-4,4.4793085213494111E-3,8.4539062233918456E-3,1.2239237368194166E-2,1.5824787147020805E-2,5.4004057665846268E-2,0.29971373821157082,null,1.5824787147020805E-2,5.4004057665846268E-2,0.29971373821157082]
["2013-05-02T12:00:00","2013-05-02T12:00:00",null,10.439811804938431,10.743384006594331,11.046956208250231,11.350528409906131,11.654100611562031,11.957672813217931,12.261245014873831,12.564817216529731,12.868389418185631,null,0,0,0,2.4078912004436978E-3,8.4644210321274081E-3,1.4216021410479823E-2,1.9683721952972057E-2,5.9650509956843061E-2,0.30706358951772866,null,1.9683721952972057E-2,5.9650509956843061E-2,0.30706358951772866]
["2013-05-02T13:00:00","2013-05-02T13:00:00",null,10.383572688383564,10.687144890039463,10.990717091695362,11.294289293351262,11.597861495007162,11.901433696663062,12.205005898318962,12.508578099974862,12.812150301630762,null,0,0,0,0,4.7211491222673369E-3,1.256519643899659E-2,2.000968102377448E-2,6.1858619791311083E-2,0.31105921683724225,null,2.000968102377448E-2,6.1858619791311083E-2,0.31105921683724225]
["2013-05-02T14:00:00","2013-05-02T14:00:00",null,10.331108648523854,10.634680850179752,10.938253051835652,11.241825253491552,11.545397455147452,11.848969656803352,12.152541858459252,12.456114060115151,12.759686261771051,null,0,0,0,0,7.3603661148933554E-5,1.0031127533726147E-2,1.948394058699638E-2,6.3246574544405271E-2,0.31426623350158867,null,1.948394058699638E-2,6.3246574544405271E-2,0.31426623350158867]
["2013-05-02T15:00:00","2013-05-02T15:00:00",null,10.25888191799805,10.56245411965395,10.86602632130985,11.16959852296575,11.473170724621649,11.776742926277549,12.080315127933449,12.383887329589349,12.687459531245249,null,0,0,0,0,0,1.0756649336479926E-2,2.2144187197093566E-2,6.7746912683225802E-2,0.32052254469924807,null,2.2144187197093566E-2,6.7746912683225802E-2,0.32052254469924807]
["2013-05-02T16:00:00","2013-05-02T16:00:00",null,10.148163374461561,10.451735576117461,10.755307777773361,11.05887997942926,11.36245218108516,11.66602438274106,11.96959658439696,12.27316878605286,12.57674098770876,null,0,0,0,0,6.8346256781152981E-4,1.3448440372783798E-2,2.6739158614534159E-2,7.4150431203183056E-2,0.32865049185183748,null,2.6739158614534159E-2,7.4150431203183056E-2,0.32865049185183748]
["2013-05-02T17:00:00","2013-05-02T17:00:00",null,10.110226758058367,10.413798959714267,10.717371161370167,11.020943363026067,11.324515564681967,11.628087766337867,11.931659967993767,12.235232169649667,12.538804371305567,null,0,0,0,4.1007754068691788E-4,3.164957429404161E-3,1.7896204467926523E-2,3.305855866460692E-2,8.2236319120830237E-2,0.33842926397591011,null,3.305855866460692E-2,8.2236319120830237E-2,0.33842926397591011]
["2013-05-02T18:00:00","2013-05-02T18:00:00",null,10.014712951051514,10.318285152707414,10.621857354363314,10.925429556019214,11.229001757675114,11.532573959331014,11.836146160986914,12.139718362642814,12.443290564298714,null,0,0,0,1.9452396160789696E-3,6.7610220169663643E-3,2.3437508671567697E-2,4.0450469205707003E-2,9.1394717529504732E-2,0.34925951697353896,null,4.0450469205707003E-2,9.1394717529504732E-2,0.34925951697353896]
["2013-05-02T19:00:00","2013-05-02T19:00:00",null,9.9677129454045446,10.271285147060444,10.574857348716343,10.878429550372243,11.182001752028143,11.485573953684042,11.789146155339942,12.092718356995842,12.396290558651742,null,0,0,1.8506063374589116E-3,5.9198373181214049E-3,1.273343337876558E-2,3.1313100414503636E-2,5.0124093242424041E-2,0.10278225539011837,0.36226633537942915,null,5.0124093242424041E-2,0.10278225539011837,0.36226633537942915]
["2013-05-02T20:00:00","2013-05-02T20:00:00",null,9.8070386768451652,10.110610878501065,10.414183080156965,10.717755281812865,11.021327483468765,11.324899685124665,11.628471886780565,11.932044088436465,12.235616290092365,null,0,0,1.5561916928631756E-3,7.5391178633979527E-3,1.6161261026558793E-2,3.6454841886193454E-2,5.6885115259390405E-2,0.11108895429121235,0.37203459269476624,null,5.6885115259390405E-2,0.11108895429121235,0.37203459269476624]
["2013-05-02T21:00:00","2013-05-02T21:00:00",null,10.007697637690589,10.311269839346489,10.614842041002387,10.918414242658287,11.221986444314187,11.525558645970087,11.829130847625986,12.132703049281886,12.436275250937786,null,0,0,1.2722918570030016E-3,9.4212686270635504E-3,2.0093799493658981E-2,4.2332619969372612E-2,6.4602984871292915E-2,0.12056279696195371,0.38316977514572642,null,6.4602984871292915E-2,0.12056279696195371,0.38316977514572642]
["2013-05-02T22:00:00","2013-05-02T22:00:00",null,9.9755945745446084,10.279166776200508,10.582738977856408,10.886311179512308,11.189883381168208,11.493455582824108,11.797027784480008,12.100599986135908,12.404172187791808,null,0,0,2.754879888717243E-3,1.3038362832096877E-2,2.5719222167184648E-2,4.9861223024034999E-2,7.3940135028471965E-2,0.13162437575176494,0.39586114928954974,null,7.3940135028471965E-2,0.13162437575176494,0.39586114928954974]
["2013-05-02T23:00:00","2013-05-02T23:00:00",null,9.8590692821609682,10.162641483816868,10.466213685472768,10.769785887128668,11.073358088784568,11.376930290440468,11.680502492096368,11.984074693752268,12.287646895408168,null,0,1.8190619112522257E-3,6.7820516344374885E-3,1.9147466707458399E-2,3.3794595276096261E-2,5.9808232087876653E-2,8.5653631959888038E-2,0.14500972727213537,0.41084475173772561,null,8.5653631959888038E-2,0.14500972727213537,0.41084475173772561]
["2013-05-03","2013-05-03",null,9.726584136993063,10.030156338648963,10.333728540304863,10.637300741960763,10.940872943616663,11.244445145272563,11.548017346928463,11.851589548584363,12.155161750240262,null,2.6707614188327474E-3,6.7610220169663652E-3,1.3858517913470713E-2,2.8232261454983965E-2,4.4782570404758547E-2,7.2594239510320041E-2,0.10015355320622803,0.16111841425501636,0.42849911560473419,null,0.10015355320622803,0.16111841425501636,0.42849911560473419]
["2013-05-03T01:00:00","2013-05-03T01:00:00",null,9.6223125886809342,9.9258847903368341,10.229456991992734,10.533029193648634,10.836601395304534,11.140173596960434,11.443745798616334,11.747318000272234,12.050890201928134,null,7.5075734371912659E-3,1.3826973487264027E-2,2.3027431130880772E-2,3.9377958714679681E-2,5.77999036193843E-2,8.7378060592520207E-2,0.11660922887738255,0.17916182604524075,0.44804614504414397,null,0.11660922887738255,0.17916182604524075,0.44804614504414397]
["2013-05-03T02:00:00","2013-05-03T02:00:00",null,9.5951227512538768,9.8986949529097767,10.202267154565677,10.505839356221577,10.809411557877477,11.112983759533376,11.416555961189276,11.720128162845176,12.023700364501076,null,1.390057714841296E-2,2.2417572224218179E-2,3.3678932380005078E-2,5.1964184771147393E-2,7.2226221204575364E-2,0.103539321619079,0.13441080006668901,0.1985195889274104,0.4688759811492923,null,0.13441080006668901,0.1985195889274104,0.4688759811492923]
["2013-05-03T03:00:00","2013-05-03T03:00:00",null,9.515850418678216,9.8194226203341159,10.122994821990016,10.426567023645916,10.730139225301816,11.033711426957716,11.337283628613616,11.640855830269516,11.944428031925415,null,2.0840350913883879E-2,3.1554941015421556E-2,4.486668887464304E-2,6.5097180881864322E-2,8.7188794035280084E-2,0.12022632308241589,0.15273811169277357,0.21840309224635812,0.49023155769121873,null,0.15273811169277357,0.21840309224635812,0.49023155769121873]
["2013-05-03T04:00:00","2013-05-03T04:00:00",null,9.5008286678630309,9.8044008695189309,10.107973071174831,10.411545272830731,10.715117474486631,11.018689676142531,11.322261877798431,11.62583407945433,11.92940628111023,null,2.8589764951993071E-2,4.147040565305652E-2,5.6822026406977033E-2,7.897672841280616E-2,0.10287688866873859,0.13761781673103543,0.17174888588666967,0.23894902851564626,0.51223905237474998,null,0.17174888588666967,0.23894902851564626,0.51223905237474998]
["2013-05-03T05:00:00","2013-05-03T05:00:00",null,9.5265588424472245,9.8301310441031244,10.133703245759024,10.437275447414924,10.740847649070824,11.044419850726724,11.347992052382624,11.651564254038524,11.955136455694424,null,3.4888135384594711E-2,4.9966371111390614E-2,6.7399923994952399E-2,9.1510380425596061E-2,0.11725063221025184,0.15373701852265198,0.18951891264976944,0.2582752469716092,0.53305837367116271,null,0.18951891264976944,0.2582752469716092,0.53305837367116271]
["2013-05-03T06:00:00","2013-05-03T06:00:00",null,9.461468872851432,9.7650410745073319,10.068613276163232,10.372185477819132,10.675757679475032,10.979329881130932,11.282902082786832,11.586474284442732,11.890046486098631,null,4.1039298494898478E-2,5.8346673673633526E-2,7.788318830430771E-2,0.10395991396850146,0.1315612868993517,0.16980364627059072,0.20724688017792697,0.277580435810101,0.55385666535010436,null,0.20724688017792697,0.277580435810101,0.55385666535010436]
["2013-05-03T07:00:00","2013-05-03T07:00:00",null,9.5404484329163601,9.8440206345722601,10.14759283622816,10.45116503788406,10.75473723953996,11.05830944119586,11.36188164285176,11.66545384450766,11.96902604616356,null,4.6580602698539648E-2,6.611711732921384E-2,8.7746078898264857E-2,0.11579958860474426,0.14526208268178897,0.18527092992060243,0.22437550360815747,0.2962862805506658,0.57406612773985455,null,0.22437550360815747,0.2962862805506658,0.57406612773985455]
["2013-05-03T08:00:00","2013-05-03T08:00:00",null,9.8685608948823464,10.172133096538246,10.475705298194146,10.779277499850046,11.082849701505946,11.386421903161846,11.689994104817746,11.993566306473646,12.297138508129546,null,4.9261878926107956E-2,7.1048562626192413E-2,9.4791000751091398E-2,0.12483180930859201,0.15617645414930231,0.19797281887316132,0.23877027676714185,0.31228981944619116,0.59159431390203643,null,0.23877027676714185,0.31228981944619116,0.59159431390203643]
["2013-05-03T09:00:00","2013-05-03T09:00:00",null,10.149112272108241,10.45268447376414,10.75625667542004,11.05982887707594,11.36340107873184,11.66697328038774,11.97054548204364,12.27411768369954,12.57768988535544,null,4.4372492864071626E-2,6.8556552955864214E-2,9.45701897676446E-2,0.12675601930719987,0.16013002223387363,0.20385059695634047,0.24646711676157324,0.32172160288199025,0.6026769223093188,null,0.24646711676157324,0.32172160288199025,0.6026769223093188]
["2013-05-03T10:00:00","2013-05-03T10:00:00",null,10.358008745726643,10.661580947382543,10.965153149038443,11.268725350694343,11.572297552350243,11.875869754006143,12.179441955662043,12.483014157317943,12.786586358973842,null,3.2364581288059822E-2,5.9103739902593974E-2,8.7535782723553626E-2,0.12201384056746141,0.15755389409366094,0.20333537132829793,0.24789713074960967,0.32501273801622116,0.60774506011985963,null,0.24789713074960967,0.32501273801622116,0.60774506011985963]
["2013-05-03T11:00:00","2013-05-03T11:00:00",null,10.485790809488481,10.789363011144381,11.092935212800281,11.396507414456181,11.700079616112081,12.003651817767981,12.307224019423881,12.610796221079781,12.914368422735681,null,1.7475612118504034E-2,4.6822443299457561E-2,7.7725466173274277E-2,0.11453781155647683,0.15229648972587995,0.20017041389889376,0.24674050178869786,0.32574877462771051,0.61030015864260123,null,0.24674050178869786,0.32574877462771051,0.61030015864260123]
["2013-05-03T12:00:00","2013-05-03T12:00:00",null,11.01655334628223,11.32012554793813,11.623697749594029,11.927269951249929,12.230842152905829,12.534414354561729,12.837986556217629,13.141558757873529,13.445130959529429,null,0,1.6413616436212263E-2,5.0145122859895155E-2,8.9638744470666012E-2,0.12994200635407513,0.18024485134500376,0.22912819715663152,0.31033406502137661,0.59698841078337972,null,0.22912819715663152,0.31033406502137661,0.59698841078337972]
["2013-05-03T13:00:00","2013-05-03T13:00:00",null,11.32693318290057,11.63050538455647,11.93407758621237,12.23764978786827,12.541221989524169,12.844794191180069,13.148366392835969,13.451938594491869,13.755510796147769,null,0,0,9.2635464960301103E-3,5.1701314552758323E-2,9.4801515559826938E-2,0.14777512196958831,0.19920305149522208,0.28283784017788199,0.57181595867044432,null,0.19920305149522208,0.28283784017788199,0.57181595867044432]
["2013-05-03T14:00:00","2013-05-03T14:00:00",null,11.446931701525351,11.750503903181251,12.054076104837151,12.357648306493051,12.661220508148951,12.964792709804851,13.26836491146075,13.57193711311665,13.87550931477255,null,0,0,0,8.3592729447717687E-3,5.4351046354119935E-2,0.11007953265259854,0.16413616436212281,0.25028399233258203,0.54167000202558813,null,0.16413616436212281,0.25028399233258203,0.54167000202558813]
["2013-05-03T15:00:00","2013-05-03T15:00:00",null,11.504893141405365,11.808465343061265,12.112037544717165,12.415609746373065,12.719181948028965,13.022754149684864,13.326326351340764,13.629898552996664,13.933470754652564,null,0,0,0,0,1.0146790429817296E-2,6.867221585195539E-2,0.12539960898031241,0.21409202066477762,0.5079174659844341,null,0.12539960898031241,0.21409202066477762,0.5079174659844341]
["2013-05-03T16:00:00","2013-05-03T16:00:00",null,11.426378099925133,11.729950301581033,12.033522503236933,12.337094704892833,12.640666906548732,12.944239108204632,13.247811309860532,13.551383511516432,13.854955713172332,null,0,0,0,0,0,3.1029200578643439E-2,9.0374781082155395E-2,0.18155920243694879,0.47778202414831339,null,9.0374781082155395E-2,0.18155920243694879,0.47778202414831339]
["2013-05-03T17:00:00","2013-05-03T17:00:00",null,11.351874616263595,11.655446817919495,11.959019019575395,12.262591221231295,12.566163422887195,12.869735624543095,13.173307826198995,13.476880027854895,13.780452229510795,null,0,0,0,0,0,0,5.9492787825809808E-2,0.15312715961598913,0.45169478367538407,null,5.9492787825809808E-2,0.15312715961598913,0.45169478367538407]
["2013-05-03T18:00:00","2013-05-03T18:00:00",null,11.306770485347222,11.610342687003122,11.913914888659022,12.217487090314922,12.521059291970822,12.824631493626722,13.128203695282622,13.431775896938522,13.735348098594422,null,0,0,0,0,0,0,3.034573801083195E-2,0.12639851581019054,0.42727939779140911,null,3.034573801083195E-2,0.12639851581019054,0.42727939779140911]
["2013-05-03T19:00:00","2013-05-03T19:00:00",null,11.115752080723087,11.419324282378987,11.722896484034887,12.026468685690787,12.330040887346687,12.633613089002587,12.937185290658487,13.240757492314387,13.544329693970287,null,0,0,0,0,0,0,5.8252040395013714E-3,0.10422278418689029,0.40734332042878357,null,5.8252040395013714E-3,0.10422278418689029,0.40734332042878357]
["2013-05-03T20:00:00","2013-05-03T20:00:00",null,10.865011912496517,11.168584114152416,11.472156315808316,11.775728517464216,12.079300719120116,12.382872920776016,12.686445122431916,12.990017324087816,13.293589525743716,null,0,0,0,0,0,0,0,8.6284520484021521E-2,0.39159213694291173,null,-1.439477315898435E-2,8.6284520484021521E-2,0.39159213694291173]
["2013-05-03T21:00:00","2013-05-03T21:00:00",null,10.66805419784146,10.97162639949736,11.27519860115326,11.57877080280916,11.88234300446506,12.18591520612096,12.48948740777686,12.79305960943276,13.09663181108866,null,0,0,0,0,0,0,0,7.3487998252842565E-2,0.38089857645884517,null,-1.5004632065646971E-2,7.3487998252842565E-2,0.38089857645884517]
["2013-05-03T22:00:00","2013-05-03T22:00:00",null,10.569523030999964,10.873095232655864,11.176667434311764,11.480239635967664,11.783811837623563,12.087384039279463,12.390956240935363,12.694528442591263,12.998100644247163,null,0,0,0,0,0,0,0,6.7820516344374651E-2,0.37718684897519178,null,-7.7178696119025066E-3,6.7820516344374651E-2,0.37718684897519178]
["2013-05-03T23:00:00","2013-05-03T23:00:00",null,10.368087520209183,10.671659721865083,10.975231923520983,11.278804125176883,11.582376326832783,11.885948528488683,12.189520730144583,12.493092931800483,12.796665133456383,null,0,0,0,0,0,0,0,6.4445262740259246E-2,0.37573580536968421,null,-5.3940968813433049E-3,6.4445262740259246E-2,0.37573580536968421]
["2013-05-04","2013-05-04",null,10.29277228252575,10.59634448418165,10.89991668583755,11.20348888749345,11.507061089149349,11.810633290805249,12.114205492461149,12.417777694117049,12.721349895772949,null,0,0,0,0,0,0,0,6.4476807166465935E-2,0.37761795613334981,null,-1.9242099986078456E-3,6.4476807166465935E-2,0.37761795613334981]
["2013-05-04T01:00:00","2013-05-04T01:00:00",null,10.235545965543054,10.539118167198954,10.842690368854853,11.146262570510753,11.449834772166653,11.753406973822553,12.056979175478453,12.360551377134353,12.664123578790253,null,0,0,0,0,0,0,5.7831448045590989E-4,6.6958302028058567E-2,0.38189748328872353,null,5.7831448045590989E-4,6.6958302028058567E-2,0.38189748328872353]
["2013-05-04T02:00:00","2013-05-04T02:00:00",null,10.138495763159341,10.442067964815241,10.745640166471141,11.049212368127041,11.352784569782941,11.656356771438841,11.95992897309474,12.26350117475064,12.56707337640654,null,0,0,0,0,0,0,2.4078912004436973E-3,7.0659514702976392E-2,0.38739672825742244,null,2.4078912004436973E-3,7.0659514702976392E-2,0.38739672825742244]
["2013-05-04T03:00:00","2013-05-04T03:00:00",null,10.115691537403992,10.419263739059891,10.72283594071579,11.02640814237169,11.329980344027589,11.633552545683489,11.937124747339389,12.240696948995289,12.544269150651189,null,0,0,0,0,0,8.5169950758052181E-4,5.2153451328387501E-3,7.5317574972830356E-2,0.39382127639485082,null,5.2153451328387501E-3,7.5317574972830356E-2,0.39382127639485082]
["2013-05-04T04:00:00","2013-05-04T04:00:00",null,10.034235757099072,10.337807958754972,10.64138016041087,10.94495236206677,11.24852456372267,11.55209676537857,11.85566896703447,12.15924116869037,12.46281337034627,null,0,0,0,0,0,2.3763467742370114E-3,8.6852320155742097E-3,8.0648583001760282E-2,0.40091877229135514,null,8.6852320155742097E-3,8.0648583001760282E-2,0.40091877229135514]
["2013-05-04T05:00:00","2013-05-04T05:00:00",null,9.9817854552639833,10.285357656919883,10.588929858575783,10.892502060231683,11.196074261887583,11.499646463543483,11.803218665199383,12.106790866855283,12.410363068511183,null,0,0,0,0,0,3.1544426206685993E-3,1.1440111904291454E-2,8.5296128462878679E-2,0.40735383523751906,null,1.1440111904291454E-2,8.5296128462878679E-2,0.40735383523751906]
["2013-05-04T06:00:00","2013-05-04T06:00:00",null,10.043041888423396,10.346614090079296,10.650186291735196,10.953758493391096,11.257330695046996,11.560902896702896,11.864475098358795,12.168047300014695,12.471619501670595,null,0,0,0,0,0,4.2269531116959228E-3,1.4478891628868871E-2,9.020654414238613E-2,0.41403073878460095,null,1.4478891628868871E-2,9.020654414238613E-2,0.41403073878460095]
["2013-05-04T07:00:00","2013-05-04T07:00:00",null,10.390544885324067,10.694117086979967,10.997689288635867,11.301261490291767,11.604833691947666,11.908405893603566,12.211978095259466,12.515550296915366,12.819122498571266,null,0,0,0,2.7338502712461192E-4,2.2922283043525153E-3,8.443391414656283E-3,2.052490665181702E-2,9.7998017415437566E-2,0.42348355183787117,null,2.052490665181702E-2,9.7998017415437566E-2,0.42348355183787117]
["2013-05-04T08:00:00","2013-05-04T08:00:00",null,10.551645066620862,10.855217268276762,11.158789469932662,11.462361671588562,11.765933873244462,12.069506074900362,12.373078276556262,12.676650478212162,12.980222679868062,null,0,0,0,0,3.6801830574466972E-4,8.5275098845407783E-3,2.2512205502838237E-2,0.10180437817771101,0.42901434123277676,null,2.2512205502838237E-2,0.10180437817771101,0.42901434123277676]
["2013-05-04T09:00:00","2013-05-04T09:00:00",null,10.834092670849149,11.13766487250505,11.44123707416095,11.74480927581685,12.04838147747275,12.35195367912865,12.65552588078455,12.95909808244045,13.26267028409635,null,0,0,0,0,0,0,1.5351620753920516E-2,9.6631092279814507E-2,0.42574423571601699,null,1.5351620753920516E-2,9.6631092279814507E-2,0.42574423571601699]
["2013-05-04T10:00:00","2013-05-04T10:00:00",null,11.260304780294515,11.563876981950415,11.867449183606315,12.171021385262215,12.474593586918115,12.778165788574015,13.081737990229914,13.385310191885814,13.688882393541714,null,0,0,0,0,0,0,0,7.7325903441322674E-2,0.40859458266831539,null,-6.2037371539815783E-3,7.7325903441322674E-2,0.40859458266831539]
["2013-05-04T11:00:00","2013-05-04T11:00:00",null,11.332810282148625,11.636382483804525,11.939954685460425,12.243526887116325,12.547099088772224,12.850671290428124,13.154243492084024,13.457815693739924,13.761387895395824,null,0,0,3.6801830574466994E-4,3.0808389595196654E-3,5.6674819084679166E-3,8.1279471525894237E-3,1.047274950061975E-2,9.0038307202617129E-2,0.4234520074116645,null,1.047274950061975E-2,9.0038307202617129E-2,0.4234520074116645]
["2013-05-04T12:00:00","2013-05-04T12:00:00",null,11.520097670868356,11.823669872524256,12.127242074180156,12.430814275836056,12.734386477491956,13.037958679147856,13.341530880803756,13.645103082459656,13.948675284115556,null,3.3395032544144908E-2,3.6486386312400129E-2,3.9777521446631041E-2,4.5287281224065529E-2,5.0523655974375394E-2,5.5518190123767346E-2,6.0281398480976932E-2,0.14216021410479796,0.47778202414831333,null,6.0281398480976932E-2,0.14216021410479796,0.47778202414831333]
["2013-05-04T13:00:00","2013-05-04T13:00:00",null,11.517182350870334,11.820754552526234,12.124326754182134,12.427898955838034,12.731471157493933,13.035043359149833,13.338615560805733,13.642187762461633,13.945759964117533,null,6.6916242793116559E-2,7.3098950329627002E-2,7.9323717101079716E-2,8.7619901193438127E-2,9.5506007745109617E-2,0.10303461079977201,0.11021622516616086,0.19439778390306994,0.53222770378105333,null,0.11021622516616086,0.19439778390306994,0.53222770378105333]
["2013-05-04T14:00:00","2013-05-04T14:00:00",null,11.604378666262344,11.907950867918244,12.211523069574143,12.515095271230043,12.818667472885943,13.122239674541843,13.425811876197743,13.729384077853643,14.032956279509543,null,9.9890682987838986E-2,0.10914371467513354,0.11829159827507248,0.12937420668235483,0.13991004503538793,0.14996220218658521,0.15955170775341776,0.24604652441215047,0.58607403931586632,null,0.15955170775341776,0.24604652441215047,0.58607403931586632]
["2013-05-04T15:00:00","2013-05-04T15:00:00",null,11.670720846887709,11.974293048543609,12.277865250199509,12.581437451855409,12.885009653511309,13.188581855167209,13.492154056823109,13.795726258479009,14.099298460134909,null,0.1301838469549931,0.14257029164548513,0.15469386611758812,0.16860495807473663,0.18184310227280917,0.19446087275548357,0.20651084356643765,0.29536097738193623,0.63762814654632682,null,0.20651084356643765,0.29536097738193623,0.63762814654632682]
["2013-05-04T16:00:00","2013-05-04T16:00:00",null,11.63228346810009,11.935855669755989,12.239427871411889,12.543000073067789,12.846572274723689,13.150144476379589,13.453716678035489,13.757288879691389,14.060861081347289,null,0.15876309709825062,0.17433552883561793,0.1894768534148272,0.2062690029655197,0.22225151224357392,0.23747695529266771,0.25201893577394996,0.34325593117242115,0.68780481383242864,null,0.25201893577394996,0.34325593117242115,0.68780481383242864]
["2013-05-04T17:00:00","2013-05-04T17:00:00",null,11.601008154732327,11.904580356388227,12.208152558044127,12.511724759700027,12.815296961355926,13.118869163011826,13.422441364667726,13.726013566323626,14.029585767979526,null,0.1857440963137027,0.20454457433288753,0.22276673787161649,0.24248200425079522,0.26126145265250894,0.2791471423116999,0.29622319169825262,0.3898891079146386,0.73676176330520526,null,0.29622319169825262,0.3898891079146386,0.73676176330520526]
["2013-05-04T18:00:00","2013-05-04T18:00:00",null,11.475598800827132,11.779171002483032,12.082743204138932,12.386315405794832,12.689887607450732,12.993459809106632,13.297032010762532,13.600604212418432,13.904176414074332,null,0.21140022962847396,0.23350235759062526,0.2548579341325517,0.27755940619263003,0.29917785295294552,0.31976584845717593,0.33942854079267687,0.43556543706191991,0.78479340960925248,null,0.33942854079267687,0.43556543706191991,0.78479340960925248]
["2013-05-04T19:00:00","2013-05-04T19:00:00",null,11.276143444460624,11.579715646116524,11.883287847772424,12.186860049428324,12.490432251084224,12.794004452740124,13.097576654396024,13.401148856051924,13.704721057707824,null,0.23888593966323302,0.26428971756835079,0.28878922192221024,0.31446638485445266,0.33892382997336989,0.36221413132263969,0.38445295179835337,0.48305031331171788,0.83463360301581635,null,0.38445295179835337,0.48305031331171788,0.83463360301581635]
["2013-05-04T20:00:00","2013-05-04T20:00:00",null,11.132001503198275,11.435573704854175,11.739145906510075,12.042718108165975,12.346290309821875,12.649862511477775,12.953434713133674,13.257006914789574,13.560579116445474,null,0.27935743848641115,0.3077579368811641,0.33510695440236082,0.36348642317964269,0.39050948163003707,0.41624973341469279,0.44082284142970124,0.54163882758626936,0.89534610865495134,null,0.44082284142970124,0.54163882758626936,0.89534610865495134]
["2013-05-04T21:00:00","2013-05-04T21:00:00",null,10.85613663506993,11.15970883672583,11.46328103838173,11.76685324003763,12.07042544169353,12.37399764334943,12.67756984500533,12.98114204666123,13.28471424831713,null,0.32578031905391736,0.35709341946842099,0.38719731687833497,0.41819497303077174,0.44771004115149432,0.47581612490165148,0.50263940198607027,0.60560040912469293,0.9613580778968096,null,0.50263940198607027,0.60560040912469293,0.9613580778968096]
["2013-05-04T22:00:00","2013-05-04T22:00:00",null,10.730340250664268,11.03391245232017,11.33748465397607,11.64105685563197,11.94462905728787,12.248201258943769,12.551773460599669,12.855345662255569,13.158917863911469,null,0.37796531480851153,0.4120648395379391,0.44479743913174358,0.47829761976324414,0.51017851984946816,0.5405452874777712,0.56951358554424458,0.67451446557756622,1,null,0.56951358554424458,0.67451446557756622,1]
["2013-05-04T23:00:00","2013-05-04T23:00:00",null,10.634667593536252,10.938239795192153,11.241811996848053,11.545384198503953,11.848956400159853,12.152528601815753,12.456100803471653,12.759673005127553,13.063245206783453,null,0.43472425236307521,0.47150505332007109,0.50677172181914598,0.54267979365109031,0.57683189242419564,0.60936471065202447,0.64039391123066802,0.74735054568880421,1,null,0.64039391123066802,0.74735054568880421,1]
["2013-05-05","2013-05-05",null,10.510722729602174,10.814294931258074,11.117867132913974,11.421439334569873,11.725011536225773,12.028583737881673,12.332155939537573,12.635728141193473,12.939300342849373,null,0.43000310324080787,0.46942312119042984,0.50718179935983287,0.54545570315727865,0.58184745619105871,0.61650426578347106,0.64955230963934252,0.75843315409608658,1,null,0.64955230963934252,0.75843315409608658,1]
["2013-05-05T01:00:00","2013-05-05T01:00:00",null,10.398394589796863,10.701966791452762,11.005538993108662,11.309111194764562,11.612683396420461,11.916255598076361,12.219827799732261,12.523400001388161,12.826972203044061,null,0.41480920461792081,0.45683689513396214,0.49705603854748664,0.53766422988422724,0.57626409275247525,0.61302386409200005,0.64805920679889273,0.75884323163677347,1,null,0.64805920679889273,0.75884323163677347,1]
["2013-05-05T02:00:00","2013-05-05T02:00:00",null,10.313783236990332,10.617355438646232,10.920927640302132,11.224499841958032,11.528072043613932,11.831644245269832,12.135216446925732,12.438788648581632,12.742360850237532,null,0.40403152566396977,0.44856174065907484,0.49114671603810078,0.53399456163551606,0.5747184158683476,0.61348651567636481,0.65043555357312977,0.76302812551352717,1,null,0.65043555357312977,0.76302812551352717,1]
["2013-05-05T03:00:00","2013-05-05T03:00:00",null,10.181407502531004,10.484979704186904,10.788551905842802,11.092124107498702,11.395696309154602,11.699268510810501,12.002840712466401,12.306412914122301,12.609985115778201,null,0.39639777452195174,0.44337793995244279,0.48826565844455677,0.53329006945023338,0.57608534100397069,0.61680919523680244,0.65561935427976181,0.7699784140877336,1,null,0.65561935427976181,0.7699784140877336,1]
["2013-05-05T04:00:00","2013-05-05T04:00:00",null,10.232841111708005,10.536413313363905,10.839985515019805,11.143557716675705,11.447129918331605,11.750702119987505,12.054274321643405,12.357846523299305,12.661418724955205,null,0.38977344501854766,0.43916150164948242,0.48632041882847782,0.53348985081620903,0.57831448045590983,0.62096254468734946,0.66160228045029656,0.77770679850837166,1,null,0.66160228045029656,0.77770679850837166,1]
["2013-05-05T05:00:00","2013-05-05T05:00:00",null,10.121745743118577,10.425317944774477,10.728890146430377,11.032462348086277,11.336034549742177,11.639606751398077,11.943178953053977,12.246751154709877,12.550323356365777,null,0.3815718942048093,0.43343093088860113,0.48292413560689129,0.53230167742909051,0.57921875400716816,0.62384360228089342,0.66636548880750612,0.78425752435062679,1,null,0.66636548880750612,0.78425752435062679,1]
["2013-05-05T06:00:00","2013-05-05T06:00:00",null,10.170027020681001,10.473599222336901,10.777171423992801,11.080743625648701,11.384315827304601,11.687888028960501,11.991460230616401,12.295032432272301,12.598604633928201,null,0.3708047300595938,0.42520835045739164,0.47708841675865438,0.52872664245899947,0.57778874001913172,0.62444294637882047,0.66889955771277654,0.78862116997588505,1,null,0.66889955771277654,0.78862116997588505,1]
["2013-05-05T07:00:00","2013-05-05T07:00:00",null,10.419019206044739,10.722591407700639,11.026163609356539,11.329735811012439,11.633308012668339,11.936880214324239,12.240452415980139,12.544024617636039,12.847596819291939,null,0.35816592995944829,0.415093104453781,0.46937054714675186,0.52326945672524283,0.57447657526742968,0.62316013971308193,0.66955147585438135,0.79112369445494879,1,null,0.66955147585438135,0.79112369445494879,1]
["2013-05-05T08:00:00","2013-05-05T08:00:00",null,10.535895662832061,10.839467864487961,11.143040066143861,11.446612267799761,11.750184469455661,12.053756671111561,12.357328872767461,12.660901074423361,12.964473276079261,null,0.34330850521609918,0.40280129304190904,0.45950765655279469,0.51570930924437375,0.56909299319482198,0.61984797496137989,0.66820558033622945,0.7916599497004625,1,null,0.66820558033622945,0.7916599497004625,1]
["2013-05-05T09:00:00","2013-05-05T09:00:00",null,10.727851670254097,11.031423871909997,11.334996073565897,11.638568275221797,11.942140476877697,12.245712678533597,12.549284880189497,12.852857081845396,13.156429283501296,null,0.32256278758083534,0.3847473664429491,0.44398779885910516,0.50259734275112788,0.55827325500592873,0.61119428737201231,0.66162331006776764,0.78705446347428631,0.99726614972875383,null,0.66162331006776764,0.78705446347428631,0.99726614972875383]
["2013-05-05T10:00:00","2013-05-05T10:00:00",null,10.986439382027278,11.290011583683178,11.593583785339078,11.897155986994978,12.200728188650878,12.504300390306778,12.807872591962678,13.111444793618578,13.415016995274478,null,0.29649657672537716,0.36144655028494371,0.42331568488499027,0.48441723844734119,0.54245898266764347,0.59763018410313729,0.65020422778094733,0.77767525408216498,0.98984269476144704,null,0.65020422778094733,0.77767525408216498,0.98984269476144704]
["2013-05-05T11:00:00","2013-05-05T11:00:00",null,11.146983722524725,11.450555924180625,11.754128125836525,12.057700327492425,12.361272529148325,12.664844730804225,12.968416932460125,13.271989134116025,13.575561335771924,null,0.26301742571134779,0.33089051609940057,0.39553556020563546,0.45927633076061247,0.51982059945997849,0.57737866247844483,0.63222390484313629,0.76187149655261532,0.97611035455280304,null,0.63222390484313629,0.76187149655261532,0.97611035455280304]
["2013-05-05T12:00:00","2013-05-05T12:00:00",null,11.280929412144252,11.584501613800152,11.888073815456051,12.191646017111951,12.495218218767851,12.798790420423751,13.102362622079651,13.405934823735551,13.709507025391451,null,0.23016916322145209,0.30092331120304888,0.3682916907717943,0.43462961908445513,0.49763435302794268,0.55754773320317486,0.61463262982854105,0.74641472771133921,0.9627039734149615,null,0.61463262982854105,0.74641472771133921,0.9627039734149615]
["2013-05-05T13:00:00","2013-05-05T13:00:00",null,11.440537304577681,11.744109506233581,12.047681707889481,12.351253909545381,12.654826111201281,12.958398312857181,13.261970514513081,13.565542716168981,13.869114917824881,null,0.19363020286537413,0.26731798248419275,0.3374727863678621,0.40646044648188456,0.47198873452190698,0.53429949108884722,0.59367661601856603,0.72765630892709665,0.94603800156909568,null,0.59367661601856603,0.72765630892709665,0.94603800156909568]
["2013-05-05T14:00:00","2013-05-05T14:00:00",null,11.649577061166433,11.953149262822333,12.256721464478233,12.560293666134132,12.863865867790032,13.167438069445932,13.471010271101832,13.774582472757732,14.078154674413632,null,0.15440996628172787,0.23104189234650385,0.30400415016256827,0.3756520568866879,0.44372492864071633,0.50846460602557142,0.5701549888771138,0.70634279162011249,0.92684847562669503,null,0.5701549888771138,0.70634279162011249,0.92684847562669503]
["2013-05-05T15:00:00","2013-05-05T15:00:00",null,11.708297477484756,12.011869679140656,12.315441880796556,12.619014082452455,12.922586284108355,13.226158485764255,13.529730687420155,13.833302889076055,14.136875090731955,null,0.11264514598407561,0.19227379253848675,0.2680855635218885,0.34244629089978312,0.41310580560275978,0.48030594823173639,0.54435164824004467,0.68280013486118918,0.90546135465856192,null,0.54435164824004467,0.68280013486118918,0.90546135465856192]
["2013-05-05T16:00:00","2013-05-05T16:00:00",null,11.905744368556988,12.209316570212888,12.512888771868788,12.816460973524688,13.120033175180588,13.423605376836488,13.727177578492388,14.030749780148287,14.334321981804187,null,6.8966630496551079E-2,0.15159199754059738,0.23025328169133644,0.30733734453174161,0.38058350218366654,0.45025462486550022,0.51666615683930994,0.65737532733860027,0.88221311254423429,null,0.51666615683930994,0.65737532733860027,0.88221311254423429]
["2013-05-05T17:00:00","2013-05-05T17:00:00",null,11.916197158367748,12.219769360023648,12.523341561679548,12.826913763335448,13.130485964991347,13.434058166647247,13.737630368303147,14.041202569959047,14.344774771614947,null,2.484649304213294E-2,0.11046858057581441,0.19200040751136188,0.2718078058142776,0.34765112122388636,0.4198037387673127,0.4885916175153594,0.63156147189279555,0.85857582250669096,null,0.4885916175153594,0.63156147189279555,0.85857582250669096]
["2013-05-05T18:00:00","2013-05-05T18:00:00",null,11.863304752103048,12.166876953758948,12.470449155414848,12.774021357070747,13.077593558726647,13.381165760382547,13.684737962038447,13.988310163694347,14.291882365350247,null,0,6.8472434485979783E-2,0.15289583382380681,0.23545811201543979,0.31393012960893901,0.38859578644016468,0.4597810415799195,0.60504312426170814,0.83425506990133602,null,0.4597810415799195,0.60504312426170814,0.83425506990133602]
["2013-05-05T19:00:00","2013-05-05T19:00:00",null,11.783138307445547,12.086710509101447,12.390282710757347,12.693854912413247,12.997427114069147,13.300999315725047,13.604571517380947,13.908143719036847,14.211715920692747,null,0,2.6676069762120842E-2,0.11400155631096298,0.19933974400878432,0.28045097859490964,0.35762967471393459,0.43122282105413312,0.57878764684900985,0.81020770232310568,null,0.43122282105413312,0.57878764684900985,0.81020770232310568]
["2013-05-05T20:00:00","2013-05-05T20:00:00",null,11.599813687393583,11.903385889049483,12.206958090705383,12.510530292361283,12.814102494017183,13.117674695673083,13.421246897328983,13.724819098984883,14.028391300640783,null,0,0,7.9502468849584063E-2,0.16754296239244484,0.25123032511878285,0.33085897167319372,0.40679692036142262,0.55660140041697403,0.79016647687312447,null,0.40679692036142262,0.55660140041697403,0.79016647687312447]
["2013-05-05T21:00:00","2013-05-05T21:00:00",null,11.41668528265769,11.72025748431359,12.02382968596949,12.32740188762539,12.63097408928129,12.93454629093719,13.23811849259309,13.54169069424899,13.84526289590489,null,0,0,4.948268990955456E-2,0.14015188563630585,0.22635228765044316,0.30835728097909104,0.38657694316293689,0.53855798862674964,0.77419448240380584,null,0.38657694316293689,0.53855798862674964,0.77419448240380584]
["2013-05-05T22:00:00","2013-05-05T22:00:00",null,11.206424241031716,11.509996442687616,11.813568644343516,12.117140845999415,12.420713047655315,12.724285249311215,13.027857450967115,13.331429652623015,13.635001854278915,null,0,0,2.5372233478910898E-2,0.11856498330219706,0.20717327651677808,0.29147049814977849,0.37186672574188567,0.52592970333533973,0.76356401077215263,null,0.37186672574188567,0.52592970333533973,0.76356401077215263]
["2013-05-05T23:00:00","2013-05-05T23:00:00",null,11.100697626540939,11.404269828196838,11.707842029852738,12.011414231508638,12.314986433164538,12.618558634820438,12.922130836476338,13.225703038132238,13.529275239788138,null,0,0,6.0249854054768223E-3,0.1016466560466778,0.19256820718308246,0.27906302384181536,0.36156221318103493,0.5176230044342458,0.75717100706093099,null,0.36156221318103493,0.5176230044342458,0.75717100706093099]
["2013-05-06","2013-05-06",null,10.917784658739251,11.221356860395149,11.524929062051049,11.828501263706949,12.132073465362849,12.435645667018749,12.739217868674649,13.042790070330549,13.346362271986449,null,0,0,0,8.6400183380112905E-2,0.17962447762960565,0.26830637450533545,0.35289801078293187,0.51094610088716397,0.75239728389498584,null,0.35289801078293187,0.51094610088716397,0.75239728389498584]
["2013-05-06T01:00:00","2013-05-06T01:00:00",null,10.98003204837967,11.28360425003557,11.587176451691469,11.890748653347369,12.194320855003269,12.497893056659169,12.801465258315069,13.105037459970969,13.408609661626869,null,0,0,0,7.4739260492374643E-2,0.17017166457633542,0.26094600839044207,0.34753545832779525,0.50748672881316403,0.75075697373223815,null,0.34753545832779525,0.50748672881316403,0.75075697373223815]
["2013-05-06T02:00:00","2013-05-06T02:00:00",null,10.883697509549757,11.187269711205657,11.490841912861557,11.794414114517457,12.097986316173357,12.401558517829256,12.705130719485156,13.008702921141056,13.312275122796956,null,0,0,0,6.4182392521870399E-2,0.16181239163156363,0.25466866757531154,0.34324541636368594,0.50508935242145592,0.7501576296343111,null,0.34324541636368594,0.50508935242145592,0.7501576296343111]
["2013-05-06T03:00:00","2013-05-06T03:00:00",null,10.886551414296404,11.190123615952304,11.493695817608204,11.797268019264104,12.100840220920004,12.404412422575904,12.707984624231804,13.011556825887704,13.315129027543604,null,0,0,0,5.6695848702150255E-2,0.15643932436769145,0.25130392877993168,0.34179437275817837,0.50546788553593613,0.75228162099889462,null,0.34179437275817837,0.50546788553593613,0.75228162099889462]
["2013-05-06T04:00:00","2013-05-06T04:00:00",null,10.735018543849979,11.038590745505878,11.342162947161778,11.645735148817678,11.949307350473578,12.252879552129478,12.556451753785378,12.860023955441278,13.163596157097178,null,0,0,0,4.6433395376241748E-2,0.14839549568498653,0.24536306184433915,0.33785131948234259,0.50342801264123715,0.75206081001544778,null,0.33785131948234259,0.50342801264123715,0.75206081001544778]
["2013-05-06T05:00:00","2013-05-06T05:00:00",null,10.983344342320569,11.286916543976469,11.590488745632369,11.894060947288269,12.197633148944169,12.501205350600069,12.804777552255969,13.108349753911869,13.411921955567768,null,0,0,0,2.8263805881190616E-2,0.13259173815543684,0.23179895857546418,0.32643223719552228,0.49404880324911588,0.74463735504814099,null,0.32643223719552228,0.49404880324911588,0.74463735504814099]
["2013-05-06T06:00:00","2013-05-06T06:00:00",null,10.643780081637672,10.947352283293572,11.250924484949472,11.554496686605372,11.858068888261272,12.161641089917172,12.465213291573072,12.768785493228972,13.072357694884872,null,0,0,0,2.2270364901920279E-2,0.12872228854075002,0.22993783742926971,0.32649532604793563,0.49593095401278148,0.7482649640619099,null,0.32649532604793563,0.49593095401278148,0.7482649640619099]
["2013-05-06T07:00:00","2013-05-06T07:00:00",null,10.888805162215032,11.192377363870932,11.495949565526832,11.799521767182732,12.103093968838632,12.406666170494532,12.710238372150432,13.013810573806332,13.317382775462232,null,0,0,0,1.4794335890935699E-2,0.1233597360856134,0.22658361344262543,0.32506531205989919,0.49632000193599729,0.75039947023522902,null,0.32506531205989919,0.49632000193599729,0.75039947023522902]
["2013-05-06T08:00:00","2013-05-06T08:00:00",null,11.403654148750931,11.707226350406831,12.010798552062731,12.314370753718631,12.617942955374531,12.921515157030431,13.225087358686331,13.528659560342231,13.832231761998131,null,0,0,0,0,0.10509551331194221,0.21055904492962893,0.31117524972022181,0.48446981249101895,0.74049452040632957,null,0.31117524972022181,0.48446981249101895,0.74049452040632957]
["2013-05-06T09:00:00","2013-05-06T09:00:00",null,11.676300364395068,11.979872566050968,12.283444767706868,12.587016969362768,12.890589171018668,13.194161372674568,13.497733574330468,13.801305775986368,14.104877977642268,null,0,0,0,0,7.8724373003152714E-2,0.18656425139507646,0.2894516548725507,0.46491226824287363,0.72301890828782556,null,0.2894516548725507,0.46491226824287363,0.72301890828782556]
["2013-05-06T10:00:00","2013-05-06T10:00:00",null,11.931992221240829,12.235564422896729,12.539136624552629,12.842708826208529,13.146281027864429,13.449853229520329,13.753425431176229,14.056997632832129,14.360569834488029,null,0,0,0,0,4.8105249965196176E-2,0.15837404917503475,0.26358522538306817,0.4412644633965947,0.70149509480613015,null,0.26358522538306817,0.4412644633965947,0.70149509480613015]
["2013-05-06T11:00:00","2013-05-06T11:00:00",null,12.08850710101725,12.392079302673149,12.695651504329049,12.999223705984949,13.302795907640849,13.606368109296749,13.909940310952649,14.213512512608549,14.517084714264449,null,0,0,0,0,1.4405287967719976E-2,0.12714506723041563,0.23471156059521492,0.41466199729562286,0.67705867930468411,null,0.23471156059521492,0.41466199729562286,0.67705867930468411]
["2013-05-06T12:00:00","2013-05-06T12:00:00",null,12.229178480049915,12.532750681705815,12.836322883361715,13.139895085017615,13.443467286673515,13.747039488329415,14.050611689985315,14.354183891641215,14.657756093297115,null,0,0,0,0,0,9.3424075615468311E-2,0.20337743056324017,0.38562009556800064,0.65021437260279435,null,0.20337743056324017,0.38562009556800064,0.65021437260279435]
["2013-05-06T13:00:00","2013-05-06T13:00:00",null,12.431158113554416,12.734730315210316,13.038302516866215,13.341874718522115,13.645446920178015,13.949019121833915,14.252591323489815,14.556163525145715,14.859735726801615,null,0,0,0,0,0,5.5160686626758201E-2,0.16756399200991601,0.35216197417144235,0.61901693508438194,null,0.16756399200991601,0.35216197417144235,0.61901693508438194]
["2013-05-06T14:00:00","2013-05-06T14:00:00",null,12.576796679335224,12.880368880991124,13.183941082647024,13.487513284302924,13.791085485958824,14.094657687614724,14.398229889270624,14.701802090926524,15.005374292582424,null,0,0,0,0,0,1.4289625071628717E-2,0.12917442531637915,0.31615926906087805,0.58530645827817018,null,0.12917442531637915,0.31615926906087805,0.58530645827817018]
["2013-05-06T15:00:00","2013-05-06T15:00:00",null,12.635417415864902,12.938989617520802,13.242561819176702,13.546134020832602,13.849706222488502,14.153278424144402,14.456850625800302,14.760422827456201,15.063995029112101,null,0,0,0,0,0,0,8.8860648624234456E-2,0.27825338356917706,0.54972434551702842,null,8.8860648624234456E-2,0.27825338356917706,0.54972434551702842]
["2013-05-06T16:00:00","2013-05-06T16:00:00",null,12.623547704698382,12.927119906354282,13.230692108010182,13.534264309666082,13.837836511321981,14.141408712977881,14.444980914633781,14.748553116289681,15.052125317945581,null,0,0,0,0,0,0,4.8883345811627739E-2,0.24068397195701405,0.51446819182668901,null,4.8883345811627739E-2,0.24068397195701405,0.51446819182668901]
["2013-05-06T17:00:00","2013-05-06T17:00:00",null,12.61884646377335,12.92241866542925,13.22599086708515,13.52956306874105,13.83313527039695,14.13670747205285,14.44027967370875,14.743851875364649,15.047424077020549,null,0,0,0,0,0,0,8.9586170426988326E-3,0.20316713438852885,0.47926461218002747,null,8.9586170426988326E-3,0.20316713438852885,0.47926461218002747]
["2013-05-06T18:00:00","2013-05-06T18:00:00",null,12.464442709326923,12.768014910982822,13.071587112638722,13.375159314294622,13.678731515950522,13.982303717606422,14.285875919262322,14.589448120918222,14.893020322574122,null,0,0,0,0,0,0,0,0.16842620632623201,0.44679488280461199,null,-2.8158657793835022E-2,0.16842620632623201,0.44679488280461199]
["2013-05-06T19:00:00","2013-05-06T19:00:00",null,12.298832544384847,12.602404746040747,12.905976947696647,13.209549149352547,13.513121351008447,13.816693552664347,14.120265754320247,14.423837955976147,14.727410157632047,null,0,0,0,0,0,0,0,0.13701847263310832,0.41762680337216301,null,-3.374202123241845E-2,0.13701847263310832,0.41762680337216301]
["2013-05-06T20:00:00","2013-05-06T20:00:00",null,12.151030178752405,12.454602380408305,12.758174582064205,13.061746783720105,13.365318985376005,13.668891187031905,13.972463388687805,14.276035590343705,14.579607791999605,null,0,0,0,0,0,0,0,0.10817635227146176,0.39099279284498445,null,-3.1144863474734639E-2,0.10817635227146176,0.39099279284498445]
["2013-05-06T21:00:00","2013-05-06T21:00:00",null,12.111699397286188,12.415271598942088,12.718843800597988,13.022416002253888,13.325988203909787,13.629560405565687,13.933132607221587,14.236704808877487,14.540277010533387,null,0,0,0,0,0,0,0,8.3435007316684379E-2,0.3683754392547906,null,-2.6959969597980964E-2,8.3435007316684379E-2,0.3683754392547906]
["2013-05-06T22:00:00","2013-05-06T22:00:00",null,11.975428800066448,12.279001001722348,12.582573203378248,12.886145405034148,13.189717606690047,13.493289808345947,13.796862010001847,14.100434211657747,14.404006413313647,null,0,0,0,0,0,0,0,6.0975375857523953E-2,0.34801876954274258,null,-2.4646711676157323E-2,6.0975375857523953E-2,0.34801876954274258]
["2013-05-06T23:00:00","2013-05-06T23:00:00",null,12.103672751558545,12.407244953214445,12.710817154870345,13.014389356526245,13.317961558182144,13.621533759838044,13.925105961493944,14.228678163149844,14.532250364805744,null,0,0,0,0,0,0,0,3.3605328718856076E-2,0.32282528781233605,null,-2.9641245825549271E-2,3.3605328718856076E-2,0.32282528781233605]
["2013-05-07","2013-05-07",null,11.889811136448795,12.193383338104695,12.496955539760595,12.800527741416495,13.104099943072395,13.407672144728295,13.711244346384195,14.014816548040095,14.318388749695995,null,0,0,0,0,0,0,0,1.1334963816935766E-2,0.30264736984879259,null,-2.4467959927652768E-2,1.1334963816935766E-2,0.30264736984879259]
["2013-05-07T01:00:00","2013-05-07T01:00:00",null,11.873723936279795,12.177296137935695,12.480868339591595,12.784440541247495,13.088012742903395,13.391584944559295,13.695157146215195,13.998729347871095,14.302301549526995,null,0,0,0,0,0,0,0,4.2059234942247309E-3,0.29754768761204503,null,-9.2530316872945582E-3,4.2059234942247309E-3,0.29754768761204503]
["2013-05-07T02:00:00","2013-05-07T02:00:00",null,11.900878435504401,12.204450637160301,12.508022838816201,12.811595040472101,13.115167242128001,13.418739443783901,13.722311645439801,14.025883847095701,14.329456048751601,null,4.0681794997889369E-2,4.3510278547755549E-2,4.6212584392794978E-2,4.8788712533007671E-2,5.1238662968393613E-2,5.3583465316423939E-2,5.5812604768363083E-2,6.2163549244642465E-2,0.35755570106589735,null,5.5812604768363083E-2,6.2163549244642465E-2,0.35755570106589735]
["2013-05-07T03:00:00","2013-05-07T03:00:00",null,11.781107173638448,12.084679375294348,12.388251576950248,12.691823778606148,12.995395980262048,13.298968181917948,13.602540383573848,13.906112585229748,14.209684786885648,null,8.3109048245882028E-2,8.8755500536878834E-2,9.4128567800751003E-2,9.9259794463705253E-2,0.10413866571700603,0.10880724079559556,0.11325500489073828,0.12171942592286561,0.41914093583008394,null,0.11325500489073828,0.12171942592286561,0.41914093583008394]
["2013-05-07T04:00:00","2013-05-07T04:00:00",null,11.74006628098445,12.04363848264035,12.34721068429625,12.65078288595215,12.95435508760805,13.25792728926395,13.56149949091985,13.86507169257575,14.16864389423165,null,0.12422195040192943,0.13273894547773468,0.14082483339538182,0.14855321781601991,0.15590306912217775,0.16292696135753315,0.16962489452208615,0.18024485134500368,0.47972726376439218,null,0.16962489452208615,0.18024485134500368,0.47972726376439218]
["2013-05-07T05:00:00","2013-05-07T05:00:00",null,11.8006529741075,12.1042251757634,12.4077973774193,12.7113695790752,13.0149417807311,13.318513982387,13.6220861840429,13.925658385698799,14.229230587354699,null,0.16273769480029304,0.17416729189584895,0.18502908931968445,0.1953966907329486,0.20525958132690575,0.2146808499539693,0.22367101142287482,0.23648856327152479,0.53807393743802567,null,0.22367101142287482,0.23648856327152479,0.53807393743802567]
["2013-05-07T06:00:00","2013-05-07T06:00:00",null,11.703016207773764,12.006588409429664,12.310160611085564,12.613732812741464,12.917305014397364,13.220877216053264,13.524449417709164,13.828021619365064,14.131593821020964,null,0.19899275532051081,0.21341907290570189,0.2271303834968747,0.24020029075517829,0.25264982429808369,0.26453155816926871,0.27587703679494013,0.29094475771300038,0.59467515286155592,null,0.27587703679494013,0.29094475771300038,0.59467515286155592]
["2013-05-07T07:00:00","2013-05-07T07:00:00",null,11.978357031205086,12.281929232860985,12.585501434516885,12.889073636172785,13.192645837828685,13.496218039484585,13.799790241140485,14.103362442796385,14.406934644452285,null,0.23634135594922701,0.25366976074543324,0.2701359512253233,0.28583456066751733,0.30079713349822207,0.3150762437611152,0.32871395069113918,0.3459687518261963,0.65180210872186428,null,0.32871395069113918,0.3459687518261963,0.65180210872186428]
["2013-05-07T08:00:00","2013-05-07T08:00:00",null,12.165001076683149,12.468573278339049,12.772145479994949,13.075717681650849,13.379289883306749,13.682862084962649,13.986434286618548,14.290006488274448,14.593578689930348,null,0.26922116286532938,0.28952525853369965,0.30880941775472032,0.32721033304195379,0.34474903401287121,0.36147809471115028,0.37747111879794015,0.39697608900240755,0.70497549649760127,null,0.37747111879794015,0.39697608900240755,0.70497549649760127]
["2013-05-07T09:00:00","2013-05-07T09:00:00",null,12.344568958183485,12.648141159839385,12.951713361495285,13.255285563151185,13.558857764807085,13.862429966462985,14.166002168118885,14.469574369774785,14.773146571430685,null,0.297989679565827,0.32132204015003912,0.3434872569646038,0.36463253733181894,0.38479994048662686,0.40404204047270526,0.42244295575993884,0.44425066907749428,0.7544687012158916,null,0.42244295575993884,0.44425066907749428,0.7544687012158916]
["2013-05-07T10:00:00","2013-05-07T10:00:00",null,12.5738816797969,12.8774538814528,13.1810260831087,13.4845982847646,13.788170486420499,14.091742688076399,14.395314889732299,14.698887091388199,15.002459293044099,null,0.32389816829025175,0.35026930859904132,0.37533661262462109,0.39925780249802462,0.42207493745419411,0.44385110634554298,0.46468094245069136,0.48881242849880602,0.80127011489787803,null,0.46468094245069136,0.48881242849880602,0.80127011489787803]
["2013-05-07T11:00:00","2013-05-07T11:00:00",null,12.674614305888452,12.978186507544352,13.281758709200252,13.585330910856152,13.888903112512052,14.192475314167952,14.496047515823852,14.799619717479752,15.103191919135652,null,0.34585308893010519,0.37533661262462115,0.40336909271362936,0.43012928094563463,0.45564872174684357,0.48002204839587626,0.50333337936261724,0.52985172699370453,0.84460164169712904,null,0.50333337936261724,0.52985172699370453,0.84460164169712904]
["2013-05-07T12:00:00","2013-05-07T12:00:00",null,12.761849681151203,13.065421882807103,13.368994084463003,13.672566286118903,13.976138487774802,14.279710689430702,14.583282891086602,14.886855092742502,15.190427294398402,null,0.36738741722053614,0.39997280949204289,0.43095995083574407,0.46054862261761548,0.48877036926386386,0.51573033886184483,0.54151264988144288,0.57041785909550269,0.8874494872945442,null,0.54151264988144288,0.57041785909550269,0.8874494872945442]
["2013-05-07T13:00:00","2013-05-07T13:00:00",null,12.827356678785005,13.130928880440905,13.434501082096805,13.738073283752705,14.041645485408605,14.345217687064505,14.648789888720405,14.952362090376305,15.255934292032205,null,0.38655591354546565,0.42227471882016987,0.45625858065350622,0.48871779522018605,0.5196733921376806,0.54926206391955201,0.57755741422694939,0.60888102945018852,0.92822591557105361,null,0.57755741422694939,0.60888102945018852,0.92822591557105361]
["2013-05-07T14:00:00","2013-05-07T14:00:00",null,12.816229366222798,13.119801567878698,13.423373769534598,13.726945971190498,14.030518172846397,14.334090374502297,14.637662576158197,14.941234777814097,15.244806979469997,null,0.40336909271362931,0.44228439984394435,0.47932807101932923,0.51471040241449528,0.54845242364691382,0.58072237165635354,0.61157282048649242,0.64535690095385312,0.96706761904021965,null,0.61157282048649242,0.64535690095385312,0.96706761904021965]
["2013-05-07T15:00:00","2013-05-07T15:00:00",null,12.954430842734057,13.258003044389957,13.561575246045857,13.865147447701757,14.168719649357657,14.472291851013557,14.775864052669457,15.079436254325357,15.383008455981257,null,0.41793210281238269,0.46006494141577969,0.50017893674194869,0.53849489977433651,0.57505488974788566,0.61001662879362928,0.64345372057271644,0.6797087810929342,1,null,0.64345372057271644,0.6797087810929342,1]
["2013-05-07T16:00:00","2013-05-07T16:00:00",null,13.124396737610814,13.427968939266714,13.731541140922614,14.035113342578514,14.338685544234414,14.642257745890314,14.945829947546214,15.249402149202114,15.552974350858014,null,0.42911985930702068,0.47450177380970632,0.51771763771286605,0.55900929161741797,0.5984187947583044,0.6361038692665586,0.67215914842080071,0.71092724822881781,1,null,0.67215914842080071,0.71092724822881781,1]
["2013-05-07T17:00:00","2013-05-07T17:00:00",null,13.212524836331086,13.516097037986986,13.819669239642886,14.123241441298786,14.426813642954686,14.730385844610586,15.033958046266486,15.337530247922386,15.641102449578286,null,0.43715317318099006,0.48583673762664215,0.53220704415047049,0.57651644816212866,0.61881752370529464,0.65927850771973728,0.69799403348407651,0.73931723181483522,1,null,0.69799403348407651,0.73931723181483522,1]
["2013-05-07T18:00:00","2013-05-07T18:00:00",null,13.12840899462352,13.43198119627942,13.73555339793532,14.03912559959122,14.34269780124712,14.64627000290302,14.949842204558919,15.253414406214819,15.556986607870719,null,0.44252624044486222,0.49458505849462975,0.54419392610901118,0.59159468388892456,0.63686093549551903,0.68016091786856336,0.72159977909541317,0.76554116480132683,1,null,0.72159977909541317,0.76554116480132683,1]
["2013-05-07T19:00:00","2013-05-07T19:00:00",null,13.023504909755978,13.327077111411878,13.630649313067778,13.934221514723678,14.237793716379578,14.541365918035478,14.844938119691378,15.148510321347278,15.452082523003178,null,0.38329632283744147,0.43867782044764658,0.49146216030016776,0.54189118299592298,0.59007003662226809,0.63615644331023635,0.68026606595591899,0.72677306499330974,0.96369236543610437,null,0.68026606595591899,0.72677306499330974,0.96369236543610437]
["2013-05-07T20:00:00","2013-05-07T20:00:00",null,12.826355083498184,13.129927285154084,13.433499486809984,13.737071688465884,14.040643890121784,14.344216091777684,14.647788293433583,14.951360495089483,15.254932696745383,null,0.31949246343005128,0.37815458136575175,0.43406181941273481,0.48747704778938966,0.53851592939180759,0.58733618635102203,0.6340745111805951,0.68309454950578519,0.92243225595775913,null,0.6340745111805951,0.68309454950578519,0.92243225595775913]
["2013-05-07T21:00:00","2013-05-07T21:00:00",null,12.63509088537077,12.93866308702667,13.24223528868257,13.54580749033847,13.84937969199437,14.15295189365027,14.45652409530617,14.76009629696207,15.06366849861797,null,0.2629333072414633,0.32474986779783238,0.38366434114318615,0.43996062711338502,0.4937438737957846,0.54519283293888954,0.59444419705626195,0.64588264139063123,0.88754412057316445,null,0.59444419705626195,0.64588264139063123,0.88754412057316445]
["2013-05-07T22:00:00","2013-05-07T22:00:00",null,12.339430982642874,12.643003184298774,12.946575385954674,13.250147587610574,13.553719789266474,13.857291990922374,14.160864192578273,14.464436394234173,14.768008595890073,null,0.21488063131994498,0.27972545679215588,0.34152098773105366,0.40056163878123419,0.45697358764752427,0.510925071269693,0.56258432658750912,0.61632551403496649,0.86019510305196767,null,0.56258432658750912,0.61632551403496649,0.86019510305196767]
["2013-05-07T23:00:00","2013-05-07T23:00:00",null,12.015624916989248,12.319197118645148,12.622769320301048,12.926341521956948,13.229913723612848,13.533485925268748,13.837058126924648,14.140630328580547,14.444202530236447,null,0.17383081801631095,0.24159876031700808,0.30619123037956536,0.36788161323110752,0.42682763100266802,0.48320803544275159,0.53718054868239129,0.59314036077305232,0.83913394115463702,null,0.53718054868239129,0.59314036077305232,0.83913394115463702]
["2013-05-08","2013-05-08",null,11.961341907496742,12.264914109152642,12.568486310808542,12.872058512464442,13.175630714120341,13.479202915776241,13.782775117432141,14.086347319088041,14.389919520743941,null,0.13501014416461604,0.20566965886759275,0.27300649401013172,0.33731506423682878,0.39875309167871748,0.45752035770177363,0.51377458443703028,0.5719109619359527,0.81999698925591413,null,0.51377458443703028,0.5719109619359527,0.81999698925591413]
["2013-05-08T01:00:00","2013-05-08T01:00:00",null,11.889018645421094,12.192590847076994,12.496163048732894,12.799735250388794,13.103307452044694,13.406879653700594,13.710451855356494,14.014024057012394,14.317596258668294,null,9.9144131567614063E-2,0.17263212982045695,0.24266075599929979,0.30953493955747396,0.37341240262601305,0.43451395618836397,0.49299732237555977,0.55326820604780125,0.80339410626246177,null,0.49299732237555977,0.55326820604780125,0.80339410626246177]
["2013-05-08T02:00:00","2013-05-08T02:00:00",null,11.763157439274522,12.066729640930422,12.370301842586322,12.673874044242222,12.977446245898122,13.281018447554022,13.584590649209922,13.888162850865822,14.191735052521722,null,6.5549317657493472E-2,0.14184476984273142,0.21453364263167143,0.28394189509511608,0.35023776417283442,0.41365257565700897,0.47433353686993723,0.53671789709802664,0.78886264058991507,null,0.47433353686993723,0.53671789709802664,0.78886264058991507]
["2013-05-08T03:00:00","2013-05-08T03:00:00",null,11.786221639828444,12.089793841484344,12.393366043140244,12.696938244796144,13.000510446452044,13.304082648107943,13.607654849763843,13.911227051419743,14.214799253075643,null,3.4183643199312032E-2,0.11321294565579611,0.18850949101115549,0.26039923833619277,0.32907145418814809,0.39473643474173292,0.45758344655418698,0.52202870929444656,0.77615023682862061,null,0.45758344655418698,0.52202870929444656,0.77615023682862061]
["2013-05-08T04:00:00","2013-05-08T04:00:00",null,11.678403790303683,11.981975991959583,12.285548193615483,12.589120395271383,12.892692596927283,13.196264798583183,13.499837000239083,13.803409201894983,14.106981403550883,null,1.0514808735561793E-3,8.2888237262435299E-2,0.16085554403662744,0.23528987507567073,0.3063804969368053,0.37435873541221376,0.43941385705913583,0.50597259635524339,0.76211296716664534,null,0.43941385705913583,0.50597259635524339,0.76211296716664534]
["2013-05-08T05:00:00","2013-05-08T05:00:00",null,11.90602424884222,12.20959645049812,12.51316865215402,12.81674085380992,13.12031305546582,13.42388525712172,13.72745745877762,14.03102966043352,14.33460186208942,null,0,4.9272393734843593E-2,0.12995252116281072,0.2069629803420667,0.28050355263858723,0.35082659346202599,0.4181213693696228,0.48682512964778502,0.74502640297135714,null,0.4181213693696228,0.48682512964778502,0.74502640297135714]
["2013-05-08T06:00:00","2013-05-08T06:00:00",null,12.019557078462979,12.323129280118879,12.626701481774779,12.930273683430679,13.233845885086579,13.537418086742479,13.840990288398379,14.144562490054279,14.448134691710179,null,0,1.4068814088182023E-2,9.7461762169924152E-2,0.17705886429812839,0.25307041664750596,0.32575928943644616,0.39531474922218884,0.46617404529114126,0.72644673593561904,null,0.39531474922218884,0.46617404529114126,0.72644673593561904]
["2013-05-08T07:00:00","2013-05-08T07:00:00",null,12.186979451289547,12.490551652945447,12.794123854601347,13.097696056257247,13.401268257913147,13.704840459569047,14.008412661224947,14.311984862880847,14.615557064536747,null,0,0,6.119618684097082E-2,0.14343250596180113,0.22196761240771357,0.29706437639709748,0.36893309410466379,0.44200050000808422,0.70438666720840992,null,0.36893309410466379,0.44200050000808422,0.70438666720840992]
["2013-05-08T08:00:00","2013-05-08T08:00:00",null,12.36655691329832,12.67012911495422,12.97370131661012,13.27727351826602,13.580845719921919,13.884417921577819,14.187990123233719,14.491562324889619,14.795134526545519,null,0,0,2.0829836105148311E-2,0.10576846107101806,0.18687969565714319,0.26444743969938417,0.33867147456371638,0.41401007915401816,0.6785622969538696,null,0.33867147456371638,0.41401007915401816,0.6785622969538696]
["2013-05-08T09:00:00","2013-05-08T09:00:00",null,12.475742071161585,12.779314272817485,13.082886474473385,13.386458676129285,13.690030877785185,13.993603079441085,14.297175281096985,14.600747482752885,14.904319684408785,null,0,0,0,6.6895213175645354E-2,0.15059309071071875,0.23063181480581679,0.30723219644438599,0.38484199972156918,0.65157078292968196,null,0.30723219644438599,0.38484199972156918,0.65157078292968196]
["2013-05-08T10:00:00","2013-05-08T10:00:00",null,12.604306486404132,12.907878688060032,13.211450889715932,13.515023091371832,13.818595293027732,14.122167494683632,14.425739696339532,14.729311897995432,15.032884099651332,null,0,0,0,2.6097755281664803E-2,0.11240330538315757,0.19494455395731936,0.27393179717886113,0.35383382876039687,0.62276020699424206,null,0.27393179717886113,0.35383382876039687,0.62276020699424206]
["2013-05-08T11:00:00","2013-05-08T11:00:00",null,12.67239835694116,12.97597055859706,13.27954276025296,13.58311496190886,13.88668716356476,14.19025936522066,14.49383156687656,14.79740376853246,15.10097597018836,null,0,0,0,0,6.8998174922757644E-2,0.15413658125460325,0.23560531933773765,0.31789421250224598,0.58910230423170806,null,0.23560531933773765,0.31789421250224598,0.58910230423170806]
["2013-05-08T12:00:00","2013-05-08T12:00:00",null,12.827094324117677,13.130666525773577,13.434238727429477,13.737810929085377,14.041383130741277,14.344955332397177,14.648527534053077,14.952099735708977,15.255671937364877,null,0,0,0,0,2.2754046103755976E-2,0.11051063981075651,0.19450293199042579,0.27919971635537782,0.55273158081539908,null,0.19450293199042579,0.27919971635537782,0.55273158081539908]
["2013-05-08T13:00:00","2013-05-08T13:00:00",null,13.025287661916531,13.328859863572431,13.632432065228331,13.936004266884231,14.239576468540131,14.543148670196031,14.846720871851931,15.15029307350783,15.45386527516373,null,0,0,0,0,0,6.5296962247839929E-2,0.15180229371530851,0.2389174840894398,0.51476260647128469,null,0.15180229371530851,0.2389174840894398,0.51476260647128469]
["2013-05-08T14:00:00","2013-05-08T14:00:00",null,13.145037228462746,13.448609430118646,13.752181631774546,14.055753833430446,14.359326035086346,14.662898236742246,14.966470438398146,15.270042640054045,15.573614841709945,null,0,0,0,0,0,1.6150746217823149E-2,0.10523220582550442,0.19481837625249279,0.47303984540857469,null,0.10523220582550442,0.19481837625249279,0.47303984540857469]
["2013-05-08T15:00:00","2013-05-08T15:00:00",null,13.388154540652451,13.691726742308351,13.995298943964251,14.298871145620151,14.602443347276051,14.906015548931951,15.209587750587851,15.51315995224375,15.81673215389965,null,0,0,0,0,0,0,5.320493220194366E-2,0.14533568634293803,0.42599659112567029,null,5.320493220194366E-2,0.14533568634293803,0.42599659112567029]
["2013-05-08T17:00:00","2013-05-08T17:00:00",null,13.562153013840117,13.865725215496017,14.169297417151917,14.472869618807817,14.776441820463717,15.080014022119617,15.383586223775517,15.687158425431416,15.990730627087316,null,0,0,0,0,0,0,4.7453331823591245E-2,0.14220227333974056,0.42538673221900769,null,4.7453331823591245E-2,0.14220227333974056,0.42538673221900769]
["2013-05-08T18:00:00","2013-05-08T18:00:00",null,13.926972672063581,14.230544873719481,14.534117075375381,14.837689277031281,15.141261478687181,15.444833680343081,15.748405881998981,16.05197808365488,16.35555028531078,null,0,0,0,0,0,2.3342875392947634E-3,5.2616102912752184E-2,0.15008837989141205,0.43590154095456968,null,5.2616102912752184E-2,0.15008837989141205,0.43590154095456968]
["2013-05-08T19:00:00","2013-05-08T19:00:00",null,13.484314452548874,13.787886654204774,14.091458855860674,14.395031057516574,14.698603259172474,15.002175460828374,15.305747662484274,15.609319864140174,15.912892065796074,null,0,0,2.2817134956169536E-3,5.3835820726077432E-3,8.3592729447717878E-3,1.3543073651403854E-2,6.6569254104842962E-2,0.16667023326739333,0.45501746323582137,null,6.6569254104842962E-2,0.16667023326739333,0.45501746323582137]
["2013-05-08T20:00:00","2013-05-08T20:00:00",null,13.231504094481398,13.535076296137298,13.838648497793198,14.142220699449098,14.445792901104998,14.749365102760898,15.052937304416798,15.356509506072697,15.660081707728597,null,2.7653946974528056E-3,6.0775594491548346E-3,1.1524230374175949E-2,1.7654363867008596E-2,2.3532141950187751E-2,3.1502366971743745E-2,8.7199308844015597E-2,0.1898659013380431,0.48067359655059266,null,8.7199308844015597E-2,0.1898659013380431,0.48067359655059266]
["2013-05-08T21:00:00","2013-05-08T21:00:00",null,13.127817735862557,13.431389937518457,13.734962139174357,14.038534340830257,14.342106542486157,14.645678744142057,14.949250945797957,15.252823147453856,15.556395349109756,null,1.026245332590851E-2,1.6823693976899194E-2,2.538274828764666E-2,3.4488572652643351E-2,4.320534909442425E-2,5.390942438722636E-2,0.11222455363465315,0.21740418541647996,0.51063028663820875,null,0.11222455363465315,0.21740418541647996,0.51063028663820875]
["2013-05-08T22:00:00","2013-05-08T22:00:00",null,12.862466648682016,13.166038850337916,13.469611051993816,13.773183253649716,14.076755455305616,14.380327656961516,14.683899858617416,14.987472060273316,15.291044261929216,null,2.0398728946990276E-2,3.0061838174971749E-2,4.1565038931676575E-2,5.3499346846539439E-2,6.4918429133359767E-2,7.8209147375110144E-2,0.13900577148412957,0.24656175004019337,0.54208007956627469,null,0.13900577148412957,0.24656175004019337,0.54208007956627469]
["2013-05-08T23:00:00","2013-05-08T23:00:00",null,12.72420562711298,13.02777782876888,13.33135003042478,13.63492223208068,13.938494433736579,14.242066635392479,14.545638837048379,14.849211038704279,15.152783240360179,null,4.6328247288886161E-2,5.8998591815238366E-2,7.3361820548016057E-2,8.8040493542860601E-2,0.10207776320483586,0.11787100592565,0.18107552123511311,0.29093424290426501,0.58867119707354987,null,0.18107552123511311,0.29093424290426501,0.58867119707354987]
["2013-05-09","2013-05-09",null,12.704355324381059,13.007927526036958,13.311499727692858,13.615071929348758,13.918644131004658,14.222216332660558,14.525788534316458,14.829360735972358,15.132932937628258,null,7.2352398909402107E-2,8.8008949116653912E-2,0.10523220582550447,0.12263421428285957,0.13927915651125422,0.1575749237111321,0.22316630060356779,0.33531725057707218,0.63526231458082505,null,0.22316630060356779,0.33531725057707218,0.63526231458082505]
["2013-05-09T01:00:00","2013-05-09T01:00:00",null,12.642170045340611,12.945742246996511,13.249314448652411,13.552886650308311,13.856458851964211,14.160031053620111,14.463603255276011,14.767175456931911,15.070747658587811,null,9.7545880639808652E-2,0.11622018095416675,0.13632449525656129,0.15648138360263364,0.1757550280149188,0.19656383450259599,0.26457361740421093,0.37903782529953894,0.68120151394649542,null,0.26457361740421093,0.37903782529953894,0.68120151394649542]
["2013-05-09T02:00:00","2013-05-09T02:00:00",null,12.444634238431782,12.748206440087682,13.051778641743581,13.355350843399481,13.658923045055381,13.962495246711281,14.266067448367181,14.569639650023081,14.873211851678981,null,0.12722918570030017,0.14884763246061564,0.17176991550414078,0.194618594886517,0.21645785263027928,0.23971660955334242,0.31008170961172327,0.42679608657646151,0.73112582582294383,null,0.31008170961172327,0.42679608657646151,0.73112582582294383]
["2013-05-09T03:00:00","2013-05-09T03:00:00",null,12.349544123670562,12.653116325326462,12.956688526982362,13.260260728638261,13.563832930294161,13.867405131950061,14.170977333605961,14.474549535261861,14.778121736917761,null,0.16051907015708947,0.18501857451094891,0.21069573744319131,0.23616260420072246,0.26050438642354851,0.2861605197383198,0.35881784810105311,0.47772982009152382,0.78416252108511852,null,0.35881784810105311,0.47772982009152382,0.78416252108511852]
["2013-05-09T04:00:00","2013-05-09T04:00:00",null,12.393508622867623,12.697080824523523,13.000653026179423,13.304225227835323,13.607797429491223,13.911369631147123,14.214941832803023,14.518514034458923,14.822086236114822,null,0.19209504078998213,0.21950714716359226,0.24797073441075859,0.27608733296965138,0.30296318409774786,0.3310377234216984,0.40601882451499094,0.52715993595740074,0.83571662831557902,null,0.40601882451499094,0.52715993595740074,0.83571662831557902]
["2013-05-09T05:00:00","2013-05-09T05:00:00",null,12.667595063123581,12.971167264779481,13.274739466435381,13.578311668091281,13.881883869747181,14.185456071403081,14.489028273058981,14.792600474714881,15.096172676370781,null,0.21618446760315466,0.24663535370134221,0.27799051335078812,0.30888302141586926,0.33839808953659178,0.3690066977658128,0.44641671967702012,0.56988160384998909,0.88067795046884212,null,0.44641671967702012,0.56988160384998909,0.88067795046884212]
["2013-05-09T06:00:00","2013-05-09T06:00:00",null,12.860498032947882,13.164070234603782,13.467642436259682,13.771214637915582,14.074786839571482,14.378359041227382,14.681931242883282,14.985503444539182,15.289075646195082,null,0.236173119009458,0.26971535887590081,0.30402517978003962,0.33773565658625138,0.36995303055201334,0.40314828173018258,0.48303979850298256,0.60888102945018852,0.92195908956465855,null,0.48303979850298256,0.60888102945018852,0.92195908956465855]
["2013-05-09T07:00:00","2013-05-09T07:00:00",null,12.933763807630122,13.237336009286022,13.540908210941922,13.844480412597822,14.148052614253722,14.451624815909621,14.755197017565521,15.058769219221421,15.362341420877321,null,0.25335431648336632,0.29004048416174216,0.32734702555551615,0.36391753033780072,0.3988792693835444,0.43470322274560413,0.5171077788062034,0.6453674157625886,0.96076924860761792,null,0.5171077788062034,0.6453674157625886,0.96076924860761792]
["2013-05-09T08:00:00","2013-05-09T08:00:00",null,13.045142556585839,13.348714758241739,13.652286959897639,13.955859161553539,14.259431363209439,14.563003564865339,14.866575766521239,15.170147968177139,15.473720169833038,null,0.26938939980509835,0.30920898048667167,0.34951224237008083,0.38895328993717382,0.42666990887163475,0.46512256441758498,0.55005067457471912,0.68073923234901912,0.99846483792460772,null,0.55005067457471912,0.68073923234901912,0.99846483792460772]
["2013-05-09T09:00:00","2013-05-09T09:00:00",null,13.172054187547717,13.475626389203617,13.779198590859517,14.082770792515417,14.386342994171317,14.689915195827217,14.993487397483117,15.297059599139017,15.600631800794917,null,0.2803563453162895,0.32339345747094478,0.36676704350513806,0.40915223751818841,0.44967631038504441,0.49083127177603408,0.57834602488211651,0.71152659232674464,1,null,0.57834602488211651,0.71152659232674464,1]
["2013-05-09T10:00:00","2013-05-09T10:00:00",null,13.390539511149779,13.694111712805679,13.997683914461579,14.301256116117479,14.604828317773379,14.908400519429279,15.211972721085179,15.515544922741078,15.819117124396978,null,0.28225952569742624,0.32857725817757683,0.37507374240623204,0.42045565690891756,0.46385027256058198,0.50776011384028885,0.59792459874773296,0.73364974990636711,1,null,0.59792459874773296,0.73364974990636711,1]
["2013-05-09T11:00:00","2013-05-09T11:00:00",null,13.47850220453639,13.78207440619229,14.08564660784819,14.38921880950409,14.69279101115999,14.99636321281589,15.29993541447179,15.60350761612769,15.90707981778359,null,0.283657995259256,0.33323531844743082,0.38284418606181236,0.43121230624539747,0.47746694987313476,0.52413167104155889,0.61692485813289344,0.75518407819679811,1,null,0.61692485813289344,0.75518407819679811,1]
["2013-05-09T12:00:00","2013-05-09T12:00:00",null,13.493781846494279,13.797354048150179,14.100926249806079,14.404498451461979,14.708070653117879,15.011642854773779,15.315215056429679,15.618787258085579,15.922359459741479,null,0.28449917995810098,0.33734660866303556,0.39007837447187904,0.44143270033636373,0.49055788674890943,0.53997748780605082,0.635420406698747,0.77621369566792209,1,null,0.635420406698747,0.77621369566792209,1]
["2013-05-09T13:00:00","2013-05-09T13:00:00",null,13.498509220130199,13.802081421786099,14.105653623441999,14.409225825097899,14.712798026753799,15.016370228409698,15.319942430065598,15.623514631721498,15.927086833377398,null,0.28516161290844139,0.34127914713013574,0.39714432594217669,0.45148485748756101,0.50349110149365073,0.55566558243950936,0.65374771832483158,0.79708559100801268,1,null,0.65374771832483158,0.79708559100801268,1]
["2013-05-09T14:00:00","2013-05-09T14:00:00",null,13.387807729566546,13.691379931222446,13.994952132878346,14.298524334534246,14.602096536190146,14.905668737846046,15.209240939501946,15.512813141157846,15.816385342813746,null,0.28812678897186988,0.34745133985791066,0.40638684282073567,0.46367152081207735,0.51849573355929768,0.57336200554146022,0.6740412991844662,0.81987118153797556,1,null,0.6740412991844662,0.81987118153797556,1]
["2013-05-09T15:00:00","2013-05-09T15:00:00",null,13.099846278711565,13.403418480367465,13.706990682023365,14.010562883679265,14.314135085335165,14.617707286991065,14.921279488646965,15.224851690302865,15.528423891958765,null,0.29262712711069044,0.35519023908728431,0.41721709581836453,0.47745643506439911,0.53511964617022123,0.59269873880615875,0.6959857050155841,0.84431811184815719,1,null,0.6959857050155841,0.84431811184815719,1]
["2013-05-09T16:00:00","2013-05-09T16:00:00",null,13.082378928552142,13.385951130208042,13.689523331863942,13.993095533519842,14.296667735175742,14.600239936831642,14.903812138487542,15.207384340143442,15.510956541799342,null,0.26493112090122012,0.33065919030721819,0.39570379714540466,0.45883470879371879,0.51926331459699371,0.57949213903429286,0.68532368895772422,0.8360955314169477,0.99413273672555635,null,0.68532368895772422,0.8360955314169477,0.99413273672555635]
["2013-05-09T17:00:00","2013-05-09T17:00:00",null,13.025788135285083,13.329360336940983,13.632932538596883,13.936504740252783,14.240076941908683,14.543649143564583,14.847221345220483,15.150793546876383,15.454365748532283,null,0.20004423619406703,0.26889520379452703,0.33693653112234867,0.40291695593800009,0.46608992682125672,0.52893693863371083,0.63728152784494141,0.7904717763133442,0.95082223954377654,null,0.63728152784494141,0.7904717763133442,0.95082223954377654]
["2013-05-09T18:00:00","2013-05-09T18:00:00",null,13.093162848649051,13.396735050304951,13.700307251960851,14.003879453616751,14.307451655272651,14.611023856928551,14.914596058584451,15.218168260240351,15.52174046189625,null,0.13457903700645801,0.20653187318390881,0.27753837657515895,0.34635779974941211,0.41225410609517932,0.4776982756653172,0.58854538935561151,0.74413301421572253,0.90678622055924285,null,0.58854538935561151,0.74413301421572253,0.90678622055924285]
["2013-05-09T19:00:00","2013-05-09T19:00:00",null,13.043868321975097,13.347440523630997,13.651012725286897,13.954584926942797,14.258157128598697,14.561729330254597,14.865301531910497,15.168873733566397,15.472445935222296,null,7.0995988582514616E-2,0.14601914891074952,0.21996979874795702,0.29159667585460525,0.36017425842794076,0.42820507094702687,0.54152316469017825,0.69947662151579071,0.86441154135492804,null,0.54152316469017825,0.69947662151579071,0.86441154135492804]
["2013-05-09T20:00:00","2013-05-09T20:00:00",null,13.058381027790309,13.361953229446209,13.665525431102109,13.969097632758009,14.272669834413909,14.576242036069809,14.879814237725709,15.183386439381609,15.486958641037509,null,3.9745977020424483E-3,8.2141685842210377E-2,0.15909957097778862,0.23360750567798083,0.3049399681400336,0.37560999765174574,0.49146216030016759,0.6518445379436949,0.819113745322127,null,0.49146216030016759,0.6518445379436949,0.819113745322127]
["2013-05-09T21:00:00","2013-05-09T21:00:00",null,12.996220397516652,13.299792599172552,13.603364800828452,13.906937002484351,14.210509204140251,14.514081405796151,14.817653607452051,15.121225809107951,15.424798010763851,null,0,2.0482847416874825E-2,0.10041642342461712,0.17776335648341107,0.25181915440797437,0.32508634167737033,0.44344102880485597,0.6062207828400914,0.77579273333161158,null,0.44344102880485597,0.6062207828400914,0.77579273333161158]
["2013-05-09T22:00:00","2013-05-09T22:00:00",null,12.896027686970903,13.199599888626803,13.503172090282703,13.806744291938603,14.110316493594503,14.413888695250403,14.717460896906303,15.021033098562203,15.324605300218103,null,0,0,4.80737055389895E-2,0.12814397406029401,0.20480744455127667,0.28056664149100086,0.40130819020145903,0.5663906873497826,0.73816023286703514,null,0.40130819020145903,0.5663906873497826,0.73816023286703514]
["2013-05-09T23:00:00","2013-05-09T23:00:00",null,12.795393100842118,13.098965302498017,13.402537504153917,13.706109705809817,14.009681907465717,14.313254109121617,14.616826310777517,14.920398512433417,15.223970714089317,null,0,0,0,7.9523498467055337E-2,0.15878412671572181,0.2370353333257742,0.36017425842794049,0.52754898388061655,0.70151612442360156,null,0.36017425842794049,0.52754898388061655,0.70151612442360156]
["2013-05-10","2013-05-10",null,12.939641993742082,13.243214195397982,13.546786397053882,13.850358598709782,14.153930800365682,14.457503002021582,14.761075203677482,15.064647405333382,15.368219606989282,null,0,0,0,2.8284835498661724E-2,0.11018468073995426,0.19094892663780597,0.31650625774915153,0.48619424112365123,0.66239052111857533,null,0.31650625774915153,0.48619424112365123,0.66239052111857533]
["2013-05-10T01:00:00","2013-05-10T01:00:00",null,12.889310872475068,13.192883074130968,13.496455275786868,13.800027477442768,14.103599679098668,14.407171880754568,14.710744082410468,15.014316284066368,15.317888485722268,null,0,0,0,0,6.3540989189001237E-2,0.14679724475718114,0.27474143745149926,0.44672164913035151,0.62511552415100802,null,0.27474143745149926,0.44672164913035151,0.62511552415100802]
["2013-05-10T02:00:00","2013-05-10T02:00:00",null,12.864946876411413,13.168519078067312,13.472091279723212,13.775663481379112,14.079235683035012,14.382807884690912,14.686380086346812,14.989952288002712,15.293524489658612,null,0,0,0,0,1.7748997145628741E-2,0.10348674757540127,0.2338072870439564,0.40805869740969003,0.58863965264734341,null,0.2338072870439564,0.40805869740969003,0.58863965264734341]
["2013-05-10T03:00:00","2013-05-10T03:00:00",null,12.727719850655449,13.031292052311349,13.334864253967249,13.638436455623149,13.942008657279048,14.245580858934948,14.549153060590848,14.852725262246748,15.156297463902648,null,0,0,0,0,0,6.3257089353141061E-2,0.19592243116972652,0.372434525413606,0.55518153125078518,null,0.19592243116972652,0.372434525413606,0.55518153125078518]
["2013-05-10T04:00:00","2013-05-10T04:00:00",null,12.769057520300532,13.072629721956432,13.376201923612332,13.679774125268231,13.983346326924131,14.286918528580031,14.590490730235931,14.894062931891831,15.197635133547731,null,0,0,0,0,0,2.9567642164400422E-2,0.16455675671154507,0.34328747559862816,0.52817950241786193,null,0.16455675671154507,0.34328747559862816,0.52817950241786193]
["2013-05-10T05:00:00","2013-05-10T05:00:00",null,12.910586152296602,13.214158353952502,13.517730555608402,13.821302757264302,14.124874958920202,14.428447160576102,14.732019362232002,15.035591563887902,15.339163765543802,null,0,0,0,0,0,0,0.12821757772144282,0.30925103972161394,0.49635117637531578,null,0.12821757772144282,0.30925103972161394,0.49635117637531578]
["2013-05-10T06:00:00","2013-05-10T06:00:00",null,12.855693039055794,13.159265240711694,13.462837442367594,13.766409644023494,14.069981845679393,14.373554047335293,14.677126248991193,14.980698450647093,15.284270652302993,null,0,0,0,0,0,0,9.1289569442149082E-2,0.2746468041728794,0.46397608027852039,null,9.1289569442149082E-2,0.2746468041728794,0.46397608027852039]
["2013-05-10T07:00:00","2013-05-10T07:00:00",null,12.796252410106931,13.099824611762831,13.40339681341873,13.70696901507463,14.01054121673053,14.31411341838643,14.61768562004233,14.92125782169823,15.22483002335413,null,0,0,0,0,0,0,5.2731765808843235E-2,0.23843380288760388,0.43001324806265512,null,5.2731765808843235E-2,0.23843380288760388,0.43001324806265512]
["2013-05-10T08:00:00","2013-05-10T08:00:00",null,12.89317528409391,13.19674748574981,13.50031968740571,13.80389188906161,14.10746409071751,14.41103629237341,14.71460849402931,15.01818069568521,15.32175289734111,null,0,0,0,0,0,0,1.01047311948749E-2,0.19815157062166586,0.39198118486612737,null,1.01047311948749E-2,0.19815157062166586,0.39198118486612737]
["2013-05-10T09:00:00","2013-05-10T09:00:00",null,12.964083654833136,13.267655856489036,13.571228058144936,13.874800259800836,14.178372461456735,14.481944663112635,14.785516864768535,15.089089066424435,15.392661268080335,null,0,0,0,0,0,0,0,0.15474644016126593,0.35086828271007997,null,-3.5676746039762036E-2,0.15474644016126593,0.35086828271007997]
["2013-05-10T10:00:00","2013-05-10T10:00:00",null,13.098191661191503,13.401763862847403,13.705336064503303,14.008908266159203,14.312480467815103,14.616052669471003,14.919624871126903,15.223197072782803,15.526769274438703,null,0,0,0,0,0,0,0,0.10991129571282957,0.30829382213978945,null,-4.7179946796466685E-2,0.10991129571282957,0.30829382213978945]
["2013-05-10T11:00:00","2013-05-10T11:00:00",null,13.424864885143016,13.728437086798916,14.032009288454816,14.335581490110716,14.639153691766616,14.942725893422516,15.246298095078416,15.549870296734316,15.853442498390216,null,0,0,0,0,0,0,0,4.8042161112782769E-2,0.24884309354892192,null,-6.4382173887846117E-2,4.8042161112782769E-2,0.24884309354892192]
["2013-05-10T12:00:00","2013-05-10T12:00:00",null,13.391720262726373,13.695292464382273,13.998864666038173,14.302436867694073,14.606009069349973,14.909581271005873,15.213153472661773,15.516725674317673,15.820297875973573,null,0,0,0,0,0,0,0,0,0.19042281621413948,null,-6.3320178205554356E-2,-1.2786007422443388E-2,0.19042281621413948]
["2013-05-10T13:00:00","2013-05-10T13:00:00",null,13.415852198560511,13.719424400216411,14.022996601872311,14.326568803528211,14.630141005184111,14.933713206840011,15.237285408495911,15.540857610151811,15.844429811807711,null,0,0,0,0,0,0,0,0,0.13625052160852408,null,-5.9082710285122866E-2,-5.6580185806059106E-2,0.13625052160852408]
["2013-05-10T14:00:00","2013-05-10T14:00:00",null,13.34702457651602,13.65059677817192,13.95416897982782,14.25774118148372,14.56131338313962,14.86488558479552,15.16845778645142,15.47202998810732,15.775602189763219,null,0,0,0,0,0,0,0,0,0.10147804912002055,null,-3.9619799315597608E-2,-3.7148819262740537E-2,0.10147804912002055]
["2013-05-10T15:00:00","2013-05-10T15:00:00",null,13.76400332349284,14.06757552514874,14.37114772680464,14.67471992846054,14.97829213011644,15.28186433177234,15.58543653342824,15.88900873508414,16.19258093674004,null,0,0,0,0,0,0,0,0,0.10238232267127888,null,-4.3215863903159814E-3,-1.6613397802187956E-3,0.10238232267127888]
["2013-05-10T16:00:00","2013-05-10T16:00:00",null,13.672693870598582,13.976266072254482,14.279838273910382,14.583410475566282,14.886982677222182,15.190554878878082,15.494127080533982,15.797699282189882,16.101271483845782,null,0,0,0,0,0,0,0,0,0.10176194895588073,null,-5.8462336569724705E-3,-3.1859870468752853E-3,0.10176194895588073]
["2013-05-10T17:00:00","2013-05-10T17:00:00",null,13.545737560248122,13.849309761904022,14.152881963559922,14.456454165215822,14.760026366871722,15.063598568527622,15.367170770183522,15.670742971839422,15.974315173495322,null,0,0,0,0,0,0,0,0,0.10390696993793537,null,-3.0703241507841032E-3,-4.1007754068691788E-4,0.10390696993793537]
["2013-05-10T18:00:00","2013-05-10T18:00:00",null,13.396728940350046,13.700301142005946,14.003873343661846,14.307445545317746,14.611017746973646,14.914589948629546,15.218162150285446,15.521734351941346,15.825306553597246,null,0,0,0,0,0,0,0,2.2922283043525153E-3,0.10873326714755832,null,-3.4698868827354591E-4,2.2922283043525153E-3,0.10873326714755832]
["2013-05-10T19:00:00","2013-05-10T19:00:00",null,13.124947670045858,13.428519871701758,13.732092073357657,14.035664275013557,14.339236476669457,14.642808678325357,14.946380879981257,15.249953081637157,15.553525283293057,null,0,0,0,1.4089843705653077E-3,4.3110715815804189E-3,7.0974958965043487E-3,9.7682573153370957E-3,1.462609895116674E-2,0.12352760303849405,null,9.7682573153370957E-3,1.462609895116674E-2,0.12352760303849405]
["2013-05-10T20:00:00","2013-05-10T20:00:00",null,12.924038090809082,13.227610292464982,13.531182494120882,13.834754695776782,14.138326897432682,14.441899099088582,14.745471300744482,15.049043502400382,15.352615704056282,null,3.7432719098600712E-3,6.9397737654709182E-3,9.9890682987838972E-3,1.4321169497835441E-2,2.0020195832510045E-2,2.5477381566266721E-2,3.0724271125312157E-2,3.8042578005263311E-2,0.14930991405809207,null,3.0724271125312157E-2,3.8042578005263311E-2,0.14930991405809207]
["2013-05-10T21:00:00","2013-05-10T21:00:00",null,12.754684646358946,13.058256848014846,13.361829049670746,13.665401251326646,13.968973452982546,14.272545654638446,14.576117856294346,14.879690057950246,15.183262259606146,null,1.2859611083592324E-2,1.9221070368607332E-2,2.5288115009026606E-2,3.2501273801622134E-2,4.0955180025013985E-2,4.9051582751396719E-2,5.6832541215712601E-2,6.6579768913578571E-2,0.18017087769696655,null,5.6832541215712601E-2,6.6579768913578571E-2,0.18017087769696655]
["2013-05-10T22:00:00","2013-05-10T22:00:00",null,12.519319464059432,12.822891665715332,13.126463867371232,13.430036069027132,13.733608270683032,14.037180472338932,14.340752673994832,14.644324875650732,14.947897077306632,null,2.8684398230613129E-2,3.8126696475147805E-2,4.7127372752788874E-2,5.7137470669043899E-2,6.8262138311268497E-2,7.8924154369128349E-2,8.9155063268830187E-2,0.10125760812346205,0.21709888597626029,null,8.9155063268830187E-2,0.10125760812346205,0.21709888597626029]
["2013-05-10T23:00:00","2013-05-10T23:00:00",null,12.354471694958606,12.658043896614506,12.961616098270406,13.265188299926306,13.568760501582206,13.872332703238106,14.175904904894006,14.479477106549906,14.783049308205806,null,5.1491018378047107E-2,6.3887977877274696E-2,7.5706622896046377E-2,8.8419026657340832E-2,0.10210930763104256,0.11523178893302394,0.12781801498949164,0.14217072891353377,0.26017805736585781,null,0.12781801498949164,0.14217072891353377,0.26017805736585781]
["2013-05-11","2013-05-11",null,12.172793499546446,12.476365701202345,12.779937902858245,13.083510104514145,13.387082306170045,13.690654507825945,13.994226709481845,14.297798911137745,14.601371112793645,null,7.8472017593499199E-2,9.3771064303741894E-2,0.10834458921123082,0.12369620996515134,0.13989953022665239,0.15541938792034188,0.17030835708989767,0.18685866603967227,0.30697947104784429,null,0.17030835708989767,0.18685866603967227,0.30697947104784429]
["2013-05-11T01:00:00","2013-05-11T01:00:00",null,11.99675989898514,12.30033210064104,12.603904302296939,12.907476503952839,13.211048705608739,13.514620907264639,13.818193108920539,14.121765310576439,14.425337512232339,null,0.10961688106823383,0.12775492613707828,0.14503075688960662,0.16294799097500429,0.18161177648062682,0.19947643652234665,0.21660505995257714,0.23530038988440638,0.35747158259601297,null,0.21660505995257714,0.23530038988440638,0.35747158259601297]
["2013-05-11T02:00:00","2013-05-11T02:00:00",null,11.965190546971199,12.268762748627099,12.572334950282999,12.875907151938899,13.179479353594798,13.483051555250698,13.786623756906598,14.090195958562498,14.393768160218398,null,0.1421391844873271,0.16309519829730215,0.18304179046866326,0.20351412307680247,0.22460682940033982,0.24479526217261885,0.26414251024605295,0.28496183154246568,0.40917289714877131,null,0.26414251024605295,0.28496183154246568,0.40917289714877131]
["2013-05-11T03:00:00","2013-05-11T03:00:00",null,11.910513281314765,12.214085482970665,12.517657684626565,12.821229886282465,13.124802087938365,13.428374289594265,13.731946491250165,14.035518692906065,14.339090894561965,null,0.17703783468065737,0.20075924318808522,0.22333453754333682,0.24631990943927537,0.2697994773457853,0.29228013842241685,0.31380395190411225,0.33671572013890183,0.46292459940496422,null,0.31380395190411225,0.33671572013890183,0.46292459940496422]
["2013-05-11T04:00:00","2013-05-11T04:00:00",null,11.770117892285169,12.073690093941069,12.377262295596969,12.680834497252869,12.984406698908769,13.287978900564669,13.591551102220569,13.895123303876469,14.198695505532369,null,0.21161052580318523,0.23813938824300812,0.26338544401709246,0.28891539962703705,0.3148238883514618,0.33961780734991698,0.36334973066608039,0.38837497545671795,0.51660269800000824,null,0.36334973066608039,0.38837497545671795,0.51660269800000824]
["2013-05-11T05:00:00","2013-05-11T05:00:00",null,11.931325313630673,12.234897515286573,12.538469716942473,12.842041918598373,13.145614120254272,13.449186321910172,13.752758523566072,14.056330725221972,14.359902926877872,null,0.24232428211976184,0.27171317253565758,0.2996825637722525,0.32780967713988085,0.35618914591716272,0.38334889688111934,0.40934150407542857,0.43652228465685633,0.56682142452105233,null,0.40934150407542857,0.43652228465685633,0.56682142452105233]
["2013-05-11T06:00:00","2013-05-11T06:00:00",null,11.929164748759371,12.232736950415271,12.536309152071171,12.839881353727071,13.143453555382971,13.447025757038871,13.750597958694771,14.054170160350671,14.357742362006571,null,0.269999258711761,0.30233229557361413,0.33309862593386852,0.36388598591159405,0.39481003840288192,0.4243881953760178,0.45270457530088626,0.48210398052551762,0.61452711175429708,null,0.45270457530088626,0.48210398052551762,0.61452711175429708]
["2013-05-11T07:00:00","2013-05-11T07:00:00",null,11.999735350751477,12.303307552407377,12.606879754063277,12.910451955719177,13.214024157375077,13.517596359030977,13.821168560686877,14.124740762342777,14.428312963998676,null,0.29788453147847144,0.33314068516881079,0.36668292503525357,0.40010950200560513,0.43355710859342789,0.46555367157574301,0.49617279461369956,0.52778030967279899,0.66231691745742638,null,0.49617279461369956,0.52778030967279899,0.66231691745742638]
["2013-05-11T08:00:00","2013-05-11T08:00:00",null,12.182063757854159,12.485635959510059,12.789208161165959,13.092780362821859,13.396352564477759,13.699924766133659,14.003496967789559,14.307069169445459,14.610641371101359,null,0.32140615861992361,0.3596485179911626,0.39602975621620712,0.43215863903159812,0.4681928885683691,0.50266043160354135,0.53564538660699934,0.56951358554424458,0.70621624392839777,null,0.53564538660699934,0.56951358554424458,0.70621624392839777]
["2013-05-11T09:00:00","2013-05-11T09:00:00",null,12.301754365967891,12.605326567623791,12.908898769279691,13.212470970935591,13.516043172591491,13.819615374247391,14.123187575903291,14.426759777559191,14.730331979215091,null,0.34012251816922395,0.38142468688251152,0.42073955674477781,0.45965486387509275,0.4983493600219609,0.53536148677113915,0.57078587740124753,0.60698836387778754,0.74593067652261547,null,0.57078587740124753,0.60698836387778754,0.74593067652261547]
["2013-05-11T10:00:00","2013-05-11T10:00:00",null,12.441808990249219,12.745381191905119,13.048953393561019,13.352525595216919,13.656097796872819,13.959669998528719,14.263242200184619,14.566814401840519,14.870386603496419,null,0.35703033061600764,0.40142385309755046,0.44368286940577406,0.48541614527721966,0.52680243246039171,0.5663906873497826,0.60427554322401245,0.6428438616660539,0.78404685818902775,null,0.60427554322401245,0.6428438616660539,0.78404685818902775]
["2013-05-11T11:00:00","2013-05-11T11:00:00",null,12.485412766005592,12.788984967661492,13.092557169317391,13.396129370973291,13.699701572629191,14.003273774285091,14.306845975940991,14.610418177596891,14.913990379252791,null,0.37781810748621369,0.4252714393098051,0.47043254282904379,0.51495224301541331,0.558988261999947,0.60112110060334389,0.64143487729548854,0.68233748327682475,0.82578013406047335,null,0.64143487729548854,0.68233748327682475,0.82578013406047335]
["2013-05-11T12:00:00","2013-05-11T12:00:00",null,12.409063031637105,12.712635233293005,13.016207434948905,13.319779636604805,13.623351838260705,13.926924039916605,14.230496241572505,14.534068443228405,14.837640644884305,null,0.38517847360110707,0.4357021295754826,0.48379686473194311,0.53111350404197211,0.57782028444533851,0.62249770676274141,0.66526143389027204,0.70850884221963861,0.85419114726396184,null,0.66526143389027204,0.70850884221963861,0.85419114726396184]
["2013-05-11T13:00:00","2013-05-11T13:00:00",null,12.519087842534434,12.822660044190334,13.126232245846234,13.429804447502134,13.733376649158034,14.036948850813934,14.340521052469834,14.644093254125734,14.947665455781634,null,0.32745217364287171,0.38111975742918025,0.43221121307527594,0.48239839517011335,0.53183902584472587,0.57913463553728373,0.62441140195261369,0.67006670148242398,0.81805174963983529,null,0.62441140195261369,0.67006670148242398,0.81805174963983529]
["2013-05-11T14:00:00","2013-05-11T14:00:00",null,12.647426124015023,12.950998325670923,13.254570527326823,13.558142728982723,13.861714930638623,14.165287132294523,14.468859333950423,14.772431535606323,15.076003737262223,null,0.26616135352328085,0.32298337993025794,0.37709258568345994,0.43016082537184136,0.48235633593517113,0.53229116262035503,0.58009148313221992,0.628175703479945,0.77848452436791549,null,0.58009148313221992,0.628175703479945,0.77848452436791549]
["2013-05-11T15:00:00","2013-05-11T15:00:00",null,12.615084363428281,12.918656565084181,13.222228766740081,13.525800968395981,13.82937317005188,14.13294537170778,14.43651757336368,14.74008977501958,15.04366197667548,null,0.20316713438852893,0.26319617745985241,0.32036519255510298,0.37635654907197064,0.43134899875895988,0.48396510167171208,0.53433103551505412,0.58487572110690067,0.73753985915163711,null,0.53433103551505412,0.58487572110690067,0.73753985915163711]
["2013-05-11T16:00:00","2013-05-11T16:00:00",null,12.809317084478156,13.112889286134056,13.416461487789956,13.720033689445856,14.023605891101756,14.327178092757656,14.630750294413556,14.934322496069456,15.237894697725356,null,0.13584081405472548,0.19912944783407316,0.25942136112378567,0.31838840851281736,0.37623037136714388,0.43156980974240666,0.4845539309609036,0.53760114103181389,0.69267317027699404,null,0.4845539309609036,0.53760114103181389,0.69267317027699404]
["2013-05-11T17:00:00","2013-05-11T17:00:00",null,12.778028137643952,13.081600339299852,13.385172540955752,13.688744742611652,13.992316944267552,14.295889145923452,14.599461347579352,14.903033549235252,15.206605750891152,null,6.6716461427140911E-2,0.1333172599581906,0.19677413067730729,0.25875892817344526,0.31949246343005133,0.37759729650276691,0.43323114952262548,0.48882294330754178,0.64634492298810786,null,0.43323114952262548,0.48882294330754178,0.64634492298810786]
["2013-05-11T18:00:00","2013-05-11T18:00:00",null,12.676602482854532,12.980174684510432,13.283746886166332,13.587319087822232,13.890891289478132,14.194463491134032,14.498035692789932,14.801607894445832,15.105180096101732,null,0,6.5496743613815717E-2,0.13218166061474995,0.19725781187914312,0.26094600839044213,0.32186881020428831,0.38021548387792187,0.43840443542052199,0.59841842477141627,null,0.38021548387792187,0.43840443542052199,0.59841842477141627]
["2013-05-11T19:00:00","2013-05-11T19:00:00",null,12.593676121015422,12.897248322671322,13.200820524327222,13.504392725983122,13.807964927639022,14.111537129294922,14.415109330950822,14.718681532606722,15.022253734262621,null,0,7.675810376960579E-4,7.0627970276770008E-2,0.13875341607447617,0.20534369979679029,0.26904241111682481,0.33005984620929113,0.3908038962746328,0.55326783606091301,null,0.33005984620929113,0.3908038962746328,0.55326783606091301]
["2013-05-11T20:00:00","2013-05-11T20:00:00",null,12.394656556531604,12.698228758187504,13.001800959843404,13.305373161499304,13.608945363155204,13.912517564811104,14.216089766467004,14.519661968122904,14.823234169778804,null,0,0,1.6581853375981337E-2,8.7693504854587101E-2,0.15713330174423853,0.2235553485267836,0.28718045618566929,0.35042703073007475,0.51528834690806313,null,0.28718045618566929,0.35042703073007475,0.51528834690806313]
["2013-05-11T21:00:00","2013-05-11T21:00:00",null,12.258718547266366,12.562290748922265,12.865862950578165,13.169435152234065,13.473007353889965,13.776579555545865,14.080151757201765,14.383723958857665,14.687296160513565,null,0,0,0,4.1869968385007915E-2,0.11407515997211215,0.18313642374728328,0.24929560031143941,0.31496058086502415,0.48214566977357171,null,0.24929560031143941,0.31496058086502415,0.48214566977357171]
["2013-05-11T22:00:00","2013-05-11T22:00:00",null,12.082880009152685,12.386452210808585,12.690024412464485,12.993596614120385,13.297168815776285,13.600741017432185,13.904313219088085,14.207885420743985,14.511457622399885,null,0,0,0,2.6917910363039102E-3,7.753619961603421E-2,0.1491315322964758,0.21770911486981118,0.28568735334521955,0.45510158170570625,null,0.21770911486981118,0.28568735334521955,0.45510158170570625]
["2013-05-11T23:00:00","2013-05-11T23:00:00",null,12.03007066935637,12.33364287101227,12.63721507266817,12.94078727432407,13.244359475979969,13.547931677635869,13.851503879291769,14.155076080947669,14.458648282603569,null,0,0,0,0,4.8683564445652083E-2,0.12264472909159513,0.19349351035181189,0.26363779942674603,0.43512344510813844,null,0.19349351035181189,0.26363779942674603,0.43512344510813844]
["2013-05-12","2013-05-12",null,11.90575022034872,12.20932242200462,12.51289462366052,12.81646682531642,13.12003902697232,13.42361122862822,13.72718343028412,14.03075563194002,14.334327833595919,null,0,0,0,0,2.1807713317555617E-2,9.8113680311528992E-2,0.17121263064115602,0.24350194069814482,0.41703797408297183,null,0.17121263064115602,0.24350194069814482,0.41703797408297183]
["2013-05-12T01:00:00","2013-05-12T01:00:00",null,11.797355276043548,12.100927477699448,12.404499679355348,12.708071881011248,13.011644082667148,13.315216284323048,13.618788485978948,13.922360687634848,14.225932889290748,null,0,0,0,0,0,7.7735980982009845E-2,0.15299046710242709,0.22735119448032159,0.4028745267161698,null,0.15299046710242709,0.22735119448032159,0.4028745267161698]
["2013-05-12T02:00:00","2013-05-12T02:00:00",null,11.571854886339263,11.875427087995163,12.178999289651063,12.482571491306963,12.786143692962863,13.089715894618763,13.393288096274663,13.696860297930563,14.000432499586463,null,0,0,0,0,0,5.7726299958235361E-2,0.13517838110438507,0.2116315554206564,0.38916321612499694,null,0.13517838110438507,0.2116315554206564,0.38916321612499694]
["2013-05-12T03:00:00","2013-05-12T03:00:00",null,11.355574540679186,11.659146742335086,11.962718943990986,12.266291145646885,12.569863347302785,12.873435548958685,13.177007750614585,13.480579952270485,13.784152153926385,null,0,0,0,0,0,4.0587161719269307E-2,0.12020529346494478,0.19871937029338627,0.37822781504001246,null,0.12020529346494478,0.19871937029338627,0.37822781504001246]
["2013-05-12T04:00:00","2013-05-12T04:00:00",null,11.188853676879294,11.492425878535194,11.795998080191094,12.099570281846994,12.403142483502894,12.706714685158794,13.010286886814693,13.313859088470593,13.617431290126493,null,0,0,0,0,0,2.4425900692710518E-2,0.10621008303791177,0.18679557718725895,0.3682808059761708,null,0.10621008303791177,0.18679557718725895,0.3682808059761708]
["2013-05-12T05:00:00","2013-05-12T05:00:00",null,11.105404587884083,11.408976789539983,11.712548991195883,12.016121192851783,12.319693394507683,12.623265596163582,12.926837797819482,13.230409999475382,13.533982201131282,null,0,0,0,0,0,5.7305707608812859E-3,8.9754407366757244E-2,0.17247440768942351,0.35601002418176997,null,8.9754407366757244E-2,0.17247440768942351,0.35601002418176997]
["2013-05-12T06:00:00","2013-05-12T06:00:00",null,10.994017725459754,11.297589927115654,11.601162128771554,11.904734330427454,12.208306532083354,12.511878733739254,12.815450935395154,13.119023137051053,13.422595338706953,null,0,0,0,0,0,0,7.4928527049614835E-2,0.15976200392812906,0.34532697850643895,null,7.4928527049614835E-2,0.15976200392812906,0.34532697850643895]
["2013-05-12T07:00:00","2013-05-12T07:00:00",null,11.2286903508622,11.5322625525181,11.835834754174,12.1394069558299,12.4429791574858,12.7465513591417,13.0501235607976,13.3536957624535,13.657267964109399,null,0,0,0,0,0,0,5.9261462033627463E-2,0.14619790065925409,0.33376068889732075,null,5.9261462033627463E-2,0.14619790065925409,0.33376068889732075]
["2013-05-12T08:00:00","2013-05-12T08:00:00",null,11.321217904379626,11.624790106035526,11.928362307691426,12.231934509347326,12.535506711003226,12.839078912659126,13.142651114315026,13.446223315970926,13.749795517626826,null,0,0,0,0,0,0,3.7117274836533896E-2,0.12628285291409966,0.31598014732548541,null,3.7117274836533896E-2,0.12628285291409966,0.31598014732548541]
["2013-05-12T09:00:00","2013-05-12T09:00:00",null,11.52953789579108,11.83311009744698,12.13668229910288,12.44025450075878,12.74382670241468,13.04739890407058,13.350971105726479,13.654543307382379,13.958115509038279,null,0,0,0,0,0,0,9.6946536541882081E-3,0.10117348965357761,0.29308940870816691,null,9.6946536541882081E-3,0.10117348965357761,0.29308940870816691]
["2013-05-12T10:00:00","2013-05-12T10:00:00",null,11.589119552279577,11.892691753935477,12.196263955591377,12.499836157247277,12.803408358903177,13.106980560559077,13.410552762214976,13.714124963870876,14.017697165526776,null,0,0,0,0,0,0,0,7.6705529725924843E-2,0.27081904380624661,null,-1.7065534577817076E-2,7.6705529725924843E-2,0.27081904380624661]
["2013-05-12T11:00:00","2013-05-12T11:00:00",null,11.624462883530061,11.928035085185961,12.231607286841861,12.535179488497761,12.838751690153661,13.142323891809561,13.445896093465461,13.74946829512136,14.05304049677726,null,0,0,0,0,0,0,0,5.0839100236442329E-2,0.24717123895996768,null,-2.8179687411306154E-2,5.0839100236442329E-2,0.24717123895996768]
["2013-05-12T12:00:00","2013-05-12T12:00:00",null,11.749489196306646,12.053061397962546,12.356633599618446,12.660205801274346,12.963778002930246,13.267350204586146,13.570922406242046,13.874494607897946,14.178066809553846,null,0,0,0,0,0,0,0,2.3037945939616406E-2,0.22160973892381647,null,-3.0145956644856246E-2,2.3037945939616406E-2,0.22160973892381647]
["2013-05-12T13:00:00","2013-05-12T13:00:00",null,11.825341783431449,12.128913985087349,12.432486186743249,12.736058388399149,13.039630590055049,13.343202791710949,13.646774993366849,13.950347195022749,14.253919396678649,null,0,0,0,0,0,0,0,0,0.19325129976400576,null,-3.3037529047135798E-2,-7.6022067158112543E-3,0.19325129976400576]
["2013-05-12T14:00:00","2013-05-12T14:00:00",null,11.89603486067397,12.19960706232987,12.50317926398577,12.806751465641669,13.110323667297569,13.413895868953469,13.717468070609369,14.021040272265269,14.324612473921169,null,0,0,0,0,0,0,0,0,0.16234827689018905,null,-3.5666231231026295E-2,-3.3237310413111475E-2,0.16234827689018905]
["2013-05-12T15:00:00","2013-05-12T15:00:00",null,12.059269445489093,12.362841647144993,12.666413848800893,12.969986050456793,13.273558252112693,13.577130453768593,13.880702655424493,14.184274857080393,14.487847058736293,null,0,0,0,0,0,0,0,0,0.12846956314420829,null,-3.8726040573074841E-2,-3.625506052021777E-2,0.12846956314420829]
["2013-05-12T16:00:00","2013-05-12T16:00:00",null,12.139466458651494,12.443038660307394,12.746610861963294,13.050183063619194,13.353755265275094,13.657327466930994,13.960899668586894,14.264471870242794,14.568044071898694,null,0,0,0,0,0,0,0,0,9.1688762187212419E-2,null,-4.1722761062710008E-2,-3.9199206966175126E-2,9.1688762187212419E-2]
["2013-05-12T17:00:00","2013-05-12T17:00:00",null,12.174964466992911,12.478536668648811,12.782108870304711,13.085681071960611,13.389253273616511,13.692825475272411,13.996397676928311,14.299969878584211,14.603542080240111,null,0,0,0,0,0,0,0,0,5.379339150424698E-2,null,-4.2868875214886262E-2,-4.033480630961582E-2,5.379339150424698E-2]
["2013-05-12T18:00:00","2013-05-12T18:00:00",null,12.213661288847206,12.517233490503106,12.820805692159006,13.124377893814906,13.427950095470806,13.731522297126705,14.035094498782605,14.338666700438505,14.642238902094405,null,0,0,0,0,0,0,0,0,1.4552125303129604E-2,null,-4.4267344776716011E-2,-4.1701731445238879E-2,1.4552125303129604E-2]
["2013-05-12T19:00:00","2013-05-12T19:00:00",null,12.140941087041845,12.444513288697745,12.748085490353645,13.051657692009545,13.355229893665445,13.658802095321345,13.962374296977245,14.265946498633145,14.569518700289045,null,0,0,0,0,0,0,0,0,0,null,-4.1617612975354386E-2,-3.9094058878819504E-2,-2.2123527566510641E-2]
["2013-05-12T20:00:00","2013-05-12T20:00:00",null,11.894216744108867,12.197788945764767,12.501361147420667,12.804933349076567,13.108505550732467,13.412077752388367,13.715649954044267,14.019222155700167,14.322794357356067,null,0,0,0,0,0,0,0,0,0,null,-3.8168755710090055E-2,-3.5676746039761856E-2,-3.3289884456789286E-2]
["2013-05-12T21:00:00","2013-05-12T21:00:00",null,11.722603078837199,12.026175280493099,12.329747482148999,12.633319683804899,12.936891885460799,13.240464087116699,13.544036288772599,13.847608490428499,14.151180692084399,null,0,0,0,0,0,0,0,0,0,null,-3.4688354018619028E-2,-3.2238403583233086E-2,-2.990411604393832E-2]
["2013-05-12T22:00:00","2013-05-12T22:00:00",null,11.569637499158789,11.873209700814689,12.176781902470589,12.480354104126489,12.783926305782389,13.087498507438289,13.391070709094189,13.694642910750089,13.998215112405989,null,0,0,0,0,0,0,0,0,0,null,-2.6076725664193754E-2,-2.3795012168576799E-2,-2.1607931951579906E-2]
["2013-05-12T23:00:00","2013-05-12T23:00:00",null,11.35007259453913,11.65364479619503,11.95721699785093,12.26078919950683,12.56436140116273,12.86793360281863,13.171505804474529,13.475078006130429,13.778650207786329,null,0,0,0,0,0,0,0,0,0,null,-2.0482847416874773E-2,-1.8285252391142315E-2,-1.6192805452765476E-2]
["2013-05-13","2013-05-13",null,11.284692084193658,11.588264285849558,11.891836487505458,12.195408689161358,12.498980890817258,12.802553092473158,13.106125294129058,13.409697495784958,13.713269697440857,null,0,0,0,0,0,0,0,0,0,null,-1.7780541571835336E-2,-1.563552058978069E-2,-1.35851328863461E-2]
["2013-05-13T01:00:00","2013-05-13T01:00:00",null,11.241798466976615,11.545370668632515,11.848942870288415,12.152515071944315,12.456087273600215,12.759659475256115,13.063231676912014,13.366803878567914,13.670376080223814,null,0,0,0,0,0,0,0,0,0,null,-1.6140231409087668E-2,-1.4037269661975266E-2,-1.2018426384747363E-2]
["2013-05-13T02:00:00","2013-05-13T02:00:00",null,11.174230257861714,11.477802459517614,11.781374661173514,12.084946862829414,12.388519064485314,12.692091266141214,12.995663467797113,13.299235669453013,13.602807871108913,null,0,0,0,0,0,0,0,0,0,null,-1.6224349878972161E-2,-1.4089843705653077E-2,-1.2060485619689611E-2]
["2013-05-13T03:00:00","2013-05-13T03:00:00",null,11.069015895816291,11.372588097472191,11.676160299128091,11.979732500783991,12.28330470243989,12.58687690409579,12.89044910575169,13.19402130740759,13.49759350906349,null,0,0,0,0,0,0,0,0,0,null,-1.4909998787026913E-2,-1.279652223117895E-2,-1.078819376268661E-2]
["2013-05-13T04:00:00","2013-05-13T04:00:00",null,11.029005130943597,11.332577332599497,11.636149534255397,11.939721735911297,12.243293937567197,12.546866139223097,12.850438340878997,13.154010542534897,13.457582744190796,null,0,0,0,0,2.1345061733190856E-3,4.4267344776716009E-3,6.6032998859329346E-3,8.6747172068386488E-3,1.0662016057859866E-2,null,6.6032998859329346E-3,8.6747172068386488E-3,1.0662016057859866E-2]
["2013-05-13T05:00:00","2013-05-13T05:00:00",null,11.101191572746909,11.404763774402809,11.708335976058709,12.011908177714609,12.315480379370509,12.619052581026409,12.922624782682309,13.226196984338209,13.529769185994109,null,3.9115088496290633E-2,4.2090779368454678E-2,4.4908748109585291E-2,4.7579509528418037E-2,5.2258599415743123E-2,5.6979748538010459E-2,6.1459057059359876E-2,6.5728069405998041E-2,6.9818330004131665E-2,null,6.1459057059359876E-2,6.5728069405998041E-2,6.9818330004131665E-2]
["2013-05-13T06:00:00","2013-05-13T06:00:00",null,11.22331349540187,11.52688569705777,11.83045789871367,12.13403010036957,12.43760230202547,12.74117450368137,13.044746705337269,13.348318906993169,13.651891108649069,null,7.6022067158113243E-2,8.1994478519912456E-2,8.766196042838037E-2,9.3035027692252553E-2,0.10027973091105477,0.10745083046870804,0.11426442652935223,0.12075206351919397,0.12697683029064669,null,0.11426442652935223,0.12075206351919397,0.12697683029064669]
["2013-05-13T07:00:00","2013-05-13T07:00:00",null,11.148551304336831,11.452123505992729,11.755695707648629,12.059267909304529,12.362840110960429,12.666412312616329,12.969984514272229,13.273556715928128,13.577128917584028,null,7.8450987976028064E-2,8.6999527478039962E-2,9.5095930204422696E-2,0.10279277019885409,0.11223506844338876,0.12149861493941887,0.13031002465981983,0.13871135683953387,0.14675518552223882,null,0.13031002465981983,0.13871135683953387,0.14675518552223882]
["2013-05-13T08:00:00","2013-05-13T08:00:00",null,11.771144208891794,12.074716410547694,12.378288612203594,12.681860813859494,12.985433015515394,13.289005217171294,13.592577418827194,13.896149620483094,14.199721822138994,null,0.11194065379879303,0.1234543693642334,0.13436874083174677,0.14475737186248203,0.15676528343849383,0.16846826556117431,0.17962447762960559,0.19025494926125877,0.20043328411728281,null,0.17962447762960559,0.19025494926125877,0.20043328411728281]
["2013-05-13T09:00:00","2013-05-13T09:00:00",null,12.118614369781724,12.422186571437624,12.725758773093524,13.029330974749424,13.332903176405324,13.636475378061224,13.940047579717124,14.243619781373024,14.547191983028924,null,0.14036218181101712,0.15488313267482823,0.16866804692715001,0.18178001342039582,0.19639559756282698,0.21059058935583566,0.22413366300723953,0.23704584813450966,0.2494112632075306,null,0.22413366300723953,0.23704584813450966,0.2494112632075306]
["2013-05-13T10:00:00","2013-05-13T10:00:00",null,12.413400066374438,12.716972268030338,13.020544469686238,13.324116671342138,13.627688872998037,13.931261074653937,14.234833276309837,14.538405477965737,14.841977679621637,null,0.16328446485454226,0.18087573986913749,0.19759428575868107,0.21350319137558638,0.23078953693685028,0.24755014206133608,0.2635326513393903,0.27878963881469077,0.29340522295712201,null,0.2635326513393903,0.27878963881469077,0.29340522295712201]
["2013-05-13T11:00:00","2013-05-13T11:00:00",null,12.553893677347565,12.857465879003465,13.161038080659365,13.464610282315265,13.768182483971165,14.071754685627065,14.375326887282965,14.678899088938865,14.982471290594765,null,0.18362010494911918,0.20430273373196961,0.22398645568494169,0.2427133300429776,0.26270198144928092,0.28203871471397945,0.30049220404489074,0.31812553829442819,0.33501232112374085,null,0.30049220404489074,0.31812553829442819,0.33501232112374085]
["2013-05-13T12:00:00","2013-05-13T12:00:00",null,12.696727702158773,13.000299903814673,13.303872105470573,13.607444307126473,13.911016508782373,14.214588710438273,14.518160912094173,14.821733113750073,15.125305315405972,null,0.20150579460831014,0.22531132158562248,0.24797073441075862,0.26954712193613184,0.29225910880494571,0.31420351463606361,0.33515952844603863,0.35517972427854866,0.37436925022094941,null,0.33515952844603863,0.35517972427854866,0.37436925022094941]
["2013-05-13T13:00:00","2013-05-13T13:00:00",null,12.92280880764168,13.22638100929758,13.529953210953479,13.833525412609379,14.137097614265279,14.440669815921179,14.744242017577079,15.047814219232979,15.351386420888879,null,0.21426025760454684,0.24126228643747002,0.26697099379591915,0.2914704981497786,0.31697942414225194,0.34159459139220261,0.36511621853365478,0.38759687961028633,0.40915223751818852,null,0.36511621853365478,0.38759687961028633,0.40915223751818852]
["2013-05-13T14:00:00","2013-05-13T14:00:00",null,12.871822680731002,13.175394882386902,13.478967084042802,13.782539285698702,14.086111487354602,14.389683689010502,14.693255890666402,14.996828092322302,15.300400293978202,null,0.22337659677827909,0.25354358304060642,0.28228055531489743,0.30967163207103643,0.33794595276096256,0.36520033700353927,0.39126654785899745,0.41618664456227938,0.44007629000947635,null,0.39126654785899745,0.41618664456227938,0.44007629000947635]
["2013-05-13T15:00:00","2013-05-13T15:00:00",null,13.147583831588546,13.451156033244446,13.754728234900346,14.058300436556246,14.361872638212146,14.665444839868046,14.969017041523946,15.272589243179846,15.576161444835746,null,0.22613147666699634,0.2596316572984968,0.29154410181092755,0.32198447310037953,0.35317139581005635,0.38322271917629253,0.41197020625931902,0.43946643110281364,0.46582705660286766,null,0.41197020625931902,0.43946643110281364,0.46582705660286766]
["2013-05-13T16:00:00","2013-05-13T16:00:00",null,13.203101273179726,13.506673474835626,13.810245676491526,14.113817878147426,14.417390079803326,14.720962281459226,15.024534483115126,15.328106684771026,15.631678886426926,null,0.22680442442607232,0.26365882904421706,0.29878880502972976,0.33229950046996587,0.36643056962560006,0.39929986173296683,0.43076016946976831,0.46085355207094675,0.48971670205006451,null,0.43076016946976831,0.46085355207094675,0.48971670205006451]
["2013-05-13T17:00:00","2013-05-13T17:00:00",null,13.268008789889135,13.571580991545035,13.875153193200935,14.178725394856835,14.482297596512735,14.785869798168635,15.089441999824535,15.393014201480435,15.696586403136335,null,0.22511154021964683,0.26536222805937809,0.30373076513544389,0.34035384396140633,0.37746060398920461,0.41317940926390867,0.4473840820806918,0.48010616686576074,0.51149287094141338,null,0.4473840820806918,0.48010616686576074,0.51149287094141338]
["2013-05-13T18:00:00","2013-05-13T18:00:00",null,13.263061581265774,13.566633782921674,13.870205984577574,14.173778186233474,14.477350387889373,14.780922589545273,15.084494791201173,15.388066992857073,15.691639194512973,null,0.22075840940312416,0.26445795450811976,0.3061386563358876,0.34591617778251865,0.38605120272615878,0.42468261002061347,0.46167370715232053,0.49707706816495778,0.53102938557208756,null,0.46167370715232053,0.49707706816495778,0.53102938557208756]
["2013-05-13T19:00:00","2013-05-13T19:00:00",null,13.086496395498031,13.390068597153931,13.693640798809831,13.997213000465731,14.300785202121631,14.604357403777531,14.907929605433431,15.211501807089331,15.515074008745231,null,0.21702565230199966,0.26421611390720184,0.30923001010414281,0.35220403340638473,0.39538835288333785,0.4369533918150143,0.47675194287911643,0.51484709492805758,0.55138605528413565,null,0.47675194287911643,0.51484709492805758,0.55138605528413565]
["2013-05-13T20:00:00","2013-05-13T20:00:00",null,12.87780834353244,13.18138054518834,13.48495274684424,13.78852494850014,14.092097150156039,14.395669351811939,14.699241553467839,15.002813755123739,15.306385956779639,null,0.21807713317555585,0.26870593723728681,0.31700045375972313,0.36311840487389807,0.40929944484048636,0.45374554136570683,0.49629897231852615,0.53704385616882899,0.57612740023891307,null,0.49629897231852615,0.53704385616882899,0.57612740023891307]
["2013-05-13T21:00:00","2013-05-13T21:00:00",null,12.692387179984394,12.995959381640294,13.299531583296194,13.603103784952093,13.906675986607993,14.210248188263893,14.513820389919793,14.817392591575693,15.120964793231593,null,0.22567933989136718,0.27963082351353574,0.33111132708284735,0.38025754311286414,0.42934067029046752,0.47656267632187638,0.52177635388479282,0.56507633625783726,0.60660983076330732,null,0.52177635388479282,0.56507633625783726,0.60660983076330732]
["2013-05-13T22:00:00","2013-05-13T22:00:00",null,12.536906989918741,12.840479191574641,13.144051393230541,13.447623594886441,13.751195796542341,14.054767998198241,14.35834019985414,14.66191240151004,14.96548460316594,null,0.23927498758644886,0.29646503229917048,0.35101586001926621,0.40310622249524036,0.45499680360523881,0.50491060067295157,0.55270040637608064,0.59847136880198215,0.64237069527295365,null,0.55270040637608064,0.59847136880198215,0.64237069527295365]
["2013-05-13T23:00:00","2013-05-13T23:00:00",null,12.346712830384243,12.650285032040143,12.953857233696043,13.257429435351943,13.561001637007843,13.864573838663743,14.168146040319643,14.471718241975543,14.775290443631443,null,0.2601784273527461,0.3204703406424585,0.37797582961724718,0.43288416083435194,0.48746653298065423,0.53995645818857974,0.59021724394456587,0.63834352352723323,0.68450353387635055,null,0.59021724394456587,0.63834352352723323,0.68450353387635055]
["2013-05-14","2013-05-14",null,12.137484218166472,12.441056419822372,12.744628621478272,13.048200823134172,13.351773024790072,13.655345226445972,13.958917428101872,14.262489629757772,14.566061831413672,null,0.2864969936178578,0.34981717182341204,0.41019320358300915,0.46784589988009556,0.52505697421028841,0.58004942389727765,0.63269707123623631,0.68311557912325616,0.73147318449810594,null,0.63269707123623631,0.68311557912325616,0.73147318449810594]
["2013-05-14T01:00:00","2013-05-14T01:00:00",null,12.028816098179885,12.332388299835785,12.635960501491684,12.939532703147584,13.243104904803484,13.546677106459384,13.850249308115284,14.153821509771184,14.457393711427084,null,0.3167060391151274,0.38295984895790347,0.44613281984116004,0.50645627755707923,0.56621193560127803,0.62363330610618217,0.6786047261757,0.73125237351465899,0.7817339702540923,null,0.6786047261757,0.73125237351465899,0.7817339702540923]
["2013-05-14T02:00:00","2013-05-14T02:00:00",null,11.93431185343079,12.23788405508669,12.54145625674259,12.84502845839849,13.14860066005439,13.45217286171029,13.75574506336619,14.05931726502209,14.36288946667799,null,0.3501536457029501,0.41927799833053458,0.48517430467630174,0.54809492014990469,0.61032155824696055,0.67010876071736625,0.7273408646650299,0.78215456260351468,0.83470757666385365,null,0.7273408646650299,0.78215456260351468,0.83470757666385365]
["2013-05-14T03:00:00","2013-05-14T03:00:00",null,11.852883575044077,12.156455776699977,12.460027978355876,12.763600180011776,13.067172381667676,13.370744583323576,13.674316784979476,13.977888986635376,14.281461188291276,null,0.38692393185121043,0.45884522360245439,0.52740177655831877,0.59285646093719213,0.65750150504342719,0.71960196543565658,0.77903166440905269,0.8359588389033854,0.89053069624095227,null,0.77903166440905269,0.8359588389033854,0.89053069624095227]
["2013-05-14T04:00:00","2013-05-14T04:00:00",null,11.735469625293479,12.039041826949379,12.342614028605279,12.646186230261179,12.949758431917079,13.253330633572979,13.556902835228879,13.860475036884779,14.164047238540679,null,0.42254810384729447,0.4973294235746113,0.56860931199298625,0.6366506393208079,0.70375614867116443,0.76821192622015966,0.82989179426296611,0.88897450454808902,0.94559674958909046,null,0.82989179426296611,0.88897450454808902,0.94559674958909046]
["2013-05-14T05:00:00","2013-05-14T05:00:00",null,11.857267723113589,12.160839924769489,12.464412126425389,12.767984328081289,13.071556529737189,13.375128731393088,13.678700933048988,13.982273134704888,14.285845336360788,null,0.4533880378686978,0.53105041518955864,0.60506415387917967,0.67572366858215627,0.74531067279410546,0.81214279711733772,0.87609386384702548,0.93735313954040977,0.99604680190231698,null,0.87609386384702548,0.93735313954040977,0.99604680190231698]
["2013-05-14T06:00:00","2013-05-14T06:00:00",null,11.823887381711675,12.127459583367575,12.431031785023475,12.734603986679375,13.038176188335274,13.341748389991174,13.645320591647074,13.948892793302974,14.252464994958874,null,0.41696474040871107,0.49747663089690919,0.57420319024030519,0.64744934789223008,0.71950733215703633,0.78868425882829896,0.85488549462739694,0.91828979130283583,0.97904435617691321,null,0.85488549462739694,0.91828979130283583,0.97904435617691321]
["2013-05-14T07:00:00","2013-05-14T07:00:00",null,12.145352902950457,12.448925104606356,12.752497306262256,13.056069507918156,13.359641709574056,13.663213911229956,13.966786112885856,14.270358314541756,14.573930516197656,null,0.37367527284440233,0.45714182458729336,0.53668635267181997,0.61261378655131316,0.68722686933886101,0.75885374644550962,0.82738926978390226,0.8930332207200159,0.95594332138488347,null,0.82738926978390226,0.8930332207200159,0.95594332138488347]
["2013-05-14T08:00:00","2013-05-14T08:00:00",null,12.534064626597772,12.837636828253672,13.141209029909572,13.444781231565472,13.748353433221371,14.051925634877271,14.355497836533171,14.659070038189071,14.962642239844971,null,0.32406640523002084,0.41055070708001817,0.4929657779493532,0.57163757690882799,0.6488793618802664,0.72301927827471435,0.7939626928135507,0.86190938686275242,0.92702759736208795,null,0.7939626928135507,0.86190938686275242,0.92702759736208795]
["2013-05-14T09:00:00","2013-05-14T09:00:00",null,12.950149746434974,13.253721948090874,13.557294149746774,13.860866351402674,14.164438553058574,14.468010754714474,14.771582956370374,15.075155158026273,15.378727359682173,null,0.26452104336053323,0.35415978783119917,0.43958209399890491,0.52112443574318812,0.60112110060334378,0.67788971918168228,0.75136720262578904,0.82173230268417008,0.88918480072280037,null,0.75136720262578904,0.82173230268417008,0.88918480072280037]
["2013-05-14T10:00:00","2013-05-14T10:00:00",null,13.202366476044833,13.505938677700733,13.809510879356633,14.113083081012533,14.416655282668433,14.720227484324333,15.023799685980233,15.327371887636133,15.630944089292033,null,0.19855113335361724,0.29141792410610073,0.37993158404206168,0.46442858704103784,0.54725373545105971,0.62673517468317319,0.70282033069369931,0.77568795523114409,0.8455378296614825,null,0.70282033069369931,0.77568795523114409,0.8455378296614825]
["2013-05-14T11:00:00","2013-05-14T11:00:00",null,13.481800729938424,13.785372931594324,14.088945133250224,14.392517334906124,14.696089536562024,14.999661738217924,15.303233939873824,15.606806141529724,15.910378343185624,null,0.12840684427868315,0.22453322573919088,0.31615926906087816,0.40364247774075396,0.48933816893558424,0.57156397324767938,0.65028834625083154,0.72569003969354684,0.79797934975053564,null,0.65028834625083154,0.72569003969354684,0.79797934975053564]
["2013-05-14T12:00:00","2013-05-14T12:00:00",null,13.568727902016064,13.872300103671964,14.175872305327864,14.479444506983764,14.783016708639664,15.086588910295564,15.390161111951464,15.693733313607364,15.997305515263264,null,5.5276349522849461E-2,0.15470438092632366,0.24949538167741508,0.34000685527313274,0.42860463367897816,0.51362737711473283,0.5950225115367177,0.67300033311964569,0.74777113803822715,null,0.5950225115367177,0.67300033311964569,0.74777113803822715]
["2013-05-14T13:00:00","2013-05-14T13:00:00",null,13.61162049247331,13.91519269412921,14.21876489578511,14.52233709744101,14.82590929909691,15.12948150075281,15.43305370240871,15.73662590406461,16.04019810572051,null,0,8.3392948081742191E-2,0.18135942107097336,0.27493070400873953,0.36645159924307119,0.45428179661122092,0.53837923687824518,0.61894370141012145,0.69621703080776665,null,0.53837923687824518,0.61894370141012145,0.69621703080776665]
["2013-05-14T14:00:00","2013-05-14T14:00:00",null,13.587951512928585,13.891523714584485,14.195095916240385,14.498668117896285,14.802240319552185,15.105812521208085,15.409384722863985,15.712956924519885,16.016529126175787,null,0,7.5075734371912589E-3,0.10876518156065333,0.20548039231035253,0.30002955246052604,0.39075132223095532,0.47763518681290351,0.56088092757234809,0.64073038511020597,null,0.47763518681290351,0.56088092757234809,0.64073038511020597]
["2013-05-14T15:00:00","2013-05-14T15:00:00",null,13.716383697666245,14.019955899322145,14.323528100978045,14.627100302633945,14.930672504289845,15.234244705945745,15.537816907601645,15.841389109257545,16.144961310913445,null,0,0,0,5.9009106623973906E-2,0.15658653168998926,0.25021038867143364,0.33989119237704135,0.42581820936405423,0.5082543098508604,null,0.33989119237704135,0.42581820936405423,0.5082543098508604]
["2013-05-14T16:00:00","2013-05-14T16:00:00",null,13.681690888262883,13.985263089918783,14.288835291574683,14.592407493230583,14.895979694886483,15.199551896542383,15.503124098198283,15.806696299854183,16.110268501510085,null,0,0,0,0,9.3371501571790361E-3,0.10590515358458077,0.19841444084005466,0.28705427848084253,0.37210856634280365,null,0.19841444084005466,0.28705427848084253,0.37210856634280365]
["2013-05-14T17:00:00","2013-05-14T17:00:00",null,13.6293888660508,13.9329610677067,14.236533269362599,14.540105471018499,14.843677672674399,15.147249874330299,15.450822075986199,15.754394277642099,16.057966479297999,null,0,0,0,0,0,0,5.611753422169416E-2,0.14750173694246368,0.2351847269883153,null,5.611753422169416E-2,0.14750173694246368,0.2351847269883153]
["2013-05-14T18:00:00","2013-05-14T18:00:00",null,13.207849923837898,13.511422125493798,13.814994327149698,14.118566528805598,14.422138730461498,14.725710932117398,15.029283133773298,15.332855335429198,15.636427537085098,null,0,0,0,0,0,0,4.7484876249797761E-2,0.14142417749330885,0.23155711797454642,null,4.7484876249797761E-2,0.14142417749330885,0.23155711797454642]
["2013-05-14T19:00:00","2013-05-14T19:00:00",null,13.538407217589789,13.841979419245689,14.145551620901589,14.449123822557489,14.752696024213389,15.056268225869289,15.359840427525189,15.663412629181089,15.966984830836989,null,0,0,0,0,9.5684759493614184E-4,3.9430532758357494E-3,5.4287957501706376E-2,0.1509821386339347,0.24375429610779834,null,5.4287957501706376E-2,0.1509821386339347,0.24375429610779834]
["2013-05-14T20:00:00","2013-05-14T20:00:00",null,13.31389448776368,13.617466689419579,13.921038891075479,14.224611092731379,14.528183294387279,14.831755496043179,15.135327697699079,15.438899899354979,15.742472101010879,null,0,0,2.1765654082613337E-3,5.3099784114588088E-3,9.2635464960301207E-3,1.5130809770473715E-2,6.8230593885061586E-2,0.16757450681865152,0.26290176281525673,null,6.8230593885061586E-2,0.16757450681865152,0.26290176281525673]
["2013-05-14T21:00:00","2013-05-14T21:00:00",null,13.252536007254244,13.556108208910144,13.859680410566044,14.163252612221944,14.466824813877844,14.770397015533744,15.073969217189644,15.377541418845544,15.681113620501444,null,0,3.1439278119330372E-3,8.4959654583340941E-3,1.4678672994844547E-2,2.1544843099166534E-2,3.0198530688534057E-2,8.5979591030690236E-2,0.18789963210449287,0.28570838296269069,null,8.5979591030690236E-2,0.18789963210449287,0.28570838296269069]
["2013-05-14T22:00:00","2013-05-14T22:00:00",null,13.169561289921546,13.473133491577446,13.776705693233346,14.080277894889246,14.383850096545146,14.687422298201046,14.990994499856946,15.294566701512846,15.598138903168746,null,7.3288216886867128E-3,1.3690280973701721E-2,2.211264277088688E-2,3.1228981944619132E-2,4.0913120790071734E-2,5.2258599415743123E-2,0.11062630270684756,0.21503835345097838,0.3152339658921488,null,0.11062630270684756,0.21503835345097838,0.3152339658921488]
["2013-05-14T23:00:00","2013-05-14T23:00:00",null,13.091039970049456,13.394612171705356,13.698184373361256,14.001756575017156,14.305328776673056,14.608900978328956,14.912473179984856,15.216045381640756,15.519617583296656,null,1.9336733264698515E-2,2.8873664787853245E-2,4.0313776692144698E-2,5.2332203076892063E-2,6.478173661979747E-2,7.8787461855566038E-2,0.13969974886067649,0.24656175004019326,0.34911267963812953,null,0.13969974886067649,0.24656175004019326,0.34911267963812953]
["2013-05-15","2013-05-15",null,13.003025169967707,13.306597371623607,13.610169573279506,13.913741774935406,14.217313976591306,14.520886178247206,14.824458379903106,15.128030581559006,15.431602783214906,null,3.6623078825962441E-2,4.9272393734843517E-2,6.3688196511299019E-2,7.8545621254648118E-2,9.3718490260064083E-2,0.11033188806225203,0.17374669954642624,0.28301659192638673,0.38787026463741103,null,0.17374669954642624,0.28301659192638673,0.38787026463741103]
["2013-05-15T01:00:00","2013-05-15T01:00:00",null,13.1582725294708,13.4618447311267,13.7654169327826,14.0689891344385,14.3725613360944,14.676133537750299,14.979705739406199,15.283277941062099,15.586850142717999,null,5.3888394769755238E-2,6.9608033829420421E-2,8.6967983051833286E-2,0.104643376536313,0.12250803657803283,0.14170807732916901,0.20760438367493589,0.31925062282913336,0.42639652384451021,null,0.20760438367493589,0.31925062282913336,0.42639652384451021]
["2013-05-15T02:00:00","2013-05-15T02:00:00",null,13.253734197440629,13.557306399096529,13.860878600752429,14.164450802408329,14.468023004064229,14.771595205720129,15.075167407376028,15.378739609031928,15.682311810687828,null,6.7925664431730509E-2,8.6778716494593164E-2,0.1071353862066412,0.12768132247592934,0.14829034759763085,0.1701296053413931,0.23854946578369485,0.35262462575580711,0.46210481431047878,null,0.23854946578369485,0.35262462575580711,0.46210481431047878]
["2013-05-15T03:00:00","2013-05-15T03:00:00",null,13.319997296407273,13.623569498063173,13.927141699719073,14.230713901374973,14.534286103030873,14.837858304686772,15.141430506342672,15.445002707998572,15.748574909654472,null,8.2351982016921565E-2,0.10430690265677502,0.12763926324098709,0.15103471267761254,0.1743670732618246,0.19882451838074178,0.26974690330210727,0.38624046928339884,0.49803391575989414,null,0.26974690330210727,0.38624046928339884,0.49803391575989414]
["2013-05-15T04:00:00","2013-05-15T04:00:00",null,13.306626808046804,13.610199009702704,13.913771211358604,14.217343413014504,14.520915614670404,14.824487816326304,15.128060017982204,15.431632219638104,15.735204421294004,null,9.441246763661118E-2,0.11953234570586879,0.14588245639718717,0.17217999304482773,0.19828826313522815,0.2254059548642425,0.29888343830834957,0.41782695472502707,0.53197571835828827,null,0.29888343830834957,0.41782695472502707,0.53197571835828827]
["2013-05-15T05:00:00","2013-05-15T05:00:00",null,13.46692429619667,13.770496497852569,14.074068699508469,14.377640901164369,14.681213102820269,14.984785304476169,15.288357506132069,15.591929707787969,15.895501909443869,null,0.1010473119487508,0.12941626591729707,0.15886824518560624,0.18815198751414641,0.21710977077188412,0.24697182758088015,0.32307801320887775,0.44455559853082566,0.56113328298200171,null,0.32307801320887775,0.44455559853082566,0.56113328298200171]
["2013-05-15T06:00:00","2013-05-15T06:00:00",null,13.528231034947023,13.831803236602923,14.135375438258823,14.438947639914723,14.742519841570623,15.046092043226523,15.349664244882423,15.653236446538322,15.956808648194222,null,0.10410712129079934,0.13575669558484096,0.16835260266508317,0.20064358029199406,0.23248242114327577,0.26512038745846017,0.34388681969655494,0.4679195035412444,0.58695765323654203,null,0.34388681969655494,0.4679195035412444,0.58695765323654203]
["2013-05-15T07:00:00","2013-05-15T07:00:00",null,13.627814239398745,13.931386441054645,14.234958642710545,14.538530844366445,14.842103046022345,15.145675247678245,15.449247449334145,15.752819650990045,16.056391852645945,null,9.0921551136404599E-2,0.12595689384329717,0.16180187682282804,0.19720523783546529,0.23203028436764661,0.26753879346763942,0.34906010559445144,0.47574252124050254,0.59732525464980613,null,0.34906010559445144,0.47574252124050254,0.59732525464980613]
["2013-05-15T08:00:00","2013-05-15T08:00:00",null,13.63737753871338,13.94094974036928,14.24452194202518,14.54809414368108,14.85166634533698,15.15523854699288,15.45881074864878,15.76238295030468,16.06595515196058,null,7.7441566337414114E-2,0.11581010341347985,0.15485158824862155,0.19332527341204292,0.23108395158144604,0.26941042942256949,0.35364456220315649,0.48293465041562694,0.60701990830399433,null,0.35364456220315649,0.48293465041562694,0.60701990830399433]
["2013-05-15T09:00:00","2013-05-15T09:00:00",null,13.768167911066978,14.071740112722878,14.375312314378778,14.678884516034678,14.982456717690578,15.286028919346478,15.589601121002378,15.893173322658278,16.196745524314178,null,6.2415904654296021E-2,0.10412815090827046,0.14636613759902303,0.18791014691322849,0.22861297152858898,0.26976793291957857,0.35672540116267615,0.48863367675030156,0.61523197392646822,null,0.35672540116267615,0.48863367675030156,0.61523197392646822]
["2013-05-15T10:00:00","2013-05-15T10:00:00",null,13.815562574888716,14.119134776544616,14.422706978200516,14.726279179856416,15.029851381512316,15.333423583168216,15.636995784824116,15.940567986480016,16.244140188135916,null,4.5728903190959132E-2,9.0805888240313409E-2,0.13627192121288351,0.1809072842953442,0.22457528497413318,0.26857975953246005,0.35828159285553934,0.49281857062705525,0.62196145151722793,null,0.35828159285553934,0.49281857062705525,0.62196145151722793]
["2013-05-15T11:00:00","2013-05-15T11:00:00",null,13.998345604838569,14.301917806494469,14.605490008150369,14.909062209806269,15.212634411462169,15.516206613118069,15.819778814773969,16.123351016429869,16.426923218085768,null,2.5614074079829029E-2,7.408734235076983E-2,0.12280245122262859,0.17056071249955118,0.21722543366797534,0.26411096581984622,0.35657819384037831,0.49378593303072693,0.62549442725237681,null,0.35657819384037831,0.49378593303072693,0.62549442725237681]
["2013-05-15T12:00:00","2013-05-15T12:00:00",null,14.041617365015455,14.345189566671355,14.648761768327255,14.952333969983155,15.255906171639054,15.559478373294954,15.863050574950854,16.166622776606754,16.470194978262654,null,4.1533494505469927E-3,5.6043930560545442E-2,0.10802914494916398,0.15893133403801962,0.20861380531355006,0.25839090986770047,0.35364456220315649,0.49353357762107342,0.62782871479167157,null,0.35364456220315649,0.49353357762107342,0.62782871479167157]
["2013-05-15T13:00:00","2013-05-15T13:00:00",null,14.086547414507244,14.390119616163144,14.693691817819044,14.997264019474944,15.300836221130844,15.604408422786744,15.907980624442644,16.211552826098544,16.515125027754443,null,0,3.6591534399755751E-2,9.1867883922605184E-2,0.14592451563212944,0.19864576663223729,0.25133547320613836,0.34939657947398944,0.49197738592821022,0.62888019566522779,null,0.34939657947398944,0.49197738592821022,0.62888019566522779]
["2013-05-15T14:00:00","2013-05-15T14:00:00",null,14.1355982327538,14.4391704344097,14.7427426360656,15.0463148377215,15.3498870393774,15.6534592410333,15.9570314426892,16.2606036443451,16.564175846001,null,0,1.5698609442194061E-2,7.4287123716745521E-2,0.13151922766440949,0.1873002880065659,0.24292362621768876,0.34381321603540604,0.4891068431434018,0.62862784025557428,null,0.34381321603540604,0.4891068431434018,0.62862784025557428]
["2013-05-15T15:00:00","2013-05-15T15:00:00",null,14.277530613593648,14.581102815249547,14.884675016905447,15.188247218561347,15.491819420217247,15.795391621873147,16.098963823529047,16.402536025184947,16.706108226840847,null,0,0,0,2.1387120968133125E-2,8.0280564696015883E-2,0.13890062339677392,0.24266075599929962,0.39073029261348374,0.53292205114448898,null,0.24266075599929962,0.39073029261348374,0.53292205114448898]
["2013-05-15T16:00:00","2013-05-15T16:00:00",null,14.451353735683082,14.754925937338982,15.058498138994882,15.362070340650781,15.665642542306681,15.969214743962581,16.272786945618481,16.576359147274381,16.879931348930281,null,0,0,0,0,0,0,9.0227573759857349E-2,0.2410835346889654,0.38596708425627452,null,9.0227573759857349E-2,0.2410835346889654,0.38596708425627452]
["2013-05-15T17:00:00","2013-05-15T17:00:00",null,14.450664714306058,14.754236915961958,15.057809117617857,15.361381319273757,15.664953520929657,15.968525722585557,16.272097924241457,16.575670125897357,16.879242327553257,null,0,0,0,0,0,0,0,9.1457806381918166E-2,0.23903314698553116,null,-6.2184578862113815E-2,9.1457806381918166E-2,0.23903314698553116]
["2013-05-15T18:00:00","2013-05-15T18:00:00",null,13.911778841860897,14.215351043516797,14.518923245172697,14.822495446828597,15.126067648484497,15.429639850140397,15.733212051796297,16.036784253452197,16.340356455108097,null,0,0,0,0,0,0,0,7.4676171639961222E-2,0.22473300710516683,null,-1.9368277690905201E-2,7.4676171639961222E-2,0.22473300710516683]
["2013-05-15T19:00:00","2013-05-15T19:00:00",null,14.428251795913582,14.731823997569482,15.035396199225382,15.338968400881281,15.642540602537181,15.946112804193081,16.249685005848981,16.553257207504881,16.856829409160781,null,0,0,0,0,0,0,0,6.9702667108040392E-2,0.22248283803575655,null,-7.7914732730514401E-3,6.9702667108040392E-2,0.22248283803575655]
["2013-05-15T20:00:00","2013-05-15T20:00:00",null,13.887262033435061,14.190834235090961,14.494406436746861,14.797978638402761,15.10155084005866,15.40512304171456,15.70869524337046,16.01226744502636,16.31583964668226,null,0,0,0,3.6801830574466994E-4,3.4173128390576494E-3,6.3509444762794463E-3,9.1689132174100612E-3,8.1584400979225452E-2,0.23697224447336099,null,9.1689132174100612E-3,8.1584400979225452E-2,0.23697224447336099]
["2013-05-15T21:00:00","2013-05-15T21:00:00",null,13.723420273491332,14.026992475147232,14.330564676803132,14.634136878459032,14.937709080114931,15.241281281770831,15.544853483426731,15.848425685082631,16.151997886738531,null,1.9662692335500934E-3,5.2784339852521229E-3,8.4644210321274081E-3,1.1881733871185058E-2,1.7854145232984273E-2,2.3595230802601123E-2,2.9115505388771168E-2,0.10412815090827038,0.26200800407273411,null,2.9115505388771168E-2,0.10412815090827038,0.26200800407273411]
["2013-05-15T22:00:00","2013-05-15T22:00:00",null,13.153934086297873,13.457506287953773,13.761078489609673,14.064650691265573,14.368222892921473,14.671795094577373,14.975367296233273,15.278939497889173,15.582511699545073,null,9.6210499930392285E-3,1.6266409113914412E-2,2.262786839892942E-2,2.9094475771300046E-2,3.79900039615855E-2,4.6528028654861844E-2,5.4729579468600194E-2,0.13231835312831208,0.29267970115436848,null,5.4729579468600194E-2,0.13231835312831208,0.29267970115436848]
["2013-05-15T23:00:00","2013-05-15T23:00:00",null,12.695290954527147,12.998863156183047,13.302435357838947,13.606007559494847,13.909579761150747,14.213151962806647,14.516724164462547,14.820296366118447,15.123868567774347,null,3.1334130031974751E-2,4.110238734731185E-2,5.0450052313226468E-2,5.9766172852934396E-2,7.1385036505730415E-2,8.2520218956690566E-2,9.3224294249492662E-2,0.1732104443009127,0.33586402063132159,null,9.3224294249492662E-2,0.1732104443009127,0.33586402063132159]
["2013-05-16","2013-05-16",null,12.444036558401958,12.747608760057858,13.051180961713758,13.354753163369658,13.658325365025558,13.961897566681458,14.265469768337358,14.569041969993258,14.872614171649158,null,0.11591525150083545,0.12863817007086548,0.14079328896917515,0.15280120054518695,0.16698567752946009,0.18057081041580619,0.19363020286537419,0.27586652198620448,0.44068614891613916,null,0.19363020286537419,0.27586652198620448,0.44068614891613916]
["2013-05-16T01:00:00","2013-05-16T01:00:00",null,12.42083233935112,12.72440454100702,13.02797674266292,13.33154894431882,13.63512114597472,13.93869334763062,14.24226554928652,14.54583775094242,14.84940995259832,null,0.22289291557644322,0.23854946578369504,0.25350152380566421,0.26818019680050875,0.28491977230752347,0.30094434082051996,0.31633802080938267,0.4008139941908877,0.56778915691161258,null,0.31633802080938267,0.4008139941908877,0.56778915691161258]
["2013-05-16T02:00:00","2013-05-16T02:00:00",null,12.299009407934001,12.602581609589901,12.906153811245801,13.209726012901701,13.513298214557601,13.816870416213501,14.120442617869401,14.424014819525301,14.727587021181201,null,0.33159500828468313,0.35016416051168564,0.36790264284857876,0.38523104764478489,0.40451520686580561,0.42295818138798136,0.44067563410740329,0.52737023213211187,0.69646938621742027,null,0.44067563410740329,0.52737023213211187,0.69646938621742027]
["2013-05-16T03:00:00","2013-05-16T03:00:00",null,12.271078305554335,12.574650507210235,12.878222708866135,13.181794910522035,13.485367112177935,13.788939313833835,14.092511515489734,14.396083717145634,14.699655918801534,null,0.44131703744027256,0.46278827687829022,0.48329215391263614,0.50324926089273281,0.52505697421028841,0.54589732512417222,0.56591752095668224,0.65482022881585888,0.82603285945701521,null,0.56591752095668224,0.65482022881585888,0.82603285945701521]
["2013-05-16T04:00:00","2013-05-16T04:00:00",null,12.330299027539921,12.633871229195821,12.937443430851721,13.24101563250762,13.54458783416352,13.84816003581942,14.15173223747532,14.45530443913122,14.75887664078712,null,0.55162789588505345,0.57596967810787958,0.59920740541347162,0.62177218495998765,0.64607190794787139,0.66929912044472784,0.69160102977285476,0.78268030304029279,0.95599589542856145,null,0.69160102977285476,0.78268030304029279,0.95599589542856145]
["2013-05-16T05:00:00","2013-05-16T05:00:00",null,12.524444346622024,12.828016548277924,13.131588749933824,13.435160951589724,13.738733153245624,14.042305354901524,14.345877556557424,14.649449758213324,14.953021959869224,null,0.59312984596431662,0.62047886348551351,0.64658713357591402,0.67188576339367612,0.69880367375671482,0.72454392554137059,0.74924321126120563,0.84261471283299616,1,null,0.74924321126120563,0.84261471283299616,1]
["2013-05-16T06:00:00","2013-05-16T06:00:00",null,12.600323651677297,12.903895853333196,13.207468054989096,13.511040256644996,13.814612458300896,14.118184659956796,14.421756861612696,14.725329063268596,15.028901264924496,null,0.61224576824556831,0.64265459510881373,0.67168598202770047,0.69977103616038649,0.72935970794225802,0.7576445434409198,0.78479377959614072,0.88049956870722601,1,null,0.78479377959614072,0.88049956870722601,1]
["2013-05-16T07:00:00","2013-05-16T07:00:00",null,12.767824360345736,13.071396562001636,13.374968763657536,13.678540965313436,13.982113166969336,14.285685368625236,14.589257570281136,14.892829771937036,15.196401973592936,null,0.61383350436463813,0.64734419980487434,0.67934076278718958,0.71025430046974181,0.74254527809665272,0.77341675654426278,0.80305800236981195,0.90114013825513417,1,null,0.80305800236981195,0.90114013825513417,1]
["2013-05-16T08:00:00","2013-05-16T08:00:00",null,12.935817720931137,13.239389922587037,13.542962124242937,13.846534325898837,14.150106527554737,14.453678729210637,14.757250930866537,15.060823132522437,15.364395334178337,null,0.60851301114444378,0.64515711958787747,0.68015040305982788,0.71393448352718847,0.74896982623408115,0.78247000686558166,0.81462429197893016,0.91512483387343158,1,null,0.81462429197893016,0.91512483387343158,1]
["2013-05-16T09:00:00","2013-05-16T09:00:00",null,13.104735121361365,13.408307323017265,13.711879524673165,14.015451726329065,14.319023927984965,14.622596129640865,14.926168331296765,15.229740532952665,15.533312734608565,null,0.60201485934586652,0.64183444002743983,0.67986650322396769,0.71655267090234342,0.75436392311542444,0.79053486516575766,0.82524424880184777,0.92819474113173517,1,null,0.82524424880184777,0.92819474113173517,1]
["2013-05-16T10:00:00","2013-05-16T10:00:00",null,13.389389814530546,13.692962016186446,13.996534217842346,14.300106419498245,14.603678621154145,14.907250822810045,15.210823024465945,15.514395226121845,15.817967427777745,null,0.59814540973117969,0.64117200707709943,0.6822743944244114,0.72190470854874444,0.76253392950295606,0.80140717739832878,0.83870320398336717,0.94414570598358272,1,null,0.83870320398336717,0.94414570598358272,1]
["2013-05-16T11:00:00","2013-05-16T11:00:00",null,13.60674293779957,13.91031513945547,14.21388734111137,14.51745954276727,14.82103174442317,15.12460394607907,15.42817614773497,15.73174834939087,16.03532055104677,null,0.5895232665680189,0.63580945462196281,0.68003474016373666,0.72266177477770488,0.76616153851672497,0.80778966630081495,0.84772490987847937,0.95571199559270092,1,null,0.84772490987847937,0.95571199559270092,1]
["2013-05-16T12:00:00","2013-05-16T12:00:00",null,13.8748094821606,14.1783816838165,14.4819538854724,14.7855260871283,15.0890982887842,15.3926704904401,15.696242692096,15.9998148937519,16.3033870954078,null,0.57759947346189155,0.62716628184133083,0.67453549519503775,0.72016976510737674,0.76656110124867638,0.81096513853895469,0.85357114353545183,0.96413435738988607,1,null,0.85357114353545183,0.96413435738988607,1]
["2013-05-16T13:00:00","2013-05-16T13:00:00",null,14.093806514317096,14.397378715972996,14.700950917628896,15.004523119284796,15.308095320940696,15.611667522596596,15.915239724252496,16.218811925908398,16.522384127564294,null,0.49617279461369945,0.54906228255357625,0.5996279977628941,0.64831156220854602,0.69764704479580308,0.744869050827212,0.79019839128621971,0.90336927770707331,0.94175847441372207,null,0.79019839128621971,0.90336927770707331,0.94175847441372207]
["2013-05-16T14:00:00","2013-05-16T14:00:00",null,14.489814203280131,14.793386404936031,15.096958606591931,15.400530808247831,15.704103009903731,16.007675211559629,16.311247413215533,16.614819614871429,16.918391816527333,null,0.40576646910533742,0.46204172545806516,0.51585651656667164,0.56766297920678555,0.62000569709241327,0.67010876071736614,0.71822452549129778,0.83407668813971969,0.87504201298658124,null,0.71822452549129778,0.83407668813971969,0.87504201298658124]
["2013-05-16T15:00:00","2013-05-16T15:00:00",null,14.750170891123455,15.053743092779355,15.357315294435255,15.660887496091155,15.964459697747055,16.268031899402956,16.571604101058853,16.875176302714756,17.178748504370652,null,0.23377574261774983,0.29354191547068414,0.35070041575719935,0.40573492467913075,0.46116899633301373,0.51425826563886623,0.56524457319760624,0.68387264535221659,0.72750873161791085,null,0.56524457319760624,0.68387264535221659,0.72750873161791085]
["2013-05-16T16:00:00","2013-05-16T16:00:00",null,14.860755439823604,15.164327641479504,15.467899843135404,15.771472044791304,16.075044246447206,16.378616448103102,16.682188649759006,16.985760851414902,17.289333053070806,null,5.7442400122375142E-2,0.12074154871045828,0.18128581740982444,0.23957991703978007,0.29815791650559609,0.3542649359185549,0.40816384549704554,0.52959937158405102,0.57593776369478467,null,0.40816384549704554,0.52959937158405102,0.57593776369478467]
["2013-05-16T17:00:00","2013-05-16T17:00:00",null,14.746495932693293,15.050068134349193,15.353640336005093,15.657212537660993,15.960784739316892,16.264356940972792,16.567929142628692,16.871501344284592,17.175073545940492,null,0,0,1.5204413431622682E-2,7.6716044534660299E-2,0.13839591257746708,0.19747862286258996,0.25424807522588899,0.37845951081908286,0.42746866434864927,null,0.25424807522588899,0.37845951081908286,0.42746866434864927]
["2013-05-16T18:00:00","2013-05-16T18:00:00",null,14.325100304241424,14.628672505897324,14.932244707553224,15.235816909209124,15.539389110865024,15.842961312520924,16.146533514176824,16.450105715832724,16.753677917488623,null,0,0,0,3.8852218277901543E-2,0.10351829200160795,0.16547154507153924,0.22500639213229107,0.3518780743355821,0.40345284119662567,null,0.22500639213229107,0.3518780743355821,0.40345284119662567]
["2013-05-16T19:00:00","2013-05-16T19:00:00",null,14.688070887568497,14.991643089224397,15.295215290880297,15.598787492536196,15.902359694192096,16.205931895847996,16.509504097503896,16.813076299159796,17.116648500815696,null,0,0,0,2.556150003615118E-2,9.3350471954319503E-2,0.15831096032262151,0.22073737978565289,0.35040600111260345,0.40467255900995086,null,0.22073737978565289,0.35040600111260345,0.40467255900995086]
["2013-05-16T20:00:00","2013-05-16T20:00:00",null,14.401652210067883,14.705224411723783,15.008796613379683,15.312368815035583,15.615941016691483,15.919513218347383,16.223085420003283,16.526657621659183,16.830229823315083,null,0,0,0,1.8411430095969024E-2,8.9260211356185892E-2,0.15716484617044527,0.22243026399207838,0.35483273559027506,0.41172799567151297,null,0.22243026399207838,0.35483273559027506,0.41172799567151297]
["2013-05-16T21:00:00","2013-05-16T21:00:00",null,14.280080790854099,14.583652992509998,14.887225194165898,15.190797395821798,15.494369597477698,15.797941799133598,16.1015140007895,16.405086202445396,16.7086584041013,null,0,0,0,1.497308763944025E-2,8.8839619006763418E-2,0.1596463410320379,0.22769818316859494,0.3627924458030955,0.42227434883328163,null,0.22769818316859494,0.3627924458030955,0.42227434883328163]
["2013-05-16T22:00:00","2013-05-16T22:00:00",null,14.056618126266562,14.360190327922462,14.663762529578362,14.967334731234262,15.270906932890162,15.574479134546062,15.878051336201962,16.18162353785786,16.485195739513763,null,0,0,2.9441464459573595E-3,2.0913954575032777E-2,9.7651028727164371E-2,0.1712126306411561,0.24192471938781032,0.37957408054505243,0.44151644881936009,null,0.24192471938781032,0.37957408054505243,0.44151644881936009]
["2013-05-16T23:00:00","2013-05-16T23:00:00",null,13.895068396264508,14.198640597920408,14.502212799576307,14.805785001232207,15.109357202888107,15.412929404544007,15.716501606199907,16.020073807855809,16.323646009511705,null,3.9220236583646251E-3,7.0869810877687862E-3,1.3080422067039126E-2,3.3962832215865213E-2,0.1134968454916563,0.18975023844195191,0.26304897013755435,0.40317982615638909,0.46751957082240492,null,0.26304897013755435,0.40317982615638909,0.46751957082240492]
["2013-05-17","2013-05-17",null,13.809470599166723,14.113042800822623,14.416615002478522,14.720187204134422,15.023759405790322,15.327331607446222,15.630903809102122,15.934476010758022,16.238048212413922,null,5.3457287611597196E-2,5.98187468966122E-2,6.8861482409195526E-2,9.2667009386507848E-2,0.17501899140342955,0.25396417539002902,0.32986006484331531,0.4724829305324782,0.53923056639893774,null,0.32986006484331531,0.4724829305324782,0.53923056639893774]
["2013-05-17T01:00:00","2013-05-17T01:00:00",null,13.791145400275774,14.094717601931674,14.398289803587573,14.701862005243473,15.005434206899373,15.309006408555273,15.612578610211173,15.916150811867073,16.219723013522973,null,0.11759762089852538,0.12719764127409347,0.1393422453636676,0.16611294840440841,0.25132495839740299,0.33300399265524855,0.41153909910116093,0.55669603369559428,0.62587259037996856,null,0.41153909910116093,0.55669603369559428,0.62587259037996856]
["2013-05-17T02:00:00","2013-05-17T02:00:00",null,13.739780920880214,14.043353122536114,14.346925324192014,14.650497525847914,14.954069727503814,15.257641929159714,15.561214130815614,15.864786332471514,16.168358534127414,null,0.18681660680473,0.19956055499223113,0.21473342399764711,0.24439569944066747,0.33238361893985041,0.41673341461652874,0.49782361958518268,0.64545153423247315,0.71699392288234887,null,0.49782361958518268,0.64545153423247315,0.71699392288234887]
["2013-05-17T03:00:00","2013-05-17T03:00:00",null,13.606731340440419,13.910303542096319,14.213875743752219,14.517447945408119,14.821020147064019,15.124592348719919,15.428164550375818,15.731736752031718,16.035308953687618,null,0.26839049297522,0.28421528012224079,0.30234281038234967,0.33483356937523623,0.42553430952819415,0.51248126296255625,0.59607399241027403,0.74610979825800816,0.81996544482970757,null,0.59607399241027403,0.74610979825800816,0.81996544482970757]
["2013-05-17T04:00:00","2013-05-17T04:00:00",null,13.701170760207313,14.004742961863213,14.308315163519113,14.611887365175013,14.915459566830913,15.219031768486813,15.522603970142713,15.826176171798613,16.129748373454511,null,0.34692559942113255,0.36588379957135081,0.38700805032109487,0.42237986690752544,0.51583548694920056,0.60543217218492429,0.69156948534664808,0.8440447268210326,0.92025569054949785,null,0.69156948534664808,0.8440447268210326,0.92025569054949785]
["2013-05-17T05:00:00","2013-05-17T05:00:00",null,14.072331601506155,14.375903803162055,14.679476004817955,14.983048206473855,15.286620408129755,15.590192609785655,15.893764811441555,16.197337013097453,16.500909214753356,null,0.4089734857696839,0.43118076181919085,0.45543842557213232,0.49380696264819807,0.59013312547468166,0.68249520540785813,0.77129276517967915,0.92633361998554076,1,null,0.77129276517967915,0.92633361998554076,1]
["2013-05-17T06:00:00","2013-05-17T06:00:00",null,14.145486320924428,14.449058522580328,14.752630724236228,15.056202925892128,15.359775127548028,15.663347329203928,15.966919530859828,16.27049173251573,16.574063934171626,null,0.46681544862401048,0.49231385980774833,0.51972596618135836,0.56112276817326601,0.66036153301950029,0.75552055207633617,0.8470099028844611,1,1,null,0.8470099028844611,1,1]
["2013-05-17T07:00:00","2013-05-17T07:00:00",null,14.437844641603562,14.741416843259461,15.044989044915361,15.348561246571261,15.652133448227161,15.955705649883061,16.259277851538961,16.562850053194861,16.866422254850761,null,0.50642473313087255,0.53534045715366807,0.56603318385277335,0.61058442846534966,0.71285145822742579,0.81092307930401231,0.90521988404453235,1,1,null,0.90521988404453235,1,1]
["2013-05-17T08:00:00","2013-05-17T08:00:00",null,14.268667442283862,14.572239643939762,14.875811845595662,15.179384047251562,15.482956248907461,15.786528450563361,16.090100652219263,16.393672853875159,16.697245055531063,null,0.52714942114866525,0.55940885434936949,0.59330859771282118,0.6409511960936527,0.74617288711042173,0.84709402135434553,0.94413519117484734,1,1,null,0.94413519117484734,1,1]
["2013-05-17T09:00:00","2013-05-17T09:00:00",null,14.448031994635127,14.751604196291026,15.055176397946926,15.358748599602826,15.662320801258726,15.965893002914626,16.269465204570526,16.573037406226426,16.876609607882326,null,0.51284928126830098,0.54848396807312061,0.5856117577183898,0.63636673948494771,0.74457463618261632,0.84836631321134848,0.94817287772930314,1,1,null,0.94817287772930314,1,1]
["2013-05-17T10:00:00","2013-05-17T10:00:00",null,14.659489294405654,14.963061496061554,15.266633697717454,15.570205899373354,15.873778101029254,16.177350302685156,16.480922504341052,16.784494705996956,17.088066907652852,null,0.48744550336318321,0.52647647338958936,0.56687436855161832,0.6207732781301093,0.73199892493488417,0.83869268917463147,0.94129619281624555,0.9958256209319819,0.99843329349840126,null,0.94129619281624555,0.9958256209319819,0.99843329349840126]
["2013-05-17T11:00:00","2013-05-17T11:00:00",null,14.883592095393618,15.187164297049518,15.490736498705418,15.794308700361318,16.097880902017216,16.40145310367312,16.705025305329016,17.00859750698492,17.312169708640816,null,0.4444504504434702,0.48702491101376078,0.53081908939737621,0.58798810449262695,0.70235767910933489,0.81207970826492404,0.91760632873502435,0.97495372559189131,0.98027421881208565,null,0.91760632873502435,0.97495372559189131,0.98027421881208565]
["2013-05-17T12:00:00","2013-05-17T12:00:00",null,15.250838874118504,15.554411075774404,15.857983277430304,16.161555479086203,16.465127680742103,16.768699882398003,17.072272084053903,17.375844285709803,17.679416487365703,null,0.3928963432130097,0.43908789798833364,0.48635196325468455,0.54686468752784401,0.66446230842636944,0.77728620615894939,0.88580954711868487,0.94604851637783138,0.95415543391294966,null,0.88580954711868487,0.94604851637783138,0.95415543391294966]
["2013-05-17T13:00:00","2013-05-17T13:00:00",null,15.326080181578323,15.629652383234223,15.933224584890123,16.236796786546023,16.540368988201923,16.843941189857823,17.147513391513723,17.451085593169623,17.754657794825523,null,0.34367652352184397,0.39346414288473014,0.44417706541634538,0.50801246924994237,0.62881710681281422,0.74472184350491388,0.85622087533681346,0.91934090218950393,0.93022372923081054,null,0.85622087533681346,0.91934090218950393,0.93022372923081054]
["2013-05-17T14:00:00","2013-05-17T14:00:00",null,15.418952892086956,15.722525093742856,16.026097295398756,16.329669497054656,16.633241698710556,16.936813900366456,17.240386102022356,17.543958303678256,17.847530505334156,null,0.27570879985517122,0.3291135134230907,0.38330683764617696,0.45049646546641825,0.57452914931110766,0.6935462693889336,0.80805253651920395,0.87407465058290956,0.88775441674787559,null,0.80805253651920395,0.87407465058290956,0.88775441674787559]
["2013-05-17T15:00:00","2013-05-17T15:00:00",null,15.796306932139959,16.099879133795859,16.403451335451759,16.707023537107659,17.010595738763559,17.314167940419459,17.617740142075359,17.921312343731259,18.224884545387159,null,8.0406742400842668E-2,0.13749163902620884,0.19523896860191506,0.26584590926121399,0.3931697282401343,0.51536232055609998,0.63293891183715445,0.70192620196428857,0.71847651091406295,null,0.63293891183715445,0.70192620196428857,0.71847651091406295]
["2013-05-17T16:00:00","2013-05-17T16:00:00",null,15.78682323288718,16.09039543454308,16.39396763619898,16.69753983785488,17.00111203951078,17.304684241166679,17.608256442822579,17.911828644478479,18.215400846134379,null,0,0,7.4129401585711074E-3,8.143719365692767E-2,0.21205214777007889,0.33742021232418429,0.45806712775602287,0.53001959394658549,0.54942993087243275,null,0.45806712775602287,0.53001959394658549,0.54942993087243275]
["2013-05-17T17:00:00","2013-05-17T17:00:00",null,15.783417262503008,16.086989464158908,16.390561665814808,16.694133867470708,16.997706069126608,17.301278270782507,17.604850472438407,17.908422674094307,18.211994875750207,null,0,0,0,0,2.8810575935439953E-2,0.15739617196262731,0.28114495597145672,0.35610465746039005,0.37840656678851686,null,0.28114495597145672,0.35610465746039005,0.37840656678851686]
["2013-05-17T18:00:00","2013-05-17T18:00:00",null,14.879817414823441,15.18338961647934,15.48696181813524,15.79053401979114,16.094106221447042,16.397678423102938,16.701250624758842,17.004822826414738,17.308395028070642,null,0,0,0,0,0,5.5518190123765021E-3,0.13212908657107209,0.20982263833125153,0.23476376465200441,null,0.13212908657107209,0.20982263833125153,0.23476376465200441]
["2013-05-17T19:00:00","2013-05-17T19:00:00",null,14.598516033351126,14.902088235007026,15.205660436662926,15.509232638318826,15.812804839974726,16.116377041630628,16.419949243286524,16.723521444942428,17.027093646598324,null,0,0,0,0,0,0,9.7598454683486491E-2,0.17792070862755643,0.20540641866231532,null,9.7598454683486491E-2,0.17792070862755643,0.20540641866231532]
["2013-05-17T20:00:00","2013-05-17T20:00:00",null,14.822692375010586,15.126264576666486,15.429836778322386,15.733408979978286,16.036981181634186,16.340553383290086,16.644125584945986,16.947697786601886,17.251269988257786,null,0,0,0,0,0,0,9.16470729391584E-2,0.17472420677194558,0.20487016341680167,null,9.16470729391584E-2,0.17472420677194558,0.20487016341680167]
["2013-05-17T21:00:00","2013-05-17T21:00:00",null,14.738874358362242,15.042446560018142,15.346018761674042,15.649590963329942,15.953163164985842,16.256735366641742,16.560307568297642,16.863879769953542,17.167451971609442,null,0,0,0,0,0,0,8.5800839282185931E-2,0.17160130857748368,0.20437596740623026,null,8.5800839282185931E-2,0.17160130857748368,0.20437596740623026]
["2013-05-17T22:00:00","2013-05-17T22:00:00",null,14.634297778556054,14.937869980211953,15.241442181867853,15.545014383523753,15.848586585179653,16.152158786835553,16.455730988491453,16.759303190147353,17.062875391803253,null,0,0,0,0,0,0,7.8198632566374604E-2,0.16664883366303399,0.20197859101452212,null,7.8198632566374604E-2,0.16664883366303399,0.20197859101452212]
["2013-05-17T23:00:00","2013-05-17T23:00:00",null,14.808201466541458,15.111773668197358,15.415345869853258,15.718918071509158,16.022490273165058,16.326062474820958,16.629634676476858,16.933206878132758,17.236779079788658,null,0,0,0,0,0,0,7.2121073117219769E-2,0.1633261541025964,0.20130564325544614,null,7.2121073117219769E-2,0.1633261541025964,0.20130564325544614]
["2013-05-18","2013-05-18",null,14.367681640250915,14.671253841906815,14.974826043562715,15.278398245218614,15.581970446874514,15.885542648530414,16.189114850186314,16.492687051842214,16.796259253498114,null,2.8915724022795495E-2,3.2196344348290835E-2,3.5340272160223875E-2,3.8368537076065731E-2,4.1270624287080844E-2,4.4067563410740335E-2,0.11888042756426398,0.21267215149858887,0.25315416513050237,null,0.11888042756426398,0.21267215149858887,0.25315416513050237]
["2013-05-18T01:00:00","2013-05-18T01:00:00",null,14.612451750101974,14.916023951757873,15.219596153413773,15.523168355069673,15.826740556725573,16.130312758381471,16.433884960037375,16.737457161693271,17.041029363349175,null,8.3277285185651029E-2,8.9996247967675136E-2,9.6441825722574648E-2,0.10263504806782066,0.10858642981214875,0.11431700057303004,0.19195834827641986,0.2884734076732553,0.3315841234890593,null,0.19195834827641986,0.2884734076732553,0.3315841234890593]
["2013-05-18T02:00:00","2013-05-18T02:00:00",null,14.307379298340747,14.610951499996647,14.914523701652547,15.218095903308447,15.521668104964347,15.825240306620246,16.128812508276148,16.432384709932045,16.735956911587948,null,0.1420024919737648,0.15213876759484654,0.16186496567524139,0.17120211583242045,0.18018176249259038,0.18882493527322236,0.26926322210027165,0.36847007253341096,0.41418846091563433,null,0.26926322210027165,0.36847007253341096,0.41418846091563433]
["2013-05-18T03:00:00","2013-05-18T03:00:00",null,14.112917903328229,14.416490104984129,14.720062306640029,15.023634508295929,15.327206709951829,15.630778911607729,15.934351113263629,16.237923314919527,16.541495516575431,null,0.20698400995953795,0.22045347994979284,0.23337617988579853,0.24578365419376169,0.25770744729988898,0.26917910363038716,0.35234072591994697,0.45417627853697684,0.50241822101573508,null,0.35234072591994697,0.45417627853697684,0.50241822101573508]
["2013-05-18T04:00:00","2013-05-18T04:00:00",null,13.950857898103845,14.254430099759745,14.558002301415645,14.861574503071544,15.165146704727444,15.468718906383344,15.772291108039244,16.075863309695144,16.379435511351044,null,0.27423672663219245,0.29101836137414938,0.30712704835703042,0.32257330238957094,0.33743072713292005,0.3517098373958133,0.4375737655304125,0.54200647590512618,0.59275094286294816,null,0.4375737655304125,0.54200647590512618,0.59275094286294816]
["2013-05-18T05:00:00","2013-05-18T05:00:00",null,13.938573183488426,14.242145385144326,14.545717586800226,14.849289788456126,15.152861990112026,15.456434191767926,15.760006393423826,16.063578595079726,16.367150796735626,null,0.33948111483635468,0.35962748837369141,0.37896422163839,0.39750182943918572,0.41533494505469892,0.43246356848492945,0.52107186169951036,0.62814378906685009,0.68143283973867808,null,0.52107186169951036,0.62814378906685009,0.68143283973867808]
["2013-05-18T06:00:00","2013-05-18T06:00:00",null,13.912380948103465,14.215953149759365,14.519525351415265,14.823097553071165,15.126669754727065,15.430241956382964,15.733814158038864,16.037386359694764,16.340958561350664,null,0.4052827879035017,0.42878338542748268,0.45132713535652769,0.47294558211684307,0.49374387379578477,0.51371149558461704,0.60505363907044407,0.71475426862167424,0.77057738819877275,null,0.60505363907044407,0.71475426862167424,0.77057738819877275]
["2013-05-18T07:00:00","2013-05-18T07:00:00",null,14.051584517968422,14.355156719624322,14.658728921280222,14.962301122936122,15.265873324592022,15.569445526247922,15.873017727903822,16.176589929559722,16.480162131215621,null,0.46671030053665491,0.4936282108996935,0.51945258115423387,0.54421495572648226,0.56803099751253028,0.59090070651237769,0.68502927431312866,0.79742169490066273,0.85583145742670941,null,0.68502927431312866,0.79742169490066273,0.85583145742670941]
["2013-05-18T08:00:00","2013-05-18T08:00:00",null,14.159336893469757,14.462909095125656,14.766481296781556,15.070053498437456,15.373625700093356,15.677197901749256,15.980770103405156,16.284342305061056,16.587914506716956,null,0.52742280617578985,0.5577580293778861,0.5868525051491863,0.61474829272463216,0.64158208461778643,0.6673433660199134,0.76425835813558829,0.87934256975942626,0.94032846042568563,null,0.76425835813558829,0.87934256975942626,0.94032846042568563]
["2013-05-18T09:00:00","2013-05-18T09:00:00",null,14.347941402244377,14.651513603900277,14.955085805556177,15.258658007212077,15.562230208867977,15.865802410523877,16.169374612179777,16.472946813835676,16.776519015491576,null,0.58758854176067565,0.62130953337562278,0.65364257023747607,0.68466125600738392,0.71448125358143777,0.74312359257710869,0.84281449419897192,0.96056946724164272,1,null,0.84281449419897192,0.96056946724164272,1]
["2013-05-18T10:00:00","2013-05-18T10:00:00",null,14.717274378591481,15.020846580247381,15.324418781903281,15.627990983559181,15.931563185215081,16.235135386870979,16.538707588526883,16.842279790182779,17.145851991838683,null,0.6370607168614949,0.67425159535917745,0.70992834139893946,0.74415404383319372,0.77706539517550277,0.80867291023460219,0.91123435464127378,1,1,null,0.91123435464127378,1,1]
["2013-05-18T11:00:00","2013-05-18T11:00:00",null,15.113319842723056,15.416892044378956,15.720464246034856,16.024036447690754,16.327608649346658,16.631180851002554,16.934753052658458,17.238325254314354,17.541897455970258,null,0.66994052377759727,0.71069592243663537,0.74980049612419053,0.78732784850141124,0.82342518689059563,0.85809251129174358,0.96359810214437247,1,1,null,0.96359810214437247,1,1]
["2013-05-18T12:00:00","2013-05-18T12:00:00",null,15.294829787613633,15.598401989269533,15.901974190925433,16.205546392581333,16.509118594237233,16.812690795893133,17.116262997549033,17.419835199204933,17.723407400860832,null,0.6997920657778578,0.74412249940698694,0.78667593035980643,0.82751544748872918,0.86680928773352439,0.90454693628545646,1,1,1,null,1,1,1]
["2013-05-18T13:00:00","2013-05-18T13:00:00",null,15.546533283522569,15.850105485178469,16.153677686834371,16.457249888490267,16.760822090146171,17.064394291802067,17.367966493457971,17.671538695113867,17.97511089676977,null,0.72547974351883571,0.77345881577920494,0.81953470765843772,0.86375999320021135,0.90632393896176633,0.94721603013436706,1,1,1,null,1,1,1]
["2013-05-18T14:00:00","2013-05-18T14:00:00",null,15.663738737669641,15.967310939325541,16.270883140981439,16.574455342637343,16.878027544293239,17.181599745949143,17.485171947605039,17.788744149260943,18.092316350916839,null,0.72341884100666554,0.77508861113321703,0.82471850836506977,0.87236110674590106,0.91822670245042248,0.96230478066989855,1,1,1,null,1,1,1]
["2013-05-18T15:00:00","2013-05-18T15:00:00",null,15.657829216170509,15.961401417826409,16.264973619482308,16.568545821138208,16.872118022794108,17.175690224450008,17.479262426105908,17.782834627761808,18.086406829417708,null,0.53184954065346146,0.58715743460251746,0.64029927795204788,0.69131712993699457,0.74044231634954016,0.7876643223809493,0.8283878066268926,0.83132143826411442,0.83414992181398062,null,0.8283878066268926,0.83132143826411442,0.83414992181398062]
["2013-05-18T16:00:00","2013-05-18T16:00:00",null,15.859018331418097,16.162590533073995,16.466162734729899,16.769734936385795,17.073307138041699,17.376879339697595,17.680451541353499,17.984023743009395,18.287595944665298,null,0.33487562861017856,0.39388473523415235,0.45059109874503833,0.50504729318651376,0.55748464435076139,0.60790315223778135,0.65170747544324437,0.65762731276136577,0.66333685390477592,null,0.65170747544324437,0.65762731276136577,0.66333685390477592]
["2013-05-18T17:00:00","2013-05-18T17:00:00",null,15.883053866677605,16.186626068333503,16.490198269989406,16.793770471645303,17.097342673301206,17.400914874957103,17.704487076613006,18.008059278268902,18.311631479924806,null,0.13490499607726048,0.19766788941982991,0.25798083232701363,0.31592794326869567,0.37171951841958761,0.42537658739716067,0.47231432360582115,0.48125191103104881,0.48988456900294519,null,0.47231432360582115,0.48125191103104881,0.48988456900294519]
["2013-05-18T18:00:00","2013-05-18T18:00:00",null,15.472689461021353,15.776261662677253,16.079833864333153,16.383406065989053,16.686978267644953,16.990550469300853,17.294122670956753,17.597694872612653,17.901267074268553,null,0,4.9913797067712706E-2,0.11372817128383858,0.17504002102090047,0.23408067207108108,0.2908711540518516,0.34082664036761834,0.35267682981259674,0.36412745652562373,null,0.34082664036761834,0.35267682981259674,0.36412745652562373]
["2013-05-18T19:00:00","2013-05-18T19:00:00",null,15.759252332196453,16.062824533852353,16.366396735508253,16.669968937164153,16.973541138820053,17.277113340475953,17.580685542131853,17.884257743787753,18.187829945443653,null,0,7.2657328362732421E-3,7.4623597596283509E-2,0.13934224536366749,0.20166351673934343,0.26162947095825367,0.31464476661606899,0.3294496173157403,0.34376027200484016,null,0.31464476661606899,0.3294496173157403,0.34376027200484016]
["2013-05-18T20:00:00","2013-05-18T20:00:00",null,15.67868974486511,15.98226194652101,16.28583414817691,16.58940634983281,16.89297855148871,17.19655075314461,17.50012295480051,17.80369515645641,18.10726735811231,null,0,0,3.1144863474734649E-2,9.9333398124854089E-2,0.16499837867843875,0.22819237917916652,0.28432005822270817,0.30213214422075024,0.3193448861208652,null,0.28432005822270817,0.30213214422075024,0.3193448861208652]
["2013-05-18T21:00:00","2013-05-18T21:00:00",null,15.298207946344419,15.601780148000319,15.905352349656219,16.208924551312119,16.512496752968019,16.816068954623919,17.119641156279819,17.423213357935719,17.726785559591619,null,0,0,0,6.6989846454265381E-2,0.13593544733334539,0.20228389045474177,0.26146086403159641,0.28221709647559584,0.30226883673431254,null,0.26146086403159641,0.28221709647559584,0.30226883673431254]
["2013-05-18T22:00:00","2013-05-18T22:00:00",null,14.793068082779415,15.096640284435315,15.400212486091215,15.703784687747115,16.007356889403013,16.310929091058917,16.614501292714813,16.918073494370717,17.221645696026613,null,0,0,0,4.5487062590041094E-2,0.11763968013346751,0.18706896221438354,0.24922162666340225,0.27283788708347456,0.29565502203964406,null,0.24922162666340225,0.27283788708347456,0.29565502203964406]
["2013-05-18T23:00:00","2013-05-18T23:00:00",null,14.439020999163962,14.742593200819861,15.046165402475761,15.349737604131661,15.653309805787561,15.956882007443461,16.260454209099361,16.564026410755261,16.867598612411161,null,0,0,0,3.8336992649858938E-2,0.11361250838774727,0.18604902576703403,0.25109326261833231,0.27749594735332855,0.30299435853706636,null,0.25109326261833231,0.27749594735332855,0.30299435853706636]
["2013-05-19","2013-05-19",null,14.090800649398336,14.394372851054236,14.697945052710136,15.001517254366036,15.305089456021935,15.608661657677835,15.912233859333735,16.215806060989635,16.519378262645535,null,6.2794437768776246E-2,6.6180206181627219E-2,6.9418767272180312E-2,0.11086814330776559,0.18912986472655352,0.26442641008191314,0.33223604163066423,0.36129897297575769,0.38935248268223704,null,0.33223604163066423,0.36129897297575769,0.38935248268223704]
["2013-05-19T01:00:00","2013-05-19T01:00:00",null,14.12097969220217,14.424551893858069,14.728124095513969,15.031696297169869,15.335268498825769,15.638840700481669,15.942412902137569,16.245985103793469,16.549557305449369,null,0.12636697138398409,0.13320159706209939,0.13974180809561895,0.18436665636934396,0.26567767232144485,0.34390784931402629,0.41453544960390798,0.44631120160277643,0.4769723838756752,null,0.41453544960390798,0.44631120160277643,0.4769723838756752]
["2013-05-19T02:00:00","2013-05-19T02:00:00",null,13.818156269924604,14.121728471580504,14.425300673236404,14.728872874892303,15.032445076548203,15.336017278204103,15.639589479860003,15.943161681515903,16.246733883171803,null,0.19679516029477834,0.20700503957700905,0.21676278208361061,0.26448949893432638,0.34876569094985577,0.42984538110977449,0.50321734647963789,0.53762180066239684,0.57082756664930157,null,0.50321734647963789,0.53762180066239684,0.57082756664930157]
["2013-05-19T03:00:00","2013-05-19T03:00:00",null,13.540349567737888,13.843921769393788,14.147493971049688,14.451066172705588,14.754638374361488,15.058210576017387,15.361782777673287,15.665354979329187,15.968927180985087,null,0.27368995657794326,0.28719097099440483,0.30009264131293945,0.35083710827076153,0.43800487268857047,0.52186047235467758,0.59790319914337364,0.6348627518488742,0.67053949788863598,null,0.59790319914337364,0.6348627518488742,0.67053949788863598]
["2013-05-19T04:00:00","2013-05-19T04:00:00",null,13.528913305032511,13.83248550668841,14.13605770834431,14.43962991000021,14.74320211165611,15.04677431331201,15.35034651496791,15.65391871662381,15.95749091827971,null,0.35111049329788624,0.36790264284857871,0.3839377261703108,0.4376999432352392,0.52774876524659209,0.61438027441888765,0.69308324781768083,0.73259789904592298,0.77073511032980624,null,0.69308324781768083,0.73259789904592298,0.77073511032980624]
["2013-05-19T05:00:00","2013-05-19T05:00:00",null,13.672622858089571,13.976195059745471,14.279767261401371,14.583339463057271,14.886911664713171,15.190483866369071,15.494056068024971,15.797628269680871,16.101200471336771,null,0.42365215876452844,0.44380904711060076,0.46305114709667927,0.51989420312112733,0.61289768638717312,0.70236819391807048,0.78379450277937424,0.82592734138277124,0.86658810676318943,null,0.78379450277937424,0.82592734138277124,0.86658810676318943]
["2013-05-19T06:00:00","2013-05-19T06:00:00",null,13.737500365353615,14.041072567009515,14.344644768665415,14.648216970321315,14.951789171977214,15.255361373633114,15.558933575289014,15.862505776944914,16.166077978600814,null,0.49666699062427094,0.52015707333951644,0.54258516037247018,0.60248802573896687,0.69841462583349889,0.79070310210552686,0.87483171681187,0.91957222798168636,0.96273551784116829,null,0.87483171681187,0.91957222798168636,0.96273551784116829]
["2013-05-19T07:00:00","2013-05-19T07:00:00",null,13.827711515143914,14.131283716799814,14.434855918455714,14.738428120111614,15.042000321767514,15.345572523423414,15.649144725079314,15.952716926735214,16.256289128391114,null,0.56682179450794057,0.59368713082730151,0.61934326414207275,0.68234799808556024,0.78123977424352076,0.8763882784916216,0.9632612582779464,1,1,null,0.9632612582779464,1,1]
["2013-05-19T08:00:00","2013-05-19T08:00:00",null,14.082480548447357,14.386052750103257,14.689624951759157,14.993197153415057,15.296769355070957,15.600341556726857,15.903913758382757,16.207485960038657,16.511058161694557,null,0.63149838304038242,0.66179154700753662,0.6907388154565387,0.75689799202069485,0.85882854790323271,0.95688965417108429,1,1,1,null,1,1,1]
["2013-05-19T09:00:00","2013-05-19T09:00:00",null,13.018267535579778,13.321839737235678,13.625411938891578,13.928984140547477,14.232556342203377,14.536128543859277,14.839700745515177,15.143272947171077,15.446845148826977,null,0.57650593335339317,0.60958552163547131,0.6412035515033061,0.70991782659020386,0.8142983329081277,0.91469372671527405,0.96005424161359998,0.96220977740439018,0.96428119472529594,null,0.96005424161359998,0.96220977740439018,0.96428119472529594]
["2013-05-19T10:00:00","2013-05-19T10:00:00",null,14.070928218528957,14.374500420184857,14.678072621840757,14.981644823496657,15.285217025152557,15.588789226808457,15.892361428464357,16.195933630120258,16.499505831776155,null,0.41956189816639478,0.45596416600891054,0.49075766811488503,0.56252123773509577,0.66982486088150583,0.77303822342978279,0.82110104417314822,0.82586425253035778,0.83043819433032728,null,0.82110104417314822,0.82586425253035778,0.83043819433032728]
["2013-05-19T11:00:00","2013-05-19T11:00:00",null,14.310578207457397,14.614150409113297,14.917722610769196,15.221294812425096,15.524867014080996,15.828439215736896,16.132011417392796,16.435583619048696,16.739155820704596,null,0.254921022984965,0.29474060366653843,0.33281472609800822,0.40773273833888757,0.51806462640113948,0.62418007616043159,0.67505035083619203,0.68250535022970549,0.68968696459609435,null,0.67505035083619203,0.68250535022970549,0.68968696459609435]
["2013-05-19T12:00:00","2013-05-19T12:00:00",null,15.024287755939072,15.327859957594972,15.631432159250872,15.935004360906772,16.23857656256267,16.542148764218574,16.84572096587447,17.149293167530374,17.45286536918627,null,7.3792927706174016E-2,0.11719805816657408,0.15872103786330821,0.2369512148558896,0.3504796047737524,0.45966537868382856,0.51350082942301745,0.52381585679260378,0.5337628658564455,null,0.51350082942301745,0.52381585679260378,0.5337628658564455]
["2013-05-19T13:00:00","2013-05-19T13:00:00",null,14.765875412964089,15.069447614619989,15.373019816275889,15.676592017931789,15.980164219587689,16.283736421243589,16.587308622899489,16.890880824555389,17.194453026211288,null,0,0,1.0893341850042093E-2,9.2309505889498766E-2,0.20889770514941008,0.32102762550544361,0.37770207460323424,0.3907509522440667,0.4033371783005345,null,0.37770207460323424,0.3907509522440667,0.4033371783005345]
["2013-05-19T14:00:00","2013-05-19T14:00:00",null,14.984818912009473,15.288391113665373,15.591963315321273,15.895535516977173,16.199107718633073,16.502679920288973,16.806252121944873,17.109824323600773,17.413396525256672,null,0,0,0,6.7799486726903752E-2,0.18753161379874811,0.30267928426188795,0.36226633537942921,0.37812266695265673,0.39341119885416398,null,0.36226633537942921,0.37812266695265673,0.39341119885416398]
["2013-05-19T15:00:00","2013-05-19T15:00:00",null,15.211670072783171,15.515242274439071,15.818814476094971,16.122386677750871,16.425958879406771,16.729531081062671,17.033103282718571,17.336675484374471,17.640247686030371,null,0,0,0,4.6811928490722007E-2,0.16975107222691277,0.28799009645830786,0.3505633532567487,0.36930074242352023,0.38736518383121582,null,0.3505633532567487,0.36930074242352023,0.38736518383121582]
["2013-05-19T16:00:00","2013-05-19T16:00:00",null,15.25994499942073,15.56351720107663,15.86708940273253,16.170661604388428,16.474233806044332,16.777806007700228,17.081378209356131,17.384950411012028,17.688522612667931,null,0,0,0,2.4552078397537258E-2,0.15070875360680999,0.27206016122393145,0.33763013851200746,0.35925910008105855,0.3801204806124136,null,0.33763013851200746,0.35925910008105855,0.3801204806124136]
["2013-05-19T17:00:00","2013-05-19T17:00:00",null,15.373490453502367,15.677062655158267,15.980634856814167,16.284207058470066,16.587779260125966,16.891351461781866,17.194923663437766,17.498495865093666,17.802068066749566,null,0,0,0,0,0.12865919968833647,0.253154535117391,0.32175277732130886,0.34630485571884617,0.36999471980006737,null,0.32175277732130886,0.34630485571884617,0.36999471980006737]
["2013-05-19T18:00:00","2013-05-19T18:00:00",null,15.366630973513919,15.670203175169819,15.973775376825719,16.277347578481617,16.580919780137521,16.884491981793417,17.18806418344932,17.491636385105217,17.79520858676112,null,0,0,0,0,0.10451719883148612,0.23218800649868038,0.30385657285338236,0.33137382731434811,0.35792371937164219,null,0.30385657285338236,0.33137382731434811,0.35792371937164219]
["2013-05-19T19:00:00","2013-05-19T19:00:00",null,15.345861979901878,15.649434181557778,15.953006383213678,16.25657858486958,16.560150786525476,16.863722988181379,17.167295189837276,17.470867391493179,17.774439593149076,null,0,0,0,0,8.0942997646356124E-2,0.21177876274295454,0.28651765324844064,0.3169895689640993,0.34638897418873066,null,0.28651765324844064,0.3169895689640993,0.34638897418873066]
["2013-05-19T20:00:00","2013-05-19T20:00:00",null,15.302627192386007,15.606199394041907,15.909771595697807,16.213343797353708,16.516915999009605,16.820488200665508,17.124060402321405,17.427632603977308,17.731204805633205,null,0,0,0,0,5.8556969848344631E-2,0.19254717756561165,0.27033536260441071,0.30375142476602673,0.33598982834925983,null,0.27033536260441071,0.30375142476602673,0.33598982834925983]
["2013-05-19T21:00:00","2013-05-19T21:00:00",null,15.491057384577861,15.794629586233761,16.098201787889661,16.401773989545561,16.70534619120146,17.00891839285736,17.31249059451326,17.61606279616916,17.91963499782506,null,0,0,0,0,2.8894694405324235E-2,0.16614449283061547,0.24707660568134757,0.28352093275880547,0.31869296797926033,null,0.24707660568134757,0.28352093275880547,0.31869296797926033]
["2013-05-19T22:00:00","2013-05-19T22:00:00",null,15.017078963777339,15.320651165433238,15.624223367089138,15.927795568745038,16.231367770400936,16.53493997205684,16.838512173712736,17.14208437536864,17.445656577024536,null,0,0,0,0,1.1692467313944806E-2,0.15206516393369796,0.23599399727406523,0.27534041156253825,0.31330938590665258,null,0.23599399727406523,0.27534041156253825,0.31330938590665258]
["2013-05-19T23:00:00","2013-05-19T23:00:00",null,14.604196806646932,14.907769008302832,15.211341209958732,15.514913411614632,15.818485613270532,16.122057814926432,16.425630016582332,16.729202218238232,17.032774419894132,null,0,0,0,0,1.4720732229785444E-3,0.14491509399351579,0.23179858858857599,0.27398400123565075,0.31469734065974675,null,0.23179858858857599,0.27398400123565075,0.31469734065974675]
["2013-05-20","2013-05-20",null,14.231073357846935,14.534645559502835,14.838217761158734,15.141789962814634,15.445362164470534,15.748934366126434,16.052506567782334,16.356078769438234,16.659650971094134,null,3.6086823580448776E-2,3.9535680845713114E-2,4.2826815979944019E-2,4.6002288218083741E-2,5.0513141165639701E-2,0.19687927876466318,0.28658074210085399,0.33147897540170373,0.37479998739221915,null,0.28658074210085399,0.33147897540170373,0.37479998739221915]
["2013-05-20T01:00:00","2013-05-20T01:00:00",null,14.254004954264364,14.557577155920264,14.861149357576164,15.164721559232063,15.468293760887963,15.771865962543863,16.075438164199763,16.379010365855663,16.682582567511563,null,8.5159435949316617E-2,9.2057150479845293E-2,9.8660450365778224E-2,0.10501139484205768,0.11257154232292661,0.26188182636790747,0.35440125844522885,0.40202282720858917,0.44796202657425954,null,0.35440125844522885,0.40202282720858917,0.44796202657425954]
["2013-05-20T02:00:00","2013-05-20T02:00:00",null,14.152714550078777,14.456286751734677,14.759858953390577,15.063431155046477,15.367003356702376,15.670575558358276,15.974147760014176,16.277719961670076,16.581292163325976,null,0.13586184367219656,0.14616635623304733,0.15603976163574004,0.16552411911521697,0.17609150189445666,0.32829335834171702,0.42359921473396234,0.47390205972489097,0.52242790203950962,null,0.42359921473396234,0.47390205972489097,0.52242790203950962]
["2013-05-20T03:00:00","2013-05-20T03:00:00",null,14.00267538921905,14.30624759087495,14.60981979253085,14.91339199418675,15.21696419584265,15.52053639749855,15.824108599154449,16.127680800810349,16.431253002466249,null,0.19767840422856553,0.21132662596732504,0.22439653322562858,0.2369512148558896,0.25046274408108665,0.40550359888694876,0.50353279074170465,0.55645382310778824,0.60750321951894171,null,0.50353279074170465,0.55645382310778824,0.60750321951894171]
["2013-05-20T04:00:00","2013-05-20T04:00:00",null,13.970381269082743,14.273953470738643,14.577525672394543,14.881097874050443,15.184670075706343,15.488242277362243,15.791814479018143,16.095386680674043,16.398958882329943,null,0.26432126199455747,0.28129216329375456,0.29754805759893338,0.31316254857124298,0.3296077094336618,0.48746653298065451,0.58820854548918544,0.64373725042168839,0.69729968612064119,null,0.58820854548918544,0.64373725042168839,0.69729968612064119]
["2013-05-20T05:00:00","2013-05-20T05:00:00",null,14.144612966511005,14.448185168166905,14.751757369822805,15.055329571478705,15.358901773134605,15.662473974790505,15.966046176446405,16.269618378102304,16.573190579758204,null,0.32530715266081706,0.34567433718160068,0.36520033700353927,0.38394824097904634,0.40340063713983587,0.56415103308910819,0.66766895510382751,0.72587893626389866,0.78201750010306426,null,0.66766895510382751,0.72587893626389866,0.78201750010306426]
["2013-05-20T06:00:00","2013-05-20T06:00:00",null,14.11934066548535,14.42291286714125,14.72648506879715,15.03005727045305,15.333629472108949,15.637201673764849,15.940773875420749,16.244346077076649,16.547918278732549,null,0.38431625928479096,0.40813230107083892,0.43095995083574401,0.45288332704939083,0.47538501774349329,0.63905853052125183,0.74539442127710176,0.80631722309094789,0.86506345949653296,null,0.74539442127710176,0.80631722309094789,0.86506345949653296]
["2013-05-20T07:00:00","2013-05-20T07:00:00",null,14.214008380771656,14.517580582427556,14.821152784083456,15.124724985739356,15.428297187395255,15.731869389051155,16.035441590707055,16.339013792362955,16.642585994018855,null,0.44279962547198681,0.47005400971456351,0.49617279461369951,0.52126112825675053,0.54679108386669484,0.71338771347293961,0.82253105816118455,0.88615616582007017,0.94751007479207461,null,0.82253105816118455,0.88615616582007017,0.94751007479207461]
["2013-05-20T08:00:00","2013-05-20T08:00:00",null,14.396941033232755,14.700513234888655,15.004085436544555,15.307657638200455,15.611229839856355,15.914802041512255,16.218374243168157,16.521946444824053,16.825518646479956,null,0.49300783718429536,0.523721593500872,0.55315254315170992,0.58142686384163622,0.61001662879362917,0.77955740484583125,0.89152923308394239,0.95788819101407408,1,null,0.89152923308394239,0.95788819101407408,1]
["2013-05-20T09:00:00","2013-05-20T09:00:00",null,14.738996504950666,15.042568706606566,15.346140908262466,15.649713109918366,15.953285311574266,16.256857513230166,16.560429714886066,16.864001916541966,17.167574118197866,null,0.52613999951005119,0.56038673156177665,0.59321396443420116,0.62475839064088723,0.65648156859607765,0.82905060956412158,0.94393503982198335,1,1,null,0.94393503982198335,1,1]
["2013-05-20T10:00:00","2013-05-20T10:00:00",null,15.013493693645955,15.317065895301855,15.620638096957755,15.924210298613655,16.227782500269555,16.531354701925455,16.834926903581355,17.138499105237255,17.442071306893155,null,0.5513019368142511,0.5891342186448032,0.62539979397375645,0.66026689974088004,0.6951760647429458,0.87081542986177385,0.98866503618306412,1,1,null,0.98866503618306412,1,1]
["2013-05-20T11:00:00","2013-05-20T11:00:00",null,15.379762325029454,15.683334526685353,15.986906728341253,16.290478929997153,16.594051131653053,16.897623333308953,17.201195534964853,17.504767736620753,17.808339938276653,null,0.56403537019301664,0.60556886469848659,0.64538844538005979,0.68368337879497665,0.72189419374000885,0.90071954590571213,1,1,1,null,1,1,1]
["2013-05-20T12:00:00","2013-05-20T12:00:00",null,15.47566382095426,15.77923602261016,16.08280822426606,16.38638042592196,16.68995262757786,16.99352482923376,17.29709703088966,17.60066923254556,17.90424143420146,null,0.5822575337317456,0.62747121129466221,0.67083428252011978,0.7125465287740943,0.75404847885335746,0.93603878844846489,1,1,1,null,1,1,1]
["2013-05-20T13:00:00","2013-05-20T13:00:00",null,15.576757761302142,15.880329962958042,16.18390216461394,16.487474366269844,16.79104656792574,17.094618769581643,17.39819097123754,17.701763172893443,18.00533537454934,null,0.60659931595457162,0.65547214695746381,0.70236819391807026,0.74747672339363125,0.79224877898965418,0.97740404601416575,1,1,1,null,1,1,1]
["2013-05-20T14:00:00","2013-05-20T14:00:00",null,15.596952718075217,15.900524919731117,16.204097121387015,16.507669323042919,16.811241524698815,17.114813726354718,17.418385928010615,17.721958129666518,18.025530331322415,null,0.62138313703677184,0.6739256362883751,0.72435465898413043,0.77286998649001348,0.82092266241153178,1,1,1,1,null,1,1,1]
["2013-05-20T15:00:00","2013-05-20T15:00:00",null,16.209054371815533,16.512626573471429,16.816198775127333,17.119770976783229,17.423343178439133,17.726915380095029,18.030487581750933,18.334059783406829,18.637631985062733,null,0.41303220194161083,0.46940209157295865,0.52352181213489624,0.57560165980213485,0.62709267818018188,0.80948218052035215,0.81268919718469856,0.81579106576168936,0.81879830106006013,null,0.81268919718469856,0.81579106576168936,0.81879830106006013]
["2013-05-20T16:00:00","2013-05-20T16:00:00",null,16.214937514719082,16.518509716374986,16.822081918030882,17.125654119686786,17.429226321342682,17.732798522998586,18.036370724654482,18.339942926310385,18.643515127966282,null,0.20453405952415199,0.26473133953524436,0.32254175796336421,0.37818612579195832,0.43311548662653415,0.61882766852714199,0.62524170185583483,0.63144543900981642,0.63745990960655785,null,0.62524170185583483,0.63144543900981642,0.63745990960655785]
["2013-05-20T17:00:00","2013-05-20T17:00:00",null,16.056062921340676,16.359635122996579,16.663207324652475,16.966779526308379,17.270351727964275,17.573923929620179,17.877496131276075,18.181068332931979,18.484640534587875,null,0,5.947175820833861E-2,0.12102544854631853,0.18027639577121041,0.23868615829725726,0.42775256418450935,0.43741567341249088,0.44675282356966994,0.45579555908225322,null,0.43741567341249088,0.44675282356966994,0.45579555908225322]
["2013-05-20T18:00:00","2013-05-20T18:00:00",null,15.360653434671887,15.664225636327787,15.967797837983687,16.271370039639585,16.574942241295489,16.878514442951385,17.182086644607288,17.485658846263185,17.789231047919088,null,0,0,3.8726040573074771E-2,0.10140481544575987,0.16310571310603761,0.35535810604016499,0.3680810246101951,0.3803833508308026,0.39228611431945876,null,0.3680810246101951,0.3803833508308026,0.39228611431945876]
["2013-05-20T19:00:00","2013-05-20T19:00:00",null,15.642144845693679,15.945717047349579,16.249289249005479,16.552861450661378,16.856433652317278,17.160005853973178,17.463578055629078,17.767150257284978,18.070722458940878,null,0,0,0,4.5539636633718975E-2,0.11061578789811212,0.30612777154026372,0.32199461792222683,0.33733572386741179,0.35217211899328971,null,0.32199461792222683,0.33733572386741179,0.35217211899328971]
["2013-05-20T20:00:00","2013-05-20T20:00:00",null,15.533944504148968,15.837516705804868,16.14108890746077,16.444661109116666,16.748233310772569,17.051805512428466,17.355377714084369,17.658949915740266,17.962522117396169,null,0,0,0,0,6.0754564874077127E-2,0.25948407998931067,0.27847382456573572,0.29682216580929144,0.31456064814618445,null,0.27847382456573572,0.29682216580929144,0.31456064814618445]
["2013-05-20T21:00:00","2013-05-20T21:00:00",null,15.267933885711653,15.571506087367553,15.875078289023453,16.178650490679352,16.482222692335252,16.785794893991152,17.089367095647052,17.392939297302952,17.696511498958852,null,0,0,0,0,1.8085471025166541E-2,0.21995891395233313,0.24198743825333557,0.26326941113411312,0.28384689182960787,null,0.24198743825333557,0.26326941113411312,0.28384689182960787]
["2013-05-20T22:00:00","2013-05-20T22:00:00",null,14.797528830856633,15.101101032512533,15.404673234168433,15.708245435824333,16.011817637480235,16.315389839136131,16.618962040792034,16.922534242447931,17.226106444103834,null,0,0,0,0,0,0.19961275904902068,0.22453285575230267,0.24860125294800414,0.27187052467980277,null,0.22453285575230267,0.24860125294800414,0.27187052467980277]
["2013-05-20T23:00:00","2013-05-20T23:00:00",null,14.602610386434105,14.906182588090005,15.209754789745904,15.513326991401804,15.816899193057704,16.120471394713604,16.424043596369504,16.727615798025404,17.031187999681304,null,0,0,0,0,0,0.18345149802246188,0.21118956346687448,0.23798129612508653,0.26386875523204012,null,0.21118956346687448,0.23798129612508653,0.26386875523204012]
["2013-05-21","2013-05-21",null,14.340483035415714,14.644055237071614,14.947627438727514,15.251199640383414,15.554771842039314,15.858344043695213,16.161916245351115,16.465488447007012,16.769060648662915,null,1.0577897587975369E-2,1.4016240044504143E-2,1.7307375178735047E-2,2.0461817799403648E-2,2.3500597523981065E-2,0.20987521237492918,0.24043124656047241,0.26993579987245941,0.29843093154583239,null,0.24043124656047241,0.26993579987245941,0.29843093154583239]
["2013-05-21T01:00:00","2013-05-21T01:00:00",null,14.271508404315984,14.575080605971884,14.878652807627784,15.182225009283684,15.485797210939584,15.789369412595484,16.092941614251384,16.396513815907284,16.700086017563184,null,4.5981258600612612E-2,5.2815884278727916E-2,5.9377124929718597E-2,6.5664980553584676E-2,7.1710995576532821E-2,0.26097718282976046,0.29431964133022764,0.32651598567851853,0.35758724549210419,null,0.29431964133022764,0.32651598567851853,0.35758724549210419]
["2013-05-21T02:00:00","2013-05-21T02:00:00",null,14.178615241829103,14.482187443485003,14.785759645140903,15.089331846796803,15.392904048452703,15.696476250108603,16.000048451764503,16.303620653420403,16.607192855076303,null,8.1689549066581157E-2,9.1941487583754117E-2,0.10178334856024013,0.11121513199603925,0.12027889712609369,0.31244717159033641,0.34858656921446313,0.38347470459905786,0.41714312217032734,null,0.34858656921446313,0.38347470459905786,0.41714312217032734]
["2013-05-21T03:00:00","2013-05-21T03:00:00",null,13.968935179263902,14.272507380919802,14.576079582575701,14.879651784231601,15.183223985887501,15.486796187543401,15.790368389199301,16.093940590855201,16.397512792511101,null,0.13216063099727876,0.14567216022247592,0.1586474342021594,0.17108645293632926,0.18303127565992769,0.37796494482162324,0.41677510386458266,0.454218337771919,0.49035773539604555,null,0.41677510386458266,0.454218337771919,0.49035773539604555]
["2013-05-21T04:00:00","2013-05-21T04:00:00",null,14.077635909497182,14.381208111153082,14.684780312808982,14.988352514464882,15.291924716120782,15.595496917776682,15.899069119432582,16.202641321088482,16.506213522744382,null,0.18489239680612218,0.20172660559175692,0.21787735180958012,0.23336566507706297,0.24824411943788321,0.4459957573407094,0.48750822222870821,0.52755912870246391,0.56621156561438979,null,0.48750822222870821,0.52755912870246391,0.56621156561438979]
["2013-05-21T05:00:00","2013-05-21T05:00:00",null,14.347117559836585,14.650689761492485,14.954261963148385,15.257834164804285,15.561406366460185,15.864978568116085,16.168550769771983,16.472122971427886,16.775695173083783,null,0.23247190633454023,0.25273394276796818,0.27218633892875782,0.29083960962564487,0.30875684371104251,0.50943159844235497,0.55376203207148433,0.59652575919901507,0.63778586867736031,null,0.55376203207148433,0.59652575919901507,0.63778586867736031]
["2013-05-21T06:00:00","2013-05-21T06:00:00",null,14.502968340108426,14.806540541764326,15.110112743420226,15.413684945076126,15.717257146732026,16.020829348387927,16.324401550043824,16.627973751699727,16.931545953355624,null,0.27410003411863015,0.2978635018610003,0.3206701220084342,0.3425514389871388,0.36357054164952718,0.56722098725300374,0.61443247847567706,0.65996160030066064,0.7038924711978386,null,0.61443247847567706,0.65996160030066064,0.7038924711978386]
["2013-05-21T07:00:00","2013-05-21T07:00:00",null,14.635834504620751,14.939406706276651,15.242978907932551,15.546551109588451,15.850123311244351,16.153695512900249,16.457267714556153,16.760839916212049,17.064412117867953,null,0.29814740169686044,0.32546487479185054,0.35167829296960651,0.37682971546507094,0.40100326074812787,0.60768197126744627,0.65781657931860582,0.70616366988472001,0.75280736143567306,null,0.65781657931860582,0.70616366988472001,0.75280736143567306]
["2013-05-21T08:00:00","2013-05-21T08:00:00",null,14.759979406821973,15.063551608477873,15.367123810133773,15.670696011789673,15.974268213445573,16.277840415101473,16.581412616757373,16.884984818413272,17.188557020069172,null,0.31942937457763793,0.3502903382165124,0.37990003961585489,0.40833208243681468,0.43564955553180462,0.64535653096696488,0.69841425584661065,0.74957931515385545,0.79893582735858359,null,0.69841425584661065,0.74957931515385545,0.79893582735858359]
["2013-05-21T09:00:00","2013-05-21T09:00:00",null,14.942842670647622,15.246414872303522,15.549987073959421,15.853559275615321,16.157131477271221,16.460703678927121,16.764275880583021,17.067848082238921,17.371420283894821,null,0.33362436637064663,0.36809190940581887,0.40117149768789684,0.43293673487802975,0.46347173944610165,0.67627006864951711,0.73230348440132698,0.78633908649338025,0.83847150820429672,null,0.73230348440132698,0.78633908649338025,0.83847150820429672]
["2013-05-21T10:00:00","2013-05-21T10:00:00",null,15.062209866533212,15.365782068189112,15.669354269845012,15.972926471500912,16.276498673156812,16.580070874812712,16.883643076468612,17.187215278124512,17.490787479780412,null,0.34548507062436057,0.3836012522907728,0.42019278669052851,0.45533327748477681,0.48911735795213734,0.70503858535001473,0.76408975120893086,0.82103795532073487,0.87597783096404636,null,0.76408975120893086,0.82103795532073487,0.87597783096404636]
["2013-05-21T11:00:00","2013-05-21T11:00:00",null,15.036395335910079,15.339967537565979,15.643539739221879,15.947111940877779,16.250684142533679,16.554256344189579,16.857828545845479,17.161400747501379,17.464972949157278,null,0.35826056323806837,0.40002538353572065,0.44011834924441851,0.47862357883404666,0.51564622039196029,0.73469034598429961,0.79674874714158639,0.85659903846440555,0.91433585323137656,null,0.79674874714158639,0.85659903846440555,0.91433585323137656]
["2013-05-21T12:00:00","2013-05-21T12:00:00",null,15.107776607489839,15.411348809145739,15.714921010801639,16.018493212457539,16.322065414113439,16.625637615769339,16.929209817425239,17.232782019081139,17.536354220737039,null,0.36889103486972158,0.41432552341608497,0.45794095005119612,0.4998319480536752,0.5401246951283486,0.76231274853262099,0.82739941460574962,0.890172822757055,0.95072760626515662,null,0.82739941460574962,0.890172822757055,0.95072760626515662]
["2013-05-21T13:00:00","2013-05-21T13:00:00",null,15.107160919104041,15.410733120759941,15.714305322415841,16.017877524071743,16.321449725727639,16.625021927383543,16.928594129039439,17.232166330695343,17.535738532351239,null,0.3819188828930829,0.43095995083574407,0.47805577916232622,0.52329048634271402,0.56680076489046938,0.79209068687173256,0.86017407343449637,0.92582853917934571,0.98916974700237126,null,0.86017407343449637,0.92582853917934571,0.98916974700237126]
["2013-05-21T14:00:00","2013-05-21T14:00:00",null,13.967537954502845,14.271110156158745,14.574682357814645,14.878254559470545,15.181826761126445,15.485398962782345,15.788971164438244,16.092543366094144,16.396115567750044,null,0.39806962911090615,0.45094860224204741,0.50172461362607623,0.55048178173287732,0.59738834350221925,0.82592734138277102,0.8971441409487324,0.96580584199195241,1,null,0.8971441409487324,0.96580584199195241,1]
["2013-05-21T15:00:00","2013-05-21T15:00:00",null,12.811192583515123,13.114764785171023,13.418336986826922,13.721909188482822,14.025481390138722,14.329053591794622,14.632625793450522,14.936197995106422,15.239770196762322,null,0.27405797488368794,0.33020705353158897,0.38409544830134418,0.4358283072803093,0.48558438221698852,0.71685723036878646,0.79068170250116721,0.86185644283218654,0.89845849204067774,null,0.79068170250116721,0.86185644283218654,0.89845849204067774]
["2013-05-21T16:00:00","2013-05-21T16:00:00",null,12.777586186717331,13.081158388373231,13.384730590029131,13.688302791685031,13.991874993340931,14.29544719499683,14.59901939665273,14.90259159830863,15.20616379996453,null,0.13136150553337606,0.19082274893297912,0.24787610113213851,0.30262671021820992,0.35527435755716869,0.58931260040641942,0.6657868043401618,0.73950612838518714,0.77855812802906432,null,0.6657868043401618,0.73950612838518714,0.77855812802906432]
["2013-05-21T17:00:00","2013-05-21T17:00:00",null,12.738219828385891,13.04179203004179,13.34536423169769,13.64893643335359,13.95250863500949,14.25608083666539,14.55965303832129,14.86322523997719,15.16679744163309,null,0,5.2878973131141288E-2,0.11307625314223371,0.17082358271794026,0.22634177284170748,0.46312438077093987,0.5422272868885728,0.61847016503013297,0.65994057068318945,null,0.5422272868885728,0.61847016503013297,0.65994057068318945]
["2013-05-21T18:00:00","2013-05-21T18:00:00",null,12.590629158958782,12.894201360614682,13.197773562270582,13.501345763926482,13.804917965582382,14.108490167238282,14.412062368894182,14.715634570550082,15.019206772205981,null,0,0,5.1343811055749221E-2,0.11200374265120644,0.17029784228116202,0.40975121162922717,0.49139870146086612,0.57009153003781221,0.61390673803889906,null,0.49139870146086612,0.57009153003781221,0.61390673803889906]
["2013-05-21T19:00:00","2013-05-21T19:00:00",null,13.038705282804703,13.342277484460602,13.645849686116502,13.949421887772402,14.252994089428302,14.556566291084202,14.860138492740102,15.163710694396002,15.467282896051902,null,0,0,3.2816718063688979E-2,9.6589033044872555E-2,0.15784830873825662,0.40015119125365906,0.48453253135654412,0.56584354730864517,0.61218230940626694,null,0.48453253135654412,0.56584354730864517,0.61218230940626694]
["2013-05-21T20:00:00","2013-05-21T20:00:00",null,12.838102315384536,13.141674517040435,13.445246718696335,13.748818920352235,14.052391122008135,14.355963323664035,14.659535525319935,14.963107726975835,15.266679928631735,null,1.847451894838243E-2,2.1755139273877774E-2,5.7705270340764225E-2,0.12447430581158297,0.1885936094810399,0.43364085707642402,0.52065089936319953,0.60448546941183556,0.65325315232737213,null,0.52065089936319953,0.60448546941183556,0.65325315232737213]
["2013-05-21T21:00:00","2013-05-21T21:00:00",null,12.581868786204298,12.885440987860198,13.189013189516098,13.492585391171998,13.796157592827898,14.099729794483798,14.403301996139698,14.706874197795598,15.010446399451498,null,7.9838942729122259E-2,8.6305550101492878E-2,0.12529446089295676,0.1949655835747906,0.26186079675043589,0.50956829095591716,0.59912291695669873,0.68539692263198515,0.73650940789555208,null,0.59912291695669873,0.68539692263198515,0.73650940789555208]
["2013-05-21T22:00:00","2013-05-21T22:00:00",null,12.296792980680664,12.600365182336564,12.903937383992464,13.207509585648364,13.511081787304263,13.814653988960163,14.118226190616063,14.421798392271963,14.725370593927863,null,0.14924719519256702,0.15877361190698616,0.2006856395269363,0.27314318652369407,0.34269864630943653,0.59295072422892381,0.68493427104762017,0.77354256426220136,0.82689470378644303,null,0.68493427104762017,0.77354256426220136,0.82689470378644303]
["2013-05-21T23:00:00","2013-05-21T23:00:00",null,12.184075744057903,12.487647945713803,12.791220147369703,13.094792349025603,13.398364550681503,13.701936752337403,14.005508953993303,14.309081155649203,14.612653357305103,null,0.235910248791069,0.24849647484753667,0.29332110448723747,0.36855456099018363,0.44075975257728772,0.69354589940204547,0.78794785222992103,0.8788799181750615,0.93446119715124221,null,0.78794785222992103,0.8788799181750615,0.93446119715124221]
["2013-05-22","2013-05-22",null,11.997159136039308,12.300731337695208,12.604303539351108,12.907875741007008,13.211447942662907,13.515020144318807,13.818592345974707,14.122164547630607,14.425736749286507,null,0.34132120636507801,0.35690415291118088,0.40457829571821896,0.48252457287494011,0.55731640741099242,0.81257353428860735,0.90934131908198435,1,1,null,0.90934131908198435,1,1]
["2013-05-22T01:00:00","2013-05-22T01:00:00",null,11.895829544125167,12.199401745781067,12.502973947436967,12.806546149092867,13.110118350748767,13.413690552404667,13.717262754060567,14.020834955716467,14.324407157372367,null,0.4130111723241397,0.43143311722884431,0.48179905107218629,0.56231094156038453,0.63955272653182282,0.89714414094873252,0.99615158000278425,1,1,null,0.99615158000278425,1,1]
["2013-05-22T02:00:00","2013-05-22T02:00:00",null,11.708609900294508,12.012182101950408,12.315754303606308,12.619326505262208,12.922898706918108,13.226470908574008,13.530043110229908,13.833615311885808,14.137187513541708,null,0.4541345892889227,0.47538501774349345,0.52845325743187488,0.61153076125155026,0.69122249665837443,0.95114819861457889,1,1,1,null,1,1,1]
["2013-05-22T03:00:00","2013-05-22T03:00:00",null,11.794946998095419,12.098519199751319,12.402091401407219,12.705663603063119,13.009235804719019,13.312808006374919,13.616380208030819,13.919952409686719,14.223524611342619,null,0.49497410641784551,0.51905301842228246,0.57480253433823214,0.66044565148938472,0.74257682252285928,1,1,1,1,null,1,1,1]
["2013-05-22T04:00:00","2013-05-22T04:00:00",null,11.784117661126967,12.087689862782867,12.391262064438767,12.694834266094666,12.998406467750566,13.301978669406466,13.605550871062366,13.909123072718266,14.212695274374166,null,0.53619215666124853,0.56308903740681615,0.62151982955033414,0.70971804522422821,0.79427813707561767,1,1,1,1,null,1,1,1]
["2013-05-22T05:00:00","2013-05-22T05:00:00",null,11.630306182223917,11.933878383879817,12.237450585535717,12.541022787191617,12.844594988847517,13.148167190503417,13.451739392159316,13.755311593815216,14.058883795471116,null,0.57130110302929005,0.60121573388196392,0.66250655400155478,0.75342810513795944,0.84058535474703266,1,1,1,1,null,1,1,1]
["2013-05-22T06:00:00","2013-05-22T06:00:00",null,11.733776404322334,12.037348605978234,12.340920807634134,12.644493009290034,12.948065210945934,13.251637412601834,13.555209614257734,13.858781815913634,14.162354017569534,null,0.6051482723490641,0.63809116811757982,0.70224201621324356,0.79589741762089439,0.88566233979638698,1,1,1,1,null,1,1,1]
["2013-05-22T07:00:00","2013-05-22T07:00:00",null,12.189872085843444,12.493444287499344,12.797016489155244,13.100588690811144,13.404160892467043,13.707733094122943,14.011305295778843,14.314877497434743,14.618449699090643,null,0.63603026560540965,0.67195936705482506,0.73894921350909049,0.8353174355705163,0.92767951550369276,1,1,1,1,null,1,1,1]
["2013-05-22T08:00:00","2013-05-22T08:00:00",null,12.73024888374664,13.03382108540254,13.33739328705844,13.64096548871434,13.94453769037024,14.24810989202614,14.551682093682039,14.855254295337939,15.158826496993839,null,0.65490434728574343,0.69397737654709191,0.7639639434909925,0.86320270833722668,0.95830915335038491,1,1,1,1,null,1,1,1]
["2013-05-22T09:00:00","2013-05-22T09:00:00",null,12.89191508196159,13.19548728361749,13.49905948527339,13.80263168692929,14.10620388858519,14.40977609024109,14.71334829189699,15.01692049355289,15.32049269520879,null,0.66778498798680685,0.71010709314744402,0.78318501385959982,0.88538895476926249,0.98333439814102241,1,1,1,1,null,1,1,1]
["2013-05-22T10:00:00","2013-05-22T10:00:00",null,13.133813114839105,13.437385316495005,13.740957518150905,14.044529719806805,14.348101921462705,14.651674123118605,14.955246324774505,15.258818526430405,15.562390728086305,null,0.67007721629115935,0.7156589121598208,0.79184921625770288,0.89702884803952965,0.99782380457862685,1,1,1,1,null,1,1,1]
["2013-05-22T11:00:00","2013-05-22T11:00:00",null,13.295912763258755,13.599484964914655,13.903057166570555,14.206629368226455,14.510201569882355,14.813773771538255,15.117345973194155,15.420918174850055,15.724490376505955,null,0.66823712476243602,0.71710995576532832,0.79643367286640787,0.90462053994660541,1,1,1,1,1,null,1,1,1]
["2013-05-22T12:00:00","2013-05-22T12:00:00",null,13.37135031172955,13.67492251338545,13.97849471504135,14.28206691669725,14.58563911835315,14.88921132000905,15.19278352166495,15.49635572332085,15.79992792497675,null,0.66355803487511089,0.71575354543844083,0.79826324958639561,0.90948889639117059,1,1,1,1,1,null,1,1,1]
["2013-05-22T13:00:00","2013-05-22T13:00:00",null,13.413494611619377,13.717066813275277,14.020639014931177,14.324211216587077,14.627783418242977,14.931355619898877,15.234927821554777,15.538500023210677,15.842072224866577,null,0.65732275329492262,0.71286197303616128,0.79856817903972688,0.91286414999528598,1,1,1,1,1,null,1,1,1]
["2013-05-22T14:00:00","2013-05-22T14:00:00",null,13.541827577466767,13.845399779122667,14.148971980778567,14.452544182434467,14.756116384090367,15.059688585746267,15.363260787402167,15.666832989058067,15.970405190713967,null,0.63645085795483203,0.6954704793875417,0.78449936495154493,0.90197080814524377,0.99216646749200632,0.99508958432049255,0.99790755306162315,1,1,null,0.99790755306162315,1,1]
["2013-05-22T15:00:00","2013-05-22T15:00:00",null,13.644672396852522,13.948244598508422,14.251816800164322,14.555389001820222,14.858961203476122,15.162533405132022,15.466105606787922,15.769677808443822,16.073250010099724,null,0.47737231659451457,0.53986182490995971,0.63220287522566498,0.75284979065750357,0.84609474453757905,0.8519409781945515,0.85756640086807723,0.86236115365149346,0.86495831140917723,null,0.85756640086807723,0.86236115365149346,0.86495831140917723]
["2013-05-22T16:00:00","2013-05-22T16:00:00",null,13.587078276847306,13.890650478503206,14.194222680159106,14.497794881815006,14.801367083470906,15.104939285126806,15.408511486782706,15.712083688438605,16.015655890094507,null,0.31747362015282327,0.38345404496847502,0.47914931927082455,0.60299273655827401,0.69931852939786909,0.70810890950079897,0.71657333053292638,0.72409141877885319,0.72930676391169191,null,0.71657333053292638,0.72409141877885319,0.72930676391169191]
["2013-05-22T17:00:00","2013-05-22T17:00:00",null,13.837420752642963,14.140992954298863,14.444565155954763,14.748137357610663,15.051709559266563,15.355281760922463,15.658853962578362,15.962426164234262,16.265998365890162,null,0.15473592535253022,0.22420726666838856,0.32324625014864683,0.45029668410044266,0.54970331589955745,0.56145887206591583,0.57276229145664492,0.58301422997381791,0.59086879209928267,null,0.57276229145664492,0.58301422997381791,0.59086879209928267]
["2013-05-22T18:00:00","2013-05-22T18:00:00",null,13.375997128187125,13.679569329843025,13.983141531498925,14.286713733154825,14.590285934810725,14.893858136466624,15.197430338122524,15.501002539778424,15.804574741434324,null,6.5717554597262348E-2,0.13857466432597165,0.24085220889678302,0.37101502623430521,0.47338683409684845,0.4880024182392797,0.50203968790125497,0.514930843411054,0.52530895963305357,null,0.50203968790125497,0.514930843411054,0.52530895963305357]
["2013-05-22T19:00:00","2013-05-22T19:00:00",null,13.697766670780547,14.001338872436447,14.304911074092347,14.608483275748247,14.912055477404147,15.215627679060047,15.519199880715947,15.822772082371847,16.126344284027748,null,7.1595332680441506E-2,0.14794335890935739,0.25355409784934191,0.38692393185121049,0.49236606386453785,0.50992579445292652,0.52679154766476788,0.54240603863707748,0.55541285704296761,null,0.52679154766476788,0.54240603863707748,0.55541285704296761]
["2013-05-22T20:00:00","2013-05-22T20:00:00",null,13.823480132723969,14.127052334379869,14.430624536035769,14.734196737691668,15.037768939347568,15.341341141003468,15.644913342659368,15.948485544315268,16.252057745971168,null,0.13052032083453094,0.21042235241606677,0.31942937457763781,0.45604828447879509,0.56462382949531986,0.5851802805733437,0.60492709137872913,0.62331749185722707,0.63899507168194991,null,0.60492709137872913,0.62331749185722707,0.63899507168194991]
["2013-05-22T21:00:00","2013-05-22T21:00:00",null,13.690387940351888,13.993960142007788,14.297532343663688,14.601104545319588,14.904676746975488,15.208248948631388,15.511821150287288,15.815393351943188,16.118965553599089,null,0.18467158582267523,0.26811710794809546,0.38052041333125303,0.52038839913169899,0.63207632753395004,0.65562949910160906,0.67825736750053855,0.69941316267648923,0.7177509891113093,null,0.67825736750053855,0.69941316267648923,0.7177509891113093]
["2013-05-22T22:00:00","2013-05-22T22:00:00",null,13.334423219226945,13.637995420882845,13.941567622538745,14.245139824194645,14.548712025850545,14.852284227506445,15.155856429162345,15.459428630818245,15.763000832474145,null,0.25218717271371882,0.33900794844325444,0.45462878529949402,0.59757761005945964,0.7122201997164036,0.73860185483392882,0.76395305869536889,0.78771652643773893,0.80856739216035822,null,0.76395305869536889,0.78771652643773893,0.80856739216035822]
["2013-05-22T23:00:00","2013-05-22T23:00:00",null,12.97977654381827,13.28334874547417,13.58692094713007,13.89049314878597,14.194065350441869,14.497637552097769,14.801209753753669,15.104781955409569,15.408354157065469,null,0.3415840765834669,0.43163289859482007,0.55034508921931491,0.69624857523397343,0.813709133632048,0.8428036094033482,0.87075197102247215,0.89700744843517033,0.92025569054949774,null,0.87075197102247215,0.89700744843517033,0.92025569054949774]
["2013-05-23","2013-05-23",null,12.959520789408774,13.263092991064674,13.566665192720574,13.870237394376474,14.173809596032374,14.477381797688274,14.780953999344174,15.084526201000074,15.388098402655974,null,0.41638642592825492,0.50952660170786335,0.63118293877831555,0.77990439353410468,0.90006725777721863,0.93174837649746711,0.96217823297818372,0.99081005716511894,1,null,0.96217823297818372,0.99081005716511894,1]
["2013-05-23T01:00:00","2013-05-23T01:00:00",null,13.193953468384692,13.497525670040591,13.801097871696491,14.104670073352391,14.408242275008291,14.711814476664191,15.015386678320091,15.318958879975991,15.622531081631891,null,0.41950932412271685,0.51581445733172937,0.64048854450928794,0.7921120864760921,0.91504034541665891,0.94938171074700461,0.98235615094172724,1,1,null,0.98235615094172724,1,1]
["2013-05-23T02:00:00","2013-05-23T02:00:00",null,13.21254578602181,13.51611798767771,13.81969018933361,14.12326239098951,14.42683459264541,14.73040679430131,15.033978995957209,15.337551197613109,15.641123399269009,null,0.42751109357047956,0.52692861016521841,0.65457838821494096,0.80904092854034693,0.93469252294342431,0.97165207564892497,1,1,1,null,1,1,1]
["2013-05-23T03:00:00","2013-05-23T03:00:00",null,13.287314489391722,13.590886691047622,13.894458892703522,14.198031094359422,14.501603296015322,14.805175497671222,15.108747699327122,15.412319900983022,15.715892102638922,null,0.43152775050746423,0.53409970972287169,0.66475672307096501,0.82211083579865052,0.95052782489918064,0.99013710940604294,1,1,1,null,1,1,1]
["2013-05-23T04:00:00","2013-05-23T04:00:00",null,13.496759347435226,13.800331549091126,14.103903750747026,14.407475952402926,14.711048154058826,15.014620355714726,15.318192557370626,15.621764759026526,15.925336960682426,null,0.43330475318377421,0.53902064021111473,0.67268488885757871,0.83292005917880829,0.96410244297679115,1,1,1,1,null,1,1,1]
["2013-05-23T05:00:00","2013-05-23T05:00:00",null,13.800477858254968,14.104050059910868,14.407622261566768,14.711194463222668,15.014766664878568,15.318338866534468,15.621911068190368,15.925483269846268,16.229055471502168,null,0.41698577002618198,0.52606639584890236,0.66294817596844835,0.82626418524919754,0.96041174511060889,0.99914830049241943,1,1,1,null,1,1,1]
["2013-05-23T06:00:00","2013-05-23T06:00:00",null,14.095861960256846,14.399434161912746,14.703006363568646,15.006578565224546,15.310150766880446,15.613722968536345,15.917295170192245,16.220867371848144,16.524439573504047,null,0.39800654025849258,0.51040984564165059,0.65048812761680741,0.81686394623960512,0.9539451377382383,0.99551017666991493,0.99907469683127059,1,1,null,0.99907469683127059,1,1]
["2013-05-23T07:00:00","2013-05-23T07:00:00",null,14.27269299948963,14.57626520114553,14.87983740280143,15.18340960445733,15.48698180611323,15.79055400776913,16.094126209425028,16.397698411080931,16.701270612736828,null,0.37331776934739302,0.48912787276087311,0.63246574544405409,0.80197497707004928,0.94207391867578882,0.986530530009745,0.9928814744860246,0.99648805388232231,0.99907469683127059,null,0.9928814744860246,0.99648805388232231,0.99907469683127059]
["2013-05-23T08:00:00","2013-05-23T08:00:00",null,14.468617578557547,14.772189780213447,15.075761981869347,15.379334183525247,15.682906385181147,15.986478586837046,16.290050788492948,16.593622990148845,16.897195191804748,null,0.34516962636229354,0.46440755742356687,0.61103656524097871,0.78371075429637804,0.92684847562669503,0.97423871859787303,0.98339711700654764,0.98972703186535593,0.99492134738072358,null,0.98339711700654764,0.98972703186535593,0.99492134738072358]
["2013-05-23T09:00:00","2013-05-23T09:00:00",null,14.58101366217039,14.88458586382629,15.18815806548219,15.49173026713809,15.79530246879399,16.098874670449888,16.402446872105791,16.706019073761688,17.009591275417591,null,0.31247908600343127,0.43519741875617562,0.58515962094276064,0.76104082666250639,0.90726990176107858,0.95762532079568508,0.96964374718043256,0.97871802711922251,0.98657258924468738,null,0.96964374718043256,0.97871802711922251,0.98657258924468738]
["2013-05-23T10:00:00","2013-05-23T10:00:00",null,14.795014399502689,15.098586601158589,15.402158802814489,15.705731004470389,16.00930320612629,16.312875407782187,16.61644760943809,16.920019811093987,17.22359201274989,null,0.2726069312781802,0.39883721014860224,0.55216415113056705,0.73128391794086589,0.88062537642516447,0.93397751594940615,0.94888751473643318,0.96074821899014706,0.97129457215191584,null,0.94888751473643318,0.96074821899014706,0.97129457215191584]
["2013-05-23T11:00:00","2013-05-23T11:00:00",null,14.886017671056658,15.189589872712558,15.493162074368458,15.796734276024358,16.100306477680256,16.40387867933616,16.707450880992056,17.011023082647959,17.314595284303856,null,0.23014813360398084,0.3599219030182873,0.51664512722183864,0.69903499954889725,0.8515203858451289,0.90790079028521242,0.92573390590072568,0.94041257889557017,0.95367175271111393,null,0.92573390590072568,0.94041257889557017,0.95367175271111393]
["2013-05-23T12:00:00","2013-05-23T12:00:00",null,15.019402775813029,15.322974977468929,15.626547179124829,15.930119380780729,16.233691582436627,16.537263784092531,16.840835985748427,17.144408187404331,17.447980389060227,null,0.18375679746268131,0.31711611665581441,0.47728819812463008,0.66299023520339073,0.81867212335523321,0.87812285194610085,0.89892114362504261,0.91645984459595997,0.93247389830022098,null,0.89892114362504261,0.91645984459595997,0.93247389830022098]
["2013-05-23T13:00:00","2013-05-23T13:00:00",null,15.253139295563107,15.556711497219007,15.860283698874907,16.163855900530805,16.467428102186709,16.771000303842605,17.074572505498509,17.378144707154405,17.681716908810309,null,0.1331279934009503,0.27010440679911674,0.43375688995940342,0.62280263621607279,0.78170205584099728,0.8442651678175912,0.86804966517743254,0.88847993855062946,0.90729093137854999,null,0.86804966517743254,0.88847993855062946,0.90729093137854999]
["2013-05-23T14:00:00","2013-05-23T14:00:00",null,15.383419405081517,15.686991606737417,15.990563808393317,16.294136010049215,16.597708211705118,16.901280413361015,17.204852615016918,17.508424816672814,17.811997018328718,null,7.1942321368715034E-2,0.21252531416317924,0.37964768420620137,0.57203713964077951,0.7341540907387859,0.79981907129237062,0.82660028914184713,0.8499221349173236,0.87151955206016807,null,0.82660028914184713,0.8499221349173236,0.87151955206016807]
["2013-05-23T15:00:00","2013-05-23T15:00:00",null,15.670937480270936,15.974509681926836,16.278081883582736,16.581654085238636,16.885226286894536,17.188798488550436,17.492370690206336,17.795942891862236,18.099515093518136,null,0,1.9547029439409891E-2,0.19026546406999423,0.38612480638730784,0.55158546666322295,0.62046797868988968,0.65036157992509247,0.67669066099893971,0.70120068016153481,null,0.65036157992509247,0.67669066099893971,0.70120068016153481]
["2013-05-23T16:00:00","2013-05-23T16:00:00",null,15.537819063917311,15.841391265573211,16.144963467229111,16.448535668885011,16.752107870540911,17.055680072196811,17.359252273852711,17.662824475508611,17.966396677164511,null,0,0,2.0819321296411675E-3,0.20141116132969022,0.37022604559224959,0.44233660390073387,0.475342588521663,0.50467890489388101,0.53210152607622674,null,0.475342588521663,0.50467890489388101,0.53210152607622674]
["2013-05-23T17:00:00","2013-05-23T17:00:00",null,15.513910126081567,15.817482327737467,16.121054529393369,16.424626731049266,16.728198932705169,17.031771134361065,17.335343336016969,17.638915537672865,17.942487739328769,null,0,0,0,1.7328404796206343E-2,0.18948699823667442,0.26481508801824066,0.30093345602489618,0.33326649288674931,0.36359120128011013,null,0.30093345602489618,0.33326649288674931,0.36359120128011013]
["2013-05-23T18:00:00","2013-05-23T18:00:00",null,14.801252824030282,15.104825025686182,15.408397227342082,15.711969428997982,16.015541630653882,16.319113832309782,16.622686033965682,16.926258235621582,17.229830437277482,null,0,0,0,0,0.13449454854968518,0.21287193286456441,0.25192393250844169,0.28708545292016102,0.32013349677603242,null,0.25192393250844169,0.28708545292016102,0.32013349677603242]
["2013-05-23T19:00:00","2013-05-23T19:00:00",null,14.923231885986725,15.226804087642625,15.530376289298525,15.833948490954425,16.137520692610323,16.441092894266227,16.744665095922123,17.048237297578027,17.351809499233923,null,0,0,0,0,0.11253962790983173,0.19400836599296617,0.23602554170027196,0.2740576048967997,0.3098710434501239,null,0.23602554170027196,0.2740576048967997,0.3098710434501239]
["2013-05-23T20:00:00","2013-05-23T20:00:00",null,14.894887550499098,15.198459752154998,15.502031953810897,15.805604155466797,16.109176357122699,16.412748558778596,16.716320760434499,17.019892962090395,17.323465163746299,null,2.178668370008446E-2,2.5372233478911099E-2,2.8831605552910998E-2,3.2143770304613024E-2,0.14787990007005561,0.23242947711270973,0.27741182888344396,0.31829340524730904,0.35687223849808603,null,0.27741182888344396,0.31829340524730904,0.35687223849808603]
["2013-05-23T21:00:00","2013-05-23T21:00:00",null,14.925260140697858,15.228832342353758,15.532404544009658,15.835976745665558,16.139548947321458,16.443121148977358,16.746693350633258,17.050265552289158,17.353837753945058,null,5.0565715209317644E-2,5.7747329575706489E-2,6.4676588532441848E-2,7.1311432844581468E-2,0.19025457927437045,0.27788499527654426,0.32584303791944252,0.36959515706811602,0.4109393850163458,null,0.32584303791944252,0.36959515706811602,0.4109393850163458]
["2013-05-23T22:00:00","2013-05-23T22:00:00",null,14.685857139298685,14.989429340954585,15.293001542610485,15.596573744266385,15.900145945922285,16.203718147578186,16.507290349234083,16.810862550889986,17.114434752545883,null,8.3529640595304516E-2,9.4286289931784423E-2,0.104643376536313,0.11456935598268353,0.23667745984187666,0.32735717037736345,0.37824884465748354,0.42483996216475878,0.46890752557549908,null,0.37824884465748354,0.42483996216475878,0.46890752557549908]
["2013-05-23T23:00:00","2013-05-23T23:00:00",null,14.46822984306313,14.771802044719029,15.075374246374929,15.378946448030829,15.682518649686729,15.986090851342629,16.289663052998527,16.593235254654431,16.896807456310327,null,0.12728175974397798,0.14146623672825109,0.15511445846701061,0.16820539534278528,0.2933522789265558,0.38696562109926441,0.44067526412051511,0.48997920228156533,0.53665443825872505,null,0.44067526412051511,0.48997920228156533,0.53665443825872505]
["2013-05-24","2013-05-24",null,14.221898364831398,14.525470566487298,14.829042768143198,15.132614969799098,15.436187171454998,15.739759373110898,16.043331574766796,16.3469037764227,16.650475978078596,null,0.17297911850873043,0.1905493639058545,0.20743614673516711,0.22363946699666815,0.35178307107007384,0.44826695602759087,0.50474199374629436,0.55671669332617735,0.60595754263481416,null,0.50474199374629436,0.55671669332617735,0.60595754263481416]
["2013-05-24T01:00:00","2013-05-24T01:00:00",null,14.134665267019759,14.438237468675659,14.741809670331559,15.045381871987459,15.348954073643359,15.652526275299259,15.956098476955159,16.259670678611059,16.563242880266959,null,0.22694111693963459,0.24780249747098959,0.26783320811223521,0.28706479328957812,0.41811048457399891,0.51739130865517546,0.57654762260144721,0.63110896513027848,0.68284182410924354,null,0.57654762260144721,0.63110896513027848,0.68284182410924354]
["2013-05-24T02:00:00","2013-05-24T02:00:00",null,13.990354444847844,14.293926646503744,14.597498848159644,14.901071049815544,15.204643251471444,15.508215453127344,15.811787654783243,16.115359856439142,16.418932058095045,null,0.28596073837234409,0.31009222442045886,0.33326686287363749,0.35551619815808672,0.48945346184478705,0.591510195432152,0.65333727079725645,0.71047474146630041,0.76467858049812254,null,0.65333727079725645,0.71047474146630041,0.76467858049812254]
["2013-05-24T03:00:00","2013-05-24T03:00:00",null,13.868569085179846,14.172141286835746,14.475713488491646,14.779285690147546,15.082857891803446,15.386430093459346,15.690002295115246,15.993574496771146,16.297146698427046,null,0.3481348024257222,0.37554690879933228,0.40185496025570844,0.42712204564726391,0.56394036692750826,0.6687730100210616,0.73327084680499877,0.79297393080551981,0.84964874989019901,null,0.73327084680499877,0.79297393080551981,0.84964874989019901]
["2013-05-24T04:00:00","2013-05-24T04:00:00",null,13.93380878051892,14.23738098217482,14.54095318383072,14.844525385486619,15.148097587142519,15.451669788798419,15.755241990454319,16.058814192110219,16.362386393766119,null,0.41230668013885707,0.44296786241175579,0.47239881206259388,0.50065210313504893,0.64033045239136621,0.7479179753736368,0.8150655439589356,0.87731321167346255,0.93644849600226332,null,0.8150655439589356,0.87731321167346255,0.93644849600226332]
["2013-05-24T05:00:00","2013-05-24T05:00:00",null,14.188344992785282,14.491917194441182,14.795489396097082,15.099061597752982,15.402633799408882,15.706206001064782,16.009778202720682,16.313350404376582,16.616922606032482,null,0.46824546261204691,0.50228189848906102,0.53494089442171666,0.56629605407116246,0.70895009419964383,0.8193976451579873,0.88930009363200335,0.95419749314789182,1,null,0.88930009363200335,0.95419749314789182,1]
["2013-05-24T06:00:00","2013-05-24T06:00:00",null,14.335969913866924,14.639542115522824,14.943114317178724,15.246686518834624,15.550258720490524,15.853830922146424,16.157403123802325,16.460975325458222,16.764547527114125,null,0.52198665005950429,0.55939833954063378,0.59529589656384252,0.62976343959901471,0.77540368540839566,0.8887217791515476,0.96138962232301639,1,1,null,0.96138962232301639,1,1]
["2013-05-24T07:00:00","2013-05-24T07:00:00",null,14.562947057570812,14.866519259226711,15.170091460882611,15.473663662538511,15.777235864194411,16.080808065850313,16.384380267506209,16.687952469162113,16.991524670818009,null,0.56482398084818386,0.60565298316837102,0.64483116051707512,0.68244263136418026,0.83112165689813866,0.94735235266104134,1,1,1,null,1,1,1]
["2013-05-24T08:00:00","2013-05-24T08:00:00",null,14.763287597940456,15.066859799596356,15.370432001252256,15.674004202908156,15.977576404564056,16.281148606219958,16.584720807875854,16.888293009531758,17.191865211187654,null,0.60052175650541684,0.6448416753258106,0.6873845914698945,0.72821359379008166,0.88000500270976634,0.99922190415356871,1,1,1,null,1,1,1]
["2013-05-24T09:00:00","2013-05-24T09:00:00",null,15.125004954242069,15.428577155897969,15.732149357553869,16.035721559209769,16.339293760865669,16.642865962521569,16.946438164177469,17.250010365833369,17.553582567489268,null,0.62947953976315463,0.67737449355363943,0.72335575215425207,0.76748640441740568,0.92246380038396569,1,1,1,1,null,1,1,1]
["2013-05-24T10:00:00","2013-05-24T10:00:00",null,15.243461490959787,15.547033692615686,15.850605894271586,16.154178095927485,16.457750297583388,16.761322499239284,17.064894700895188,17.368466902551084,17.672039104206988,null,0.65578759121953079,0.7072996392150489,0.75675078469839696,0.80422514613945928,0.96242007357910131,1,1,1,1,null,1,1,1]
["2013-05-24T11:00:00","2013-05-24T11:00:00",null,15.281530855967247,15.585103057623147,15.888675259279047,16.192247460934947,16.495819662590847,16.799391864246747,17.102964065902647,17.406536267558547,17.710108469214447,null,0.68105467661108632,0.73619433362037323,0.7891258807951923,0.83995446622289893,1,1,1,1,1,null,1,1,1]
["2013-05-24T12:00:00","2013-05-24T12:00:00",null,15.389745817685084,15.693318019340984,15.996890220996884,16.300462422652785,16.604034624308682,16.907606825964585,17.211179027620481,17.514751229276385,17.818323430932281,null,0.70277827145875738,0.76157708190801987,0.81803109000925223,0.87224544384980984,1,1,1,1,1,null,1,1,1]
["2013-05-24T13:00:00","2013-05-24T13:00:00",null,15.415895574875403,15.719467776531303,16.023039978187203,16.326612179843103,16.630184381499003,16.933756583154903,17.237328784810803,17.540900986466703,17.844473188122603,null,0.72123176078966866,0.78370023948764234,0.84367670851528798,0.90128734557743206,1,1,1,1,1,null,1,1,1]
["2013-05-24T14:00:00","2013-05-24T14:00:00",null,15.470441067054303,15.774013268710203,16.077585470366103,16.381157672022002,16.684729873677902,16.988302075333802,17.291874276989702,17.595446478645602,17.899018680301502,null,0.7238709777822947,0.79001963953771515,0.85353959910924515,0.91455703420171131,1,1,1,1,1,null,1,1,1]
["2013-05-24T15:00:00","2013-05-24T15:00:00",null,15.704910021961627,16.008482223617527,16.312054425273427,16.615626626929327,16.919198828585227,17.222771030241127,17.526343231897027,17.829915433552927,18.133487635208827,null,0.52624514759740693,0.5961370812626875,0.66326362023051522,0.72776145701445238,0.81655864679938539,0.81978669308120289,0.82290959127566488,0.82592734138277113,0.82883994340252176,null,0.82290959127566488,0.82592734138277113,0.82883994340252176]
["2013-05-24T16:00:00","2013-05-24T16:00:00",null,15.406867538457272,15.710439740113172,16.01401194176907,16.317584143424973,16.62115634508087,16.924728546736773,17.22830074839267,17.531872950048573,17.835445151704469,null,0.33428679932098709,0.40789046046992106,0.47859203440783982,0.54651769883957024,0.63862705337620529,0.64505160151363361,0.6512553386676152,0.65723826483815007,0.66302140964270906,null,0.6512553386676152,0.65723826483815007,0.66302140964270906]
["2013-05-24T17:00:00","2013-05-24T17:00:00",null,15.288364754538152,15.591936956194052,15.895509157849952,16.199081359505854,16.50265356116175,16.806225762817654,17.10979796447355,17.413370166129454,17.71694236778535,null,0.14563010098753373,0.22290343038517882,0.29713798005824643,0.36845992771156338,0.46384990257369374,0.47342889333179072,0.48268192501908525,0.49159848282684193,0.50022062599000261,null,0.48268192501908525,0.49159848282684193,0.50022062599000261]
["2013-05-24T18:00:00","2013-05-24T18:00:00",null,14.649939955288589,14.953512156944489,15.257084358600389,15.560656560256289,15.864228761912189,16.167800963568091,16.471373165223987,16.774945366879891,17.078517568535787,null,7.8156573331432388E-2,0.15888927480307738,0.23643598922784703,0.31094392392803927,0.40939370813221815,0.42191684533627249,0.43400887538216876,0.44565928346117156,0.45692064361695828,null,0.43400887538216876,0.44565928346117156,0.45692064361695828]
["2013-05-24T19:00:00","2013-05-24T19:00:00",null,14.835246005919347,15.138818207575246,15.442390409231146,15.745962610887046,16.049534812542944,16.353107014198848,16.656679215854744,16.960251417510648,17.263823619166544,null,3.5771379318381973E-2,0.12013168980379585,0.20115880592003654,0.27901044979813749,0.38067776547539833,0.39630277125644348,0.41138100698323932,0.42591247265578613,0.43994974231776124,null,0.41138100698323932,0.42591247265578613,0.43994974231776124]
["2013-05-24T20:00:00","2013-05-24T20:00:00",null,14.162637514456385,14.466209716112285,14.769781917768185,15.073354119424085,15.376926321079985,15.680498522735885,15.984070724391785,16.287642926047685,16.591215127703585,null,1.9242099986079009E-3,8.9912129497790663E-2,0.17443016211423795,0.25562551517024762,0.36049984751185488,0.37921620706115522,0.39725961885137956,0.41465111249999925,0.43144326205069156,null,0.39725961885137956,0.41465111249999925,0.43144326205069156]
["2013-05-24T21:00:00","2013-05-24T21:00:00",null,13.756542743648975,14.060114945304875,14.363687146960775,14.667259348616675,14.970831550272575,15.274403751928475,15.577975953584374,15.881548155240274,16.185120356896174,null,5.025027094725084E-2,0.1416975625204335,0.22951724507984725,0.31388807037399663,0.42181169724891687,0.44345117362670344,0.46430203934932285,0.48439583884298199,0.50378514615135805,null,0.46430203934932285,0.48439583884298199,0.50378514615135805]
["2013-05-24T22:00:00","2013-05-24T22:00:00",null,13.473588313578901,13.777160515234801,14.080732716890701,14.384304918546601,14.687877120202501,14.991449321858401,15.295021523514301,15.5985937251702,15.9021659268261,null,0.11858601291966828,0.21334546924455294,0.30434062404210643,0.39175022906083323,0.50258645795550416,0.5270228734569502,0.55055501540713792,0.57323545784974528,0.59510626001971401,null,0.55055501540713792,0.57323545784974528,0.59510626001971401]
["2013-05-24T23:00:00","2013-05-24T23:00:00",null,13.402673944374271,13.706246146030171,14.009818347686071,14.313390549341971,14.616962750997871,14.920534952653771,15.224107154309671,15.527679355965571,15.831251557621471,null,0.1903285529224078,0.2883686295727878,0.38249719737353877,0.47291403769063628,0.58663132417885122,0.61382261956901452,0.64000449332056386,0.66524003428591272,0.68956078689126743,null,0.64000449332056386,0.66524003428591272,0.68956078689126743]
["2013-05-25","2013-05-25",null,13.230667541939155,13.534239743595055,13.837811945250955,14.141384146906855,14.444956348562755,14.748528550218655,15.052100751874555,15.355672953530455,15.659245155186355,null,0.26814865237430213,0.36937471607155742,0.46654206359688583,0.55987150593373403,0.67638573154560844,0.70624778835460444,0.73499527543763099,0.76270179645583691,0.78938838102669306,null,0.73499527543763099,0.76270179645583691,0.78938838102669306]
["2013-05-25T01:00:00","2013-05-25T01:00:00",null,13.163339881628076,13.466912083283976,13.770484284939876,14.074056486595776,14.377628688251676,14.681200889907576,14.984773091563476,15.288345293219376,15.591917494875275,null,0.34843973187905353,0.45280972338824188,0.55298430621194106,0.64918429133359767,0.76845339683418934,0.80095467063581138,0.83223622662410834,0.86238218326896465,0.89140305537911557,null,0.83223622662410834,0.86238218326896465,0.89140305537911557]
["2013-05-25T02:00:00","2013-05-25T02:00:00",null,13.166954911464948,13.470527113120848,13.774099314776748,14.077671516432648,14.381243718088548,14.684815919744448,14.988388121400348,15.291960323056248,15.595532524712148,null,0.4284994855916226,0.53601340491274396,0.63919522303481391,0.73827626575001448,0.8603002511393234,0.89544074193357148,0.92925636682713886,0.96184175909864555,0.99319691874809124,null,0.92925636682713886,0.96184175909864555,0.99319691874809124]
["2013-05-25T03:00:00","2013-05-25T03:00:00",null,13.101816472242589,13.405388673898489,13.708960875554389,14.012533077210289,14.316105278866189,14.619677480522089,14.923249682177989,15.226821883833889,15.530394085489789,null,0.51097764531337087,0.62160394802021868,0.72775094220571701,0.82968149808825498,0.95441830413133888,0.99216646749200632,1,1,1,null,1,1,1]
["2013-05-25T04:00:00","2013-05-25T04:00:00",null,13.226322901051976,13.529895102707876,13.833467304363776,14.137039506019676,14.440611707675576,14.744183909331475,15.047756110987375,15.351328312643275,15.654900514299175,null,0.58894495208756303,0.70275724184128618,0.81194301575136196,0.91678617365365056,1,1,1,1,1,null,1,1,1]
["2013-05-25T05:00:00","2013-05-25T05:00:00",null,13.392459376967508,13.696031578623408,13.999603780279308,14.303175981935208,14.606748183591108,14.910320385247008,15.213892586902908,15.517464788558808,15.821036990214708,null,0.66110808443972502,0.77819047971020794,0.89050966662348119,0.99834954501540496,1,1,1,1,1,null,1,1,1]
["2013-05-25T06:00:00","2013-05-25T06:00:00",null,13.373587260577299,13.677159462233199,13.980731663889099,14.284303865544999,14.587876067200899,14.891448268856799,15.195020470512699,15.498592672168598,15.802164873824498,null,0.73391262012475633,0.85425460610326343,0.96969669121099855,1,1,1,1,1,1,null,1,1,1]
["2013-05-25T07:00:00","2013-05-25T07:00:00",null,13.477017159912521,13.780589361568421,14.08416156322432,14.38773376488022,14.69130596653612,14.99487816819202,15.29845036984792,15.60202257150382,15.90559477315972,null,0.77335366769184943,0.89694472956964511,1,1,1,1,1,1,1,null,1,1,1]
["2013-05-25T08:00:00","2013-05-25T08:00:00",null,13.739351405625012,14.042923607280912,14.346495808936812,14.650068010592712,14.953640212248612,15.257212413904512,15.560784615560411,15.864356817216311,16.167929018872211,null,0.76341717343674331,0.89034142968371222,0.99658268716094234,0.99964249650299086,1,1,1,1,1,null,1,1,1]
["2013-05-25T09:00:00","2013-05-25T09:00:00",null,14.016096265834189,14.319668467490089,14.623240669145989,14.926812870801889,15.230385072457789,15.533957274113689,15.837529475769589,16.141101677425489,16.444673879081389,null,0.74695098295685325,0.87728203723414422,0.98678288541939851,0.99296559295590903,0.99633033175128882,0.99921138934483289,1,1,1,null,1,1,1]
["2013-05-25T10:00:00","2013-05-25T10:00:00",null,14.265069432981134,14.568641634637034,14.872213836292934,15.175786037948834,15.479358239604734,15.782930441260634,16.086502642916535,16.390074844572432,16.693647046228335,null,0.72943331160340696,0.86316064910228441,0.97592108799556299,0.98523720853527097,0.99160918262902153,0.99738181262484515,1,1,1,null,1,1,1]
["2013-05-25T11:00:00","2013-05-25T11:00:00",null,14.457078341809757,14.760650543465657,15.064222745121556,15.367794946777456,15.671367148433356,15.974939350089256,16.278511551745154,16.582083753401058,16.885655955056954,null,0.71519626057545604,0.85229885167844888,0.96829785166228055,0.98071584077897933,0.99008453536236507,0.99872770814299705,1,1,1,null,1,1,1]
["2013-05-25T12:00:00","2013-05-25T12:00:00",null,14.364233558690822,14.667805760346722,14.971377962002622,15.274950163658522,15.578522365314422,15.882094566970322,16.18566676862622,16.489238970282123,16.79281117193802,null,0.69771013364821644,0.83826158201647361,0.95756223194327172,0.97314517848937465,0.98556316760607343,0.99713997202392723,1,1,1,null,1,1,1]
["2013-05-25T13:00:00","2013-05-25T13:00:00",null,14.608244218195308,14.911816419851208,15.215388621507108,15.518960823163008,15.822533024818908,16.126105226474806,16.429677428130709,16.733249629786606,17.036821831442509,null,0.67362070683504394,0.8176630717035076,0.94030743080821444,0.95910790882739938,0.97461725171235336,0.98916974700237126,0.99490031776325238,0.99766571246070523,1,null,0.99490031776325238,0.99766571246070523,1]
["2013-05-25T14:00:00","2013-05-25T14:00:00",null,14.962441959195468,15.266014160851368,15.569586362507268,15.873158564163168,16.176730765819066,16.480302967474969,16.783875169130866,17.087447370786769,17.391019572442666,null,0.6312775720569358,0.77888445708675491,0.904956643839255,0.92704825699267079,0.94573307211576452,0.96334537674783094,0.97202009395466948,0.97762448701072402,0.98270313963000056,null,0.97202009395466948,0.97762448701072402,0.98270313963000056]
["2013-05-25T15:00:00","2013-05-25T15:00:00",null,15.012014961837103,15.315587163493003,15.619159365148903,15.922731566804803,16.226303768460703,16.529875970116603,16.833448171772503,17.137020373428403,17.440592575084302,null,0.44800445579609016,0.59923894983967818,0.72880205309238488,0.75425840504118047,0.7761712664460918,0.7968959544638845,0.80857790696909382,0.81707387242742791,0.82494946417036386,null,0.80857790696909382,0.81707387242742791,0.82494946417036386]
["2013-05-25T16:00:00","2013-05-25T16:00:00",null,15.02796371091388,15.33153591256978,15.63510811422568,15.93868031588158,16.24225251753748,16.54582471919338,16.84939692084928,17.15296912250518,17.45654132416108,null,0.26926322210027176,0.42404120668774414,0.55700059316203743,0.58572705062759278,0.61079435465317267,0.63455782239554281,0.64916289172923836,0.66047682592870305,0.67107575313414958,null,0.64916289172923836,0.66047682592870305,0.67107575313414958]
["2013-05-25T17:00:00","2013-05-25T17:00:00",null,14.553882467393777,14.857454669049677,15.161026870705577,15.464599072361477,15.768171274017377,16.071743475673276,16.375315677329176,16.678887878985076,16.982460080640976,null,8.9323300208599299E-2,0.2477709530447828,0.38426331525422497,0.41638605594136679,0.44471295067497091,0.47160983142053853,0.48923265086134038,0.5034591870805557,0.51686556821839735,null,0.48923265086134038,0.5034591870805557,0.51686556821839735]
["2013-05-25T18:00:00","2013-05-25T18:00:00",null,13.99986092131947,14.30343312297537,14.60700532463127,14.91057752628717,15.21414972794307,15.51772192959897,15.82129413125487,16.12486633291077,16.42843853456667,null,2.7454165608552503E-2,0.18935067571000036,0.32915520267114451,0.36444290078769054,0.39581909005460764,0.42564960243739702,0.44607987581059394,0.46301923268358425,0.47903328638784526,null,0.44607987581059394,0.46301923268358425,0.47903328638784526]
["2013-05-25T19:00:00","2013-05-25T19:00:00",null,14.153521799543238,14.457094001199138,14.760666202855038,15.064238404510938,15.367810606166838,15.671382807822738,15.974955009478638,16.278527211134538,16.582099412790438,null,0,0.16470396403384305,0.30788374459910262,0.34641000380620168,0.38089857645884517,0.41371529452253414,0.43702662548927507,0.45673137705971817,0.47541619218281195,null,0.43702662548927507,0.45673137705971817,0.47541619218281195]
["2013-05-25T20:00:00","2013-05-25T20:00:00",null,14.053468912675044,14.357041114330944,14.660613315986843,14.964185517642743,15.267757719298643,15.571329920954543,15.874902122610443,16.178474324266343,16.482046525922243,null,0,0.14484149033236643,0.29135446526679915,0.33307722632950909,0.37063612313293665,0.40640750245131857,0.43255783177666124,0.45498591880961486,0.47629943611659914,null,0.43255783177666124,0.45498591880961486,0.47629943611659914]
["2013-05-25T21:00:00","2013-05-25T21:00:00",null,13.836358484175566,14.139930685831466,14.443502887487366,14.747075089143266,15.050647290799166,15.354219492455066,15.657791694110966,15.961363895766866,16.264936097422765,null,0,0.14019394487124803,0.28994548089623384,0.33477011053593458,0.37530469821152618,0.41393610550598098,0.44283079991130531,0.46789810393688502,0.49175620495787525,null,0.44283079991130531,0.46789810393688502,0.49175620495787525]
["2013-05-25T22:00:00","2013-05-25T22:00:00",null,13.766640504477458,14.070212706133358,14.373784907789258,14.677357109445158,14.980929311101058,15.284501512756957,15.588073714412857,15.891645916068757,16.195218117724657,null,5.4582372146302328E-2,0.19806745215178126,0.35096291598870011,0.39880529573550716,0.4422314558133783,0.48363877261402144,0.51520422843817859,0.54283714579523534,0.56916622686908269,null,0.51520422843817859,0.54283714579523534,0.56916622686908269]
["2013-05-25T23:00:00","2013-05-25T23:00:00",null,13.866462087812835,14.170034289468735,14.473606491124634,14.777178692780534,15.080750894436434,15.384323096092334,15.687895297748234,15.991467499404134,16.295039701060034,null,0.10792399686180834,0.25468969719278262,0.41071857403289896,0.46156818907807673,0.50788592155822743,0.5520691478650589,0.58629485029931327,0.61649338098784712,0.64529344211455153,null,0.58629485029931327,0.61649338098784712,0.64529344211455153]
["2013-05-26","2013-05-26",null,13.827264773501412,14.130836975157312,14.434409176813212,14.737981378469112,15.041553580125012,15.345125781780911,15.648697983436811,15.952270185092711,16.255842386748611,null,0.16250636900811066,0.3125211452383736,0.47167292027295188,0.52550874099902922,0.57469701626398839,0.62163512245953711,0.65851055669515302,0.69126418590642846,0.72251419746851886,null,0.65851055669515302,0.69126418590642846,0.72251419746851886]
["2013-05-26T01:00:00","2013-05-26T01:00:00",null,13.795792137950365,14.099364339606264,14.402936541262164,14.706508742918064,15.010080944573964,15.313653146229864,15.617225347885764,15.920797549541664,16.224369751197564,null,0.21554306427028538,0.36885949044351479,0.53116570809876162,0.58802979374068087,0.64013067102539067,0.68985520153586333,0.72941191199904754,0.76475218415927126,0.79848369058295432,null,0.72941191199904754,0.76475218415927126,0.79848369058295432]
["2013-05-26T02:00:00","2013-05-26T02:00:00",null,13.728304437492188,14.031876639148088,14.335448840803988,14.639021042459888,14.942593244115788,15.246165445771688,15.549737647427587,15.853309849083487,16.156882050739387,null,0.27078786936692811,0.42737440105691732,0.59280351690662603,0.65266432303818045,0.70764625791643421,0.76013618312435971,0.80234262538890555,0.84023799607187089,0.87641945293093981,null,0.80234262538890555,0.84023799607187089,0.87641945293093981]
["2013-05-26T03:00:00","2013-05-26T03:00:00",null,13.75419360569305,14.05776580734895,14.36133800900485,14.66491021066075,14.96848241231665,15.27205461397255,15.57562681562845,15.87919901728435,16.18277121894025,null,0.32777813271367412,0.48758219587674534,0.65609215068597371,0.71890761807222103,0.77672855130907648,0.83194181197951256,0.87676644161921335,0.91717485158997802,0.95577471445822626,null,0.87676644161921335,0.91717485158997802,0.95577471445822626]
["2013-05-26T04:00:00","2013-05-26T04:00:00",null,13.815588661447904,14.119160863103804,14.422733064759704,14.726305266415604,15.029877468071504,15.333449669727404,15.637021871383304,15.940594073039204,16.244166274695104,null,0.38266543431330774,0.54571857337566765,0.7173409115706223,0.78314258463776931,0.84383406065943312,0.90179168640985097,0.94926604785091329,0.99220852672694848,1,null,0.94926604785091329,0.99220852672694848,1]
["2013-05-26T05:00:00","2013-05-26T05:00:00",null,13.980379604688782,14.283951806344682,14.587524008000582,14.891096209656482,15.194668411312382,15.498240612968281,15.801812814624181,16.105385016280081,16.408957217935981,null,0.4321165797966558,0.59849239841945334,0.77331123847001881,0.84217272087921435,0.90579782853809998,0.96658393783838403,1,1,1,null,1,1,1]
["2013-05-26T06:00:00","2013-05-26T06:00:00",null,14.073522923940143,14.377095125596043,14.680667327251943,14.984239528907842,15.287811730563742,15.591383932219642,15.894956133875542,16.198528335531442,16.502100537187342,null,0.47830813457197963,0.64804869199015702,0.82610609313127559,0.89806944411746192,0.96467024264851164,1,1,1,1,null,1,1,1]
["2013-05-26T07:00:00","2013-05-26T07:00:00",null,14.133062468042489,14.436634669698389,14.740206871354289,15.043779073010189,15.347351274666089,15.650923476321989,15.954495677977889,16.258067879633789,16.561640081289688,null,0.52286989399329142,0.69601724944179089,0.87733424129093363,0.95242049047158184,1,1,1,1,1,null,1,1,1]
["2013-05-26T08:00:00","2013-05-26T08:00:00",null,14.30600274118914,14.60957494284504,14.91314714450094,15.21671934615684,15.520291547812739,15.823863749468639,16.127435951124539,16.431008152780439,16.734580354436339,null,0.56457162543853034,0.74113629372608747,0.92573390590072546,1,1,1,1,1,1,null,1,1,1]
["2013-05-26T09:00:00","2013-05-26T09:00:00",null,14.443845068608299,14.747417270264199,15.050989471920099,15.354561673575999,15.658133875231899,15.961706076887799,16.265278278543697,16.5688504801996,16.872422681855497,null,0.57802006581131415,0.75806513579034229,0.94599594233415341,1,1,1,1,1,1,null,1,1,1]
["2013-05-26T10:00:00","2013-05-26T10:00:00",null,14.611412736289367,14.914984937945267,15.218557139601167,15.522129341257067,15.825701542912967,16.129273744568867,16.432845946224766,16.736418147880666,17.039990349536566,null,0.54128132408926055,0.7248173105684953,0.91609182629021513,0.97331341542914362,0.97641528400613442,0.97939097487829851,0.98226151766310688,0.98501639755182413,0.98768715897065695,null,0.98226151766310688,0.98501639755182413,0.98768715897065695]
["2013-05-26T11:00:00","2013-05-26T11:00:00",null,14.718809641562999,15.022381843218898,15.325954044874798,15.629526246530698,15.933098448186598,16.236670649842498,16.540242851498398,16.843815053154298,17.147387254810198,null,0.50364882362468411,0.69066521179538998,0.88527292188628293,0.94571204249829344,0.95189475003480384,0.95784613177913203,0.96357670254001315,0.96909697712618326,0.97442798515511331,null,0.96357670254001315,0.96909697712618326,0.97442798515511331]
["2013-05-26T12:00:00","2013-05-26T12:00:00",null,14.876285136938536,15.179857338594436,15.483429540250336,15.787001741906236,16.090573943562134,16.394146145218038,16.697718346873934,17.001290548529838,17.304862750185734,null,0.46154752944749389,0.65210740816208412,0.85011140147456365,0.91381011279459834,0.92313674814304181,0.93211639480321185,0.9407595675838436,0.94909781091114431,0.95714163959384935,null,0.9407595675838436,0.94909781091114431,0.95714163959384935]
["2013-05-26T13:00:00","2013-05-26T13:00:00",null,14.869107516126727,15.172679717782627,15.476251919438527,15.779824121094427,16.083396322750325,16.386968524406228,16.690540726062125,16.994112927718028,17.297685129373924,null,0.41957241297513037,0.61366526742486949,0.81506554395893549,0.88202384598699446,0.89449440914737088,0.90649180591464729,0.91804758071502968,0.92920379278346099,0.93996044211994101,null,0.91804758071502968,0.92920379278346099,0.93996044211994101]
["2013-05-26T14:00:00","2013-05-26T14:00:00",null,14.999129317723334,15.302701519379234,15.606273721035134,15.909845922691034,16.213418124346934,16.516990326002833,16.820562527658733,17.124134729314633,17.427706930970533,null,0.36687219159249362,0.56449802177738162,0.76928406672429861,0.83951247426911735,0.85511645043269124,0.8701421121158095,0.88461048893594252,0.89858466974550444,0.91205413973575944,null,0.88461048893594252,0.89858466974550444,0.91205413973575944]
["2013-05-26T15:00:00","2013-05-26T15:00:00",null,15.368979662789577,15.672551864445477,15.976124066101377,16.279696267757277,16.583268469413177,16.886840671069077,17.190412872724977,17.493985074380877,17.797557276036777,null,0.17840475981628037,0.37968974344114392,0.58798773450573871,0.66159139565467284,0.68045496252627091,0.69861403721258664,0.7161211937572971,0.73301849139534525,0.74930593012673086,null,0.7161211937572971,0.73301849139534525,0.74930593012673086]
["2013-05-26T16:00:00","2013-05-26T16:00:00",null,15.245933363613025,15.549505565268925,15.853077766924825,16.156649968580723,16.460222170236626,16.763794371892523,17.067366573548426,17.370938775204323,17.674510976860226,null,0,0.19829877794396389,0.41006665589129415,0.487014026218137,0.50909512456281703,0.53035606782612355,0.55085994486046919,0.57064881490079689,0.58972267794710642,null,0.55085994486046919,0.57064881490079689,0.58972267794710642]
["2013-05-26T17:00:00","2013-05-26T17:00:00",null,15.325893557203937,15.629465758859837,15.933037960515737,16.236610162171637,16.540182363827537,16.843754565483437,17.147326767139337,17.450898968795236,17.754471170451136,null,0,1.467867299484471E-2,0.22994798225111712,0.31026009137333982,0.33557975080857294,0.35997410707507693,0.38349573421652888,0.40619720627660727,0.42807852325531182,null,0.38349573421652888,0.40619720627660727,0.42807852325531182]
["2013-05-26T18:00:00","2013-05-26T18:00:00",null,14.949254524081274,15.252826725737174,15.556398927393074,15.859971129048974,16.163543330704876,16.467115532360772,16.770687734016676,17.074259935672572,17.377832137328475,null,0,0,0.1509081649858976,0.2345114092423512,0.26300654091572406,0.29045019171554098,0.31690545049421476,0.34244592091289489,0.36706108816284555,null,0.31690545049421476,0.34244592091289489,0.36706108816284555]
["2013-05-26T19:00:00","2013-05-26T19:00:00",null,15.337274310177964,15.640846511833864,15.944418713489764,16.247990915145664,16.551563116801564,16.855135318457464,17.158707520113364,17.462279721769264,17.765851923425164,null,0,0,0.10486381753287161,0.19188437462838287,0.22367064143598664,0.25428976447394325,0.28379431778593001,0.31228944945930309,0.33976464468532663,null,0.28379431778593001,0.31228944945930309,0.33976464468532663]
["2013-05-26T20:00:00","2013-05-26T20:00:00",null,14.992608467019515,15.296180668675415,15.599752870331315,15.903325071987215,16.206897273643115,16.510469475299015,16.814041676954915,17.117613878610815,17.421186080266715,null,0,0,6.5927480785085535E-2,0.15630226186724105,0.19131657495666238,0.22504808138034532,0.25754935518196725,0.28892554444888435,0.31919767879856736,null,0.25754935518196725,0.28892554444888435,0.31919767879856736]
["2013-05-26T21:00:00","2013-05-26T21:00:00",null,14.77896840073867,15.08254060239457,15.38611280405047,15.689685005706369,15.993257207362269,16.296829409018169,16.600401610674069,16.903973812329969,17.207546013985869,null,0,0,6.1511261116149497E-2,0.15516666252380035,0.19333541823389028,0.23010570438215064,0.26553009501225883,0.29972425302030653,0.33271972283250006,null,0.26553009501225883,0.29972425302030653,0.33271972283250006]
["2013-05-26T22:00:00","2013-05-26T22:00:00",null,14.540262382912269,14.843834584568169,15.147406786224069,15.450978987879969,15.754551189535869,16.058123391191771,16.361695592847667,16.665267794503571,16.968839996159467,null,3.9146632922497315E-2,4.2658579040175025E-2,0.10753457895170436,0.20443905625864386,0.24572019535446016,0.28548720199235567,0.32379265021600784,0.36077323253897947,0.39644997857874131,null,0.32379265021600784,0.36077323253897947,0.39644997857874131]
["2013-05-26T23:00:00","2013-05-26T23:00:00",null,14.269307369463261,14.572879571119161,14.876451772775061,15.180023974430961,15.483596176086861,15.787168377742761,16.090740579398663,16.394312781054559,16.697884982710463,null,9.1836339496398495E-2,9.8755083644398278E-2,0.16689067426395182,0.26692856457408881,0.31121693896827585,0.35388603281718645,0.39496739054702701,0.43463976390630249,0.47289263808627702,null,0.39496739054702701,0.43463976390630249,0.47289263808627702]
["2013-05-27","2013-05-27",null,13.981365648920807,14.284937850576707,14.588510052232607,14.892082253888507,15.195654455544407,15.499226657200307,15.802798858856207,16.106371060512107,16.409943262168007,null,0.15206516393369762,0.16231710245087055,0.23363868011729938,0.33674689457822049,0.38396890060962929,0.42946647800840609,0.47326065639202164,0.51554070231771654,0.55631713059422594,null,0.47326065639202164,0.51554070231771654,0.55631713059422594]
["2013-05-27T01:00:00","2013-05-27T01:00:00",null,13.832547376637315,14.136119578293215,14.439691779949115,14.743263981605015,15.046836183260915,15.350408384916815,15.653980586572715,15.957552788228615,16.261124989884514,null,0.22002237279163481,0.23353390201683197,0.3079783778777227,0.41408331282827898,0.4641758616444962,0.51242831893199026,0.55887222911696743,0.60370737356540394,0.64693375227729921,null,0.55887222911696743,0.60370737356540394,0.64693375227729921]
["2013-05-27T02:00:00","2013-05-27T02:00:00",null,13.845538468882516,14.149110670538416,14.452682872194316,14.756255073850216,15.059827275506116,15.363399477162016,15.666971678817916,15.970543880473816,16.274116082129716,null,0.28627618263441096,0.30304730256763235,0.38062519143172052,0.48972684687191198,0.54268993847293767,0.59370779045788447,0.64281194725295887,0.69020219022413687,0.73588903418015372,null,0.64281194725295887,0.69020219022413687,0.73588903418015372]
["2013-05-27T03:00:00","2013-05-27T03:00:00",null,13.777415299410574,14.080987501066474,14.384559702722374,14.688131904378274,14.991704106034174,15.295276307690074,15.598848509345974,15.902420711001874,16.205992912657774,null,0.3526456553732783,0.372697395631995,0.45342972711675178,0.5655491326640496,0.62141431147609039,0.67521858777596111,0.72699350598986823,0.77695987710125891,0.82511770111013283,null,0.72699350598986823,0.77695987710125891,0.82511770111013283]
["2013-05-27T04:00:00","2013-05-27T04:00:00",null,13.69178081771372,13.99535301936962,14.29892522102552,14.60249742268142,14.90606962433732,15.20964182599322,15.51321402764912,15.81678622930502,16.12035843096092,null,0.42059234942247992,0.44395625443289866,0.52785354334705958,0.64300121381019926,0.70177899464199078,0.75838021006552092,0.81283640450699635,0.86538941856733531,0.91602873743780189,null,0.81283640450699635,0.86538941856733531,0.91602873743780189]
["2013-05-27T05:00:00","2013-05-27T05:00:00",null,13.967226354427567,14.270798556083466,14.574370757739366,14.877942959395266,15.181515161051166,15.485087362707066,15.788659564362966,16.092231766018866,16.395803967674766,null,0.47953836719404047,0.50633009985225241,0.59352903870937979,0.71183115179318812,0.77364771234955709,0.83316152979283786,0.89041466335797281,0.94566998326335117,0.99890645989150151,null,0.89041466335797281,0.94566998326335117,0.99890645989150151]
["2013-05-27T06:00:00","2013-05-27T06:00:00",null,13.941737237328894,14.245309438984794,14.548881640640694,14.852453842296594,15.156026043952494,15.459598245608394,15.763170447264294,16.066742648920194,16.370314850576094,null,0.53789555567640956,0.56811511598241471,0.65859467516503745,0.78004071606077874,0.84488554153298967,0.90730144618728548,0.96734100406734436,1,1,null,0.96734100406734436,1,1]
["2013-05-27T07:00:00","2013-05-27T07:00:00",null,14.01682048937278,14.32039269102868,14.62396489268458,14.927537094340479,15.231109295996379,15.534681497652279,15.838253699308179,16.141825900964079,16.445398102619979,null,0.59390794181074835,0.62758687419075332,0.72138911293381369,0.84601062606769473,0.91391526088195418,0.97926479717347181,1,1,1,null,1,1,1]
["2013-05-27T08:00:00","2013-05-27T08:00:00",null,14.073804654935952,14.377376856591852,14.680949058247752,14.984521259903651,15.288093461559551,15.591665663215451,15.895237864871351,16.198810066527251,16.502382268183151,null,0.65076151264393212,0.68786827267173023,0.78495113174028597,0.91272708749483555,0.98365998722493697,1,1,1,1,null,1,1,1]
["2013-05-27T09:00:00","2013-05-27T09:00:00",null,14.212102097789096,14.515674299444996,14.819246501100896,15.122818702756796,15.426390904412695,15.729963106068595,16.033535307724495,16.337107509380395,16.640679711036295,null,0.7018003942463501,0.74239807077435471,0.84282463902081917,0.97380761143971517,1,1,1,1,1,null,1,1,1]
["2013-05-27T10:00:00","2013-05-27T10:00:00",null,13.948629115938225,14.252201317594125,14.555773519250025,14.859345720905925,15.162917922561824,15.466490124217724,15.770062325873624,16.073634527529524,16.377206729185424,null,0.69134867436320147,0.73526903045164371,0.83887107093624791,0.97289282307972125,1,1,1,1,1,null,1,1,1]
["2013-05-27T11:00:00","2013-05-27T11:00:00",null,14.130010283626094,14.433582485281994,14.737154686937894,15.040726888593793,15.344299090249693,15.647871291905593,15.951443493561493,16.255015695217395,16.558587896873291,null,0.67335783661665494,0.7206219018830059,0.8274309590319564,0.96452303532621386,0.99458487350118552,0.99742387185978731,1,1,1,null,1,1,1]
["2013-05-27T12:00:00","2013-05-27T12:00:00",null,14.419108688929352,14.722680890585252,15.026253092241152,15.329825293897052,15.633397495552952,15.936969697208852,16.240541898864752,16.544114100520652,16.847686302176552,null,0.64842722510463746,0.69910860321004609,0.80918776587575636,0.94942376998194689,0.9825033582640248,0.98825495864237722,0.99362802590624943,0.99631981694255334,0.9989169747002371,null,0.99362802590624943,0.99631981694255334,0.9989169747002371]
["2013-05-27T13:00:00","2013-05-27T13:00:00",null,14.716255767922725,15.019827969578625,15.323400171234525,15.626972372890425,15.930544574546325,16.234116776202224,16.537688977858124,16.841261179514024,17.144833381169924,null,0.61156230567775705,0.66577665951831455,0.77924159059687581,0.92273718541109051,0.95895018669636589,0.96770902237308909,0.97599469165671193,0.98148342181667536,0.98678288541939851,null,0.97599469165671193,0.98148342181667536,0.98678288541939851]
["2013-05-27T14:00:00","2013-05-27T14:00:00",null,14.844594453337823,15.148166654993723,15.451738856649623,15.755311058305523,16.058883259961423,16.362455461617323,16.666027663273223,16.969599864929123,17.273172066585023,null,0.57106977723710783,0.62885916604775638,0.7457519247741109,0.89254916953129204,0.93193764305470717,0.94375628807347889,0.95499661861179463,0.96332434713035975,0.97136817581306467,null,0.95499661861179463,0.96332434713035975,0.97136817581306467]
["2013-05-27T15:00:00","2013-05-27T15:00:00",null,14.800867785376564,15.104439987032464,15.408012188688364,15.711584390344264,16.015156592000164,16.318728793656064,16.622300995311964,16.925873196967864,17.229445398623763,null,0.53173387775737035,0.59308778672937446,0.71339785829478664,0.86348623818619863,0.90602915433028242,0.92089709388236707,0.93507105605790464,0.94622726812633595,0.95699443227155145,null,0.93507105605790464,0.94622726812633595,0.95699443227155145]
["2013-05-27T16:00:00","2013-05-27T16:00:00",null,15.015853435898508,15.319425637554408,15.622997839210308,15.926570040866208,16.230142242522106,16.53371444417801,16.837286645833906,17.14085884748981,17.444431049145706,null,0.40556668773936194,0.47050614649019268,0.59426507532086914,0.74766561996398329,0.7933945231549423,0.81133278685781107,0.82847192509677714,0.84248816514128133,0.85601020917521398,null,0.82847192509677714,0.84248816514128133,0.85601020917521398]
["2013-05-27T17:00:00","2013-05-27T17:00:00",null,15.24126102976474,15.54483323142064,15.84840543307654,16.15197763473244,16.455549836388339,16.759122038044239,17.062694239700139,17.366266441356039,17.669838643011939,null,0.2182348553065894,0.28683346749739569,0.4141043424457499,0.57089065550171503,0.61987914940069822,0.64096134091550006,0.66113925887904346,0.67807861575203399,0.69441862852709724,null,0.66113925887904346,0.67807861575203399,0.69441862852709724]
["2013-05-27T18:00:00","2013-05-27T18:00:00",null,15.20084931059111,15.50442151224701,15.80799371390291,16.11156591555881,16.41513811721471,16.71871031887061,17.02228252052651,17.32585472218241,17.629426923838309,null,3.2038622217257534E-2,0.10428587303930384,0.23505817929660019,0.39521974595668075,0.44745731575495257,0.47167292027295188,0.49486858834360159,0.51472054723634275,0.53387852875253672,null,0.49486858834360159,0.51472054723634275,0.53387852875253672]
["2013-05-27T19:00:00","2013-05-27T19:00:00",null,14.540568849561987,14.844141051217887,15.147713252873787,15.451285454529687,15.754857656185587,16.058429857841489,16.362002059497385,16.665574261153289,16.969146462809185,null,0,2.5834885063275775E-2,0.15992987088100974,0.32328793939670109,0.37859583334575703,0.4057555843097137,0.43180076554770075,0.45438657471168803,0.47618377322050803,null,0.43180076554770075,0.45438657471168803,0.47618377322050803]
["2013-05-27T20:00:00","2013-05-27T20:00:00",null,14.979542337439211,15.283114539095111,15.586686740751011,15.890258942406911,16.193831144062813,16.497403345718709,16.800975547374613,17.104547749030509,17.408119950686412,null,2.367934927248562E-2,5.3194417393208092E-2,0.19081186413735532,0.35756621587463322,0.41614421534044893,0.44644789411633862,0.47552134027016751,0.50103026626264102,0.52565594832132723,null,0.47552134027016751,0.50103026626264102,0.52565594832132723]
["2013-05-27T21:00:00","2013-05-27T21:00:00",null,14.665013363296529,14.968585564952429,15.272157766608329,15.575729968264229,15.879302169920129,16.182874371576027,16.48644657323193,16.790018774887827,17.09359097654373,null,5.6285771161463376E-2,8.9354844634805808E-2,0.23040011902674623,0.40043509108951947,0.46217804798473938,0.49552050648520646,0.52752758427625712,0.55585447900986129,0.58320349653105807,null,0.52752758427625712,0.55585447900986129,0.58320349653105807]
["2013-05-27T22:00:00","2013-05-27T22:00:00",null,14.396343462677615,14.699915664333515,15.003487865989415,15.307060067645315,15.610632269301215,15.914204470957115,16.217776672613013,16.521348874268917,16.824921075924813,null,9.7219921569006232E-2,0.13373785230761301,0.27810580625999104,0.45131625056090396,0.516129531606908,0.55241613655333244,0.58725169789424925,0.61831244289909959,0.64829016260418681,null,0.58725169789424925,0.61831244289909959,0.64829016260418681]
["2013-05-27T23:00:00","2013-05-27T23:00:00",null,14.161409950051652,14.464982151707552,14.768554353363452,15.072126555019352,15.375698756675252,15.679270958331152,15.982843159987052,16.286415361642952,16.589987563298852,null,0.15413658125460333,0.19401925078858995,0.34160473621404996,0.51789601947448249,0.58567447658391503,0.62481059469767675,0.66239052111857533,0.69609048311605171,0.72861278653514494,null,0.66239052111857533,0.69609048311605171,0.72861278653514494]
["2013-05-28","2013-05-28",null,14.050851985302646,14.354424186958546,14.657996388614446,14.961568590270346,15.265140791926246,15.568712993582146,15.872285195238046,16.175857396893946,16.479429598549846,null,0.21178927755168978,0.25503668588105621,0.40583970277959819,0.58522233980828597,0.65596597298114701,0.6979621190709816,0.73828641057186184,0.77462558956196426,0.8096924766950635,null,0.73828641057186184,0.77462558956196426,0.8096924766950635]
["2013-05-28T01:00:00","2013-05-28T01:00:00",null,13.973350719037057,14.276922920692957,14.580495122348857,14.884067324004757,15.187639525660657,15.491211727316557,15.794783928972457,16.098356130628357,16.401928332284257,null,0.27090353226301933,0.31747362015282338,0.47147313890697617,0.65390507046897695,0.7275823352790598,0.7724069649187606,0.81544407707341582,0.8543909286299376,0.89197085505083618,null,0.81544407707341582,0.8543909286299376,0.89197085505083618]
["2013-05-28T02:00:00","2013-05-28T02:00:00",null,13.807500291278089,14.111072492933989,14.414644694589889,14.718216896245789,15.021789097901689,15.325361299557589,15.628933501213488,15.932505702869388,16.236077904525288,null,0.3368944718874064,0.38676620972017695,0.54393068590373395,0.72940139719031205,0.80599126402014565,0.85361283278350586,0.89933122116572939,0.94086471567119945,0.98093665176242628,null,0.89933122116572939,0.94086471567119945,0.98093665176242628]
["2013-05-28T03:00:00","2013-05-28T03:00:00",null,13.702450345931897,14.006022547587797,14.309594749243697,14.613166950899597,14.916739152555497,15.220311354211397,15.523883555867297,15.827455757523197,16.131027959179097,null,0.40059318320744097,0.45377708579191356,0.6141170342136103,0.80262652522476574,0.88212899407435008,0.93254750196136982,0.98095768137989714,1,1,null,0.98095768137989714,1,1]
["2013-05-28T04:00:00","2013-05-28T04:00:00",null,13.774041655499271,14.077613857155171,14.381186058811071,14.684758260466971,14.988330462122871,15.291902663778771,15.595474865434671,15.899047067090571,16.202619268746471,null,0.3986794880175687,0.45520709977995,0.61875406486599316,0.8103443948366682,0.89279101013220996,0.9460380015690959,0.99717151645013369,1,1,null,0.99717151645013369,1,1]
["2013-05-28T05:00:00","2013-05-28T05:00:00",null,13.929184224760377,14.232756426416277,14.536328628072177,14.839900829728077,15.143473031383976,15.447045233039876,15.750617434695776,16.054189636351676,16.357761838007576,null,0.39160302173853545,0.45155846114871001,0.61837553175151294,0.81310978953412105,0.89857415493676907,0.95472323358467015,1,1,1,null,1,1,1]
["2013-05-28T06:00:00","2013-05-28T06:00:00",null,14.00323194237362,14.30680414402952,14.61037634568542,14.91394854734132,15.21752074899722,15.52109295065312,15.82466515230902,16.12823735396492,16.43180955562082,null,0.38226587158135639,0.44567016825679528,0.61579940361130026,0.81370913363204811,0.90222279356800905,0.96130550385313196,1,1,1,null,1,1,1]
["2013-05-28T07:00:00","2013-05-28T07:00:00",null,14.113442162371886,14.417014364027786,14.720586565683686,15.024158767339586,15.327730968995485,15.631303170651385,15.934875372307285,16.238447573963185,16.542019775619085,null,0.3722137144301591,0.43906686837086234,0.61249775366833381,0.81358295592722141,0.90513539558775968,0.96715173751010441,1,1,1,null,1,1,1]
["2013-05-28T08:00:00","2013-05-28T08:00:00",null,14.272793943739892,14.576366145395792,14.879938347051691,15.183510548707591,15.487082750363491,15.790654952019391,16.094227153675291,16.397799355331191,16.701371556987091,null,0.35809232629829935,0.42840485231300246,0.60514790236217597,0.80941909166793891,0.90403134067052571,0.96899182903882775,1,1,1,null,1,1,1]
["2013-05-28T09:00:00","2013-05-28T09:00:00",null,14.459328779769432,14.762900981425332,15.066473183081232,15.370045384737132,15.673617586393032,15.977189788048932,16.280761989704832,16.584334191360732,16.887906393016632,null,0.33983861833336371,0.41363154603953783,0.59371830526662006,0.80119651123672941,0.89888959919883593,0.96682577843930195,1,1,1,null,1,1,1]
["2013-05-28T10:00:00","2013-05-28T10:00:00",null,14.707648780248947,15.011220981904847,15.314793183560747,15.618365385216647,15.921937586872547,16.225509788528448,16.529081990184345,16.832654191840248,17.136226393496145,null,0.31338335955468971,0.39075132223095493,0.5742764239145659,0.7850562798276417,0.88592484002788796,0.95691031380166702,0.99302868180832238,0.99586768016692417,0.99861204524690583,null,0.99302868180832238,0.99586768016692417,0.99861204524690583]
["2013-05-28T11:00:00","2013-05-28T11:00:00",null,14.905572311193914,15.209144512849814,15.512716714505714,15.816288916161614,16.119861117817514,16.423433319473414,16.727005521129314,17.030577722785214,17.334149924441114,null,0.28098723384042318,0.36199332033919285,0.54903036814048156,0.76317496284893716,0.86728208413973651,0.94139045610797756,0.98052657422173917,0.98626765979135611,0.99180896399499718,null,0.98052657422173917,0.98626765979135611,0.99180896399499718]
["2013-05-28T12:00:00","2013-05-28T12:00:00",null,14.687082856055561,14.990655057711461,15.294227259367361,15.597799461023261,15.901371662679161,16.204943864335061,16.50851606599096,16.81208826764686,17.11566046930276,null,0.25248158735831461,0.33710476806211759,0.52762221755487737,0.74511052144124168,0.85243517420512294,0.9296348999416193,0.97174670892754489,0.9803583372819703,0.98867555099179971,null,0.97174670892754489,0.9803583372819703,0.98867555099179971]
["2013-05-28T13:00:00","2013-05-28T13:00:00",null,14.843328929116526,15.146901130772426,15.450473332428325,15.754045534084225,16.057617735740124,16.361189937396027,16.664762139051923,16.968334340707827,17.271906542363723,null,0.22168371257185351,0.30993450228942537,0.50393235347365617,0.72476436653792919,0.83531706558362795,0.91561865989711511,0.96071667456394039,0.97220936051190976,0.9833129985366631,null,0.96071667456394039,0.97220936051190976,0.9833129985366631]
["2013-05-28T14:00:00","2013-05-28T14:00:00",null,15.033265096009423,15.336837297665323,15.640409499321223,15.943981700977123,16.247553902633022,16.551126104288922,16.854698305944822,17.158270507600722,17.461842709256622,null,0.17950881473351435,0.27145030231726847,0.46899164404538363,0.69324096994871431,0.80707428931990843,0.89054084106279974,0.93868815026293806,0.95312498265686474,0.96706761904021976,null,0.93868815026293806,0.95312498265686474,0.96706761904021976]
["2013-05-28T15:00:00","2013-05-28T15:00:00",null,14.945566987387954,15.249139189043854,15.552711390699754,15.856283592355654,16.159855794011555,16.463427995667452,16.767000197323355,17.070572398979252,17.374144600635155,null,3.980906587283764E-2,0.13535713285288953,0.33636836146374016,0.56395088173624397,0.6810017325805201,0.76755963809166661,0.81868263816396902,0.83600052815143966,0.85270855923224742,null,0.81868263816396902,0.83600052815143966,0.85270855923224742]
["2013-05-28T16:00:00","2013-05-28T16:00:00",null,14.94944485891838,15.25301706057428,15.55658926223018,15.86016146388608,16.163733665541979,16.467305867197879,16.770878068853779,17.074450270509679,17.378022472165579,null,0,0,0.15957236738400074,0.39054065606935551,0.51085109762165581,0.60054241613599979,0.65469368112414417,0.67492417313136543,0.6944501729533038,null,0.65469368112414417,0.67492417313136543,0.6944501729533038]
["2013-05-28T17:00:00","2013-05-28T17:00:00",null,14.849544019930212,15.153116221586112,15.456688423242012,15.760260624897912,16.063832826553814,16.36740502820971,16.670977229865613,16.97454943152151,17.278121633177413,null,0,0,0,0.21994839914359765,0.34347637216897997,0.43626955926031469,0.49341754473809424,0.51652909433885952,0.53884151847572181,null,0.49341754473809424,0.51652909433885952,0.53884151847572181]
["2013-05-28T18:00:00","2013-05-28T18:00:00",null,14.600551525311337,14.904123726967237,15.207695928623137,15.511268130279037,15.814840331934937,16.118412533590835,16.421984735246738,16.725556936902635,17.029129138558538,null,0,0,0,0.190580538345173,0.31724192437375276,0.41305286157219379,0.47311344906972402,0.49902193779414877,0.52403666777605051,null,0.47311344906972402,0.49902193779414877,0.52403666777605051]
["2013-05-28T19:00:00","2013-05-28T19:00:00",null,14.855337237217984,15.158909438873884,15.462481640529784,15.766053842185684,16.069626043841584,16.373198245497484,16.676770447153384,16.980342648809284,17.283914850465184,null,3.9356929097208559E-2,4.3037112154655256E-2,4.6570087889804088E-2,0.2405469094565636,0.37047840100190316,0.46944378082101279,0.53253263323438482,0.5613747535960314,0.5892074523190638,null,0.53253263323438482,0.5613747535960314,0.5892074523190638]
["2013-05-28T20:00:00","2013-05-28T20:00:00",null,14.633513950374216,14.937086152030115,15.240658353686015,15.544230555341915,15.847802756997815,16.151374958653715,16.454947160309615,16.758519361965515,17.062091563621415,null,8.5148921140581063E-2,9.2425168785589956E-2,9.9417516594738686E-2,0.29671701772193582,0.4298450111228862,0.53189122990151549,0.59793474356958043,0.62963689190729988,0.66022447051904953,null,0.59793474356958043,0.62963689190729988,0.66022447051904953]
["2013-05-28T21:00:00","2013-05-28T21:00:00",null,14.487178381916745,14.790750583572645,15.094322785228545,15.397894986884445,15.701467188540345,16.005039390196245,16.308611591852145,16.612183793508045,16.915755995163945,null,0.13546228094024521,0.14629253393787406,0.15668116496860932,0.35725077161256624,0.49352269282544964,0.59859717651992084,0.66754277739900081,0.70205237966911538,0.73534226412590442,null,0.66754277739900081,0.70205237966911538,0.73534226412590442]
["2013-05-28T22:00:00","2013-05-28T22:00:00",null,14.224645707645983,14.528217909301883,14.831790110957783,15.135362312613683,15.438934514269583,15.742506715925483,16.046078917581383,16.349651119237283,16.653223320893183,null,0.1991294478340731,0.21339804328823073,0.22708832426193246,0.43082288833529353,0.57013358927275437,0.67813118979571174,0.74989475941592243,0.78710666753107639,0.82300422455428479,null,0.74989475941592243,0.78710666753107639,0.82300422455428479]
["2013-05-28T23:00:00","2013-05-28T23:00:00",null,14.423891439890047,14.727463641545947,15.031035843201847,15.334608044857747,15.638180246513647,15.941752448169547,16.245324649825449,16.548896851481345,16.852469053137249,null,0.26022048658768832,0.27794845411584584,0.29497192945872069,0.50190299538769267,0.64428402047593758,0.75523628225358785,0.82983885023240034,0.86979512342753595,0.9083318974433704,null,0.82983885023240034,0.86979512342753595,0.9083318974433704]
["2013-05-29","2013-05-29",null,14.412673911095361,14.716246112751261,15.019818314407161,15.323390516063061,15.626962717718961,15.93053491937486,16.23410712103076,16.53767932268666,16.84125152434256,null,0.32166902883831261,0.34285636844047007,0.3632025233437825,0.5733300911283653,0.71877092555865874,0.83267784859100202,0.91011941492841619,0.95280953839479787,0.99398552940325846,null,0.91011941492841619,0.95280953839479787,0.99398552940325846]
["2013-05-29T01:00:00","2013-05-29T01:00:00",null,14.264615836779569,14.568188038435469,14.871760240091369,15.175332441747269,15.478904643403169,15.782476845059069,16.086049046714969,16.389621248370869,16.693193450026769,null,0.3865559135454657,0.41113953636920969,0.43474528198054635,0.64800626276832662,0.79645433249699082,0.91325282793161366,0.99348081858395165,1,1,null,0.99348081858395165,1,1]
["2013-05-29T02:00:00","2013-05-29T02:00:00",null,14.115738087437894,14.419310289093794,14.722882490749694,15.026454692405594,15.330026894061493,15.633599095717393,15.937171297373293,16.240743499029193,16.544315700685093,null,0.45443951874225397,0.48241942478758448,0.50927424629820983,0.72565812528045193,0.8771029154987513,0.99678246852691821,1,1,1,null,1,1,1]
["2013-05-29T03:00:00","2013-05-29T03:00:00",null,14.011013637357884,14.314585839013784,14.618158040669684,14.921730242325584,15.225302443981484,15.528874645637384,15.832446847293284,16.136019048949183,16.439591250605083,null,0.52578249601304217,0.5571061112362814,0.58716794941125316,0.80662215254427927,0.96102160401727166,1,1,1,1,null,1,1,1]
["2013-05-29T04:00:00","2013-05-29T04:00:00",null,14.032654974007539,14.336227175663439,14.639799377319338,14.943371578975238,15.246943780631138,15.550515982287038,15.854088183942938,16.157660385598838,16.461232587254738,null,0.5965366439946389,0.63121448320452234,0.66449385285257612,0.88702889494512183,1,1,1,1,1,null,1,1,1]
["2013-05-29T05:00:00","2013-05-29T05:00:00",null,14.342185681534151,14.645757883190051,14.94933008484595,15.25290228650185,15.55647448815775,15.86004668981365,16.16361889146955,16.46719109312545,16.77076329478135,null,0.65682855728435141,0.69504988703811921,0.73172553990775957,0.95752017270832945,1,1,1,1,1,null,1,1,1]
["2013-05-29T06:00:00","2013-05-29T06:00:00",null,14.182446493046385,14.486018694702285,14.789590896358185,15.093163098014085,15.396735299669984,15.700307501325884,16.003879702981784,16.307451904637684,16.611024106293584,null,0.69445054294019226,0.73608918553301772,0.77604545872815334,1,1,1,1,1,1,null,1,1,1]
["2013-05-29T07:00:00","2013-05-29T07:00:00",null,14.169499542548099,14.473071744203999,14.776643945859899,15.080216147515799,15.383788349171699,15.687360550827599,15.990932752483499,16.294504954139398,16.598077155795298,null,0.68730047300001007,0.73235642843189319,0.77558280714378858,1,1,1,1,1,1,null,1,1,1]
["2013-05-29T08:00:00","2013-05-29T08:00:00",null,14.267323221815781,14.570895423471681,14.874467625127581,15.178039826783481,15.481612028439381,15.785184230095281,16.088756431751179,16.392328633407082,16.695900835062979,null,0.67721677142260617,0.72566901007607576,0.77216549430473091,0.99970558535540421,1,1,1,1,1,null,1,1,1]
["2013-05-29T09:00:00","2013-05-29T09:00:00",null,14.254913920577319,14.558486122233219,14.862058323889119,15.165630525545019,15.469202727200919,15.772774928856819,16.076347130512719,16.379919332168619,16.683491533824519,null,0.66683865520060648,0.71868717707566254,0.76844325201234198,0.99911675606621275,1,1,1,1,1,null,1,1,1]
["2013-05-29T10:00:00","2013-05-29T10:00:00",null,14.388802231052825,14.692374432708725,14.995946634364625,15.299518836020525,15.603091037676425,15.906663239332325,16.210235440988225,16.513807642644124,16.817379844300024,null,0.64763861444947024,0.70288341954611289,0.7558990851908165,0.98970600224788474,0.99359648148004276,0.99649856869105791,0.99928499300598184,1,1,null,0.99928499300598184,1,1]
["2013-05-29T11:00:00","2013-05-29T11:00:00",null,14.896995899512767,15.200568101168667,15.504140302824567,15.807712504480467,16.111284706136367,16.414856907792267,16.718429109448167,17.022001311104066,17.325573512759966,null,0.59922843503094281,0.65806930471514768,0.71453382762511564,0.9516634242426214,0.95875040533039035,0.96472281669218951,0.97047441707054194,0.97404945204063298,0.97681484673808583,null,0.97047441707054194,0.97404945204063298,0.97681484673808583]
["2013-05-29T12:00:00","2013-05-29T12:00:00",null,14.954167128182412,15.257739329838312,15.561311531494212,15.864883733150112,16.168455934806012,16.472028136461912,16.775600338117812,17.079172539773712,17.382744741429612,null,0.54251155671132134,0.6050115798355018,0.66499856367188304,0.90551392870223979,0.91586050049803291,0.92496632486302954,0.93374619015722393,0.9402338271470656,0.94581719058564906,null,0.93374619015722393,0.9402338271470656,0.94581719058564906]
["2013-05-29T13:00:00","2013-05-29T13:00:00",null,15.059315300564565,15.362887502220465,15.666459703876365,15.970031905532265,16.273604107188163,16.577176308844066,16.880748510499963,17.184320712155866,17.487892913811763,null,0.48756116625927437,0.55365725397101695,0.61710360988139812,0.86095216928092799,0.87449524293233205,0.88669242106558388,0.89844797723194225,0.9078061570065924,0.9161549151426287,null,0.89844797723194225,0.9078061570065924,0.9161549151426287]
["2013-05-29T14:00:00","2013-05-29T14:00:00",null,15.048080217899225,15.351652419555124,15.655224621211024,15.958796822866924,16.262369024522826,16.565941226178722,16.869513427834626,17.173085629490522,17.476657831146426,null,0.4177954102988205,0.48747704778938972,0.55438277577377082,0.80155401473373822,0.81830410504948869,0.83358212214226024,0.84831336918078271,0.86053157693150562,0.87164572976499477,null,0.84831336918078271,0.86053157693150562,0.87164572976499477]
["2013-05-29T15:00:00","2013-05-29T15:00:00",null,15.204835696960354,15.508407898616253,15.811980100272153,16.115552301928055,16.419124503583951,16.722696705239855,17.026268906895751,17.329841108551655,17.633413310207551,null,0.23149402912213302,0.30481379043520673,0.37523146453726552,0.62577795710134831,0.64577712331638737,0.6641885534123565,0.68193755055798522,0.69706836032845876,0.71100048190307863,null,0.68193755055798522,0.69706836032845876,0.71100048190307863]
["2013-05-29T16:00:00","2013-05-29T16:00:00",null,15.480393738516055,15.783965940171955,16.087538141827856,16.391110343483753,16.694682545139656,16.998254746795553,17.301826948451456,17.605399150107353,17.908971351763256,null,3.9945758386400104E-2,0.11694570275692051,0.19091738221159926,0.44487067280600412,0.46816097415527413,0.48974787648938295,0.51055668297706025,0.52864215400222669,0.54542378874418385,null,0.51055668297706025,0.52864215400222669,0.54542378874418385]
["2013-05-29T17:00:00","2013-05-29T17:00:00",null,15.505793332544611,15.809365534200511,16.112937735856413,16.416509937512309,16.720082139168213,17.023654340824109,17.327226542480012,17.630798744135909,17.934370945791812,null,0,0,3.5855497788267188E-3,0.26100872725596702,0.28763222297441016,0.31243665678160099,0.33635784665500462,0.35744003816980624,0.37712376012277848,null,0.33635784665500462,0.35744003816980624,0.37712376012277848]
["2013-05-29T18:00:00","2013-05-29T18:00:00",null,14.888509887368897,15.192082089024797,15.495654290680697,15.799226492336597,16.102798693992497,16.406370895648397,16.709943097304297,17.013515298960197,17.317087500616097,null,0,0,0,9.1867513935716738E-2,0.12181368921459745,0.1498251396861347,0.17683768332779357,0.20089556571475922,0.22344983045253988,null,0.17683768332779357,0.20089556571475922,0.22344983045253988]
["2013-05-29T19:00:00","2013-05-29T19:00:00",null,14.382234425225601,14.685806626881501,14.989378828537401,15.292951030193301,15.596523231849201,15.900095433505101,16.203667635161001,16.5072398368169,16.8108120384728,null,0,0,0,5.2699851395748294E-2,8.5842528530239853E-2,0.11692430315256121,0.14690202285764856,0.17380941841195152,0.19911856303844941,null,0.14690202285764856,0.17380941841195152,0.19911856303844941]
["2013-05-29T20:00:00","2013-05-29T20:00:00",null,14.469800743260629,14.773372944916529,15.076945146572429,15.380517348228329,15.684089549884229,15.987661751540129,16.291233953196027,16.594806154851931,16.898378356507827,null,0,0,0,4.2532031348459842E-2,7.8755547442471069E-2,0.11281301293695646,0.14565076061811669,0.17531303606113688,0.20328242729773197,null,0.14565076061811669,0.17531303606113688,0.20328242729773197]
["2013-05-29T21:00:00","2013-05-29T21:00:00",null,14.527712627693209,14.831284829349109,15.134857031005009,15.438429232660908,15.742001434316808,16.045573635972708,16.349145837628608,16.652718039284508,16.956290240940408,null,0,0,0,3.2974070207833987E-2,7.225739564389376E-2,0.1092590075843365,0.14493575362409847,0.17733187933836478,0.20794048756758593,null,0.14493575362409847,0.17733187933836478,0.20794048756758593]
["2013-05-29T22:00:00","2013-05-29T22:00:00",null,14.59941995010359,14.90299215175949,15.20656435341539,15.51013655507129,15.813708756727189,16.117280958383091,16.420853160038988,16.724425361694891,17.027997563350787,null,1.4352713924042127E-2,1.7843630424248712E-2,2.1187339602157424E-2,5.7368426474337819E-2,9.9743105678652827E-2,0.13972040849125961,0.17825718250709444,0.21341870291881354,0.24668755775813189,null,0.17825718250709444,0.21341870291881354,0.24668755775813189]
["2013-05-29T23:00:00","2013-05-29T23:00:00",null,14.538616073892134,14.842188275548034,15.145760477203934,15.449332678859834,15.752904880515734,16.056477082171632,16.360049283827536,16.663621485483432,16.967193687139336,null,5.2321688268156502E-2,5.9324550886040793E-2,6.6032998859329339E-2,0.10545264682206283,0.15095022422083976,0.19392424752308171,0.23534207913246052,0.27327950905036802,0.30922964011725462,null,0.23534207913246052,0.27327950905036802,0.30922964011725462]
["2013-05-30","2013-05-30",null,14.442496129096806,14.746068330752706,15.049640532408606,15.353212734064506,15.656784935720406,15.960357137376306,16.263929339032206,16.567501540688106,16.871073742344006,null,9.5022326543273777E-2,0.10549507604389352,0.11553671838635522,0.15816338301343513,0.20673128456299616,0.25267048392866659,0.29693782870538271,0.33761962370327187,0.3762194865715201,null,0.29693782870538271,0.33761962370327187,0.3762194865715201]
["2013-05-30T01:00:00","2013-05-30T01:00:00",null,14.289862856299896,14.593435057955796,14.897007259611696,15.200579461267596,15.504151662923496,15.807723864579396,16.111296066235298,16.414868267891194,16.718440469547097,null,0.14528311229926014,0.15917317463893751,0.172484922498159,0.21825551493717193,0.26984116659383928,0.31868245317052479,0.36573622226216485,0.4091098082963579,0.4503068289222899,null,0.36573622226216485,0.4091098082963579,0.4503068289222899]
["2013-05-30T02:00:00","2013-05-30T02:00:00",null,14.257769336451219,14.561341538107119,14.864913739763018,15.168485941418918,15.472058143074818,15.775630344730718,16.079202546386618,16.382774748042518,16.686346949698418,null,0.19592243116972671,0.21320877673099062,0.22978011529823633,0.2786736059317112,0.33326649288674925,0.38499935186571432,0.4348395452722783,0.48088389272530407,0.52466755630018436,null,0.4348395452722783,0.48088389272530407,0.52466755630018436]
["2013-05-30T03:00:00","2013-05-30T03:00:00",null,14.079551345809346,14.383123547465246,14.686695749121146,14.990267950777046,15.293840152432946,15.597412354088846,15.900984555744746,16.204556757400645,16.508128959056545,null,0.25693986626219301,0.2776014654275723,0.29741136508537108,0.34940672429583675,0.40698581693177444,0.46157870388681232,0.51417377718209356,0.56286785643648096,0.60920661853410285,null,0.51417377718209356,0.56286785643648096,0.60920661853410285]
["2013-05-30T04:00:00","2013-05-30T04:00:00",null,14.084194214678039,14.387766416333939,14.691338617989839,14.994910819645739,15.298483021301639,15.602055222957539,15.905627424613439,16.209199626269339,16.512771827925238,null,0.31901929703695103,0.34305614980644572,0.36610461055479759,0.42121235315098959,0.48176713665909138,0.53923056639893763,0.59458051958293612,0.64592433063868515,0.69482870606778424,null,0.59458051958293612,0.64592433063868515,0.69482870606778424]
["2013-05-30T05:00:00","2013-05-30T05:00:00",null,14.374667852227272,14.678240053883172,14.981812255539072,15.285384457194972,15.588956658850872,15.892528860506772,16.196101062162672,16.499673263818572,16.803245465474472,null,0.37166694437590997,0.39920522845434681,0.42560791318934293,0.48394370206735249,0.54760035415244501,0.6080394747644553,0.66625997073326226,0.72036917648646415,0.77194431333439595,null,0.66625997073326226,0.72036917648646415,0.77194431333439595]
["2013-05-30T06:00:00","2013-05-30T06:00:00",null,14.550119299279578,14.853691500935478,15.157263702591377,15.460835904247277,15.764408105903177,16.067980307559075,16.371552509214979,16.675124710870875,16.978696912526779,null,0.41164424718851667,0.44270499219336679,0.47248293053247831,0.53405728050104095,0.60083683078059535,0.66427267188224082,0.72538474025332733,0.78228037032145314,0.83653678339695325,null,0.72538474025332733,0.78228037032145314,0.83653678339695325]
["2013-05-30T07:00:00","2013-05-30T07:00:00",null,14.546079024381909,14.849651226037809,15.153223427693709,15.456795629349608,15.760367831005508,16.063940032661407,16.36751223431731,16.671084435973206,16.97465663762911,null,0.44889821453861284,0.48347090566114065,0.51662409760436756,0.58143700866348336,0.65133945713749963,0.71777201872878027,0.78177565950214634,0.84145771388519608,0.8983954031882645,null,0.78177565950214634,0.84145771388519608,0.8983954031882645]
["2013-05-30T08:00:00","2013-05-30T08:00:00",null,14.794988146278106,15.098560347934006,15.402132549589906,15.705704751245806,16.009276952901708,16.312849154557604,16.616421356213507,16.919993557869404,17.223565759525307,null,0.48003256320461191,0.51815925967975973,0.55472976446204425,0.6228338106553909,0.69589070175007584,0.7653725578746694,0.83229931547652169,0.89480985340943764,0.95447087817501663,null,0.83229931547652169,0.89480985340943764,0.95447087817501663]
["2013-05-30T09:00:00","2013-05-30T09:00:00",null,14.961896882344417,15.265469084000317,15.569041285656217,15.872613487312117,16.176185688968019,16.479757890623915,16.783330092279819,17.086902293935715,17.390474495591619,null,0.50884313914005175,0.55053435577655507,0.59053268820663285,0.66193838434294594,0.73816023286703503,0.81070189833367712,0.88057280238148683,0.94592233867300446,1,null,0.88057280238148683,0.94592233867300446,1]
["2013-05-30T10:00:00","2013-05-30T10:00:00",null,15.204804916749007,15.508377118404907,15.811949320060807,16.115521521716708,16.419093723372605,16.722665925028508,17.026238126684405,17.329810328340308,17.633382529996204,null,0.53269072535230633,0.57797800657637188,0.62143571108044959,0.6961746015859358,0.77560346677437131,0.8512364860092686,0.92408308092924241,0.99231367481430399,1,null,0.92408308092924241,0.99231367481430399,1]
["2013-05-30T11:00:00","2013-05-30T11:00:00",null,15.350918571209061,15.65449077286496,15.95806297452086,16.26163517617676,16.56520737783266,16.86877957948856,17.17235178114446,17.47592398280036,17.77949618445626,null,0.55078671118620848,0.59972263104151413,0.64668176685453393,0.72479591096413554,0.80748436686059533,0.88625079909869009,0.96211514412577015,1,1,null,0.96211514412577015,1,1]
["2013-05-30T12:00:00","2013-05-30T12:00:00",null,15.507156671599429,15.810728873255329,16.114301074911229,16.417873276567128,16.721445478223028,17.025017679878928,17.328589881534828,17.632162083190728,17.935734284846628,null,0.56695848702150287,0.61954304550804851,0.6700036126300104,0.75150352515246299,0.83744105694821147,0.9193514169982393,0.99824402694116121,1,1,null,0.99824402694116121,1,1]
["2013-05-30T13:00:00","2013-05-30T13:00:00",null,15.460017796551247,15.763589998207147,16.067162199863048,16.370734401518945,16.674306603174848,16.977878804830745,17.281451006486648,17.585023208142545,17.888595409798448,null,0.58196311908714982,0.63822786063114223,0.6922214034882529,0.77712811404102755,0.86635678097100699,0.95143209845043897,1,1,1,null,1,1,1]
["2013-05-30T14:00:00","2013-05-30T14:00:00",null,15.722169474484264,16.025741676140164,16.329313877796064,16.632886079451964,16.936458281107864,17.240030482763764,17.543602684419664,17.847174886075564,18.150747087731464,null,0.56425618117646337,0.62422213539537363,0.68179071322257534,0.77013576623187885,0.86267659791356033,0.95094841724860313,1,1,1,null,1,1,1]
["2013-05-30T15:00:00","2013-05-30T15:00:00",null,16.016359720710106,16.319931922366006,16.623504124021906,16.927076325677806,17.230648527333706,17.534220728989606,17.837792930645506,18.141365132301406,18.444937333957306,null,0.36081566176080981,0.42456694712452242,0.48578416358296417,0.57764116270994537,0.67357827761321332,0.76512020246501589,0.81733674264581702,0.82039655198786554,0.82335121324255844,null,0.81733674264581702,0.82039655198786554,0.82335121324255844]
["2013-05-30T16:00:00","2013-05-30T16:00:00",null,15.994246758715095,16.297818960370996,16.601391162026893,16.904963363682796,17.208535565338693,17.512107766994596,17.815679968650493,18.119252170306396,18.422824371962292,null,0.15795345682561218,0.22547955852539156,0.29033489880633778,0.38570384405099667,0.48502672736711561,0.57983875773567795,0.63520974053714763,0.64131884441250919,0.647228166921895,null,0.63520974053714763,0.64131884441250919,0.647228166921895]
["2013-05-30T17:00:00","2013-05-30T17:00:00",null,16.094724949474397,16.398297151130297,16.701869352786197,17.005441554442097,17.309013756097997,17.612585957753897,17.916158159409797,18.219730361065697,18.523302562721597,null,0,2.3826556594783582E-2,9.2351565124440926E-2,0.19125348610424864,0.29398316745068964,0.39209684776221848,0.45064330280182785,0.45983324563670913,0.46870774420952344,null,0.45064330280182785,0.45983324563670913,0.46870774420952344]
["2013-05-30T18:00:00","2013-05-30T18:00:00",null,15.352341959312872,15.655914160968772,15.959486362624672,16.26305856428057,16.566630765936473,16.87020296759237,17.173775169248273,17.47734737090417,17.780919572560073,null,0,0,2.1734109656406556E-2,0.12396922500538742,0.22990592301617482,0.33111095709595889,0.39264361781646789,0.40471461824489313,0.41637554113263137,null,0.39264361781646789,0.40471461824489313,0.41637554113263137]
["2013-05-30T19:00:00","2013-05-30T19:00:00",null,15.897215171514709,16.200787373170609,16.504359574826509,16.807931776482409,17.111503978138309,17.415076179794209,17.718648381450109,18.022220583106009,18.325792784761909,null,0,0,0,7.168959597217317E-2,0.18103309201328266,0.28551874641856206,0.35021636456847521,0.36535768914768457,0.37997327329011571,null,0.35021636456847521,0.36535768914768457,0.37997327329011571]
["2013-05-30T20:00:00","2013-05-30T20:00:00",null,15.770492397090624,16.074064598746524,16.377636800402424,16.681209002058324,16.984781203714224,17.288353405370124,17.591925607026024,17.895497808681924,18.199070010337824,null,0,0,0,2.189146180055155E-2,0.13459969663704088,0.24233442694160895,0.31017597290345511,0.32834556239850632,0.34589477817815928,null,0.31017597290345511,0.32834556239850632,0.34589477817815928]
["2013-05-30T21:00:00","2013-05-30T21:00:00",null,15.357827055085682,15.661399256741582,15.964971458397482,16.268543660053382,16.572115861709282,16.875688063365182,17.179260265021082,17.482832466676982,17.786404668332882,null,1.332226266795705E-2,1.6970901299197063E-2,2.0482847416874773E-2,4.5749562821541717E-2,0.16170687355731972,0.27258553167382082,0.3434448277427733,0.36453753406631073,0.3849047185870943,null,0.3434448277427733,0.36453753406631073,0.3849047185870943]
["2013-05-30T22:00:00","2013-05-30T22:00:00",null,14.988924874765543,15.292497076421443,15.596069278077342,15.899641479733242,16.203213681389144,16.50678588304504,16.810358084700944,17.11393028635684,17.417502488012744,null,3.8137211283883365E-2,4.5318825650272204E-2,5.221654018080088E-2,8.0742846293492043E-2,0.19983357003246752,0.3137299782560749,0.38750187634477806,0.4114125514094461,0.43448204177526911,null,0.38750187634477806,0.4114125514094461,0.43448204177526911]
["2013-05-30T23:00:00","2013-05-30T23:00:00",null,15.223884760647415,15.527456962303315,15.831029163959215,16.134601365615115,16.438173567271015,16.741745768926915,17.045317970582815,17.348890172238715,17.652462373894615,null,6.5633436127377986E-2,7.6411115081329029E-2,8.6778716494593164E-2,0.11863821697645749,0.24094647218851492,0.35793423418037756,0.4346923379499803,0.46148407060819235,0.48733998528893929,null,0.4346923379499803,0.46148407060819235,0.48733998528893929]
["2013-05-31","2013-05-31",null,15.059920685846006,15.363492887501906,15.667065089157806,15.970637290813706,16.274209492469605,16.577781694125505,16.881353895781405,17.184926097437305,17.488498299093205,null,0.10040590861588151,0.1147375929224525,0.12852250717477429,0.16366262798213396,0.28912532581486,0.4091623823400356,0.48885411774686016,0.51847433395493836,0.54706409890693142,null,0.48885411774686016,0.51847433395493836,0.54706409890693142]
["2013-05-31T01:00:00","2013-05-31T01:00:00",null,14.960838428004383,15.264410629660283,15.567982831316183,15.871555032972083,16.175127234627983,16.478699436283883,16.782271637939782,17.085843839595682,17.389416041251582,null,0.14138211825836661,0.15923626349135089,0.17639643134778807,0.21478562805443641,0.34337122408162435,0.46642603071390626,0.54901985333174586,0.58143700866348358,0.61272907946051614,null,0.54901985333174586,0.58143700866348358,0.61272907946051614]
["2013-05-31T02:00:00","2013-05-31T02:00:00",null,14.896252134527801,15.199824336183701,15.503396537839601,15.806968739495501,16.110540941151399,16.414113142807302,16.717685344463199,17.021257546119102,17.324829747774999,null,0.18159074686315568,0.20298838264002436,0.22355534852678363,0.26521465075019174,0.39695468939804829,0.52303776094617205,0.60855470039249793,0.64380033927410174,0.67780523072490939,null,0.60855470039249793,0.64380033927410174,0.67780523072490939]
["2013-05-31T03:00:00","2013-05-31T03:00:00",null,14.83580251139176,15.13937471304766,15.44294691470356,15.74651911635946,16.050091318015362,16.353663519671258,16.657235721327162,16.960807922983058,17.264380124638961,null,0.22451219612171974,0.24943229282500171,0.27338502712461193,0.3182934052473087,0.45316685689836272,0.58225716374485725,0.67068670521093376,0.7087292832161971,0.74543648051204414,null,0.67068670521093376,0.7087292832161971,0.74543648051204414]
["2013-05-31T04:00:00","2013-05-31T04:00:00",null,14.78099317034469,15.08456537200059,15.38813757365649,15.69170977531239,15.99528197696829,16.29885417862419,16.60242638028009,16.905998581935989,17.209570783591889,null,0.26782269330349961,0.29629679535940151,0.32365632768933383,0.37184532613752597,0.50987322040924854,0.64200230698032057,0.73336548008361879,0.77422602683001274,0.81365655958837035,null,0.73336548008361879,0.77422602683001274,0.81365655958837035]
["2013-05-31T05:00:00","2013-05-31T05:00:00",null,15.039545332588171,15.343117534244071,15.646689735899971,15.950261937555871,16.253834139211769,16.557406340867672,16.860978542523569,17.164550744179472,17.468122945835368,null,0.30487687928762008,0.33694704593108421,0.36775543552628087,0.41926711353491058,0.56049150966224404,0.69570143519283567,0.79004029916829799,0.83376087389076481,0.87595680134657516,null,0.79004029916829799,0.83376087389076481,0.87595680134657516]
["2013-05-31T06:00:00","2013-05-31T06:00:00",null,14.866182434671124,15.169754636327024,15.473326837982924,15.776899039638824,16.080471241294724,16.384043442950624,16.687615644606524,16.991187846262424,17.294760047918324,null,0.34138429521749136,0.37702949683104653,0.41128674369150753,0.46610007164310374,0.61051045481731248,0.74879070449868823,0.84608422972884345,0.89265431761864755,0.93759461015443957,null,0.84608422972884345,0.89265431761864755,0.93759461015443957]
["2013-05-31T07:00:00","2013-05-31T07:00:00",null,15.007107855608579,15.310680057264479,15.614252258920379,15.917824460576279,16.221396662232181,16.524968863888077,16.82854106554398,17.132113267199877,17.43568546885578,null,0.3733072545386576,0.4125274911223038,0.45023359524802919,0.50834857314259185,0.65595545817241141,0.79729551719583569,0.89755421848941941,0.94697381954656079,0.99466899197107006,null,0.89755421848941941,0.94697381954656079,0.99466899197107006]
["2013-05-31T08:00:00","2013-05-31T08:00:00",null,15.150883317922553,15.454455519578453,15.758027721234352,16.061599922890252,16.365172124546152,16.668744326202052,16.972316527857952,17.275888729513852,17.579460931169752,null,0.4035163000359272,0.4463115715896645,0.48746653298065423,0.54889367562691893,0.69968654770361371,0.84409693087782212,0.94732080823483433,0.99960043726804859,1,null,0.94732080823483433,0.99960043726804859,1]
["2013-05-31T09:00:00","2013-05-31T09:00:00",null,15.215245685257958,15.518817886913858,15.822390088569758,16.125962290225658,16.429534491881558,16.733106693537458,17.036678895193358,17.340251096849258,17.643823298505158,null,0.4318537095782668,0.47825556052830187,0.52286989399329142,0.58763023100872935,0.74163011974977056,0.88914237150096975,0.99534193973014595,1,1,null,0.99534193973014595,1,1]
["2013-05-31T10:00:00","2013-05-31T10:00:00",null,15.448579172498826,15.752151374154726,16.055723575810624,16.359295777466528,16.662867979122424,16.966440180778328,17.270012382434224,17.573584584090128,17.877156785746024,null,0.455543573659488,0.50557303362329198,0.55367828358848803,0.62179284459057027,0.77903129442216457,0.92966644436782575,1,1,1,null,1,1,1]
["2013-05-31T11:00:00","2013-05-31T11:00:00",null,15.638960967865263,15.942533169521163,16.246105371177062,16.549677572832962,16.853249774488862,17.156821976144762,17.460394177800662,17.763966379456562,18.067538581112462,null,0.47110549058811974,0.52481513360937049,0.5764638741184509,0.64799574795959081,0.80852533292541595,0.96233595510921688,1,1,1,null,1,1,1]
["2013-05-31T12:00:00","2013-05-31T12:00:00",null,15.858706170019262,16.162278371675164,16.465850573331061,16.769422774986964,17.07299497664286,17.376567178298764,17.68013937995466,17.983711581610564,18.28728378326646,null,0.47912828965335352,0.53653914534952207,0.59175240601995804,0.66672262231762669,0.83056437203515388,0.98757149607456562,1,1,1,null,1,1,1]
["2013-05-31T13:00:00","2013-05-31T13:00:00",null,15.938701853722916,16.242274055378815,16.545846257034718,16.849418458690614,17.152990660346518,17.456562862002414,17.760135063658318,18.063707265314214,18.367279466970118,null,0.48517430467630168,0.54630740266485922,0.60509569830538623,0.68352528667705481,0.85070023076375512,1,1,1,1,null,1,1,1]
["2013-05-31T14:00:00","2013-05-31T14:00:00",null,16.024648377034367,16.328220578690267,16.631792780346167,16.935364982002067,17.238937183657967,17.542509385313867,17.846081586969767,18.149653788625667,18.453225990281567,null,0.4679931072023934,0.53286947710081101,0.59525383732890025,0.67716382739203984,0.84769299546538435,1,1,1,1,null,1,1,1]
["2013-05-31T15:00:00","2013-05-31T15:00:00",null,16.258588375008792,16.562160576664692,16.865732778320591,17.169304979976491,17.472877181632391,17.776449383288291,18.080021584944191,18.383593786600091,18.687165988255991,null,0.26070416778952421,0.3293763836414797,0.39543041211828001,0.48087337791656848,0.65480934402023505,0.81040748368908155,0.81359347073595689,0.81667430969547661,0.81965000056764059,null,0.81359347073595689,0.81667430969547661,0.81965000056764059]
["2013-05-31T16:00:00","2013-05-31T16:00:00",null,16.339167294610117,16.642739496266017,16.946311697921917,17.249883899577817,17.553456101233717,17.857028302889617,18.160600504545517,18.464172706201417,18.767744907857317,null,5.1396385099427094E-2,0.12388547652239157,0.19361968805663859,0.28261665920754697,0.4599804529590068,0.61889075737955535,0.62527324628204151,0.63145595381855202,0.63742836518035118,null,0.62527324628204151,0.63145595381855202,0.63742836518035118]
["2013-05-31T17:00:00","2013-05-31T17:00:00",null,16.341941802631524,16.645514004287428,16.949086205943324,17.252658407599228,17.556230609255124,17.859802810911027,18.163375012566924,18.466947214222827,18.770519415878724,null,0,0,0,8.4286336837376574E-2,0.26507795823662961,0.42730042740888019,0.43688993297571277,0.44617450908921408,0.45514364094064841,null,0.43688993297571277,0.44617450908921408,0.45514364094064841]
["2013-05-31T18:00:00","2013-05-31T18:00:00",null,15.900325275307049,16.20389747696295,16.507469678618847,16.81104188027475,17.114614081930647,17.41818628358655,17.721758485242447,18.02533068689835,18.328902888554246,null,0,0,0,1.6434276066794998E-2,0.20058012145269233,0.36605166652423154,0.3787745850942616,0.39108742612360475,0.40299018961226091,null,0.3787745850942616,0.39108742612360475,0.40299018961226091]
["2013-05-31T19:00:00","2013-05-31T19:00:00",null,16.237828537581144,16.541400739237041,16.844972940892944,17.148545142548841,17.452117344204744,17.755689545860641,18.059261747516544,18.36283394917244,18.666406150828344,null,0,0,0,0,0.15113949077807981,0.31993371541005661,0.33587416545316862,0.35128887505950257,0.36619887384652949,null,0.33587416545316862,0.35128887505950257,0.36619887384652949]
["2013-05-31T20:00:00","2013-05-31T20:00:00",null,15.924471764644048,16.22804396629995,16.531616167955846,16.83518836961175,17.138760571267646,17.44233277292355,17.745904974579446,18.049477176235349,18.353049377891246,null,7.5075734371912667E-3,1.1271874964522461E-2,1.4888969169555788E-2,1.8379885669762373E-2,0.1728946300519576,0.34493793058322303,0.36401179362953251,0.38246528296044391,0.4003089133846926,null,0.36401179362953251,0.38246528296044391,0.4003089133846926]
["2013-05-31T21:00:00","2013-05-31T21:00:00",null,15.785317116642652,16.088889318298552,16.392461519954452,16.696033721610352,16.999605923266252,17.303178124922152,17.606750326578052,17.910322528233952,18.213894729889851,null,1.9368277690905201E-2,2.6854821510625342E-2,3.4057465494485309E-2,4.1007754068691796E-2,0.19885569282006016,0.37411652482440755,0.39629225644770782,0.4177424662682544,0.43848818390351824,null,0.39629225644770782,0.4177424662682544,0.43848818390351824]
["2013-05-31T22:00:00","2013-05-31T22:00:00",null,15.505672399239652,15.809244600895552,16.11281680255145,16.416389004207353,16.71996120586325,17.023533407519153,17.327105609175049,17.630677810830953,17.934250012486849,null,4.145989084432096E-2,5.2595073295281111E-2,6.3309663396818788E-2,7.3635205575140666E-2,0.23473222022579771,0.41313698004207811,0.43834097658122023,0.46271430323025309,0.48628850441538307,null,0.43834097658122023,0.46271430323025309,0.48628850441538307]
["2013-05-31T23:00:00","2013-05-31T23:00:00",null,15.387330323629094,15.690902525284994,15.994474726940894,16.298046928596793,16.601619130252693,16.905191331908593,17.208763533564493,17.512335735220393,17.815907936876293,null,6.4729162576119659E-2,7.9512983658319825E-2,9.3750034686270772E-2,0.10746134527744361,0.27181795063612485,0.45336663826433832,0.48160941452805783,0.50890585800557697,0.53530854274057316,null,0.48160941452805783,0.50890585800557697,0.53530854274057316]

{"sheet":"predict","index":2,"n_rows":8059,"n_cols":81,"rows_kept":1125,"cut":true,"hidden":false,"merged":[[0,0,0,4],[0,31,0,35],[0,37,0,41],[0,43,0,47],[0,48,0,52]],"bounds":{"rows_first":500,"rows_last":125,"rows_between":500,"halvings":2}}
["Predicted Power",null,null,null,null,6,7,8,9,10,11,12,13,14,15,16,17,18,19,20,21,22,23,24,25,26,27,28,29,30,31,"Predicted Power (kWh)",null,null,null,null,null,"Predicted Power - current flow (kWh)",null,null,null,null,null,"Predicted Power - savings (kWh)",null,null,null,null,"Predicted Power - current flow - savings (kWh)",null,null,null,null,"Total savings (kWh)","Total savings - current flow (kWh)","Yearly savings","Yearly savings (current flow)","Power - current operation",null,"cooling load (kBtu/h)","dT","chilled water flow (gpm)","Secondary pumping power ","chilled water flow (gpm)","Secondary pumping power ","Additional power",null,null,null,null,null,null,null,null,null,null,"chiller 1","chiller 2","chiller 3","chiller 4","chiller 6"]
["Ch 1","Ch 2","Ch 3","Ch 4","Ch 6",null,null,null,"DryBulbFarenheit","WetBulbFarenheit","chiller 1","Ch1 load (kBtu/h)","CW Flow (ft^3/h)","Power 1 (kWh)","chiller 2","Ch2 load (kBtu/h)","CW Flow (ft^3/hr)","Power 2 (kWh)","chiller 3","Ch3 load (kBtu/h)","CW Flow (ft^3/h)","Power 3 (kWh)","chiller 4","Ch4 load (kBtu/h)","CW Flow (ft^3/h)","Power 4 (kWh)","Chiller6","Ch6 load (kBtu/h)","CW Flow (ft^3/h)","Power 6 (kWh)",null,"Ch 1","Ch 2","Ch 3","Ch 4","Ch 6",null,"Ch 1","Ch 2","Ch 3","Ch 4","Ch 6",null,"Ch 1","Ch 2","Ch 3","Ch 4","Ch 6","Ch 1","Ch 2","Ch 3","Ch 4","Ch 6",null,null,null,null,null,null,null,null,null,null,"current operation","current operation","kWh"]
[0,0,0,1856.7039047591641,0,{"$f":"SUM(A3:E3)","v":1856.7039047591641},{"$f":"N3+R3+V3+Z3+AD3","v":2229.2746460000003},"2013-01-01",45,44,"OFF",-29.255516057949976,-71.070556740496016,-8.8484060000000007,"OFF",-6.3494981194399793,-108.03237252098002,-8.8484060000000007,"OFF",-0.34408456362500067,-33.398399859304,-1.7696810000000001,"ON",31096.26698316999,77256.063504616017,2252.9810000000002,"OFF",-6.4744811033000067,-120.37338813006001,-4.2398610000000003,null,0,0,0,1844.2940678419536,0,{"$f":"SUM(AF3:AJ3)","v":1844.2940678419536},0,0,0,1877.2363521266693,0,{"$f":"SUM(AL3:AP3)","v":1877.2363521266693},{"$f":"IF($K3=\"ON\",$N3-AF3,0)","v":0},{"$f":"IF($O3=\"ON\",$R3-AG3,0)","v":0},{"$f":"IF($S3=\"ON\",$V3-AH3,0)","v":0},{"$f":"IF($W3=\"ON\",$Z3-AI3,0)","v":408.6869321580466},{"$f":"IF($AA3=\"ON\",$AD3-AJ3,0)","v":0},{"$f":"IF($K3=\"ON\",$N3-AL3,0)","v":0},{"$f":"IF($O3=\"ON\",$R3-AM3,0)","v":0},{"$f":"IF($S3=\"ON\",$V3-AN3,0)","v":0},{"$f":"IF($W3=\"ON\",$Z3-AO3,0)","v":375.7446478733309},{"$f":"IF($AA3=\"ON\",$AD3-AP3,0)","v":0},{"$f":"SUM(AR3:AV3)+BN3","v":410.47251915892087},{"$f":"SUM(AW3:BA3)+BN3","v":377.53023487420518},{"$f":"SUM(BB3:BB8057)","v":3237402.4499348649},{"$f":"SUM(BC3:BC8057)","v":1588813.1423420534},{"$f":"N3+R3+V3+Z3+AD3","v":2229.2746460000003},{"$f":"SUM(BF3:BF8057)","v":41694750.881634541},{"$f":" -0.6251*I3^3 + 145.21*I3^2 - 8340.3*I3 + 170112","v":31886.51250000007},{"$f":"19.5285952781395+42*-0.3035722016559+BH3*0.0000340867411548605+J3*0.0608468772796604","v":10.542732706815483},{"$f":"BH3*1000/(500*BI3)","v":6049.0033062085759},{"$f":"0.00000128*BJ3^2+0*BJ3+24.024","v":70.859764478108531},{"$f":"0.094*BH3 + 3165.9","v":6163.2321750000065},{"$f":"0.00000128*BL3^2+0*BL3+24.024","v":72.645351478982803},{"$f":"BM3-BK3","v":1.7855870008742727},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF3:AJ3)","v":1844.2940678419536},{"$f":"A3-AF3","v":0},{"$f":"B3-AG3","v":0},{"$f":"C3-AH3","v":0},{"$f":"D3-AI3","v":12.409836917210441},{"$f":"E3-AJ3","v":0}]
[0,0,0,1839.2140502123443,0,{"$f":"SUM(A4:E4)","v":1839.2140502123443},{"$f":"N4+R4+V4+Z4+AD4","v":2046.8576230000001},"2013-01-01T01:00:00",46,44,"OFF",-29.707556908769991,-70.275796361938006,-8.8484060000000007,"OFF",-7.1015607671999792,-108.41247984424001,-8.8484060000000007,"OFF",-0.38725177037499742,-33.398399859304,-1.7696810000000001,"ON",30468.879509999995,77108.825054878005,2072.518,"OFF",-6.0209150675799847,-114.81174183446001,-6.1938839999999997,null,0,0,0,1827.2839331090652,0,{"$f":"SUM(AF4:AJ4)","v":1827.2839331090652},0,0,0,1859.2182175262074,0,{"$f":"SUM(AL4:AP4)","v":1859.2182175262074},{"$f":"IF($K4=\"ON\",$N4-AF4,0)","v":0},{"$f":"IF($O4=\"ON\",$R4-AG4,0)","v":0},{"$f":"IF($S4=\"ON\",$V4-AH4,0)","v":0},{"$f":"IF($W4=\"ON\",$Z4-AI4,0)","v":245.23406689093486},{"$f":"IF($AA4=\"ON\",$AD4-AJ4,0)","v":0},{"$f":"IF($K4=\"ON\",$N4-AL4,0)","v":0},{"$f":"IF($O4=\"ON\",$R4-AM4,0)","v":0},{"$f":"IF($S4=\"ON\",$V4-AN4,0)","v":0},{"$f":"IF($W4=\"ON\",$Z4-AO4,0)","v":213.29978247379267},{"$f":"IF($AA4=\"ON\",$AD4-AP4,0)","v":0},{"$f":"SUM(AR4:AV4)+BN4","v":245.86125925065366},{"$f":"SUM(AW4:BA4)+BN4","v":213.92697483351148},{"$f":"BD3/BG3","v":7.7645324207006039E-2},{"$f":"BE3/BG3","v":3.8105831279636793E-2},{"$f":"N4+R4+V4+Z4+AD4","v":2046.8576230000001},null,{"$f":" -0.6251*I4^3 + 145.21*I4^2 - 8340.3*I4 + 170112","v":32877.826400000049},{"$f":"19.5285952781395+42*-0.3035722016559+BH4*0.0000340867411548605+J4*0.0608468772796604","v":10.576523367127997},{"$f":"BH4*1000/(500*BI4)","v":6217.1330329935945},{"$f":"0.00000128*BJ4^2+0*BJ4+24.024","v":73.499511231923378},{"$f":"0.094*BH4 + 3165.9","v":6256.415681600005},{"$f":"0.00000128*BL4^2+0*BL4+24.024","v":74.126703591642183},{"$f":"BM4-BK4","v":0.62719235971880494},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF4:AJ4)","v":1827.2839331090652},{"$f":"A4-AF4","v":0},{"$f":"B4-AG4","v":0},{"$f":"C4-AH4","v":0},{"$f":"D4-AI4","v":11.930117103279144},{"$f":"E4-AJ4","v":0}]
[0,0,0,1818.1579007973382,0,1818.1579007973382,2008.4847240000001,"2013-01-01T02:00:00",45,43,"OFF",-29.916213511230008,-69.579997033272008,-8.8484060000000007,"OFF",-7.5566853671999974,-107.93010688748001,-8.8484060000000007,"OFF",-7.0957397419997459E-2,-46.618603145626004,-1.7696810000000001,"ON",29703.018388520009,77335.942990422001,2031.933,"OFF",-5.8639669550699995,-118.97704113900002,-3.9817830000000001,null,0,0,0,1806.7999533823327,0,1806.7999533823327,0,0,0,1836.8100710707911,0,1836.8100710707911,0,0,0,225.13304661766733,0,0,0,0,195.12292892920891,0,226.37329634437998,196.36317865592156,{"$f":"BD3*0.09","v":291366.22049413784},{"$f":"BE3*0.09","v":142993.18281078478},2008.4847240000001,null,{"$f":" -0.6251*I5^3 + 145.21*I5^2 - 8340.3*I5 + 170112","v":31886.51250000007},10.481885829535823,6084.1174991909102,71.405101752270156,6163.2321750000065,72.645351478982803,1.2402497267126478,null,null,null,null,null,null,null,null,null,1806.7999533823327,0,0,0,11.357947415005583,0]
[0,0,0,1786.7848331921732,0,1786.7848331921732,2066.442724,"2013-01-01T03:00:00",44,43,"OFF",-29.668131177719999,-68.884197704605995,-8.8484060000000007,"OFF",-7.1846148674000032,-109.2405507464,-8.8484060000000007,"OFF",1.9149148900025007E-3,-33.398399859304,-1.7696810000000001,"ON",28539.459756080007,76517.673547409999,2089.8910000000001,"OFF",-6.3203773303999897,-118.98177343106001,-3.9817830000000001,null,0,0,0,1776.2680317345594,0,1776.2680317345594,0,0,0,1805.3684932681256,0,1805.3684932681256,0,0,0,313.6229682654407,0,0,0,0,284.5225067318745,0,315.8765780982161,286.7761165646499,null,null,2066.442724,null,31016.841600000043,10.452241582677607,5934.9645441421744,69.110469299487647,6081.4831104000041,71.364079132263043,2.2536098327753962,null,null,null,null,null,null,null,null,null,1776.2680317345594,0,0,0,10.516801457613838,0]
[0,0,0,1952.9014857248699,0,1952.9014857248699,2166.6797240000001,"2013-01-01T04:00:00",44,43,"OFF",-29.916717360739984,-71.667395019270003,-8.8484060000000007,"OFF",-7.0926896202600265,-108.59591631782001,-8.8484060000000007,"OFF",-6.0262821895998867E-2,-33.398399859304,-1.7696810000000001,"ON",34416.92842525,77246.871628852008,2190.1280000000002,"OFF",-6.3527273869500149,-118.28596608156001,-3.9817830000000001,null,0,0,0,1937.7862635435513,0,1937.7862635435513,0,0,0,1977.9393996765066,0,1977.9393996765066,0,0,0,252.34173645644887,0,0,0,0,212.18860032349357,0,254.59534628922427,214.44221015626897,null,null,2166.6797240000001,null,31016.841600000043,10.452241582677607,5934.9645441421744,69.110469299487647,6081.4831104000041,71.364079132263043,2.2536098327753962,null,null,null,null,null,null,null,null,null,1937.7862635435513,0,0,0,15.115222181318586,0]
[0,0,0,1655.0442343277384,0,1655.0442343277384,2038.5036460000001,"2013-01-01T05:00:00",43,42,"OFF",-30.548220158880017,-71.667395019270003,-8.8484060000000007,"OFF",-7.2280624579800259,-103.62307944616001,-8.8484060000000007,"OFF",-5.7689001749996194E-2,-33.398399859304,-1.7696810000000001,"ON",23315.343515120006,76928.203894032005,2062.21,"OFF",-7.2338348735100215,-118.98177343106001,-4.2398610000000003,null,0,0,0,1647.8905616160098,0,1647.8905616160098,0,0,0,1667.2276144979026,0,1667.2276144979026,0,0,0,414.31943838399025,0,0,0,0,394.98238550209749,0,416.91052215203456,397.5734692701418,null,null,2038.5036460000001,null,30272.564300000085,10.366024717725409,5840.7277860789663,67.690049370975885,6011.521044200008,70.281133139020227,2.5910837680443422,null,null,null,null,null,null,null,null,null,1647.8905616160098,0,0,0,7.1536727117286318,0]
[0,0,0,1777.1870323940245,0,1777.1870323940245,2003.4932250000002,"2013-01-01T06:00:00",42,40,"OFF",-30.53923681949,-70.971595690604005,-8.8484060000000007,"OFF",-6.9832502764500273,-106.50849426932001,-8.8484060000000007,"OFF",-1.0748704747499986,-33.398399859304,-2.47018,"ON",28177.887052800023,76939.336811624002,2027.6420000000001,"OFF",-7.0482870260999997,-117.59015873206,-3.9817830000000001,null,0,0,0,1766.9247283229183,0,1766.9247283229183,0,0,0,1794.6557612886784,0,1794.6557612886784,0,0,0,260.71727167708173,0,0,0,0,232.98623871132168,0,263.00150800108099,235.27047503532091,null,null,2003.4932250000002,null,29657.431200000021,10.2233630804106,5801.893362630899,67.111317236915824,5953.6985328000019,69.395553560915062,2.284236323999238,null,null,null,null,null,null,null,null,null,1766.9247283229183,0,0,0,10.2623040711062,0]
[0,0,0,1964.2656023601226,0,1964.2656023601226,2121.0817240000001,"2013-01-01T07:00:00",41,39,"OFF",-31.199161741650006,-71.667395019270003,-8.8484060000000007,"OFF",-6.9827935372649845,-109.05711427282002,-8.8484060000000007,"OFF",-0.16047754587500335,-75.14639166260001,-1.7696810000000001,"ON",34795.775314310013,76850.265450054008,2144.5300000000002,"OFF",-6.93691978049001,-116.89443159090001,-3.9817830000000001,null,0,0,0,1948.8238233508609,0,1948.8238233508609,0,0,0,1990.7790626858134,0,1990.7790626858134,0,0,0,195.70617664913925,0,0,0,0,153.75093731418679,0,198.05431695705909,156.09907762210662,null,null,2121.0817240000001,null,29175.192900000024,10.14607827102388,5751.0285492910634,66.359141599693913,5908.3681326000024,68.707281907613748,2.3481403079198344,null,null,null,null,null,null,null,null,null,1948.8238233508609,0,0,0,15.441779009261609,0]
[0,0,0,1918.3140085110499,0,1918.3140085110499,2242.2522249999997,"2013-01-01T08:00:00",39,38,"OFF",-31.414690216209998,-71.667395019270003,-8.8484060000000007,"OFF",-6.2286320839399822,-108.67708715790002,-8.8484060000000007,"OFF",-0.19849185762499547,-46.618603145626004,-2.47018,"ON",33247.080682974993,76992.210149352002,2266.4009999999998,"OFF",-7.3236226089599858,-116.89443159090001,-3.9817830000000001,null,0,0,0,1904.1839393515531,0,1904.1839393515531,0,0,0,1942.2647240664155,0,1942.2647240664155,0,0,0,362.2170606484467,0,0,0,0,324.13627593358433,0,364.72169278844359,326.64090807358122,null,null,2242.2522249999997,null,28624.403100000054,10.066456764400883,5687.086085985623,65.422973631246435,5856.5938914000053,67.927605771243336,2.5046321399969003,null,null,null,null,null,null,null,null,null,1904.1839393515531,0,0,0,14.13006915949677,0]
[0,0,0,1960.4116514577711,0,1960.4116514577711,2354.2297020000001,"2013-01-01T09:00:00",40,38,"OFF",-31.994561986740003,-69.579997033272008,-8.8484060000000007,"OFF",-7.4552536369350042,-107.1531286979,-8.8484060000000007,"OFF",6.6811244660001119E-3,-75.14639166260001,-1.7696810000000001,"ON",34667.594026170002,77553.026862632003,2379.6320000000001,"OFF",-6.7538675903300014,-116.89916388296,-5.9358050000000002,null,0,0,0,1945.080774499351,0,1945.080774499351,0,0,0,1985.0984793043087,0,1985.0984793043087,0,0,0,434.55122550064902,0,0,0,0,394.53352069569132,0,436.80814899963917,396.79044419468147,null,null,2354.2297020000001,null,28829.600000000006,10.073451258016961,5723.8774004204279,65.960348793655953,5875.8824000000004,68.217272292646101,2.2569234989901474,null,null,null,null,null,null,null,null,null,1945.080774499351,0,0,0,15.330876958420049,0]
[0,0,0,1734.2459897327415,0,1734.2459897327415,2415.482724,"2013-01-01T10:00:00",40,38,"OFF",-31.732603328159993,-73.754793005267999,-8.8484060000000007,"OFF",-6.2303822023100572,-109.2405507464,-8.8484060000000007,"OFF",9.6384766819997622E-3,-75.14639166260001,-1.7696810000000001,"ON",26525.905417649996,76713.341792840001,2438.931,"OFF",-6.9630707237700165,-118.28123378950001,-3.9817830000000001,null,0,0,0,1725.1051292966179,0,1725.1051292966179,0,0,0,1750.1195391017784,0,1750.1195391017784,0,0,0,713.82587070338218,0,0,0,0,688.81146089822164,0,716.08279420237227,691.06838439721173,null,null,2415.482724,null,28829.600000000006,10.073451258016961,5723.8774004204279,65.960348793655953,5875.8824000000004,68.217272292646101,2.2569234989901474,null,null,null,null,null,null,null,null,null,1725.1051292966179,0,0,0,9.140860436123603,0]
[0,0,0,1776.5576186230053,0,1776.5576186230053,2426.0710990000002,"2013-01-01T11:00:00",40,38,"OFF",-31.724382118800005,-70.275796361938006,-8.8484060000000007,"OFF",-6.2600650404599998,-107.8489360474,-8.8484060000000007,"OFF",0.2238230209999976,-75.14639166260001,-3.2812839999999999,"ON",28154.080792174998,77358.200804772001,2452.9850000000001,"OFF",-6.5266700577999828,-120.37338813006001,-5.9358050000000002,null,0,0,0,1766.3119566009746,0,1766.3119566009746,0,0,0,1793.3461601204556,0,1793.3461601204556,0,0,0,686.67304339902557,0,0,0,0,659.63883987954455,0,688.92996689801566,661.89576337853464,null,null,2426.0710990000002,null,28829.600000000006,10.073451258016961,5723.8774004204279,65.960348793655953,5875.8824000000004,68.217272292646101,2.2569234989901474,null,null,null,null,null,null,null,null,null,1766.3119566009746,0,0,0,10.245662022030729,0]
[0,0,0,1820.4570115855076,0,1820.4570115855076,2450.3077020000001,"2013-01-01T12:00:00",42,39,"OFF",-31.654052282700025,-70.971595690604005,-8.8484060000000007,"OFF",-6.5521736165750051,-106.45732134840001,-8.8484060000000007,"OFF",4.4127518999993683E-2,-33.398399859304,-1.7696810000000001,"ON",29787.216889299998,77546.072799554007,2475.71,"OFF",-8.3456744912099783,-117.59015873206,-5.9358050000000002,null,0,0,0,1809.0368809510221,0,1809.0368809510221,0,0,0,1838.8496641218808,0,1838.8496641218808,0,0,0,666.67311904897792,0,0,0,0,636.86033587811926,0,668.43985020030755,638.62706702944888,null,null,2450.3077020000001,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1809.0368809510221,0,0,0,11.420130634485531,0]
[0,0,0,1931.6691167165066,0,1931.6691167165066,2468.8897019999999,"2013-01-01T13:00:00",43,39,"OFF",-31.406047406369989,-70.176835312046009,-8.8484060000000007,"OFF",-6.7117331193500043,-105.76159420724001,-8.8484060000000007,"OFF",-5.02055885879997E-2,-61.926196397112001,-1.7696810000000001,"ON",33701.845487079991,77104.934950388008,2494.2919999999999,"OFF",-5.9529251597500048,-120.10196310750001,-5.9358050000000002,null,0,0,0,1917.1602423768404,0,1917.1602423768404,0,0,0,1956.0137576274167,0,1956.0137576274167,0,0,0,577.1317576231595,0,0,0,0,538.27824237258324,0,578.14336871177284,539.28985346119657,null,null,2468.8897019999999,null,30272.564300000085,10.183484085886429,5945.4237949771377,69.269522050406849,6011.521044200008,70.281133139020227,1.0116110886133782,null,null,null,null,null,null,null,null,null,1917.1602423768404,0,0,0,14.508874339666136,0]
[0,0,0,0,0,0,-28.421817000000001,"2013-01-01T14:00:00",41,38,"OFF",-32.12239939281001,-71.766356069162001,-8.8484060000000007,"OFF",-7.200801102300038,-109.29164345898002,-8.8484060000000007,"OFF",9.1886449941999543E-2,-75.14639166260001,-1.139232,"check",-312.1592501449893,51602.468664036009,-3.3918889999999999,"check",6170.2627883299901,68758.390923316008,-6.1938839999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.8357610092596417,1.8357610092596417,null,null,-28.421817000000001,null,29175.192900000024,10.08523139374422,5785.7260306584812,66.871520898354106,5908.3681326000024,68.707281907613748,1.8357610092596417,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,0,1691.7597339972672,1691.7597339972672,2556.1488260000001,"2013-01-01T15:00:00",40,37,"OFF",-31.90988633000002,-70.275796361938006,-8.8484060000000007,"OFF",-6.0631112126200257,-107.79784333482002,-8.8484060000000007,"OFF",-8.8976728480500089E-2,-46.618603145626004,-1.7696810000000001,"OFF",3.1484596845799961,-160.86897482926003,-1.7696810000000001,"ON",37411.943742810006,77151.175058398003,2577.3850000000002,null,0,0,0,0,1674.6468589639142,1674.6468589639142,0,0,0,0,1720.3627493763524,1720.3627493763524,0,0,0,0,902.73814103608606,0,0,0,0,857.02225062364778,904.48381908186275,858.76792866942446,null,null,2556.1488260000001,null,28829.600000000006,10.012604380737301,5758.6615637113737,66.471594246869415,5875.8824000000004,68.217272292646101,1.7456780457766854,null,null,null,null,null,null,null,null,null,1674.6468589639142,0,0,0,0,17.112875033353021]
[0,0,0,0,1657.9543312649598,1657.9543312649598,2391.0313290000004,"2013-01-01T16:00:00",39,36,"OFF",-31.621142701259977,-73.754793005267999,-8.8484060000000007,"OFF",-7.1546965283599819,-104.36997950824001,-8.8484060000000007,"OFF",-0.33973973625000287,-75.14639166260001,-3.2812839999999999,"OFF",1.7328833729200019,-164.76541577812,-2.359575,"ON",35959.259692875014,75872.156827090002,2414.3690000000001,null,0,0,0,0,1642.1148019093187,1642.1148019093187,0,0,0,0,1687.5585016433254,1687.5585016433254,0,0,0,0,772.25419809068148,0,0,0,0,726.81049835667477,773.73943511100458,728.29573537699787,null,null,2391.0313290000004,null,28624.403100000054,9.9447630098415623,5756.678780916689,66.442368750920267,5856.5938914000053,67.927605771243336,1.4852370203230691,null,null,null,null,null,null,null,null,null,1642.1148019093187,0,0,0,0,15.839529355641162]
[0,0,0,0,0,0,2542.0287239999998,"2013-01-01T17:00:00",38,35,"OFF",-31.766067866259995,-72.363194347936002,-8.8484060000000007,"OFF",-6.9372657515199823,-106.32505779574001,-8.8484060000000007,"OFF",0.12215874487500612,-33.398399859304,-1.7696810000000001,"OFF",1.1157656703199985,-166.99199929652002,-3.9817830000000001,"check",16388.361824279993,41285.221764832,2565.4769999999999,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,1.0403322478179717,1.0403322478179717,null,null,2542.0287239999998,null,28563.352800000052,9.8818351267883742,5780.9814540557363,66.801275612334564,5850.8551632000053,67.841607860152536,1.0403322478179717,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,1941.9438078874941,0,1941.9438078874941,2304.1986219999999,"2013-01-01T18:00:00",38,35,"OFF",-31.613026892020024,-70.351561159902005,-8.8484060000000007,"OFF",-6.5525392747499547,-104.36997950824001,-8.8484060000000007,"OFF",-0.45056211212500547,-61.926196397112001,-3.9817830000000001,"ON",34049.082165655003,72706.646459816009,2329.8589999999999,"OFF",-0.23854245177000358,-120.37338813006001,-3.9817830000000001,null,0,0,0,1927.1421342494548,0,1927.1421342494548,0,0,0,1977.2980529429719,0,1977.2980529429719,0,0,0,402.71686575054514,0,0,0,0,352.56094705702799,0,403.7571979983631,353.60127930484595,null,null,2304.1986219999999,null,28563.352800000052,9.8818351267883742,5780.9814540557363,66.801275612334564,5850.8551632000053,67.841607860152536,1.0403322478179717,null,null,null,null,null,null,null,null,null,1927.1421342494548,0,0,0,14.801673638039347,0]
[0,0,0,1848.7926413750097,0,1848.7926413750097,1974.9266460000001,"2013-01-01T19:00:00",37,34,"OFF",-31.704408796060008,-73.679028207304,-8.8484060000000007,"OFF",-5.6967872836799787,-106.64075782198,-8.8484060000000007,"OFF",5.0990233896000159E-2,-75.14639166260001,-1.7696810000000001,"ON",30813.442032540006,73423.596727740005,1998.633,"OFF",-0.74721226082999148,-114.80700954240001,-4.2398610000000003,null,0,0,0,1836.6002900384651,0,1836.6002900384651,0,0,0,1876.4194353425239,0,1876.4194353425239,0,0,0,162.03270996153492,0,0,0,0,122.21356465747613,0,162.42619403642277,122.60704873236396,null,null,1974.9266460000001,null,28650.199700000056,9.8239485773091175,5832.7259094525198,67.570485164542362,5859.0187718000052,67.963969239430199,0.39348407488783721,null,null,null,null,null,null,null,null,null,1836.6002900384651,0,0,0,12.192351336544561,0]
[0,0,0,1921.7155212621735,0,1921.7155212621735,2067.4666459999999,"2013-01-01T20:00:00",37,34,"OFF",-31.529839847310019,-71.667395019270003,-8.8484060000000007,"OFF",-7.5433532324200545,-107.79784333482002,-8.8484060000000007,"OFF",-0.58885878724999974,-33.398399859304,-1.7696810000000001,"ON",33363.280101759992,74222.37554413201,2091.1729999999998,"OFF",-0.12468396171000048,-116.89443159090001,-4.2398610000000003,null,0,0,0,1907.4891641386228,0,1907.4891641386228,0,0,0,1952.0721981715265,0,1952.0721981715265,0,0,0,183.68383586137702,0,0,0,0,139.10080182847332,0,184.07731993626487,139.49428590336117,null,null,2067.4666459999999,null,28650.199700000056,9.8239485773091175,5832.7259094525198,67.570485164542362,5859.0187718000052,67.963969239430199,0.39348407488783721,null,null,null,null,null,null,null,null,null,1907.4891641386228,0,0,0,14.22635712355077,0]
[0,0,0,1862.5156970485004,0,1862.5156970485004,1908.0847240000001,"2013-01-01T21:00:00",36,33,"OFF",-31.980254409359997,-72.363194347936002,-8.8484060000000007,"OFF",-7.112726851450037,-107.1531286979,-8.8484060000000007,"OFF",-1.9417779659986496E-3,-33.398399859304,-1.7696810000000001,"ON",31303.037819880006,73947.116562919997,1931.5329999999999,"OFF",-1.4063348994099845,-116.89443159090001,-3.9817830000000001,null,0,0,0,1849.9455799801951,0,1849.9455799801951,0,0,0,1889.9025642542172,0,1889.9025642542172,0,0,0,81.587420019804767,0,0,0,0,41.630435745782734,0,81.110768476044257,41.153784202022223,null,null,1908.0847240000001,null,28888.694400000008,9.7712312071351608,5913.0100982371323,68.777521179973519,5881.4372736000005,68.300869636213008,-0.47665154376051078,null,null,null,null,null,null,null,null,null,1849.9455799801951,0,0,0,12.570117068305308,0]
[0,0,0,1845.1759432376946,0,1845.1759432376946,2097.8977239999999,"2013-01-01T22:00:00",36,33,"OFF",-31.81810917551002,-73.058993676602014,-8.8484060000000007,"OFF",-6.6207218542349642,-109.93635809590002,-8.8484060000000007,"OFF",0.11886791875000172,-33.398399859304,-1.7696810000000001,"ON",30683.618075689988,73420.813498342017,2121.346,"OFF",-2.2651941261950252,-120.37338813006001,-3.9817830000000001,null,0,0,0,1833.0827475985341,0,1833.0827475985341,0,0,0,1872.5832794550038,0,1872.5832794550038,0,0,0,288.26325240146593,0,0,0,0,248.76272054499623,0,287.78660085770542,248.28606900123572,null,null,2097.8977239999999,null,28888.694400000008,9.7712312071351608,5913.0100982371323,68.777521179973519,5881.4372736000005,68.300869636213008,-0.47665154376051078,null,null,null,null,null,null,null,null,null,1833.0827475985341,0,0,0,12.093195639160513,0]
[0,0,0,1817.3549575900274,0,1817.3549575900274,1903.1966460000001,"2013-01-01T23:00:00",36,33,"OFF",-32.028389567459989,-73.655831955376001,-8.8484060000000007,"OFF",-4.9574419700199632,-108.5447433969,-8.8484060000000007,"OFF",0.36802210312500144,-33.398399859304,-1.7696810000000001,"ON",29673.579146925014,73746.724046264018,1926.903,"OFF",-4.079462246020003,-118.28596608156001,-4.2398610000000003,null,0,0,0,1806.0187100078008,0,1806.0187100078008,0,0,0,1842.4258814348818,0,1842.4258814348818,0,0,0,120.88428999219923,0,0,0,0,84.47711856511819,0,120.40763844843872,84.000467021357679,null,null,1903.1966460000001,null,28888.694400000008,9.7712312071351608,5913.0100982371323,68.777521179973519,5881.4372736000005,68.300869636213008,-0.47665154376051078,null,null,null,null,null,null,null,null,null,1806.0187100078008,0,0,0,11.336247582226633,0]
[0,0,0,1757.5220174580004,0,1757.5220174580004,2071.0586230000004,"2013-01-02",36,33,"OFF",-32.278426449479987,-73.157954726494012,-8.8484060000000007,"OFF",-5.830581086055024,-109.2405507464,-8.8484060000000007,"OFF",-0.63734284475000325,-75.14639166260001,-1.7696810000000001,"ON",27428.468865344981,73947.942708822011,2096.7190000000001,"OFF",-3.2368771270999925,-118.98177343106001,-6.1938839999999997,null,0,0,0,1747.7768417915297,0,1747.7768417915297,0,0,0,1778.7430385548337,0,1778.7430385548337,0,0,0,348.94215820847035,0,0,0,0,317.97596144516638,0,348.46550666470984,317.49930990140587,null,null,2071.0586230000004,null,28888.694400000008,9.7712312071351608,5913.0100982371323,68.777521179973519,5881.4372736000005,68.300869636213008,-0.47665154376051078,null,null,null,null,null,null,null,null,null,1747.7768417915297,0,0,0,9.7451756664706863,0]
[0,0,0,1695.0270896893628,0,1695.0270896893628,2161.2380430000003,"2013-01-02T01:00:00",35,32,"OFF",-32.47963672913999,-74.450592333934011,-8.8484060000000007,"OFF",-6.2599981907699913,-113.41531463506001,-8.8484060000000007,"OFF",-0.15048795625000291,-33.398399859304,-3.2812839999999999,"ON",24964.463398709999,73324.515365337997,2186.4560000000001,"OFF",-4.0318726235900098,-120.37338813006001,-4.2398610000000003,null,0,0,0,1686.884239744192,0,1686.884239744192,0,0,0,1713.6005350232326,0,1713.6005350232326,0,0,0,499.57176025580816,0,0,0,0,472.85546497676751,0,497.97602936313547,471.25973408409482,null,null,2161.2380430000003,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1686.884239744192,0,0,0,8.1428499451708376,0]
[0,0,0,1727.4917843076992,0,1727.4917843076992,2199.109203,"2013-01-02T02:00:00",35,32,"OFF",-32.271802995049995,-73.754793005267999,-8.8484060000000007,"OFF",-7.261688716399993,-107.1531286979,-8.8484060000000007,"OFF",-0.10886661799999757,-75.14639166260001,-2.47018,"ON",26260.723833599997,72662.940935350009,2225.212,"OFF",-2.8420471571800032,-118.98177343106001,-5.9358050000000002,null,0,0,0,1718.524649357596,0,1718.524649357596,0,0,0,1748.9561285714715,0,1748.9561285714715,0,0,0,506.687350642404,0,0,0,0,476.25587142852851,0,505.09161974973131,474.66014053585582,null,null,2199.109203,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1718.524649357596,0,0,0,8.9671349501031727,0]
[0,0,0,1673.5944267055606,0,1673.5944267055606,2218.1177239999997,"2013-01-02T03:00:00",33,31,"OFF",-32.146931199879994,-70.971595690604005,-8.8484060000000007,"OFF",-6.2146512271099761,-107.8489360474,-8.8484060000000007,"OFF",2.6642809375002397E-2,-33.398399859304,-1.7696810000000001,"ON",24088.030530979984,73153.062017753997,2241.5659999999998,"OFF",-3.2617377882949783,-118.98177343106001,-3.9817830000000001,null,0,0,0,1665.985544434546,0,1665.985544434546,0,0,0,1691.1680330928521,0,1691.1680330928521,0,0,0,575.5804555654538,0,0,0,0,550.39796690714775,0,571.51535657366219,546.33286791535613,null,null,2218.1177239999997,null,30551.57130000004,9.7062195070385382,6295.2566192935019,74.750727555531071,6037.7477022000039,70.685628563739428,-4.0650989917916434,null,null,null,null,null,null,null,null,null,1665.985544434546,0,0,0,7.608882271014636,0]
[0,0,0,1708.8691704294715,0,1708.8691704294715,1940.565646,"2013-01-02T04:00:00",32,30,"OFF",-32.79387713644001,-70.275796361938006,-8.8484060000000007,"OFF",-6.8775231783749735,-109.93635809590002,-8.8484060000000007,"OFF",-0.29397265974999637,-46.618603145626004,-1.7696810000000001,"ON",25521.628238120011,73101.022846762004,1964.2719999999999,"OFF",-4.4587003000049883,-119.67758078056001,-4.2398610000000003,null,0,0,0,1700.3770840716659,0,1700.3770840716659,0,0,0,1728.5608433866453,0,1728.5608433866453,0,0,0,263.89491592833406,0,0,0,0,235.71115661335466,0,257.80577383278012,229.62201451780072,null,null,1940.565646,null,31434.163200000039,9.675457311399553,6497.7111031154127,78.065919461823114,6120.7113408000041,71.976777366269161,-6.089142095553953,null,null,null,null,null,null,null,null,null,1700.3770840716659,0,0,0,8.4920863578056469,0]
[0,0,0,1738.7110370617399,0,1738.7110370617399,2063.175702,"2013-01-02T05:00:00",32,30,"OFF",-32.510307867849995,-70.971595690604005,-8.8484060000000007,"OFF",-6.1963036086399867,-109.2405507464,-8.8484060000000007,"OFF",-0.2072869124999995,-61.926196397112001,-1.7696810000000001,"ON",26700.38929970999,72808.51105161602,2088.578,"OFF",-4.8579197897300181,-118.98177343106001,-5.9358050000000002,null,0,0,0,1729.4549217326305,0,1729.4549217326305,0,0,0,1760.6378310285268,0,1760.6378310285268,0,0,0,359.12307826736946,0,0,0,0,327.94016897147321,0,353.03393617181553,321.85102687591927,null,null,2063.175702,null,31434.163200000039,9.675457311399553,6497.7111031154127,78.065919461823114,6120.7113408000041,71.976777366269161,-6.089142095553953,null,null,null,null,null,null,null,null,null,1729.4549217326305,0,0,0,9.2561153291094342,0]
[0,0,0,1717.4705384328699,0,1717.4705384328699,1959.3691240000001,"2013-01-02T06:00:00",31,29,"OFF",-32.730564611699982,-73.058993676602014,-8.8484060000000007,"OFF",-5.8268107710500123,-108.59591631782001,-8.8484060000000007,"OFF",-7.339362037499661E-2,-75.14639166260001,-2.47018,"ON",25864.468129350011,72999.150234127999,1985.73,"OFF",-3.7095846808299977,-120.10196310750001,-6.1938839999999997,null,0,0,0,1708.7597664183015,0,1708.7597664183015,0,0,0,1737.8206137964946,0,1737.8206137964946,0,0,0,276.97023358169849,0,0,0,0,247.90938620350539,0,268.46439771826869,239.40355034007558,null,null,1959.3691240000001,null,32487.155900000012,9.650503523722751,6732.738000694053,82.046094062066885,6219.6926546000013,73.540258198637076,-8.5058358634298088,null,null,null,null,null,null,null,null,null,1708.7597664183015,0,0,0,8.7107720145684198,0]
[0,0,0,1692.8729870374327,0,1692.8729870374327,2074.8041469999998,"2013-01-02T07:00:00",32,30,"OFF",-33.565142514540021,-70.275796361938006,-8.8484060000000007,"OFF",-6.7300949587500085,-104.31880658732,-8.8484060000000007,"OFF",-0.4482667316250008,-75.14639166260001,-2.47018,"ON",24877.141844085018,73605.340805346015,2099.2109999999998,"OFF",-4.6074560034649998,-119.25327866196001,-4.2398610000000003,null,0,0,0,1684.7841809225156,0,1684.7841809225156,0,0,0,1710.9422859914159,0,1710.9422859914159,0,0,0,414.4268190774842,0,0,0,0,388.26871400858386,0,408.33767698193026,382.17957191302992,null,null,2074.8041469999998,null,31434.163200000039,9.675457311399553,6497.7111031154127,78.065919461823114,6120.7113408000041,71.976777366269161,-6.089142095553953,null,null,null,null,null,null,null,null,null,1684.7841809225156,0,0,0,8.0888061149171335,0]
[0,0,0,1728.7870740529431,0,1728.7870740529431,1909.1166230000001,"2013-01-02T08:00:00",32,30,"OFF",-33.557553705899991,-71.667395019270003,-8.8484060000000007,"OFF",-7.003022262080016,-105.76159420724001,-8.8484060000000007,"OFF",-0.10987377475000104,-61.926196397112001,-1.7696810000000001,"ON",26311.695989879983,73157.794309814009,1934.777,"OFF",-3.5317358333600155,-121.76500282906001,-6.1938839999999997,null,0,0,0,1719.7866810036144,0,1719.7866810036144,0,0,0,1749.5729956112827,0,1749.5729956112827,0,0,0,214.99031899638567,0,0,0,0,185.20400438871729,0,208.90117690083173,179.11486229316336,null,null,1909.1166230000001,null,31434.163200000039,9.675457311399553,6497.7111031154127,78.065919461823114,6120.7113408000041,71.976777366269161,-6.089142095553953,null,null,null,null,null,null,null,null,null,1719.7866810036144,0,0,0,9.0003930493287498,0]
[0,0,0,1790.0905946450923,0,1790.0905946450923,2047.3517019999999,"2013-01-02T09:00:00",33,31,"OFF",-34.286353986510001,-71.743159817234016,-8.8484060000000007,"OFF",-7.4212872894699471,-109.2405507464,-8.8484060000000007,"OFF",-0.58564993900000484,-46.618603145626004,-1.7696810000000001,"ON",28663.374658645007,73372.664431840007,2072.7539999999999,"OFF",-3.4535318812749982,-118.98177343106001,-5.9358050000000002,null,0,0,0,1779.4858241743314,0,1779.4858241743314,0,0,0,1814.2045383981688,0,1814.2045383981688,0,0,0,293.26817582566855,0,0,0,0,258.54946160183113,0,289.20307683387693,254.48436261003948,null,null,2047.3517019999999,null,30551.57130000004,9.7062195070385382,6295.2566192935019,74.750727555531071,6037.7477022000039,70.685628563739428,-4.0650989917916434,null,null,null,null,null,null,null,null,null,1779.4858241743314,0,0,0,10.604770470760968,0]
[0,0,0,1781.1687979412886,0,1781.1687979412886,1977.1107019999999,"2013-01-02T10:00:00",34,31,"OFF",-33.679923245220017,-69.50423223530801,-8.8484060000000007,"OFF",-6.3101912944199618,-105.68042336716,-8.8484060000000007,"OFF",-0.12099934349999593,-33.398399859304,-1.7696810000000001,"ON",28328.217769919982,72487.878212466007,2002.5129999999999,"OFF",-5.5764763903099928,-120.37338813006001,-5.9358050000000002,null,0,0,0,1770.8010774272298,0,1770.8010774272298,0,0,0,1806.3041299151985,0,1806.3041299151985,0,0,0,231.71192257277016,0,0,0,0,196.20887008480145,0,228.71781585280431,193.21476336483559,null,null,1977.1107019999999,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1770.8010774272298,0,0,0,10.367720514058874,0]
[0,0,0,1820.5639375871681,0,1820.5639375871681,1965.835147,"2013-01-02T11:00:00",36,33,"OFF",-34.256392549929998,-72.363194347936002,-8.8484060000000007,"OFF",-5.9340994942599812,-109.32172158648001,-8.8484060000000007,"OFF",-0.30618736312499578,-61.926196397112001,-2.47018,"ON",29791.129282779995,73278.860778210015,1990.242,"OFF",-4.0283490387000072,-121.06919547956002,-4.2398610000000003,null,0,0,0,1809.1409132029166,0,1809.1409132029166,0,0,0,1846.7225057984588,0,1846.7225057984588,0,0,0,181.10108679708333,0,0,0,0,143.51949420154119,0,180.62443525332282,143.04284265778068,null,null,1965.835147,null,28888.694400000008,9.7712312071351608,5913.0100982371323,68.777521179973519,5881.4372736000005,68.300869636213008,-0.47665154376051078,null,null,null,null,null,null,null,null,null,1809.1409132029166,0,0,0,11.423024384251448,0]
[0,0,0,1669.9386815832061,0,1669.9386815832061,2007.629623,"2013-01-02T12:00:00",37,33,"OFF",-33.985602327420004,-72.363194347936002,-8.8484060000000007,"OFF",-6.6640309281000274,-109.2405507464,-8.8484060000000007,"OFF",-0.51627311680000199,-33.398399859304,-1.7696810000000001,"ON",23936.814860740003,73153.070038588005,2033.29,"OFF",-3.6955277584950048,-119.67758078056001,-6.1938839999999997,null,0,0,0,1662.42002925216,0,1662.42002925216,0,0,0,1687.3035603888445,0,1687.3035603888445,0,0,0,370.86997074783994,0,0,0,0,345.98643961115545,0,370.7189712102944,345.8354400736099,null,null,2007.629623,null,28650.199700000056,9.7631017000294555,5869.0773855021125,68.114968776975758,5859.0187718000052,67.963969239430199,-0.15099953754555884,null,null,null,null,null,null,null,null,null,1662.42002925216,0,0,0,7.5186523310460416,0]
[0,0,0,1722.7822037224055,0,1722.7822037224055,1957.120623,"2013-01-02T13:00:00",37,33,"OFF",-33.500584941039989,-70.971595690604005,-8.8484060000000007,"OFF",-5.5229544214249975,-109.2405507464,-8.8484060000000007,"OFF",0.62188415975000599,-46.618603145626004,-1.7696810000000001,"ON",26074.920901299993,76276.094048163999,1982.7809999999999,"OFF",-4.4187452633800088,-119.67758078056001,-6.1938839999999997,null,0,0,0,1713.9357582520306,0,1713.9357582520306,0,0,0,1738.7412893598894,0,1738.7412893598894,0,0,0,268.84524174796934,0,0,0,0,244.03971064011057,0,268.69424221042379,243.88871110256503,null,null,1957.120623,null,28650.199700000056,9.7631017000294555,5869.0773855021125,68.114968776975758,5859.0187718000052,67.963969239430199,-0.15099953754555884,null,null,null,null,null,null,null,null,null,1713.9357582520306,0,0,0,8.8464454703748743,0]
[0,0,0,1810.8707218691711,0,1810.8707218691711,2109.8656460000002,"2013-01-02T14:00:00",39,34,"OFF",-33.848696567885007,-71.667395019270003,-8.8484060000000007,"OFF",-6.702436501064966,-109.2405507464,-8.8484060000000007,"OFF",-1.3206986996249996,-75.14639166260001,-1.7696810000000001,"ON",29435.196523460014,76258.279775850009,2133.5720000000001,"OFF",-3.0700188542799998,-119.67758078056001,-4.2398610000000003,null,0,0,0,1799.7093870652357,0,1799.7093870652357,0,0,0,1831.0438584140111,0,1831.0438584140111,0,0,0,333.86261293476446,0,0,0,0,302.52814158598903,0,334.29033409605097,302.95586274727555,null,null,2109.8656460000002,null,28624.403100000054,9.8230692552822418,5827.9957834172064,67.499884609956794,5856.5938914000053,67.927605771243336,0.42772116128654147,null,null,null,null,null,null,null,null,null,1799.7093870652357,0,0,0,11.161334803935461,0]
[0,0,0,1784.0178865759094,0,1784.0178865759094,1980.0157019999999,"2013-01-02T15:00:00",40,35,"OFF",-32.950290914520004,-72.363194347936002,-8.8484060000000007,"OFF",-6.2852882832250376,-103.02945752182002,-8.8484060000000007,"OFF",-0.82808193762500104,-46.618603145626004,-1.7696810000000001,"ON",28435.498598399994,75652.658683846006,2005.4179999999999,"OFF",-3.657056587519977,-118.98177343106001,-5.9358050000000002,null,0,0,0,1773.5745932097036,0,1773.5745932097036,0,0,0,1803.8827244539921,0,1803.8827244539921,0,0,0,231.84340679029629,0,0,0,0,201.53527554600782,0,232.53814320284008,202.23001195855161,null,null,1980.0157019999999,null,28829.600000000006,9.8909106261779804,5829.5138010240553,67.522535880102311,5875.8824000000004,68.217272292646101,0.69473641254379004,null,null,null,null,null,null,null,null,null,1773.5745932097036,0,0,0,10.443293366205808,0]
[0,0,0,1778.0061330060614,0,1778.0061330060614,1992.3656230000001,"2013-01-02T16:00:00",40,35,"OFF",-33.348064125689973,-73.754793005267999,-8.8484060000000007,"OFF",-6.7342702304750057,-105.71042128632001,-8.8484060000000007,"OFF",-0.18481190398999939,-75.14639166260001,-1.7696810000000001,"ON",28208.850252219981,75344.000949858004,2018.0260000000001,"OFF",-6.3463160095299882,-117.59015873206,-6.1938839999999997,null,0,0,0,1767.7221626303804,0,1767.7221626303804,0,0,0,1798.0711250420072,0,1798.0711250420072,0,0,0,250.30383736961971,0,0,0,0,219.95487495799284,0,250.9985737821635,220.64961137053663,null,null,1992.3656230000001,null,28829.600000000006,9.8909106261779804,5829.5138010240553,67.522535880102311,5875.8824000000004,68.217272292646101,0.69473641254379004,null,null,null,null,null,null,null,null,null,1767.7221626303804,0,0,0,10.283970375681065,0]
[0,0,0,1788.6186335728416,0,1788.6186335728416,2042.3957019999998,"2013-01-02T17:00:00",40,35,"OFF",-32.315631469470006,-70.275796361938006,-8.8484060000000007,"OFF",-6.4593090790799987,-102.84610125658,-8.8484060000000007,"OFF",6.7150121125499465E-2,-46.618603145626004,-1.7696810000000001,"ON",28608.237874670005,71345.655305028005,2067.7979999999998,"OFF",-5.2225046937700004,-119.67758078056001,-5.9358050000000002,null,0,0,0,1778.0530528262418,0,1778.0530528262418,0,0,0,1816.3479569817118,0,1816.3479569817118,0,0,0,289.74494717375796,0,0,0,0,251.45004301828794,0,290.43968358630173,252.14477943083173,null,null,2042.3957019999998,null,28829.600000000006,9.8909106261779804,5829.5138010240553,67.522535880102311,5875.8824000000004,68.217272292646101,0.69473641254379004,null,null,null,null,null,null,null,null,null,1778.0530528262418,0,0,0,10.565580746599835,0]
[0,0,0,1810.6434601475196,0,1810.6434601475196,1985.0516230000001,"2013-01-02T18:00:00",38,33,"OFF",-31.275641107899993,-70.971595690604005,-8.8484060000000007,"OFF",-6.8494633142399932,-109.37289450740002,-8.8484060000000007,"OFF",-0.25874559575000688,-33.398399859304,-1.7696810000000001,"ON",29426.82072284001,70411.89387325001,2010.712,"OFF",-5.8328118971500125,-118.98177343106001,-6.1938839999999997,null,0,0,0,1799.4882451710071,0,1799.4882451710071,0,0,0,1841.8024761441652,0,1841.8024761441652,0,0,0,211.22375482899292,0,0,0,0,168.90952385583478,0,211.1907048924576,168.87647391929946,null,null,1985.0516230000001,null,28563.352800000052,9.7601413722290538,5853.0612848032251,67.874657796687856,5850.8551632000053,67.841607860152536,-3.3049936535320512E-2,null,null,null,null,null,null,null,null,null,1799.4882451710071,0,0,0,11.155214976512525,0]
[0,0,0,1802.5354040848597,0,1802.5354040848597,2065.0224920000001,"2013-01-02T19:00:00",38,33,"OFF",-30.973116413469995,-70.351561159902005,-8.8484060000000007,"OFF",-6.7014598643999816,-108.59591631782001,-8.8484060000000007,"OFF",-0.38174754162500607,-61.926196397112001,-2.6508349999999998,"ON",29127.060584160005,71394.638538266008,2089.61,"OFF",-5.4671603530599837,-119.67758078056001,-4.2398610000000003,null,0,0,0,1791.5980541540641,0,1791.5980541540641,0,0,0,1831.1471560326297,0,1831.1471560326297,0,0,0,298.011945845936,0,0,0,0,258.46284396737042,0,297.97889590940065,258.42979403083507,null,null,2065.0224920000001,null,28563.352800000052,9.7601413722290538,5853.0612848032251,67.874657796687856,5850.8551632000053,67.841607860152536,-3.3049936535320512E-2,null,null,null,null,null,null,null,null,null,1791.5980541540641,0,0,0,10.937349930795563,0]
[0,0,0,1858.9317160400376,0,1858.9317160400376,1912.5976230000001,"2013-01-02T20:00:00",34,31,"OFF",-31.227921203569988,-73.679028207304,-8.8484060000000007,"OFF",-7.0646761799500322,-107.1531286979,-8.8484060000000007,"OFF",6.4059853749996315E-2,-46.618603145626004,-1.7696810000000001,"ON",31175.626934054999,68776.766654010004,1938.258,"OFF",-3.4582712277400161,-118.28596608156001,-6.1938839999999997,null,0,0,0,1846.4604903486754,0,1846.4604903486754,0,0,0,1897.5947668172773,0,1897.5947668172773,0,0,0,91.797509651324617,0,0,0,0,40.663233182722706,0,88.803402931358761,37.66912646275685,null,null,1912.5976230000001,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1846.4604903486754,0,0,0,12.471225691362179,0]
[0,0,0,1822.8130605260958,0,1822.8130605260958,2163.826646,"2013-01-02T21:00:00",35,31,"OFF",-30.263621204850025,-68.959962502570008,-8.8484060000000007,"OFF",-6.8828726494000394,-106.27396508316001,-8.8484060000000007,"OFF",-0.14534677237500201,-75.14639166260001,-1.7696810000000001,"ON",29873.352798899999,69273.288361946004,2187.5329999999999,"OFF",-6.5374386501900217,-118.98177343106001,-4.2398610000000003,null,0,0,0,1811.3291317274573,0,1811.3291317274573,0,0,0,1857.3227730288218,0,1857.3227730288218,0,0,0,376.20386827254265,0,0,0,0,330.21022697117814,0,374.02154151882587,328.02790021746137,null,null,2163.826646,null,29282.587499999994,9.6629639847182247,6060.7878796422701,71.042431644183864,5918.4632249999995,68.860104890467056,-2.1823267537168078,null,null,null,null,null,null,null,null,null,1811.3291317274573,0,0,0,11.483928798638544,0]
[0,0,0,1790.0958181839978,0,1790.0958181839978,2000.4546460000001,"2013-01-02T22:00:00",36,32,"OFF",-30.298318495199993,-70.275796361938006,-8.8484060000000007,"OFF",-7.8842447978000241,-107.9812798084,-8.8484060000000007,"OFF",7.0316579444997612E-2,-33.398399859304,-1.7696810000000001,"ON",28663.570211044993,77130.537452516,2024.1610000000001,"OFF",-5.6708065785700121,-120.37338813006001,-4.2398610000000003,null,0,0,0,1779.4909085848979,0,1779.4909085848979,0,0,0,1807.8397030187539,0,1807.8397030187539,0,0,0,244.67009141510221,0,0,0,0,216.32129698124618,0,243.63081667254193,215.2820222386859,null,null,2000.4546460000001,null,28888.694400000008,9.7103843298555006,5950.0619993338405,69.340144378773275,5881.4372736000005,68.300869636213008,-1.0392747425602664,null,null,null,null,null,null,null,null,null,1779.4909085848979,0,0,0,10.604909599099983,0]
[0,0,0,1811.1409405644638,0,1811.1409405644638,1929.8741239999999,"2013-01-02T23:00:00",34,31,"OFF",-31.088972380029997,-70.895830892640006,-8.8484060000000007,"OFF",-7.9594281551999808,-107.1531286979,-8.8484060000000007,"OFF",0.27398176937500013,-61.926196397112001,-2.47018,"ON",29445.153667740011,73920.952602412013,1956.2349999999999,"OFF",-5.0662358265399901,-118.28596608156001,-6.1938839999999997,null,0,0,0,1799.9723282285092,0,1799.9723282285092,0,0,0,1835.5173389789422,0,1835.5173389789422,0,0,0,156.26267177149066,0,0,0,0,120.71766102105767,0,153.2685650515248,117.72355430109181,null,null,1929.8741239999999,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1799.9723282285092,0,0,0,11.168612335954549,0]
[0,0,0,1712.5097895126141,0,1712.5097895126141,2095.1187020000002,"2013-01-03",33,30,"OFF",-29.794374171450002,-72.363194347936002,-8.8484060000000007,"OFF",-8.3757958299600404,-103.59300131866001,-8.8484060000000007,"OFF",-2.0622927769999563E-2,-46.618603145626004,-1.7696810000000001,"ON",25667.050255000002,74508.205984556014,2120.5210000000002,"OFF",-4.4318207350199961,-117.59015873206,-5.9358050000000002,null,0,0,0,1703.9252965599985,0,1703.9252965599985,0,0,0,1730.4099576705737,0,1730.4099576705737,0,0,0,416.59570344000167,0,0,0,0,390.11104232942648,0,411.88857666483568,385.40391555426049,null,null,2095.1187020000002,null,30551.57130000004,9.645372629758878,6334.9696217519358,75.392755338905431,6037.7477022000039,70.685628563739428,-4.7071267751660031,null,null,null,null,null,null,null,null,null,1703.9252965599985,0,0,0,8.5844929526156193,0]
[0,0,0,1706.7109386740133,0,1706.7109386740133,2038.7687019999998,"2013-01-03T01:00:00",33,30,"OFF",-30.191337373400017,-71.667395019270003,-8.8484060000000007,"OFF",-8.1024101908199633,-105.06578685774001,-8.8484060000000007,"OFF",0.53714245925000215,-61.926196397112001,-1.7696810000000001,"ON",25435.201395769996,69484.252337814003,2064.1709999999998,"OFF",-6.5199480842300197,-121.76500282906001,-5.9358050000000002,null,0,0,0,1698.2735249172413,0,1698.2735249172413,0,0,0,1731.7140542628385,0,1731.7140542628385,0,0,0,365.89747508275855,0,0,0,0,332.45694573716128,0,361.19034830759256,327.74981896199529,null,null,2038.7687019999998,null,30551.57130000004,9.645372629758878,6334.9696217519358,75.392755338905431,6037.7477022000039,70.685628563739428,-4.7071267751660031,null,null,null,null,null,null,null,null,null,1698.2735249172413,0,0,0,8.4374137567720027,0]
[0,0,0,1740.7711816774347,0,1740.7711816774347,1889.392646,"2013-01-03T02:00:00",30,28,"OFF",-29.941855289359989,-73.754793005267999,-8.8484060000000007,"OFF",-7.8457458146749834,-109.18945803382,-8.8484060000000007,"OFF",-0.10136232557499544,-46.618603145626004,-1.7696810000000001,"ON",26780.676955690004,74573.335156636007,1913.0989999999999,"OFF",-5.4550612965100047,-120.37338813006001,-4.2398610000000003,null,0,0,0,1731.461779764973,0,1731.461779764973,0,0,0,1760.0866806147931,0,1760.0866806147931,0,0,0,181.63722023502692,0,0,0,0,153.01231938520687,0,170.27193108746621,141.64703023764616,null,null,1889.392646,null,33714.300000000047,9.631485989739506,7000.8511741420052,86.759253967981437,6335.0442000000039,75.393964820420734,-11.365289147560702,null,null,null,null,null,null,null,null,null,1731.461779764973,0,0,0,9.3094019124616807,0]
[0,0,0,1667.0964402954244,0,1667.0964402954244,2093.1047239999998,"2013-01-03T03:00:00",29,27,"OFF",-30.165505760970021,-69.579997033272008,-8.8484060000000007,"OFF",-7.578341037644976,-105.8938577599,-8.8484060000000007,"OFF",6.4246581153999102E-2,-33.398399859304,-1.7696810000000001,"ON",23818.893128999996,74699.414646282006,2116.5529999999999,"OFF",-4.1951462077700121,-121.06919547956002,-3.9817830000000001,null,0,0,0,1659.6477645266918,0,1659.6477645266918,0,0,0,1682.3936307722788,0,1682.3936307722788,0,0,0,456.90523547330804,0,0,0,0,434.15936922772107,0,442.18279114745781,419.43692490187084,null,null,2093.1047239999998,null,35119.346100000024,9.61853255518119,7302.4332762864915,92.280680645908816,6467.118533400002,77.558236320058612,-14.722444325850205,null,null,null,null,null,null,null,null,null,1659.6477645266918,0,0,0,7.448675768732528,0]
[0,0,0,1689.4532542448608,0,1689.4532542448608,2120.0341469999998,"2013-01-03T04:00:00",31,29,"OFF",-30.112708883879996,-73.058993676602014,-8.8484060000000007,"OFF",-6.3815414098799979,-107.8489360474,-8.8484060000000007,"OFF",-0.20928141684600032,-46.618603145626004,-2.47018,"ON",24738.168790540007,74551.903488188007,2144.4409999999998,"OFF",-5.9574865969499955,-121.06919547956002,-4.2398610000000003,null,0,0,0,1681.4500741903225,0,1681.4500741903225,0,0,0,1706.082589705145,0,1706.082589705145,0,0,0,462.99092580967726,0,0,0,0,438.35841029485482,0,454.48508994624746,429.85257443142501,null,null,2120.0341469999998,null,32487.155900000012,9.650503523722751,6732.738000694053,82.046094062066885,6219.6926546000013,73.540258198637076,-8.5058358634298088,null,null,null,null,null,null,null,null,null,1681.4500741903225,0,0,0,8.0031800545382339,0]
[0,0,0,1698.37032623912,0,1698.37032623912,1968.017724,"2013-01-03T05:00:00",30,28,"OFF",-29.988600242579995,-71.667395019270003,-8.8484060000000007,"OFF",-6.8502996635849849,-112.15604369706001,-8.8484060000000007,"OFF",-0.11710383065499945,-75.14639166260001,-1.7696810000000001,"ON",25099.657952319991,72957.682522348012,1991.4659999999999,"OFF",-6.8688074163099886,-118.98177343106001,-3.9817830000000001,null,0,0,0,1690.1434349007091,0,1690.1434349007091,0,0,0,1717.6460949599757,0,1717.6460949599757,0,0,0,301.32256509929084,0,0,0,0,273.8199050400242,0,289.95727595173014,262.45461589246349,null,null,1968.017724,null,33714.300000000047,9.631485989739506,7000.8511741420052,86.759253967981437,6335.0442000000039,75.393964820420734,-11.365289147560702,null,null,null,null,null,null,null,null,null,1690.1434349007091,0,0,0,8.226891338410951,0]
[0,0,0,1788.5704584469177,0,1788.5704584469177,1950.8897019999999,"2013-01-03T06:00:00",29,28,"OFF",-30.419871183590008,-70.971595690604005,-8.8484060000000007,"OFF",-5.9084191622399711,-109.10828719374,-8.8484060000000007,"OFF",-0.52478722237499975,-75.14639166260001,-1.7696810000000001,"ON",28606.432272495014,74243.245754200005,1976.2919999999999,"OFF",-5.5007405415900248,-119.67758078056001,-5.9358050000000002,null,0,0,0,1778.0061597903439,0,1778.0061597903439,0,0,0,1811.0641627774701,0,1811.0641627774701,0,0,0,198.28584020965604,0,0,0,0,165.22783722252984,0,184.41885400084095,151.36085101371475,null,null,1950.8897019999999,null,35119.346100000024,9.679379432460852,7256.5284469009403,91.425222528873689,6467.118533400002,77.558236320058612,-13.866986208815078,null,null,null,null,null,null,null,null,null,1778.0061597903439,0,0,0,10.564298656573783,0]
[0,0,0,1722.0422976333734,0,1722.0422976333734,2109.1426460000002,"2013-01-03T07:00:00",30,28,"OFF",-30.241665930700005,-70.275796361938006,-8.8484060000000007,"OFF",-7.9337490631199783,-109.10828719374,-8.8484060000000007,"OFF",-0.70395572375000282,-33.398399859304,-1.7696810000000001,"ON",26045.6623965,73822.143948366007,2132.8490000000002,"OFF",-5.7735914147450247,-120.37338813006001,-4.2398610000000003,null,0,0,0,1713.2147796601871,0,1713.2147796601871,0,0,0,1741.4459148089911,0,1741.4459148089911,0,0,0,419.63422033981306,0,0,0,0,391.40308519100904,0,408.26893119225235,380.03779604344834,null,null,2109.1426460000002,null,33714.300000000047,9.631485989739506,7000.8511741420052,86.759253967981437,6335.0442000000039,75.393964820420734,-11.365289147560702,null,null,null,null,null,null,null,null,null,1713.2147796601871,0,0,0,8.8275179731863318,0]
[0,0,0,1708.8155023390079,0,1708.8155023390079,2031.8296229999999,"2013-01-03T08:00:00",32,30,"OFF",-30.249393407599996,-72.363194347936002,-8.8484060000000007,"OFF",-7.4368424988000177,-109.37289450740002,-8.8484060000000007,"OFF",-0.60550029587499798,-46.618603145626004,-1.7696810000000001,"ON",25519.481059560003,75125.240723342009,2057.4899999999998,"OFF",-5.5997373127699985,-121.76500282906001,-6.1938839999999997,null,0,0,0,1700.3247764843957,0,1700.3247764843957,0,0,0,1725.6735197525227,0,1725.6735197525227,0,0,0,357.16522351560411,0,0,0,0,331.8164802474771,0,351.07608142005017,325.72733815192316,null,null,2031.8296229999999,null,31434.163200000039,9.675457311399553,6497.7111031154127,78.065919461823114,6120.7113408000041,71.976777366269161,-6.089142095553953,null,null,null,null,null,null,null,null,null,1700.3247764843957,0,0,0,8.4907258546122648,0]
[0,0,0,1728.712855723001,0,1728.712855723001,2063.9276460000001,"2013-01-03T09:00:00",35,32,"OFF",-30.706652930999979,-71.568433969378006,-8.8484060000000007,"OFF",-7.1639822950500172,-107.8489360474,-8.8484060000000007,"OFF",-0.38145476349999635,-33.398399859304,-1.7696810000000001,"ON",26308.776859799993,74779.847569634003,2087.634,"OFF",-6.0693095554350238,-120.37338813006001,-4.2398610000000003,null,0,0,0,1719.714369065679,0,1719.714369065679,0,0,0,1747.0808772829009,0,1747.0808772829009,0,0,0,367.91963093432105,0,0,0,0,340.55312271709909,0,366.32390004164836,338.9573918244264,null,null,2063.9276460000001,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1719.714369065679,0,0,0,8.9984866573220188,0]
[0,0,0,1761.7188992342433,0,1761.7188992342433,2016.9207240000001,"2013-01-03T10:00:00",39,35,"OFF",-30.355826629199999,-72.462155397828013,-8.8484060000000007,"OFF",-7.3511585832300215,-106.32505779574001,-8.8484060000000007,"OFF",0.10075920277500219,-75.14639166260001,-1.7696810000000001,"ON",27589.39617863001,74681.046936422004,2040.3689999999999,"OFF",-6.5702285890149916,-120.37338813006001,-3.9817830000000001,null,0,0,0,1751.8638537451727,0,1751.8638537451727,0,0,0,1781.9959822179819,0,1781.9959822179819,0,0,0,288.5051462548272,0,0,0,0,258.373017782018,0,289.46650795420237,259.33437948139317,null,null,2016.9207240000001,null,28624.403100000054,9.883916132561902,5792.1177630592929,66.966244071868147,5856.5938914000053,67.927605771243336,0.961361699375189,null,null,null,null,null,null,null,null,null,1751.8638537451727,0,0,0,9.8550454890705623,0]
[0,0,0,1823.1620938932604,0,1823.1620938932604,2135.0617240000001,"2013-01-03T11:00:00",43,37,"OFF",-30.406420897559979,-70.275796361938006,-8.8484060000000007,"OFF",-7.4430990427200054,-109.42398721998001,-8.8484060000000007,"OFF",-0.21361092000000145,-46.618603145626004,-1.7696810000000001,"ON",29886.100597260003,74900.368621318019,2158.5100000000002,"OFF",-7.1007365153900066,-118.28596608156001,-3.9817830000000001,null,0,0,0,1811.6687073780479,0,1811.6687073780479,0,0,0,1846.4084734738869,0,1846.4084734738869,0,0,0,346.84129262195233,0,0,0,0,312.10152652611328,0,346.75182837260104,312.01206227676198,null,null,2135.0617240000001,null,30272.564300000085,10.061790331327108,6017.3315688654902,70.370597388371493,6011.521044200008,70.281133139020227,-8.946424935126629E-2,null,null,null,null,null,null,null,null,null,1811.6687073780479,0,0,0,11.493386515212478,0]
[0,0,0,1838.0314513689923,0,1838.0314513689923,1921.3796460000001,"2013-01-03T12:00:00",45,38,"OFF",-30.308209218630005,-72.363194347936002,-8.8484060000000007,"OFF",-7.423841769500017,-113.36422192248001,-8.8484060000000007,"OFF",-1.0483213543750012,-75.14639166260001,-1.7696810000000001,"ON",30426.174923760002,73015.296172970004,1945.086,"OFF",-5.7080377104800046,-118.28596608156001,-4.2398610000000003,null,0,0,0,1826.1336268776804,0,1826.1336268776804,0,0,0,1865.8101955569928,0,1865.8101955569928,0,0,0,118.95237312231961,0,0,0,0,79.275804443007246,0,117.31761590815518,77.641047228842808,null,null,1921.3796460000001,null,31886.51250000007,10.17765144313752,6265.9863482552601,74.280108693147241,6163.2321750000065,72.645351478982803,-1.6347572141644378,null,null,null,null,null,null,null,null,null,1826.1336268776804,0,0,0,11.897824491311894,0]
[0,0,0,1902.581771710132,0,1902.581771710132,2276.4587240000001,"2013-01-03T13:00:00",47,39,"OFF",-29.805889134560005,-70.971595690604005,-8.8484060000000007,"OFF",-6.2747517669000095,-107.02086514524001,-8.8484060000000007,"OFF",-1.0073558391250041,-33.398399859304,-1.7696810000000001,"ON",32706.282990419993,74758.40788035201,2299.9070000000002,"OFF",-6.7200282720200022,-120.10196310750001,-3.9817830000000001,null,0,0,0,1888.8952996271494,0,1888.8952996271494,0,0,0,1930.5868576289377,0,1930.5868576289377,0,0,0,411.01170037285078,0,0,0,0,369.3201423710625,0,407.16036182565233,365.46880382386405,null,null,2276.4587240000001,null,33987.03270000004,10.310098208765135,6592.9600304109508,79.66191611212335,6360.681073800004,75.810577564924898,-3.851338547198452,null,null,null,null,null,null,null,null,null,1888.8952996271494,0,0,0,13.686472082982618,0]
[0,0,0,1863.2753243236034,0,1863.2753243236034,2022.9442250000002,"2013-01-03T14:00:00",48,39,"OFF",-29.317694589149998,-71.047360488568003,-8.8484060000000007,"OFF",-5.2486990333949715,-103.67417215874002,-8.8484060000000007,"OFF",-8.8376625333999648E-2,-46.618603145626004,-2.47018,"ON",31330.001787890011,73736.698003764017,2047.0930000000001,"OFF",-5.6899528049000256,-117.16585661346001,-3.9817830000000001,null,0,0,0,1850.684226256599,0,1850.684226256599,0,0,0,1891.1479909657835,0,1891.1479909657835,0,0,0,196.40877374340107,0,0,0,0,155.94500903421658,0,190.84958245998743,150.38581775080294,null,null,2022.9442250000002,null,35210.380800000043,10.351798158792127,6802.7564409367269,83.259193849223834,6475.6757952000044,77.700002565810195,-5.5591912834136394,null,null,null,null,null,null,null,null,null,1850.684226256599,0,0,0,12.591098067004395,0]
[0,0,0,1886.2707044251217,0,1886.2707044251217,2175.3217239999999,"2013-01-03T15:00:00",48,39,"OFF",-29.222842020749994,-70.895830892640006,-8.8484060000000007,"OFF",-7.0196590134400356,-109.37289450740002,-8.8484060000000007,"OFF",-0.62290302762500493,-75.14639166260001,-1.7696810000000001,"ON",32139.609491849995,51819.560557080003,2198.77,"OFF",-5.9060733362500093,-118.98177343106001,-3.9817830000000001,null,0,0,0,1873.0410659785737,0,1873.0410659785737,0,0,0,1984.7100393471965,0,1984.7100393471965,0,0,0,325.72893402142631,0,0,0,0,214.05996065280351,0,320.1697427380127,208.50076936938987,null,null,2175.3217239999999,null,35210.380800000043,10.351798158792127,6802.7564409367269,83.259193849223834,6475.6757952000044,77.700002565810195,-5.5591912834136394,null,null,null,null,null,null,null,null,null,1873.0410659785737,0,0,0,13.229638446548051,0]
[0,0,0,0,0,0,2192.7237239999999,"2013-01-03T16:00:00",49,39,"OFF",-28.916549272029982,-73.754793005267999,-8.8484060000000007,"OFF",-6.3075708090000262,-109.93635809590002,-8.8484060000000007,"OFF",-0.62296158324999851,-46.618603145626004,-1.7696810000000001,"check",37428.484527054999,48003.520448236006,2216.172,"OFF",-6.0370471429800077,-119.67758078056001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-7.4764588737199347,-7.4764588737199347,null,null,2192.7237239999999,null,36544.120100000058,10.39726098507929,7029.5667584843977,87.274955279345733,6601.047289400005,79.798496405625798,-7.4764588737199347,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,1854.8150778758556,0,{"$f":"SUM(A68:E68)","v":1854.8150778758556},{"$f":"N68+R68+V68+Z68+AD68","v":2060.3586460000001},"2013-01-03T17:00:00",47,39,"OFF",-28.483512879009997,-72.363194347936002,-8.8484060000000007,"OFF",-6.6320884634549602,-105.76159420724001,-8.8484060000000007,"OFF",0.23301625412500324,-46.618603145626004,-1.7696810000000001,"ON",31028.885255999983,51302.722076622005,2084.0650000000001,"OFF",-7.7049763808500131,-121.06919547956002,-4.2398610000000003,null,0,0,0,1842.4572391183733,0,{"$f":"SUM(AF68:AJ68)","v":1842.4572391183733},0,0,0,1948.9369261086042,0,{"$f":"SUM(AL68:AP68)","v":1948.9369261086042},{"$f":"IF($K68=\"ON\",$N68-AF68,0)","v":0},{"$f":"IF($O68=\"ON\",$R68-AG68,0)","v":0},{"$f":"IF($S68=\"ON\",$V68-AH68,0)","v":0},{"$f":"IF($W68=\"ON\",$Z68-AI68,0)","v":241.60776088162675},{"$f":"IF($AA68=\"ON\",$AD68-AJ68,0)","v":0},{"$f":"IF($K68=\"ON\",$N68-AL68,0)","v":0},{"$f":"IF($O68=\"ON\",$R68-AM68,0)","v":0},{"$f":"IF($S68=\"ON\",$V68-AN68,0)","v":0},{"$f":"IF($W68=\"ON\",$Z68-AO68,0)","v":135.12807389139584},{"$f":"IF($AA68=\"ON\",$AD68-AP68,0)","v":0},{"$f":"SUM(AR68:AV68)+BN68","v":237.75642233442829},{"$f":"SUM(AW68:BA68)+BN68","v":131.27673534419739},null,null,{"$f":"N68+R68+V68+Z68+AD68","v":2060.3586460000001},null,33987.03270000004,{"$f":"19.5285952781395+42*-0.3035722016559+BH68*0.0000340867411548605+J68*0.0608468772796604","v":10.310098208765135},{"$f":"BH68*1000/(500*BI68)","v":6592.9600304109508},{"$f":"0.00000128*BJ68^2+0*BJ68+24.024","v":79.66191611212335},{"$f":"0.094*BH68 + 3165.9","v":6360.681073800004},{"$f":"0.00000128*BL68^2+0*BL68+24.024","v":75.810577564924898},{"$f":"BM68-BK68","v":-3.851338547198452},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF68:AJ68)","v":1842.4572391183733},{"$f":"A68-AF68","v":0},{"$f":"B68-AG68","v":0},{"$f":"C68-AH68","v":0},{"$f":"D68-AI68","v":12.357838757482341},{"$f":"E68-AJ68","v":0}]
[0,0,0,1859.8010788901952,0,1859.8010788901952,2303.712724,"2013-01-03T18:00:00",44,37,"OFF",-27.798912749580008,-71.667395019270003,-8.8484060000000007,"OFF",-6.8838188806600131,-105.76159420724001,-8.8484060000000007,"OFF",-0.67219515274999853,-61.926196397112001,-1.7696810000000001,"ON",31206.562162539991,50623.622124344001,2327.1610000000001,"OFF",-6.4749480844300038,-119.67758078056001,-3.9817830000000001,null,0,0,0,1847.3058801934696,0,1847.3058801934696,0,0,0,1957.9703688343275,0,1957.9703688343275,0,0,0,479.85511980653041,0,0,0,0,369.19063116567258,0,478.78607105056119,368.12158240970336,null,null,2303.712724,null,{"$f":" -0.6251*I69^3 + 145.21*I69^2 - 8340.3*I69 + 170112","v":31016.841600000043},10.087160318999643,6149.7667567706549,72.433127888232264,6081.4831104000041,71.364079132263043,-1.0690487559692201,null,null,null,null,null,null,null,null,null,1847.3058801934696,0,0,0,12.495198696725538,0]
[0,0,0,1967.6991418334214,0,1967.6991418334214,1950.0557240000001,"2013-01-03T19:00:00",42,36,"OFF",-27.515939777410004,-73.058993676602014,-8.8484060000000007,"OFF",-6.5870351222899748,-109.85518725582001,-8.8484060000000007,"OFF",-3.411413337500218E-2,-61.926196397112001,-1.7696810000000001,"ON",34909.718175810012,72540.759571028,1973.5039999999999,"OFF",-6.0541131806399946,-119.67758078056001,-3.9817830000000001,null,0,0,0,1952.1584250096714,0,1952.1584250096714,0,0,0,2005.2658582518204,0,2005.2658582518204,0,0,0,21.345574990328487,0,0,0,0,-31.761858251820513,0,21.502593665793768,-31.604839576355232,null,null,1950.0557240000001,null,29657.431200000021,9.9799755712919591,5943.3875339958804,69.238534885449781,5953.6985328000019,69.395553560915062,0.15701867546528092,null,null,null,null,null,null,null,null,null,1952.1584250096714,0,0,0,15.540716823750017,0]
[0,0,0,1881.8384590096025,0,1881.8384590096025,2202.1327240000001,"2013-01-03T20:00:00",44,37,"OFF",-27.504482526359979,-70.971595690604005,-8.8484060000000007,"OFF",-5.8195397006550156,-107.23437974632,-8.8484060000000007,"OFF",-4.417341757799894E-2,-61.926196397112001,-1.7696810000000001,"ON",31984.54964582,49430.466921006002,2225.5810000000001,"OFF",-5.618844314649988,-118.28596608156001,-3.9817830000000001,null,0,0,0,1868.7324031484065,0,1868.7324031484065,0,0,0,1990.5707195012462,0,1990.5707195012462,0,0,0,356.84859685159358,0,0,0,0,235.0102804987539,0,355.77954809562436,233.94123174278468,null,null,2202.1327240000001,null,31016.841600000043,10.087160318999643,6149.7667567706549,72.433127888232264,6081.4831104000041,71.364079132263043,-1.0690487559692201,null,null,null,null,null,null,null,null,null,1868.7324031484065,0,0,0,13.106055861195955,0]
[0,0,0,0,0,0,2131.536724,"2013-01-03T21:00:00",44,38,"OFF",-27.067541316900005,-70.275796361938006,-8.8484060000000007,"OFF",-5.3091959383750202,-106.45732134840001,-8.8484060000000007,"OFF",7.7091401511000177E-2,-61.926196397112001,-1.7696810000000001,"check",34256.016122399997,47721.852820658001,2154.9850000000001,"OFF",-6.5503443105100159,-115.92711901050002,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-0.4902723423124371,-0.4902723423124371,null,null,2131.536724,null,31016.841600000043,10.148007196279305,6112.8931030660178,71.854351474575481,6081.4831104000041,71.364079132263043,-0.4902723423124371,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,2022.8134970479302,0,2022.8134970479302,2074.2427239999997,"2013-01-03T22:00:00",43,37,"OFF",-26.961271645910013,-73.754793005267999,-8.8484060000000007,"OFF",-6.2306496723750024,-106.37615050832001,-8.8484060000000007,"OFF",6.0704309819999934E-2,-61.926196397112001,-1.7696810000000001,"ON",36706.888251440003,48334.163288218006,2097.6909999999998,"OFF",-6.5771744990699954,-117.59015873206,-3.9817830000000001,null,0,0,0,2005.6679586987912,0,2005.6679586987912,0,0,0,2172.5467792119202,0,2172.5467792119202,0,0,0,92.02304130120865,0,0,0,0,-74.855779211920435,0,91.933577051857384,-74.945243461271701,null,null,2074.2427239999997,null,30272.564300000085,10.061790331327108,6017.3315688654902,70.370597388371493,6011.521044200008,70.281133139020227,-8.946424935126629E-2,null,null,null,null,null,null,null,null,null,2005.6679586987912,0,0,0,17.145538349139088,0]
[0,0,0,1862.1823196110797,0,1862.1823196110797,2209.7496460000002,"2013-01-03T23:00:00",43,37,"OFF",-26.485469154199986,-70.275796361938006,-8.8484060000000007,"OFF",-6.3412340012599806,-109.32172158648001,-8.8484060000000007,"OFF",-0.22193411233000288,-61.926196397112001,-1.7696810000000001,"ON",31291.199647399997,73472.579960978008,2233.4560000000001,"OFF",-7.8471084556900008,-116.47004926396001,-4.2398610000000003,null,0,0,0,1849.6214081646935,0,1849.6214081646935,0,0,0,1890.5426020819041,0,1890.5426020819041,0,0,0,383.83459183530658,0,0,0,0,342.91339791809605,0,383.74512758595529,342.82393366874476,null,null,2209.7496460000002,null,30272.564300000085,10.061790331327108,6017.3315688654902,70.370597388371493,6011.521044200008,70.281133139020227,-8.946424935126629E-2,null,null,null,null,null,null,null,null,null,1849.6214081646935,0,0,0,12.560911446386172,0]
[0,0,0,1842.0079883698302,0,1842.0079883698302,1931.5406460000002,"2013-01-04",43,38,"OFF",-26.568773372250003,-70.275796361938006,-8.8484060000000007,"OFF",-6.3807556119299971,-107.02086514524001,-8.8484060000000007,"OFF",0.21115158374999468,-61.926196397112001,-1.7696810000000001,"ON",30569.627035079997,73205.670667960017,1955.2470000000001,"OFF",-7.6863395884799797,-117.59015873206,-4.2398610000000003,null,0,0,0,1830.0015054153218,0,1830.0015054153218,0,0,0,1869.6536439982226,0,1869.6536439982226,0,0,0,125.24549458467823,0,0,0,0,85.593356001777465,0,125.71153184335222,86.059393260451458,null,null,1931.5406460000002,null,30272.564300000085,10.122637208606768,5981.1615641546159,69.815095880346234,6011.521044200008,70.281133139020227,0.46603725867399248,null,null,null,null,null,null,null,null,null,1830.0015054153218,0,0,0,12.006482954508328,0]
[0,0,0,1721.1656719222754,0,1721.1656719222754,2179.2657020000001,"2013-01-04T01:00:00",40,36,"OFF",-26.177087397600001,-70.252600110010007,-8.8484060000000007,"OFF",-6.8055963967499649,-105.24914312298,-8.8484060000000007,"OFF",7.9616612623499741E-2,-33.398399859304,-1.7696810000000001,"ON",26010.973618100001,72693.837187918005,2204.6680000000001,"OFF",-7.7489575127300068,-114.80700954240001,-5.9358050000000002,null,0,0,0,1712.3605669939284,0,1712.3605669939284,0,0,0,1742.1949030329206,0,1742.1949030329206,0,0,0,492.30743300607173,0,0,0,0,462.47309696707953,0,493.53245941312997,463.69812337413777,null,null,2179.2657020000001,null,28829.600000000006,9.9517575034576407,5793.8710805570663,66.992245885587849,5875.8824000000004,68.217272292646101,1.2250264070582517,null,null,null,null,null,null,null,null,null,1712.3605669939284,0,0,0,8.8051049283469638,0]
[0,0,0,1925.6948409752326,0,1925.6948409752326,1978.1347240000002,"2013-01-04T02:00:00",40,36,"OFF",-26.581643785350003,-70.971595690604005,-8.8484060000000007,"OFF",-6.394851319699959,-107.79784333482002,-8.8484060000000007,"OFF",-2.8610278375002803E-2,-46.618603145626004,-1.7696810000000001,"ON",33498.894189880004,71053.696947428005,2001.5830000000001,"OFF",-7.3067688354500051,-116.89443159090001,-3.9817830000000001,null,0,0,0,1911.3556719070937,0,1911.3556719070937,0,0,0,1964.1018430071642,0,1964.1018430071642,0,0,0,90.227328092906419,0,0,0,0,37.481156992835849,0,91.45235449996467,38.706183399894101,null,null,1978.1347240000002,null,28829.600000000006,9.9517575034576407,5793.8710805570663,66.992245885587849,5875.8824000000004,68.217272292646101,1.2250264070582517,null,null,null,null,null,null,null,null,null,1911.3556719070937,0,0,0,14.339169068138972,0]
[0,0,0,1697.7035276315353,0,1697.7035276315353,2050.7876460000002,"2013-01-04T03:00:00",40,36,"OFF",-27.433715691299998,-70.298984593032003,-8.8484060000000007,"OFF",-6.549274671680025,-110.63216544540002,-8.8484060000000007,"OFF",-1.176768973374998,-46.618603145626004,-1.7696810000000001,"ON",25072.72583790002,73146.661392222013,2074.4940000000001,"OFF",-7.9288726062699828,-118.28596608156001,-4.2398610000000003,null,0,0,0,1689.4934139286286,0,1689.4934139286286,0,0,0,1716.6769156483585,0,1716.6769156483585,0,0,0,385.00058607137157,0,0,0,0,357.8170843516416,0,386.22561247842981,359.04211075869983,null,null,2050.7876460000002,null,28829.600000000006,9.9517575034576407,5793.8710805570663,66.992245885587849,5875.8824000000004,68.217272292646101,1.2250264070582517,null,null,null,null,null,null,null,null,null,1689.4934139286286,0,0,0,8.2101137029067104,0]
[0,0,0,1841.9701476607095,0,1841.9701476607095,2123.8676230000001,"2013-01-04T04:00:00",41,36,"OFF",-26.977793114719979,-69.655761831236006,-8.8484060000000007,"OFF",-5.6704141011100013,-107.71667249474001,-8.8484060000000007,"OFF",-0.58635260649999477,-46.618603145626004,-1.7696810000000001,"ON",30568.263870930001,70195.082709395996,2149.5279999999998,"OFF",-9.4118348638300073,-118.28596608156001,-6.1938839999999997,null,0,0,0,1829.9646996804402,0,1829.9646996804402,0,0,0,1875.986937380243,0,1875.986937380243,0,0,0,319.56330031955963,0,0,0,0,273.54106261975676,0,320.34599780272345,274.32376010292057,null,null,2123.8676230000001,null,29175.192900000024,9.9635376391848993,5856.3923691639311,67.924584424449961,5908.3681326000024,68.707281907613748,0.78269748316378696,null,null,null,null,null,null,null,null,null,1829.9646996804402,0,0,0,12.005447980269309,0]
[0,0,0,1842.4718512113889,0,1842.4718512113889,1895.118072,"2013-01-04T05:00:00",40,35,"OFF",-27.156077417700025,-71.591630221306005,-8.8484060000000007,"OFF",-6.2660119078799905,-100.89094276074,-8.8484060000000007,"OFF",0.52914376087500126,-33.398399859304,-1.139232,"ON",30586.334115494996,73381.567557580012,1920.1479999999999,"OFF",-9.925771279865014,-117.31873370950001,-6.1938839999999997,null,0,0,0,1830.4526797028325,0,1830.4526797028325,0,0,0,1869.7903830223415,0,1869.7903830223415,0,0,0,89.695320297167427,0,0,0,0,50.357616977658381,0,90.390056709711217,51.052353390202171,null,null,1895.118072,null,28829.600000000006,9.8909106261779804,5829.5138010240553,67.522535880102311,5875.8824000000004,68.217272292646101,0.69473641254379004,null,null,null,null,null,null,null,null,null,1830.4526797028325,0,0,0,12.019171508556383,0]
[0,0,0,1814.6963596657454,0,1814.6963596657454,2143.6890990000002,"2013-01-04T06:00:00",40,35,"OFF",-27.276259904530011,-72.363194347936002,-8.8484060000000007,"OFF",-5.9466188661599606,-107.8489360474,-8.8484060000000007,"OFF",-7.705094129799929E-2,-61.926196397112001,-3.2812839999999999,"ON",29575.978879719998,73482.036524264011,2170.6030000000001,"OFF",-7.0617094404000014,-115.77897420652,-5.9358050000000002,null,0,0,0,1803.4318983137334,0,1803.4318983137334,0,0,0,1840.1063266217247,0,1840.1063266217247,0,0,0,367.17110168626664,0,0,0,0,330.49667337827532,0,367.8658380988104,331.19140979081908,null,null,2143.6890990000002,null,28829.600000000006,9.8909106261779804,5829.5138010240553,67.522535880102311,5875.8824000000004,68.217272292646101,0.69473641254379004,null,null,null,null,null,null,null,null,null,1803.4318983137334,0,0,0,11.264461352011949,0]
[0,0,0,1897.6618046378801,0,1897.6618046378801,1984.321702,"2013-01-04T07:00:00",40,35,"OFF",-27.469777343309996,-71.667395019270003,-8.8484060000000007,"OFF",-5.130633020240027,-103.80643571140001,-8.8484060000000007,"OFF",-4.9018383800010839E-3,-61.926196397112001,-1.7696810000000001,"ON",32536.004640440005,72454.206751334001,2009.7239999999999,"OFF",-6.7451603473799864,-118.97704113900002,-5.9358050000000002,null,0,0,0,1884.1134635700314,0,1884.1134635700314,0,0,0,1930.6045642298204,0,1930.6045642298204,0,0,0,125.61053642996853,0,0,0,0,79.119435770179507,0,126.30527284251232,79.814172182723297,null,null,1984.321702,null,28829.600000000006,9.8909106261779804,5829.5138010240553,67.522535880102311,5875.8824000000004,68.217272292646101,0.69473641254379004,null,null,null,null,null,null,null,null,null,1884.1134635700314,0,0,0,13.548341067848696,0]
[0,0,0,1905.3686448014319,0,1905.3686448014319,2067.7097239999998,"2013-01-04T08:00:00",41,36,"OFF",-27.772064577979993,-72.264233298044005,-8.8484060000000007,"OFF",-6.1047064188099913,-107.02086514524001,-8.8484060000000007,"OFF",-0.47253218262499752,-75.14639166260001,-1.7696810000000001,"ON",32802.489812204985,73797.929050520019,2091.1579999999999,"OFF",-9.6907075040999917,-118.71034840850001,-3.9817830000000001,null,0,0,0,1891.6038027386155,0,1891.6038027386155,0,0,0,1935.7046977224275,0,1935.7046977224275,0,0,0,199.55419726138439,0,0,0,0,155.45330227757245,0,200.33689474454818,156.23599976073623,null,null,2067.7097239999998,null,29175.192900000024,9.9635376391848993,5856.3923691639311,67.924584424449961,5908.3681326000024,68.707281907613748,0.78269748316378696,null,null,null,null,null,null,null,null,null,1891.6038027386155,0,0,0,13.764842062816342,0]
[0,0,0,1733.72539637565,0,1733.72539637565,2177.0617240000001,"2013-01-04T09:00:00",41,36,"OFF",-27.28851266848001,-70.374749390996001,-8.8484060000000007,"OFF",-5.8375079651749759,-104.55341598182001,-8.8484060000000007,"OFF",-0.13090780373999916,-33.398399859304,-1.7696810000000001,"ON",26505.519466229995,70509.026172990008,2200.5100000000002,"OFF",-7.9435612854499995,-119.94908601146001,-3.9817830000000001,null,0,0,0,1724.5979527595591,0,1724.5979527595591,0,0,0,1759.0481658103918,0,1759.0481658103918,0,0,0,475.9120472404411,0,0,0,0,441.46183418960845,0,476.69474472360491,442.24453167277227,null,null,2177.0617240000001,null,29175.192900000024,9.9635376391848993,5856.3923691639311,67.924584424449961,5908.3681326000024,68.707281907613748,0.78269748316378696,null,null,null,null,null,null,null,null,null,1724.5979527595591,0,0,0,9.1274436160908863,0]
[0,0,0,1792.928965317421,0,1792.928965317421,1966.4547240000002,"2013-01-04T10:00:00",42,37,"OFF",-27.365428406050007,-70.275796361938006,-8.8484060000000007,"OFF",-5.9227902722000154,-109.05711427282002,-8.8484060000000007,"OFF",-0.5026297738750064,-61.926196397112001,-1.7696810000000001,"ON",28769.51859996,73500.684963314008,1989.903,"OFF",-8.2323324776399982,-118.98177343106001,-3.9817830000000001,null,0,0,0,1782.2485369759918,0,1782.2485369759918,0,0,0,1816.9857558833883,0,1816.9857558833883,0,0,0,207.65446302400824,0,0,0,0,172.91724411661176,0,208.3578168855087,173.62059797811222,null,null,1966.4547240000002,null,29657.431200000021,10.040822448571618,5907.3709055016725,68.692199699414601,5953.6985328000019,69.395553560915062,0.7033538615004602,null,null,null,null,null,null,null,null,null,1782.2485369759918,0,0,0,10.680428341429206,0]
[0,0,0,1824.2721747024073,0,1824.2721747024073,2210.338702,"2013-01-04T11:00:00",43,38,"OFF",-27.266905643880023,-70.176835312046009,-8.8484060000000007,"OFF",-6.3425562108900184,-107.33656517148002,-8.8484060000000007,"OFF",-0.19502536462499356,-75.14639166260001,-1.7696810000000001,"ON",29926.622555279995,72724.171982106011,2235.741,"OFF",-8.7404009045499969,-117.59015873206,-5.9358050000000002,null,0,0,0,1812.7486974482379,0,1812.7486974482379,0,0,0,1851.7473815912119,0,1851.7473815912119,0,0,0,422.99230255176212,0,0,0,0,383.99361840878805,0,423.45833981043609,384.45965566746202,null,null,2210.338702,null,30272.564300000085,10.122637208606768,5981.1615641546159,69.815095880346234,6011.521044200008,70.281133139020227,0.46603725867399248,null,null,null,null,null,null,null,null,null,1812.7486974482379,0,0,0,11.523477254169393,0]
[0,0,0,1805.1579513917709,0,1805.1579513917709,1941.5617240000001,"2013-01-04T12:00:00",45,39,"OFF",-28.116777264749981,-73.853754055159996,-8.8484060000000007,"OFF",-5.8469148141250287,-104.31880658732,-8.8484060000000007,"OFF",-4.0532203625000811E-2,-46.618603145626004,-1.7696810000000001,"ON",29224.217771164993,71179.503728718002,1965.01,"OFF",-9.3512440909499848,-116.19862424140001,-3.9817830000000001,null,0,0,0,1794.1502341840744,0,1794.1502341840744,0,0,0,1834.3763576034464,0,1834.3763576034464,0,0,0,170.85976581592558,0,0,0,0,130.63364239655357,0,169.82057264431398,129.59444922494197,null,null,1941.5617240000001,null,31886.51250000007,10.238498320417181,6228.747908550873,73.684544650594404,6163.2321750000065,72.645351478982803,-1.0391931716116005,null,null,null,null,null,null,null,null,null,1794.1502341840744,0,0,0,11.007717207696487,0]
[0,0,0,1852.080375723554,0,1852.080375723554,2175.0557239999998,"2013-01-04T13:00:00",46,39,"OFF",-27.377230188509987,-72.264233298044005,-8.8484060000000007,"OFF",-5.7754765795100242,-105.11687957032001,-8.8484060000000007,"OFF",-0.94220685075000332,-46.618603145626004,-1.7696810000000001,"ON",30931.169099849994,73353.454534410004,2198.5039999999999,"OFF",-7.5572413394000169,-121.06919547956002,-3.9817830000000001,null,0,0,0,1839.7977403939942,0,1839.7977403939942,0,0,0,1880.0570097208106,0,1880.0570097208106,0,0,0,358.70625960600569,0,0,0,0,318.44699027918932,0,356.35942122677795,316.10015189996159,null,null,2175.0557239999998,null,32877.826400000049,10.272288980729696,6401.2658642445167,76.473541970869888,6256.415681600005,74.126703591642183,-2.3468383792277052,null,null,null,null,null,null,null,null,null,1839.7977403939942,0,0,0,12.282635329559753,0]
[0,0,0,1993.0842824800002,0,1993.0842824800002,2104.0476230000004,"2013-01-04T14:00:00",47,40,"OFF",-27.419301912330017,-69.678950062330017,-8.8484060000000007,"OFF",-5.7366997787399843,-105.76159420724001,-8.8484060000000007,"OFF",-6.3579697625002013E-2,-33.398399859304,-1.7696810000000001,"ON",35744.795759590001,70375.711891076004,2129.7080000000001,"OFF",-9.8863301447400058,-116.89443159090001,-6.1938839999999997,null,0,0,0,1976.8082485737018,0,1976.8082485737018,0,0,0,2038.6956035792782,0,2038.6956035792782,0,0,0,152.89975142629828,0,0,0,0,91.012396420721871,0,149.69935882192968,87.812003816353268,null,null,2104.0476230000004,null,33987.03270000004,10.370945086044795,6554.2787890629543,79.0109701692935,6360.681073800004,75.810577564924898,-3.2003926043686022,null,null,null,null,null,null,null,null,null,1976.8082485737018,0,0,0,16.27603390629838,0]
[0,0,0,1817.1415831307991,0,1817.1415831307991,2067.9910990000003,"2013-01-04T15:00:00",49,41,"OFF",-27.146591406900008,-69.556800781343995,-8.8484060000000007,"OFF",-4.9166711342599854,-107.79784333482002,-8.8484060000000007,"OFF",-0.86480802562500025,-46.618603145626004,-3.2812839999999999,"ON",29665.753010400018,72979.114190795997,2094.9050000000002,"OFF",-9.2674952418300105,-115.50281689190001,-5.9358050000000002,null,0,0,0,1805.8111005806938,0,1805.8111005806938,0,0,0,1843.6628772482568,0,1843.6628772482568,0,0,0,289.09389941930635,0,0,0,0,251.24212275174341,0,283.07247513942809,245.22069847186512,null,null,2067.9910990000003,null,36544.120100000058,10.518954739638612,6948.241722590692,85.819920685504087,6601.047289400005,79.798496405625798,-6.0214242798782891,null,null,null,null,null,null,null,null,null,1805.8111005806938,0,0,0,11.330482550105216,0]
[0,0,0,1820.3129959462854,0,1820.3129959462854,2177.3567239999998,"2013-01-04T16:00:00",50,41,"OFF",-27.483395103759996,-67.515787278368009,-8.8484060000000007,"OFF",-5.3809912437500085,-108.59591631782001,-8.8484060000000007,"OFF",-2.7169809999969961E-3,-33.398399859304,-1.7696810000000001,"ON",29781.946909000002,72223.760169680012,2200.8049999999998,"OFF",-9.0131934112999907,-119.67758078056001,-3.9817830000000001,null,0,0,0,1808.8967625753676,0,1808.8967625753676,0,0,0,1848.5171127261431,0,1848.5171127261431,0,0,0,391.90823742463226,0,0,0,0,352.28788727385677,0,383.84984188954854,344.22949173877305,null,null,2177.3567239999998,null,37984.500000000058,10.568052596454578,7188.5524136666936,90.168365829162568,6736.4430000000057,82.109970294078821,-8.0583955350837471,null,null,null,null,null,null,null,null,null,1808.8967625753676,0,0,0,11.41623337091778,0]
[0,0,0,2138.6224818554265,0,2138.6224818554265,2006.7366460000001,"2013-01-04T17:00:00",48,40,"OFF",-26.946044767869992,-72.363194347936002,-8.8484060000000007,"OFF",-5.5653654636750227,-106.96977243266001,-8.8484060000000007,"OFF",-0.48954844724999824,-33.398399859304,-1.7696810000000001,"ON",40305.609785150016,73719.998627376015,2030.443,"OFF",-9.1746509026199821,-113.41539484340001,-4.2398610000000003,null,0,0,0,2118.0105412349299,0,2118.0105412349299,0,0,0,2184.3577741369668,0,2184.3577741369668,0,0,0,-87.567541234929877,0,0,0,0,-153.9147741369668,0,-92.436466853502708,-158.78369975553963,null,null,2006.7366460000001,null,35210.380800000043,10.412645036071787,6763.0041508230079,82.568928184383026,6475.6757952000044,77.700002565810195,-4.8689256185728311,null,null,null,null,null,null,null,null,null,2118.0105412349299,0,0,0,20.611940620496625,0]
[0,0,0,1917.7258170211462,0,1917.7258170211462,2172.4757239999999,"2013-01-04T18:00:00",46,39,"OFF",-26.34315264216999,-73.655831955376001,-8.8484060000000007,"OFF",-4.8688773161850243,-105.94495047248,-8.8484060000000007,"OFF",9.0231740964001578E-2,-61.926196397112001,-1.7696810000000001,"ON",33226.961411059994,73569.984969074008,2195.924,"OFF",-9.5057829766199937,-114.11593448496001,-3.9817830000000001,null,0,0,0,1903.6123845667623,0,1903.6123845667623,0,0,0,1949.3685150515073,0,1949.3685150515073,0,0,0,292.31161543323765,0,0,0,0,246.55548494849268,0,289.96477705400991,244.20864656926497,null,null,2172.4757239999999,null,32877.826400000049,10.272288980729696,6401.2658642445167,76.473541970869888,6256.415681600005,74.126703591642183,-2.3468383792277052,null,null,null,null,null,null,null,null,null,1903.6123845667623,0,0,0,14.113432454383883,0]
[0,0,0,2004.5705714759606,0,2004.5705714759606,2001.6496460000001,"2013-01-04T19:00:00",47,40,"OFF",-25.996517997519998,-71.766356069162001,-8.8484060000000007,"OFF",-4.2861096053999628,-105.76159420724001,-8.8484060000000007,"OFF",-0.7086401737500001,-75.14639166260001,-1.7696810000000001,"ON",36118.503239999998,72334.800595576002,2025.356,"OFF",-10.24157542618001,-119.67284848850001,-4.2398610000000003,null,0,0,0,1987.9596416353731,0,1987.9596416353731,0,0,0,2045.3219198985721,0,2045.3219198985721,0,0,0,37.396358364626849,0,0,0,0,-19.96591989857211,0,34.195965760258247,-23.166312502940713,null,null,2001.6496460000001,null,33987.03270000004,10.370945086044795,6554.2787890629543,79.0109701692935,6360.681073800004,75.810577564924898,-3.2003926043686022,null,null,null,null,null,null,null,null,null,1987.9596416353731,0,0,0,16.61092984058746,0]
[0,0,0,1847.3717684551063,0,1847.3717684551063,2192.4287239999999,"2013-01-04T20:00:00",46,39,"OFF",-26.005977658290025,-71.568433969378006,-8.8484060000000007,"OFF",-5.9462146119999852,-107.1531286979,-8.8484060000000007,"OFF",0.40786335037499932,-61.926196397112001,-1.7696810000000001,"ON",30762.478566159993,73226.26816967201,2215.877,"OFF",-8.7906226024399814,-115.50754918396001,-3.9817830000000001,null,0,0,0,1835.2183921779852,0,1835.2183921779852,0,0,0,1875.3140277703978,0,1875.3140277703978,0,0,0,380.6586078220148,0,0,0,0,340.56297222960211,0,378.31176944278707,338.21613385037438,null,null,2192.4287239999999,null,32877.826400000049,10.272288980729696,6401.2658642445167,76.473541970869888,6256.415681600005,74.126703591642183,-2.3468383792277052,null,null,null,null,null,null,null,null,null,1835.2183921779852,0,0,0,12.153376277121197,0]
[0,0,0,1823.7372498998825,0,1823.7372498998825,2017.045646,"2013-01-04T21:00:00",46,39,"OFF",-26.119333515510007,-73.157954726494012,-8.8484060000000007,"OFF",-6.0590012201250154,-105.71042128632001,-8.8484060000000007,"OFF",-3.2065060250000992E-2,-46.618603145626004,-1.7696810000000001,"ON",29907.099985860015,73045.630967157995,2040.752,"OFF",-9.3568159961499795,-119.67284848850001,-4.2398610000000003,null,0,0,0,1812.2282748353664,0,1812.2282748353664,0,0,0,1850.547107100185,0,1850.547107100185,0,0,0,228.52372516463356,0,0,0,0,190.20489289981492,0,226.17688678540586,187.85805452058722,null,null,2017.045646,null,32877.826400000049,10.272288980729696,6401.2658642445167,76.473541970869888,6256.415681600005,74.126703591642183,-2.3468383792277052,null,null,null,null,null,null,null,null,null,1812.2282748353664,0,0,0,11.508975064516108,0]
[0,0,0,1951.3743576913132,0,1951.3743576913132,2092.5447239999999,"2013-01-04T22:00:00",45,39,"OFF",-25.49541947701001,-72.363194347936002,-8.8484060000000007,"OFF",-6.3014762648999962,-105.11687957032001,-8.8484060000000007,"OFF",-0.81178821073000484,-46.618603145626004,-1.7696810000000001,"ON",34365.814380529991,72641.517287736002,2115.9929999999999,"OFF",-11.102773535559985,-115.50281689190001,-3.9817830000000001,null,0,0,0,1936.3029123034739,0,1936.3029123034739,0,0,0,1987.5428965078943,0,1987.5428965078943,0,0,0,179.69008769652601,0,0,0,0,128.45010349210565,0,178.65089452491441,127.41091032049405,null,null,2092.5447239999999,null,31886.51250000007,10.238498320417181,6228.747908550873,73.684544650594404,6163.2321750000065,72.645351478982803,-1.0391931716116005,null,null,null,null,null,null,null,null,null,1936.3029123034739,0,0,0,15.071445387839276,0]
[0,0,0,1825.2137154843085,0,1825.2137154843085,2198.378702,"2013-01-04T23:00:00",46,39,"OFF",-25.992825809940026,-68.884197704605995,-8.8484060000000007,"OFF",-5.7731906606400152,-106.40767238594002,-8.8484060000000007,"OFF",5.4936887375004691E-2,-46.618603145626004,-1.7696810000000001,"ON",29960.966368754995,70528.236070419996,2223.7809999999999,"OFF",-11.182117874830013,-119.67758078056001,-5.9358050000000002,null,0,0,0,1813.6647029635021,0,1813.6647029635021,0,0,0,1857.2298775630061,0,1857.2298775630061,0,0,0,410.11629703649783,0,0,0,0,366.55112243699386,0,407.76945865727009,364.20428405776613,null,null,2198.378702,null,32877.826400000049,10.272288980729696,6401.2658642445167,76.473541970869888,6256.415681600005,74.126703591642183,-2.3468383792277052,null,null,null,null,null,null,null,null,null,1813.6647029635021,0,0,0,11.5490125208064,0]
[0,0,0,2046.2011192233228,0,2046.2011192233228,1955.572099,"2013-01-05",45,40,"OFF",-25.852834941300014,-71.667395019270003,-8.8484060000000007,"OFF",-5.8417218598500451,-109.2405507464,-8.8484060000000007,"OFF",-0.77243067162500256,-33.398399859304,-3.2812839999999999,"ON",37452.22508465001,72989.132212462006,1982.4860000000001,"OFF",-10.184136747189999,-116.89443159090001,-5.9358050000000002,null,0,0,0,2028.3654566122889,0,2028.3654566122889,0,0,0,2087.9594452511751,0,2087.9594452511751,0,0,0,-45.879456612288777,0,0,0,0,-105.47344525117501,0,-46.333610020436382,-105.92759865932261,null,null,1955.572099,null,31886.51250000007,10.299345197696841,6191.9494662885154,73.099504887130408,6163.2321750000065,72.645351478982803,-0.45415340814760441,null,null,null,null,null,null,null,null,null,2028.3654566122889,0,0,0,17.835662611033968,0]
[0,0,0,1907.4033730362396,0,1907.4033730362396,1804.9337240000002,"2013-01-05T01:00:00",45,41,"OFF",-25.699395059239993,-73.754793005267999,-8.8484060000000007,"OFF",-4.2451926196799805,-106.45732134840001,-8.8484060000000007,"OFF",0.24382562249999759,-62.100144224070007,-1.7696810000000001,"ON",32872.619897639997,73191.497854282017,1828.3820000000001,"OFF",-9.8396518040100105,-115.50281689190001,-3.9817830000000001,null,0,0,0,1893.5812545191393,0,1893.5812545191393,0,0,0,1939.2718193782146,0,1939.2718193782146,0,0,0,-65.199254519139231,0,0,0,0,-110.8898193782145,0,-65.078645928060297,-110.76921078713556,null,null,1804.9337240000002,null,31886.51250000007,10.360192074976503,6155.583268966061,72.524742887903869,6163.2321750000065,72.645351478982803,0.12060859107893407,null,null,null,null,null,null,null,null,null,1893.5812545191393,0,0,0,13.822118517100307,0]
[0,0,0,1716.363991924409,0,1716.363991924409,1657.144147,"2013-01-05T02:00:00",43,40,"OFF",-25.963606810050017,-68.884197704605995,-8.8484060000000007,"OFF",-4.7432146733250224,-106.50849426932001,-8.8484060000000007,"OFF",4.3256500384500136E-2,-33.398399859304,-2.47018,"ON",25820.505114164993,73320.617240014006,1681.5509999999999,"OFF",-11.537915043060012,-118.28596608156001,-4.2398610000000003,null,0,0,0,1707.6814240186404,0,1707.6814240186404,0,0,0,1736.1762610951416,0,1736.1762610951416,0,0,0,-26.130424018640497,0,0,0,0,-54.625261095141695,0,-24.582931615656349,-53.077768692157548,null,null,1657.144147,null,30272.564300000085,10.244330963166089,5910.1105594589499,68.733640736036079,6011.521044200008,70.281133139020227,1.5474924029841475,null,null,null,null,null,null,null,null,null,1707.6814240186404,0,0,0,8.6825679057685647,0]
[0,0,0,1685.4132723033249,0,1685.4132723033249,1819.2177240000001,"2013-01-05T03:00:00",43,40,"OFF",-26.762460669560003,-70.973047461558011,-8.8484060000000007,"OFF",-5.7797732285700141,-105.01605768694,-8.8484060000000007,"OFF",-4.6824946385003091E-2,-33.398399859304,-1.7696810000000001,"ON",24573.437698600002,73155.853267986007,1842.6659999999999,"OFF",-11.299117874309989,-116.20006799152002,-3.9817830000000001,null,0,0,0,1677.5109763425564,0,1677.5109763425564,0,0,0,1703.661906813875,0,1703.661906813875,0,0,0,165.15502365744351,0,0,0,0,139.00409318612492,0,166.70251606042766,140.55158558910907,null,null,1819.2177240000001,null,30272.564300000085,10.244330963166089,5910.1105594589499,68.733640736036079,6011.521044200008,70.281133139020227,1.5474924029841475,null,null,null,null,null,null,null,null,null,1677.5109763425564,0,0,0,7.9022959607684697,0]
[0,0,0,1927.6252708066847,0,1927.6252708066847,1645.1398630000001,"2013-01-05T04:00:00",42,40,"OFF",-27.183838547789975,-72.363194347936002,-8.8484060000000007,"OFF",-4.950693008840009,-106.32505779574001,-8.8484060000000007,"OFF",-0.16273043311499874,-62.100144224070007,-1.7696810000000001,"ON",33564.557618094987,72931.510541006006,1668.837,"OFF",3187.5365693800009,40036.442077704,-4.2306439999999998,null,0,0,0,1913.231310075543,0,1913.231310075543,0,0,0,1961.4503416216817,0,1961.4503416216817,0,0,0,-244.39431007554299,0,0,0,0,-292.61334162168168,0,-242.11007375154375,-290.32910529768242,null,null,1645.1398630000001,null,29657.431200000021,10.2233630804106,5801.893362630899,67.111317236915824,5953.6985328000019,69.395553560915062,2.284236323999238,null,null,null,null,null,null,null,null,null,1913.231310075543,0,0,0,14.39396073114176,0]
[0,0,0,0,1572.7663559034893,1572.7663559034893,1615.4357239999999,"2013-01-05T05:00:00",39,37,"OFF",-26.814291178569999,-70.971595690604005,-8.8484060000000007,"OFF",-6.2381646598799998,-107.2854724589,-8.8484060000000007,"OFF",-0.27695928486600141,-61.926196397112001,-1.7696810000000001,"OFF",2.6135804256099968,-164.76541577812,-3.9817830000000001,"ON",32151.449793539996,72572.915094534008,1638.884,null,0,0,0,0,1560.0233283365644,1560.0233283365644,0,0,0,0,1603.4875490688769,1603.4875490688769,0,0,0,0,78.860671663435596,0,0,0,0,35.396450931123127,80.860255603741038,37.396034871428569,null,null,1615.4357239999999,null,28624.403100000054,10.005609887121222,5721.6708272514443,65.928021830937894,5856.5938914000053,67.927605771243336,1.9995839403054418,null,null,null,null,null,null,null,null,null,1560.0233283365644,0,0,0,0,12.743027566924866]
[0,0,0,0,1505.9999139259351,1505.9999139259351,1487.7484010000001,"2013-01-05T06:00:00",38,36,"OFF",-26.730234582869997,-70.272892820030009,-8.8484060000000007,"OFF",-6.2666296981199983,-108.59447256770001,-8.8484060000000007,"OFF",5.5898955534996256E-2,-62.100144224070007,-1.7696810000000001,"OFF",1.8525362549650086,-164.80022619768002,-3.401106,"ON",29000.29497264,70986.129441812009,1510.616,null,0,0,0,0,1495.557590511077,1495.557590511077,0,0,0,0,1534.0778188206393,1534.0778188206393,0,0,0,0,15.058409488922962,0,0,0,0,-23.461818820639337,16.620713410296815,-21.899514899265483,null,null,1487.7484010000001,null,28563.352800000052,9.9426820040680362,5745.6032061195147,66.279303938778682,5850.8551632000053,67.841607860152536,1.5623039213738537,null,null,null,null,null,null,null,null,null,1495.557590511077,0,0,0,0,10.442323414858038]
[0,0,0,0,1645.9753661309071,1645.9753661309071,1832.4197239999999,"2013-01-05T07:00:00",39,38,"OFF",-27.094615644239997,-73.754793005267999,-8.8484060000000007,"OFF",-5.6779046824499755,-107.10203598532001,-8.8484060000000007,"OFF",-0.42475079262500071,-33.398399859304,-1.7696810000000001,"OFF",0.67716942097000477,-160.86897482926003,-3.9817830000000001,"ON",35436.909763340009,72430.521228532016,1855.8679999999999,null,0,0,0,0,1630.5812353583576,1630.5812353583576,0,0,0,0,1683.4813121477844,1683.4813121477844,0,0,0,0,225.28676464164232,0,0,0,0,172.38668785221557,227.79139678163921,174.89131999221246,null,null,1832.4197239999999,null,28624.403100000054,10.066456764400883,5687.086085985623,65.422973631246435,5856.5938914000053,67.927605771243336,2.5046321399969003,null,null,null,null,null,null,null,null,null,1630.5812353583576,0,0,0,0,15.394130772549488]
[0,0,0,0,1540.1598385145744,1540.1598385145744,1486.4457239999999,"2013-01-05T08:00:00",40,38,"OFF",-26.751367306929986,-72.363194347936002,-8.8484060000000007,"OFF",-5.6190931385599869,-105.76159420724001,-8.8484060000000007,"OFF",-0.20976967099999705,-62.100144224070007,-1.7696810000000001,"OFF",0.54277554348001356,-160.83416440970004,-3.9817830000000001,"ON",30632.381169120014,70516.990861151993,1509.894,null,0,0,0,0,1528.5553432638794,1528.5553432638794,0,0,0,0,1572.3553464029878,1572.3553464029878,0,0,0,0,-18.661343263879417,0,0,0,0,-62.461346402987829,-16.404419764889269,-60.204422903997681,null,null,1486.4457239999999,null,28829.600000000006,10.073451258016961,5723.8774004204279,65.960348793655953,5875.8824000000004,68.217272292646101,2.2569234989901474,null,null,null,null,null,null,null,null,null,1528.5553432638794,0,0,0,0,11.604495250694981]
[0,0,0,0,1604.0078977039382,1604.0078977039382,1720.4091490000001,"2013-01-05T09:00:00",41,39,"OFF",-27.251464526300005,-72.361750597816012,-8.8484060000000007,"OFF",-5.2368983644899894,-107.1531286979,-8.8484060000000007,"OFF",-0.50086139400000262,-46.444647297834003,-1.7696810000000001,"OFF",0.35427615335000284,-166.99199929652002,-2.3503579999999999,"ON",33573.779724240012,72385.596537298014,1742.2260000000001,null,0,0,0,0,1590.1489334592529,1590.1489334592529,0,0,0,0,1637.8732896973431,1637.8732896973431,0,0,0,0,152.07706654074718,0,0,0,0,104.35271030265699,154.42520684866702,106.70085061057682,null,null,1720.4091490000001,null,29175.192900000024,10.14607827102388,5751.0285492910634,66.359141599693913,5908.3681326000024,68.707281907613748,2.3481403079198344,null,null,null,null,null,null,null,null,null,1590.1489334592529,0,0,0,0,13.858964244685239]
[0,0,0,0,1575.3609542377137,1575.3609542377137,1510.3227239999999,"2013-01-05T10:00:00",42,39,"OFF",-27.962197431279996,-69.579997033272008,-8.8484060000000007,"OFF",-4.9601664809100452,-103.02985856352001,-8.8484060000000007,"OFF",-0.27719061762499514,-33.398399859304,-1.7696810000000001,"OFF",-0.12774494544001308,-166.99199929652002,-3.9817830000000001,"ON",32270.778698379996,70626.964516126012,1533.771,null,0,0,0,0,1562.5261611851265,1562.5261611851265,0,0,0,0,1610.7208604625928,1610.7208604625928,0,0,0,0,-28.755161185126553,0,0,0,0,-76.949860462592824,-26.988430033796959,-75.18312931126323,null,null,1510.3227239999999,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1562.5261611851265,0,0,0,0,12.834793052587202]
[0,0,0,0,1570.9699754926253,1570.9699754926253,1775.7084010000001,"2013-01-05T11:00:00",45,41,"OFF",-27.727701144009988,-70.971595690604005,-8.8484060000000007,"OFF",-5.4742952597749746,-110.58211544124002,-8.8484060000000007,"OFF",-0.21345867537499469,-75.14639166260001,-1.7696810000000001,"OFF",-0.53039975387000049,-160.83416440970004,-3.401106,"ON",32068.70115479999,72323.042052931996,1798.576,null,0,0,0,0,1558.290383198698,1558.290383198698,0,0,0,0,1602.0848826211541,1602.0848826211541,0,0,0,0,240.28561680130201,0,0,0,0,196.49111737884596,240.40622539238095,196.61172596992489,null,null,1775.7084010000001,null,31886.51250000007,10.360192074976503,6155.583268966061,72.524742887903869,6163.2321750000065,72.645351478982803,0.12060859107893407,null,null,null,null,null,null,null,null,null,1558.290383198698,0,0,0,0,12.679592293927271]
[0,0,0,0,1609.8054546543412,1609.8054546543412,1609.9957239999999,"2013-01-05T12:00:00",47,42,"OFF",-27.270003140189985,-70.971595690604005,-8.8484060000000007,"OFF",-6.1584456057849737,-107.1531286979,-8.8484060000000007,"OFF",-0.10160820008999838,-62.100144224070007,-1.7696810000000001,"OFF",-0.52760665068999391,-158.64239131086001,-3.9817830000000001,"ON",33834.323663460011,70814.499635879998,1633.444,null,0,0,0,0,1595.7368239959408,1595.7368239959408,0,0,0,0,1648.0944082149003,1648.0944082149003,0,0,0,0,37.707176004059193,0,0,0,0,-14.650408214900381,35.774866003544886,-16.582718215414687,null,null,1609.9957239999999,null,33987.03270000004,10.492638840604116,6478.2621829082664,77.742887565439204,6360.681073800004,75.810577564924898,-1.9323100005143061,null,null,null,null,null,null,null,null,null,1595.7368239959408,0,0,0,0,14.06863065840048]
[0,0,0,0,1658.4270582667186,1658.4270582667186,1774.4954010000001,"2013-01-05T13:00:00",50,43,"OFF",-26.713166818639984,-71.667395019270003,-8.8484060000000007,"OFF",-5.8731125056799947,-107.1531286979,-8.8484060000000007,"OFF",-0.30386856037500037,-33.398399859304,-1.7696810000000001,"OFF",-0.59498367739999891,-166.99199929652002,-3.401106,"ON",35979.790087905007,72369.883723492007,1797.3630000000001,null,0,0,0,0,1642.5698885302606,1642.5698885302606,0,0,0,0,1697.2301549555384,1697.2301549555384,0,0,0,0,154.79311146973942,0,0,0,0,100.13284504446165,148.23213942609709,93.571873000819338,null,null,1774.4954010000001,null,37984.500000000058,10.689746351013898,7106.7168018252023,88.670942337721129,6736.4430000000057,82.109970294078821,-6.5609720436423089,null,null,null,null,null,null,null,null,null,1642.5698885302606,0,0,0,0,15.85716973645799]
[0,0,0,0,1667.5084737621178,1667.5084737621178,1698.838724,"2013-01-05T14:00:00",51,44,"OFF",-26.806319598750015,-69.579997033272008,-8.8484060000000007,"OFF",-5.7127810737600129,-107.8489360474,-8.8484060000000007,"OFF",-0.762605037749996,-75.14639166260001,-1.7696810000000001,"OFF",-1.0724725710299992,-164.80022619768002,-3.9817830000000001,"ON",36372.983998829994,71480.710107919993,1722.287,null,0,0,0,0,1651.3114944738522,1651.3114944738522,0,0,0,0,1709.6706737767965,1709.6706737767965,0,0,0,0,70.975505526147799,0,0,0,0,12.616326223203487,63.046071556222017,4.6868922532777049,null,null,1698.838724,null,39527.769900000014,10.803198269906943,7317.7903269825847,92.568070745190255,6881.5103706000009,84.638636775264473,-7.9294339699257819,null,null,null,null,null,null,null,null,null,1651.3114944738522,0,0,0,0,16.196979288265538]
[0,0,0,0,1673.6217742011465,1673.6217742011465,1873.0997239999999,"2013-01-05T15:00:00",52,45,"OFF",-27.28771475084999,-72.363194347936002,-8.8484060000000007,"OFF",-6.1585665000649907,-106.45732134840001,-8.8484060000000007,"OFF",-0.1535014806059983,-75.14639166260001,-1.7696810000000001,"OFF",-1.0716557201000019,-160.83416440970004,-3.9817830000000001,"ON",36636.38656993,72363.948306332008,1896.548,null,0,0,0,0,1657.1950646449666,1657.1950646449666,0,0,0,0,1713.838794338503,1713.838794338503,0,0,0,0,239.35293535503342,0,0,0,0,182.70920566149698,229.94191174446982,173.29818205093338,null,null,1873.0997239999999,null,41170.179200000071,10.920029527866042,7540.3054716914157,96.799944456216963,7035.8968448000069,87.388920845653359,-9.4110236105636034,null,null,null,null,null,null,null,null,null,1657.1950646449666,0,0,0,0,16.426709556179958]
[0,0,0,0,1724.183574662389,1724.183574662389,1775.6288260000001,"2013-01-05T16:00:00",53,46,"OFF",-26.330037856739978,-70.275796361938006,-8.8484060000000007,"OFF",-4.6865577640500282,-107.76487770708,-8.8484060000000007,"OFF",-8.1556274499999651E-2,-62.100144224070007,-1.7696810000000001,"OFF",-2.291146261579998,-164.80022619768002,-1.7696810000000001,"ON",38776.911105375002,72426.72737405001,1796.865,null,0,0,0,0,1705.8276105339039,1705.8276105339039,0,0,0,0,1768.9366451202463,1768.9366451202463,0,0,0,0,91.037389466096101,0,0,0,0,27.92835487975367,80.039672441047188,16.930637854704756,null,null,1775.6288260000001,null,42907.977300000086,11.040112279159811,7773.1052393364844,101.36309127910438,7199.249866200008,90.365374254055467,-10.997717025048914,null,null,null,null,null,null,null,null,null,1705.8276105339039,0,0,0,0,18.355964128485084]
[0,0,0,0,1718.8622703618566,1718.8622703618566,1795.067724,"2013-01-05T17:00:00",51,45,"OFF",-26.525949632135021,-68.884197704605995,-8.8484060000000007,"OFF",-6.7041143259599805,-105.84565254756001,-8.8484060000000007,"OFF",-0.14452699362499977,-75.14639166260001,-1.7696810000000001,"OFF",-1.1913902564200001,-164.80022619768002,-3.9817830000000001,"ON",38554.73270303999,72374.335286362009,1818.5160000000001,null,0,0,0,0,1700.7117329523974,1700.7117329523974,0,0,0,0,1763.2778650600335,1763.2778650600335,0,0,0,0,117.80426704760271,0,0,0,0,55.238134939966585,110.6404803271876,48.074348219551482,null,null,1795.067724,null,39527.769900000014,10.864045147186603,7276.8051613327989,91.802423495679577,6881.5103706000009,84.638636775264473,-7.1637867204151036,null,null,null,null,null,null,null,null,null,1700.7117329523974,0,0,0,0,18.150537409459275]
[0,0,0,0,1660.4604104602795,1660.4604104602795,1919.2164010000001,"2013-01-05T18:00:00",46,42,"OFF",-25.936050502035002,-71.641303246267995,-8.8484060000000007,"OFF",-5.6302872585699868,-107.8489360474,-8.8484060000000007,"OFF",7.2023418749994406E-2,-75.14639166260001,-1.7696810000000001,"OFF",-2.0035393871999903,-164.80022619768002,-3.401106,"ON",36068.026644320002,72392.542579542001,1942.0840000000001,null,0,0,0,0,1644.5273091461163,1644.5273091461163,0,0,0,0,1699.3872545048546,1699.3872545048546,0,0,0,0,297.55669085388377,0,0,0,0,242.69674549514548,297.02539431970445,242.16544896096613,null,null,1919.2164010000001,null,32877.826400000049,10.454829612568677,6289.5001866839993,74.65800012582153,6256.415681600005,74.126703591642183,-0.53129653417934719,null,null,null,null,null,null,null,null,null,1644.5273091461163,0,0,0,0,15.933101314163196]
[0,0,0,0,1674.2999567458337,1674.2999567458337,1725.8789039999999,"2013-01-05T19:00:00",45,41,"OFF",-25.926101438849972,-73.085085449603994,-8.8484060000000007,"OFF",-6.7624837668449826,-107.8489360474,-8.8484060000000007,"OFF",-0.1023219383279987,-62.100144224070007,-3.2905009999999999,"OFF",-2.1129825556700008,-166.99199929652002,-3.9817830000000001,"ON",36665.544327700001,71229.826441234007,1750.848,null,0,0,0,0,1657.8477136746778,1657.8477136746778,0,0,0,0,1717.8639602737035,1717.8639602737035,0,0,0,0,93.000286325322122,0,0,0,0,32.984039726296487,93.120894916401056,33.104648317375421,null,null,1725.8789039999999,null,31886.51250000007,10.360192074976503,6155.583268966061,72.524742887903869,6163.2321750000065,72.645351478982803,0.12060859107893407,null,null,null,null,null,null,null,null,null,1657.8477136746778,0,0,0,0,16.452243071155863]
[0,0,0,0,1606.9719641141182,1606.9719641141182,1786.9667239999999,"2013-01-05T20:00:00",43,40,"OFF",-26.082208277549995,-68.884197704605995,-8.8484060000000007,"OFF",-5.3006637424249892,-103.72414195456,-8.8484060000000007,"OFF",7.3100842250003545E-2,-62.100144224070007,-1.7696810000000001,"OFF",-1.521503432259991,-158.64239131086001,-3.9817830000000001,"ON",33707.115720979986,72370.685806891997,1810.415,null,0,0,0,0,1593.0059042949433,1593.0059042949433,0,0,0,0,1641.1356610535622,1641.1356610535622,0,0,0,0,217.40909570505664,0,0,0,0,169.27933894643775,218.95658810804079,170.82683134942189,null,null,1786.9667239999999,null,30272.564300000085,10.244330963166089,5910.1105594589499,68.733640736036079,6011.521044200008,70.281133139020227,1.5474924029841475,null,null,null,null,null,null,null,null,null,1593.0059042949433,0,0,0,0,13.966059819174916]
[0,0,0,0,1618.5874936162047,1618.5874936162047,1631.643724,"2013-01-05T21:00:00",44,40,"OFF",-26.429339890079998,-70.971595690604005,-8.8484060000000007,"OFF",-6.0329777241500402,-108.5447433969,-8.8484060000000007,"OFF",-0.38133765225000082,-33.398399859304,-1.7696810000000001,"OFF",-1.5696906198050113,-166.99199929652002,-3.9817830000000001,"ON",34227.024882349993,70875.626411794015,1655.0920000000001,null,0,0,0,0,1604.1997692448424,1604.1997692448424,0,0,0,0,1657.58802847426,1657.58802847426,0,0,0,0,50.892230755157698,0,0,0,0,-2.4960284742599015,51.528801019710826,-1.8594582097067729,null,null,1631.643724,null,31016.841600000043,10.269700950838626,6040.4566303300589,70.727508867709915,6081.4831104000041,71.364079132263043,0.6365702645531286,null,null,null,null,null,null,null,null,null,1604.1997692448424,0,0,0,0,14.38772437136231]
[0,0,0,0,1621.136632154554,1621.136632154554,1855.6217239999999,"2013-01-05T22:00:00",43,40,"OFF",-26.453032267270007,-71.667395019270003,-8.8484060000000007,"OFF",-6.1124044621499491,-106.54145989706001,-8.8484060000000007,"OFF",0.24560571349999677,-33.398399859304,-1.7696810000000001,"OFF",-0.49169155979999618,-158.64239131086001,-3.9817830000000001,"ON",34340.574605300011,72403.52310128801,1879.07,null,0,0,0,0,1606.6559516627026,1606.6559516627026,0,0,0,0,1656.4797628264689,1656.4797628264689,0,0,0,0,272.41404833729734,0,0,0,0,222.59023717353102,273.96154074028152,224.13772957651517,null,null,1855.6217239999999,null,30272.564300000085,10.244330963166089,5910.1105594589499,68.733640736036079,6011.521044200008,70.281133139020227,1.5474924029841475,null,null,null,null,null,null,null,null,null,1606.6559516627026,0,0,0,0,14.480680491851444]
[0,0,0,0,1582.8565950791092,1582.8565950791092,1633.8059040000001,"2013-01-05T23:00:00",42,39,"OFF",-26.628608807009982,-71.667395019270003,-8.8484060000000007,"OFF",-6.1599067632900031,-109.10644240192002,-8.8484060000000007,"OFF",5.7747557374998135E-2,-46.444647297834003,-3.2905009999999999,"OFF",-1.1728134852700012,-158.64239131086001,-3.9817830000000001,"ON",32614.26894297,72359.625076806013,1658.7750000000001,null,0,0,0,0,1569.7557557210775,1569.7557557210775,0,0,0,0,1614.924441280371,1614.924441280371,0,0,0,0,89.019244278922542,0,0,0,0,43.850558719629134,90.785975430252137,45.617289870958729,null,null,1633.8059040000001,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1569.7557557210775,0,0,0,0,13.100839358031635]
[0,0,0,0,1592.6457478490736,1592.6457478490736,1583.8537239999998,"2013-01-06",36,34,"OFF",-26.514759850200015,-73.754793005267999,-8.8484060000000007,"OFF",-6.340196014179976,-107.06907035758,-8.8484060000000007,"OFF",-0.12833050775000132,-62.100144224070007,-1.7696810000000001,"OFF",-2.9016773658750141,-164.80022619768002,-3.9817830000000001,"ON",33060.115108350015,72350.505388548001,1607.3019999999999,null,0,0,0,0,1579.195378460855,1579.195378460855,0,0,0,0,1625.5922564169587,1625.5922564169587,0,0,0,0,28.106621539144953,0,0,0,0,-18.290256416958755,28.182179986262994,-18.214697969840714,null,null,1583.8537239999998,null,28888.694400000008,9.832078084414821,5876.4167965249399,68.225311189094967,5881.4372736000005,68.300869636213008,7.5558447118041272E-2,null,null,null,null,null,null,null,null,null,1579.195378460855,0,0,0,0,13.450369388218633]
[0,0,0,0,1523.7706839465579,1523.7706839465579,1585.7344617000001,"2013-01-06T01:00:00",39,37,"OFF",-26.217383948980004,-69.579997033272008,-8.8484060000000007,"OFF",-5.7163831631200308,-107.28723704238001,-8.8484060000000007,"OFF",0.16235073636500233,-33.398399859304,-0.4009433,"OFF",-1.9650798372799925,-160.83416440970004,-3.9817830000000001,"ON",29854.722342999983,72406.37851819201,1607.8140000000001,null,0,0,0,0,1512.7278130339673,1512.7278130339673,0,0,0,0,1550.7024266266012,1550.7024266266012,0,0,0,0,95.086186966032756,0,0,0,0,57.111573373398869,97.085770906338198,59.111157313704311,null,null,1585.7344617000001,null,28624.403100000054,10.005609887121222,5721.6708272514443,65.928021830937894,5856.5938914000053,67.927605771243336,1.9995839403054418,null,null,null,null,null,null,null,null,null,1512.7278130339673,0,0,0,0,11.042870912590615]
[0,0,0,0,1547.2646442727882,1547.2646442727882,1637.587724,"2013-01-06T02:00:00",34,33,"OFF",-26.944910931079985,-74.450592333934011,-8.8484060000000007,"OFF",-5.4873186064800175,-110.63216544540002,-8.8484060000000007,"OFF",-0.11911468668600114,-62.100144224070007,-1.7696810000000001,"OFF",-2.2127960883049926,-158.64239131086001,-3.9817830000000001,"ON",30966.511556655001,72335.185595608011,1661.0360000000001,null,0,0,0,0,1535.4144310221905,1535.4144310221905,0,0,0,0,1576.3153320706313,1576.3153320706313,0,0,0,0,125.6215689778096,0,0,0,0,84.720667929368801,123.82707093263555,82.926169884194749,null,null,1637.587724,null,29835.629600000044,9.8035091421879876,6086.724491663238,71.445715247888785,5970.4491824000042,69.651217202714733,-1.794498045174052,null,null,null,null,null,null,null,null,null,1535.4144310221905,0,0,0,0,11.85021325059779]
[0,0,0,0,1532.9756860646262,1532.9756860646262,1563.7924010000002,"2013-01-06T03:00:00",36,35,"OFF",-26.639414041500014,-72.363194347936002,-8.8484060000000007,"OFF",-6.6150458752349985,-105.71154420308001,-8.8484060000000007,"OFF",5.9433964799999107E-2,-62.100144224070007,-1.7696810000000001,"OFF",-0.82296413695999937,-166.99199929652002,-3.401106,"ON",30292.692947909996,72350.264763528001,1586.66,null,0,0,0,0,1521.6182779521187,1521.6182779521187,0,0,0,0,1560.7862544169393,1560.7862544169393,0,0,0,0,65.041722047881422,0,0,0,0,25.873745583060781,65.659332676078321,26.491356211257681,null,null,1563.7924010000002,null,28888.694400000008,9.8929249616944812,5840.2736322892088,67.683259008016108,5881.4372736000005,68.300869636213008,0.61761062819689982,null,null,null,null,null,null,null,null,null,1521.6182779521187,0,0,0,0,11.357408112507528]
[0,0,0,0,1507.0731615975774,1507.0731615975774,1523.587724,"2013-01-06T04:00:00",34,32,"OFF",-26.201705681130012,-68.884197704605995,-8.8484060000000007,"OFF",-7.1542333371150137,-107.20317870206,-8.8484060000000007,"OFF",0.28227324587500241,-33.398399859304,-1.7696810000000001,"OFF",-2.1301627752300054,-160.83416440970004,-3.9817830000000001,"ON",29052.236531700004,70635.129725138002,1547.0360000000001,null,0,0,0,0,1496.5948232161709,1496.5948232161709,0,0,0,0,1535.9127161066776,1535.9127161066776,0,0,0,0,50.441176783829178,0,0,0,0,11.123283893322423,48.052493360236369,8.7346004697296138,null,null,1523.587724,null,29835.629600000044,9.7426622649083274,6124.7385547713593,72.039900626307542,5970.4491824000042,69.651217202714733,-2.3886834235928092,null,null,null,null,null,null,null,null,null,1496.5948232161709,0,0,0,0,10.478338381406502]
[0,0,0,0,1480.3748127421854,1480.3748127421854,1583.9177239999999,"2013-01-06T05:00:00",35,33,"OFF",-26.742324793770003,-71.667395019270003,-8.8484060000000007,"OFF",-7.3364855175299715,-103.62412215458001,-8.8484060000000007,"OFF",-0.56926414940499714,-46.444647297834003,-1.7696810000000001,"OFF",-2.2911087584699974,-160.83416440970004,-3.9817830000000001,"ON",27746.733474459987,72405.303726436003,1607.366,null,0,0,0,0,1470.7823644451812,1470.7823644451812,0,0,0,0,1503.7647981162263,1503.7647981162263,0,0,0,0,136.58363555481878,0,0,0,0,103.60120188377368,135.56359116925091,102.58115749820581,null,null,1583.9177239999999,null,29282.587499999994,9.7846577392775451,5985.4086428499004,69.880149276034928,5918.4632249999995,68.860104890467056,-1.0200443855678714,null,null,null,null,null,null,null,null,null,1470.7823644451812,0,0,0,0,9.5924482970042391]
[0,0,0,0,1517.0839938889021,1517.0839938889021,1384.280724,"2013-01-06T06:00:00",34,32,"OFF",-27.417996715899992,-68.188398375940011,-8.8484060000000007,"OFF",-7.3104052638400452,-103.72414195456,-8.8484060000000007,"OFF",1.7859465625002062E-2,-75.14639166260001,-1.7696810000000001,"OFF",-1.4754699298500018,-158.64239131086001,-3.9817830000000001,"ON",29534.615570249996,71361.696973027996,1407.729,null,0,0,0,0,1506.2681387987357,1506.2681387987357,0,0,0,0,1545.441820976911,1545.441820976911,0,0,0,0,-98.539138798735621,0,0,0,0,-137.71282097691096,-100.92782222232843,-140.10150440050376,null,null,1384.280724,null,29835.629600000044,9.7426622649083274,6124.7385547713593,72.039900626307542,5970.4491824000042,69.651217202714733,-2.3886834235928092,null,null,null,null,null,null,null,null,null,1506.2681387987357,0,0,0,0,10.815855090166451]
[0,0,0,0,1574.4981152782555,1574.4981152782555,1754.501442,"2013-01-06T07:00:00",34,31,"OFF",-27.376785268979997,-71.667395019270003,-8.8484060000000007,"OFF",-7.1218508253399904,-107.1531286979,-8.8484060000000007,"OFF",-0.10143218979500453,-75.14639166260001,-2.460963,"OFF",-2.6314457459500131,-160.83416440970004,-3.9817830000000001,"ON",32231.120345269992,72314.243198034004,1778.6410000000001,null,0,0,0,0,1561.6938577213225,1561.6938577213225,0,0,0,0,1605.9391103276409,1605.9391103276409,0,0,0,0,216.94714227867757,0,0,0,0,172.70188967235913,213.95303555871172,169.70778295239327,null,null,1754.501442,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1561.6938577213225,0,0,0,0,12.804257556932953]
[0,0,0,0,1603.1260719491338,1603.1260719491338,1675.4767239999999,"2013-01-06T08:00:00",34,31,"OFF",-27.688690574089996,-73.058993676602014,-8.8484060000000007,"OFF",-6.9990958353599853,-109.19058095058001,-8.8484060000000007,"OFF",-0.43300713575000022,-46.444647297834003,-1.7696810000000001,"OFF",-2.1478436453600005,-158.64239131086001,-3.9817830000000001,"ON",33534.058830440001,72329.322365954009,1698.925,null,0,0,0,0,1589.2989291766444,1589.2989291766444,0,0,0,0,1637.0482498122381,1637.0482498122381,0,0,0,0,109.62607082335558,0,0,0,0,61.8767501877619,106.63196410338972,58.882643467796044,null,null,1675.4767239999999,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1589.2989291766444,0,0,0,0,13.827142772489424]
[0,0,0,0,1531.020390038728,{"$f":"SUM(A132:E132)","v":1531.020390038728},{"$f":"N132+R132+V132+Z132+AD132","v":1484.1260480000001},"2013-01-06T09:00:00",38,34,"OFF",-27.630032847569996,-72.363194347936002,-8.8484060000000007,"OFF",-5.4938981478150399,-111.32797279490001,-8.8484060000000007,"OFF",-0.67443197762500129,-33.398399859304,-1.7696810000000001,"OFF",-1.7114607985299983,-166.99199929652002,-4.5624589999999996,"ON",30199.918985250002,70700.980772277995,1508.155,null,0,0,0,0,1519.7299890718366,{"$f":"SUM(AF132:AJ132)","v":1519.7299890718366},0,0,0,0,1561.9649442042501,{"$f":"SUM(AL132:AP132)","v":1561.9649442042501},{"$f":"IF($K132=\"ON\",$N132-AF132,0)","v":0},{"$f":"IF($O132=\"ON\",$R132-AG132,0)","v":0},{"$f":"IF($S132=\"ON\",$V132-AH132,0)","v":0},{"$f":"IF($W132=\"ON\",$Z132-AI132,0)","v":0},{"$f":"IF($AA132=\"ON\",$AD132-AJ132,0)","v":-11.574989071836626},{"$f":"IF($K132=\"ON\",$N132-AL132,0)","v":0},{"$f":"IF($O132=\"ON\",$R132-AM132,0)","v":0},{"$f":"IF($S132=\"ON\",$V132-AN132,0)","v":0},{"$f":"IF($W132=\"ON\",$Z132-AO132,0)","v":0},{"$f":"IF($AA132=\"ON\",$AD132-AP132,0)","v":-53.809944204250087},{"$f":"SUM(AR132:AV132)+BN132","v":-11.066360298092818},{"$f":"SUM(AW132:BA132)+BN132","v":-53.301315430506278},null,null,{"$f":"N132+R132+V132+Z132+AD132","v":1484.1260480000001},null,28563.352800000052,{"$f":"19.5285952781395+42*-0.3035722016559+BH132*0.0000340867411548605+J132*0.0608468772796604","v":9.820988249508714},{"$f":"BH132*1000/(500*BI132)","v":5816.798080667475},{"$f":"0.00000128*BJ132^2+0*BJ132+24.024","v":67.332979086408727},{"$f":"0.094*BH132 + 3165.9","v":5850.8551632000053},{"$f":"0.00000128*BL132^2+0*BL132+24.024","v":67.841607860152536},{"$f":"BM132-BK132","v":0.50862877374380844},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF132:AJ132)","v":1519.7299890718366},{"$f":"A132-AF132","v":0},{"$f":"B132-AG132","v":0},{"$f":"C132-AH132","v":0},{"$f":"D132-AI132","v":0},{"$f":"E132-AJ132","v":11.290400966891411}]
[0,0,0,0,1528.3686757429323,1528.3686757429323,1659.711724,"2013-01-06T10:00:00",43,37,"OFF",-27.68286721746,-74.450592333934011,-8.8484060000000007,"OFF",-6.7299158108249335,-108.5447433969,-8.8484060000000007,"OFF",-0.12369290224999381,-33.398399859304,-1.7696810000000001,"OFF",-1.7220535105899906,-158.64239131086001,-3.9817830000000001,"ON",30073.879849140008,72402.961642908005,1683.16,null,0,0,0,0,1517.1689810478265,1517.1689810478265,0,0,0,0,1555.6902505680623,1555.6902505680623,0,0,0,0,165.99101895217359,0,0,0,0,127.46974943193777,165.90155470282232,127.3802851825865,null,null,1659.711724,null,{"$f":" -0.6251*I133^3 + 145.21*I133^2 - 8340.3*I133 + 170112","v":30272.564300000085},10.061790331327108,6017.3315688654902,70.370597388371493,6011.521044200008,70.281133139020227,-8.946424935126629E-2,null,null,null,null,null,null,null,null,null,1517.1689810478265,0,0,0,0,11.199694695105791]
[0,0,0,0,1539.6354488052725,1539.6354488052725,1544.5167239999998,"2013-01-06T11:00:00",48,39,"OFF",-27.530063393489993,-70.971595690604005,-8.8484060000000007,"OFF",-5.8121910893549886,-104.36997950824001,-8.8484060000000007,"OFF",-3.2370284399999968E-3,-46.444647297834003,-1.7696810000000001,"OFF",-2.4616725026600088,-164.80022619768002,-3.9817830000000001,"ON",30607.6489301,70680.880562274004,1567.9649999999999,null,0,0,0,0,1528.0490361019611,1528.0490361019611,0,0,0,0,1571.4353244128854,1571.4353244128854,0,0,0,0,39.915963898038854,0,0,0,0,-3.4703244128854749,34.356772614625214,-9.0295156962991143,null,null,1544.5167239999998,null,35210.380800000043,10.351798158792127,6802.7564409367269,83.259193849223834,6475.6757952000044,77.700002565810195,-5.5591912834136394,null,null,null,null,null,null,null,null,null,1528.0490361019611,0,0,0,0,11.586412703311453]
[0,0,0,0,1601.9611735788492,1601.9611735788492,1732.5737239999999,"2013-01-06T12:00:00",51,41,"OFF",-28.174571796329978,-70.275796361938006,-8.8484060000000007,"OFF",-6.0961970881399719,-107.1531286979,-8.8484060000000007,"OFF",-0.25684206956999983,-75.14639166260001,-1.7696810000000001,"OFF",-1.2324699531900083,-160.83416440970004,-3.9817830000000001,"ON",33481.550050979997,72362.079452010003,1756.0219999999999,null,0,0,0,0,1588.1760389712094,1588.1760389712094,0,0,0,0,1635.7018642251792,1635.7018642251792,0,0,0,0,167.8459610287905,0,0,0,0,120.32013577482076,157.54010123833297,110.01427598436321,null,null,1732.5737239999999,null,39527.769900000014,10.620657638067961,7443.5635244129089,94.944496565722019,6881.5103706000009,84.638636775264473,-10.305859790457546,null,null,null,null,null,null,null,null,null,1588.1760389712094,0,0,0,0,13.785134607639748]
[0,0,0,0,1619.7670316882234,1619.7670316882234,1770.1064617,"2013-01-06T13:00:00",53,41,"OFF",-27.28139816038,-73.058993676602014,-8.8484060000000007,"OFF",-6.4992192762600203,-105.06578685774001,-8.8484060000000007,"OFF",-0.16607547878400017,-46.444647297834003,-0.4009433,"OFF",-1.9619968837700061,-164.80022619768002,-3.9817830000000001,"ON",34279.591010850017,71080.983824695999,1792.1859999999999,null,0,0,0,0,1605.3363131835354,1605.3363131835354,0,0,0,0,1658.3507905014199,1658.3507905014199,0,0,0,0,186.84968681646455,0,0,0,0,133.83520949858007,171.40657691518012,118.39209959729564,null,null,1770.1064617,null,42907.977300000086,10.735877892761508,7993.3802766013387,105.8084841553399,7199.249866200008,90.365374254055467,-15.44310990128443,null,null,null,null,null,null,null,null,null,1605.3363131835354,0,0,0,0,14.430718504688002]
[0,0,0,0,1590.6957065322817,1590.6957065322817,1746.478329,"2013-01-06T14:00:00",55,42,"OFF",-28.118462579445012,-74.450592333934011,-8.8484060000000007,"OFF",-7.0918680911999878,-107.1531286979,-8.8484060000000007,"OFF",0.10239036587499727,-46.444647297834003,-3.2905009999999999,"OFF",-2.3701324984399923,-158.64239131086001,-2.3503579999999999,"ON",32971.546041800015,72449.370188432003,1769.816,null,0,0,0,0,1577.3151510231642,1577.3151510231642,0,0,0,0,1623.2421131544409,1623.2421131544409,0,0,0,0,192.50084897683587,0,0,0,0,146.57388684555917,172.10999691347001,126.18303478219333,null,null,1746.478329,null,46654.737500000047,10.9244396151479,8541.3511619045948,117.4059899788403,7551.4453250000042,97.015137915474455,-20.390852063365841,null,null,null,null,null,null,null,null,null,1577.3151510231642,0,0,0,0,13.380555509117585]
[0,0,0,0,1741.4322523790308,1741.4322523790308,1809.8998867,"2013-01-06T15:00:00",57,43,"OFF",-27.972271162260011,-71.046012988456013,-8.8484060000000007,"OFF",-6.477448490174992,-106.45732134840001,-8.8484060000000007,"OFF",-0.68754843762499573,-62.100144224070007,-0.4009433,"OFF",-1.9858963609799907,-166.99199929652002,-2.3503579999999999,"ON",39492.273213119995,71408.209789394008,1830.348,null,0,0,0,0,1722.4066917679625,1722.4066917679625,0,0,0,0,1791.2234270734602,1791.2234270734602,0,0,0,0,107.9413082320375,0,0,0,0,39.124572926539713,82.034037097544655,13.217301792046868,null,null,1809.8998867,null,50738.045700000075,11.124473162096482,9121.8783956215957,130.53109179457027,7935.2762958000076,104.62382066007743,-25.907271134492845,null,null,null,null,null,null,null,null,null,1722.4066917679625,0,0,0,0,19.025560611068386]
[0,0,0,0,1690.4947710976805,1690.4947710976805,1807.6207239999999,"2013-01-06T16:00:00",56,43,"OFF",-27.718218584730003,-71.592977721418009,-8.8484060000000007,"OFF",-6.5483196888200137,-106.32329321226001,-8.8484060000000007,"OFF",3.3766098272999E-2,-46.444647297834003,-1.7696810000000001,"OFF",-2.2095817656499945,-158.64239131086001,-3.9817830000000001,"ON",37358.140159649985,72157.516101674017,1831.069,null,0,0,0,0,1673.4299686531956,1673.4299686531956,0,0,0,0,1732.8899043906597,1732.8899043906597,0,0,0,0,157.63903134680436,0,0,0,0,98.179095609340266,135.10466939058387,75.644733653119758,null,null,1807.6207239999999,null,48656.198400000052,11.053509772057437,8803.7554411902365,123.23182063140698,7739.5826496000045,100.69745867518647,-22.534361956220508,null,null,null,null,null,null,null,null,null,1673.4299686531956,0,0,0,0,17.06480244448494]
[0,0,0,0,1659.2350292424424,1659.2350292424424,1834.7964010000001,"2013-01-06T17:00:00",54,42,"OFF",-27.57001016700001,-69.579997033272008,-8.8484060000000007,"OFF",-6.864422086615007,-105.19989520222002,-8.8484060000000007,"OFF",-1.3104748874998998E-2,-33.398399859304,-1.7696810000000001,"OFF",-2.7632222459799953,-160.83416440970004,-3.401106,"ON",36014.865534140015,71544.916884090009,1857.664,null,0,0,0,0,1643.3476979995874,1643.3476979995874,0,0,0,0,1700.4082545488457,1700.4082545488457,0,0,0,0,214.31630200041263,0,0,0,0,157.25574545115433,196.9637901942524,139.90323364499409,null,null,1834.7964010000001,null,44737.413600000087,10.859084291658576,8239.6291249650221,110.92510478972397,7371.2168784000078,93.572592983563723,-17.352511806160251,null,null,null,null,null,null,null,null,null,1643.3476979995874,0,0,0,0,15.887331242854998]
[0,0,0,0,1709.6491531444706,1709.6491531444706,1772.4217239999998,"2013-01-06T18:00:00",48,38,"OFF",-26.535824061529997,-73.058993676602014,-8.8484060000000007,"OFF",-7.3148371901849947,-107.8489360474,-8.8484060000000007,"OFF",6.4176965000000211E-2,-46.444647297834003,-1.7696810000000001,"OFF",-2.5571123113200094,-160.83416440970004,-3.9817830000000001,"ON",38168.374038479989,71876.995453358002,1795.87,null,0,0,0,0,1691.8529834667877,1691.8529834667877,0,0,0,0,1754.7393744332728,1754.7393744332728,0,0,0,0,104.0170165332122,0,0,0,0,41.130625566727076,97.755279508483056,34.868888541997933,null,null,1772.4217239999998,null,35210.380800000043,10.290951281512466,6842.9788144571121,83.961739590539338,6475.6757952000044,77.700002565810195,-6.2617370247291433,null,null,null,null,null,null,null,null,null,1691.8529834667877,0,0,0,0,17.796169677682883]
[0,0,0,0,1663.3325531746268,1663.3325531746268,1798.297724,"2013-01-06T19:00:00",47,38,"OFF",-26.052511811270023,-70.275796361938006,-8.8484060000000007,"OFF",-6.9561263813599714,-102.28255745974,-8.8484060000000007,"OFF",0.3466961445000058,-75.14639166260001,-1.7696810000000001,"OFF",-3.1769108216450066,-160.83416440970004,-3.9817830000000001,"ON",36192.465628639991,71791.012112878001,1821.7460000000001,null,0,0,0,0,1647.292046850062,1647.292046850062,0,0,0,0,1704.2064576427354,1704.2064576427354,0,0,0,0,174.45395314993812,0,0,0,0,117.53954235726474,169.94004083986212,113.02563004718874,null,null,1798.297724,null,33987.03270000004,10.249251331485475,6632.1005507187874,80.324489875000893,6360.681073800004,75.810577564924898,-4.5139123100759946,null,null,null,null,null,null,null,null,null,1647.292046850062,0,0,0,0,16.040506324564831]
[0,0,0,0,1663.2504540273721,1663.2504540273721,1754.470724,"2013-01-06T20:00:00",45,37,"OFF",-25.646009898459994,-68.884197704605995,-8.8484060000000007,"OFF",-6.5390712974550036,-111.37794259072001,-8.8484060000000007,"OFF",-0.35543264374999961,-33.398399859304,-1.7696810000000001,"OFF",-2.4703153125000004,-158.64239131086001,-3.9817830000000001,"ON",36188.911772149993,71385.494787506002,1777.9190000000001,null,0,0,0,0,1647.2130202746307,1647.2130202746307,0,0,0,0,1705.2678500359077,1705.2678500359077,0,0,0,0,130.70597972536939,0,0,0,0,72.651149964092383,128.46488023924525,70.410050477968255,null,null,1754.470724,null,31886.51250000007,10.11680456585786,6303.6727244115227,74.886450965106931,6163.2321750000065,72.645351478982803,-2.2410994861241278,null,null,null,null,null,null,null,null,null,1647.2130202746307,0,0,0,0,16.037433752741435]
[0,0,0,0,1640.0705078047167,1640.0705078047167,1773.4167239999999,"2013-01-06T21:00:00",45,37,"OFF",-25.305066860290008,-72.363194347936002,-8.8484060000000007,"OFF",-7.8119468895299828,-108.49477360108,-8.8484060000000007,"OFF",0.10535328049999744,-46.444647297834003,-1.7696810000000001,"OFF",-2.1134568562100018,-158.64239131086001,-3.9817830000000001,"ON",35177.915869679993,72192.486937914,1796.865,null,0,0,0,0,1624.8947769929919,1624.8947769929919,0,0,0,0,1677.6695726123332,1677.6695726123332,0,0,0,0,171.97022300700814,0,0,0,0,119.19542738766677,169.729123520884,116.95432790154264,null,null,1773.4167239999999,null,31886.51250000007,10.11680456585786,6303.6727244115227,74.886450965106931,6163.2321750000065,72.645351478982803,-2.2410994861241278,null,null,null,null,null,null,null,null,null,1624.8947769929919,0,0,0,0,15.175730811724861]
[0,0,0,0,1626.3396231893335,1626.3396231893335,1383.2627239999999,"2013-01-06T22:00:00",42,35,"OFF",-25.278637780200011,-73.133410974454009,-8.8484060000000007,"OFF",-7.4415398369399615,-105.11575665356001,-8.8484060000000007,"OFF",4.0240885954499879E-2,-46.444647297834003,-1.7696810000000001,"OFF",-1.2233791928399873,-164.80022619768002,-3.9817830000000001,"ON",34571.732614799999,70985.239129238005,1406.711,null,0,0,0,0,1611.6687507452111,1611.6687507452111,0,0,0,0,1665.819578282448,1665.819578282448,0,0,0,0,-204.95775074521111,0,0,0,0,-259.10857828244798,-205.35715220829687,-259.5079797455337,null,null,1383.2627239999999,null,29657.431200000021,9.9191286940122971,5979.8460358524817,69.794955024000814,5953.6985328000019,69.395553560915062,-0.39940146308575208,null,null,null,null,null,null,null,null,null,1611.6687507452111,0,0,0,0,14.670872444122324]
[0,0,0,0,1590.18418713489,1590.18418713489,1697.6187239999999,"2013-01-06T23:00:00",43,36,"OFF",-25.332154691130015,-68.113973057254015,-8.8484060000000007,"OFF",-7.2097256232500282,-105.01573685358001,-8.8484060000000007,"OFF",9.2740398875004793E-2,-46.444647297834003,-1.7696810000000001,"OFF",-2.2296077884499854,-164.80022619768002,-3.9817830000000001,"ON",32948.293192500001,72235.566837328006,1721.067,null,0,0,0,0,1576.8219294009184,1576.8219294009184,0,0,0,0,1623.1807498631549,1623.1807498631549,0,0,0,0,144.2450705990816,0,0,0,0,97.886250136845092,143.58993482562747,97.231114363390958,null,null,1697.6187239999999,null,30272.564300000085,10.000943454047448,6053.941698420178,70.936268912474361,6011.521044200008,70.281133139020227,-0.6551357734541341,null,null,null,null,null,null,null,null,null,1576.8219294009184,0,0,0,0,13.362257733971546]
[0,0,0,0,1683.1845118187139,1683.1845118187139,1685.375401,"2013-01-07",38,33,"OFF",-25.519318954219976,-70.971595690604005,-8.8484060000000007,"OFF",-7.02884491364998,-108.59479340106,-8.8484060000000007,"OFF",6.474056879999994E-4,-33.398399859304,-1.7696810000000001,"OFF",-3.7547404229999857,-160.83416440970004,-3.401106,"ON",37046.376263749997,71033.925591617997,1708.2429999999999,null,0,0,0,0,1666.3968837505165,1666.3968837505165,0,0,0,0,1728.2288105484995,1728.2288105484995,0,0,0,0,41.84611624948343,0,0,0,0,-19.985810548499558,41.813066312948109,-20.018860485034878,null,null,1685.375401,null,28563.352800000052,9.7601413722290538,5853.0612848032251,67.874657796687856,5850.8551632000053,67.841607860152536,-3.3049936535320512E-2,null,null,null,null,null,null,null,null,null,1666.3968837505165,0,0,0,0,16.787628068197364]
[0,0,0,0,1535.6020147501347,1535.6020147501347,1599.490401,"2013-01-07T01:00:00",34,31,"OFF",-26.125343294190017,-73.754793005267999,-8.8484060000000007,"OFF",-7.8261025991499844,-106.45732134840001,-8.8484060000000007,"OFF",-0.78064017024999544,-33.398399859304,-1.7696810000000001,"OFF",-3.5117669652750125,-166.99199929652002,-3.401106,"ON",30417.088400819997,72505.884984796008,1622.3579999999999,null,0,0,0,0,1524.1544399973166,1524.1544399973166,0,0,0,0,1563.3262030719627,1563.3262030719627,0,0,0,0,98.203560002683389,0,0,0,0,59.031796928037238,95.209453282717533,56.037690208071382,null,null,1599.490401,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1524.1544399973166,0,0,0,0,11.447574752818127]
[0,0,0,0,1550.2833867252416,1550.2833867252416,1506.1097239999999,"2013-01-07T02:00:00",33,30,"OFF",-26.013092166390017,-73.058993676602014,-8.8484060000000007,"OFF",-7.0830971504299667,-109.05647260610002,-8.8484060000000007,"OFF",6.1039212509999607E-2,-75.14639166260001,-1.7696810000000001,"OFF",-2.0377795700500019,-158.64239131086001,-3.9817830000000001,"ON",31107.942465239998,70940.346521340005,1529.558,null,0,0,0,0,1538.3283664381374,1538.3283664381374,0,0,0,0,1582.5363853431465,1582.5363853431465,0,0,0,0,-8.7703664381374438,0,0,0,0,-52.978385343146556,-13.477493213303447,-57.685512118312559,null,null,1506.1097239999999,null,30551.57130000004,9.645372629758878,6334.9696217519358,75.392755338905431,6037.7477022000039,70.685628563739428,-4.7071267751660031,null,null,null,null,null,null,null,null,null,1538.3283664381374,0,0,0,0,11.955020287104162]
[0,0,0,0,1587.7049121162443,1587.7049121162443,1800.902149,"2013-01-07T03:00:00",35,33,"OFF",-26.409899668770006,-72.363194347936002,-8.8484060000000007,"OFF",-7.5502821326100023,-108.67885174138,-8.8484060000000007,"OFF",-0.18502406387499776,-75.14639166260001,-1.7696810000000001,"OFF",-2.1231273172200003,-160.83416440970004,-2.3503579999999999,"ON",32835.470493374989,72621.360931894014,1822.7190000000001,null,0,0,0,0,1574.43125148837,1574.43125148837,0,0,0,0,1619.5975371844183,1619.5975371844183,0,0,0,0,248.28774851163007,0,0,0,0,203.12146281558171,247.2677041260622,202.10141843001384,null,null,1800.902149,null,29282.587499999994,9.7846577392775451,5985.4086428499004,69.880149276034928,5918.4632249999995,68.860104890467056,-1.0200443855678714,null,null,null,null,null,null,null,null,null,1574.43125148837,0,0,0,0,13.273660627874278]
[0,0,0,0,1556.2985403516068,1556.2985403516068,1587.7641489999999,"2013-01-07T04:00:00",33,30,"OFF",-27.056373457860012,-70.971595690604005,-8.8484060000000007,"OFF",-7.5788630867249775,-110.63216544540002,-8.8484060000000007,"OFF",-7.1320751249996039E-2,-62.100144224070007,-1.7696810000000001,"OFF",-2.3166682875700033,-160.83416440970004,-2.3503579999999999,"ON",31388.81442925,71414.401873242008,1609.5809999999999,null,0,0,0,0,1544.1339697535045,1544.1339697535045,0,0,0,0,1588.0863495700789,1588.0863495700789,0,0,0,0,65.447030246495387,0,0,0,0,21.494650429920966,60.739903471329384,16.787523654754963,null,null,1587.7641489999999,null,30551.57130000004,9.645372629758878,6334.9696217519358,75.392755338905431,6037.7477022000039,70.685628563739428,-4.7071267751660031,null,null,null,null,null,null,null,null,null,1544.1339697535045,0,0,0,0,12.164570598102273]
[0,0,0,0,1496.9558481178638,1496.9558481178638,1564.4257239999999,"2013-01-07T05:00:00",31,29,"OFF",-27.290879438039997,-71.046012988456013,-8.8484060000000007,"OFF",-6.8843588412599486,-107.1531286979,-8.8484060000000007,"OFF",0.3913389529999966,-75.14639166260001,-1.7696810000000001,"OFF",-2.7520761832899963,-160.83416440970004,-3.9817830000000001,"ON",28560.824577039995,70820.948386415999,1587.874,null,0,0,0,0,1486.8156916857822,1486.8156916857822,0,0,0,0,1524.5214885768185,1524.5214885768185,0,0,0,0,101.05830831421781,0,0,0,0,63.352511423181568,92.552472450788002,54.846675559751759,null,null,1564.4257239999999,null,32487.155900000012,9.650503523722751,6732.738000694053,82.046094062066885,6219.6926546000013,73.540258198637076,-8.5058358634298088,null,null,null,null,null,null,null,null,null,1486.8156916857822,0,0,0,0,10.14015643208154]
[0,0,0,0,1549.9954439114606,1549.9954439114606,1837.172724,"2013-01-07T06:00:00",29,27,"OFF",-26.86968350766001,-72.984576378750006,-8.8484060000000007,"OFF",-8.6346593576100066,-112.71958749390001,-8.8484060000000007,"OFF",9.1062772442999651E-2,-46.444647297834003,-1.7696810000000001,"OFF",-3.1629785511099988,-160.83416440970004,-3.9817830000000001,"ON",31094.465791039998,71135.164558366014,1860.6210000000001,null,0,0,0,0,1538.0504309857686,1538.0504309857686,0,0,0,0,1581.8033898275262,1581.8033898275262,0,0,0,0,322.57056901423152,0,0,0,0,278.81761017247391,307.84812468838129,264.09516584662367,null,null,1837.172724,null,35119.346100000024,9.61853255518119,7302.4332762864915,92.280680645908816,6467.118533400002,77.558236320058612,-14.722444325850205,null,null,null,null,null,null,null,null,null,1538.0504309857686,0,0,0,0,11.945012925692026]
[0,0,0,0,1590.0351792279648,1590.0351792279648,1639.3027239999999,"2013-01-07T07:00:00",29,27,"OFF",-27.338429527919992,-69.579997033272008,-8.8484060000000007,"OFF",-8.6299370116399778,-105.06578685774001,-8.8484060000000007,"OFF",-0.10606044084599951,-75.14639166260001,-1.7696810000000001,"OFF",-3.5391252293599975,-158.64239131086001,-3.9817830000000001,"ON",32941.51795767001,71947.105563352001,1662.751,null,0,0,0,0,1576.6782505244587,1576.6782505244587,0,0,0,0,1623.6905371603541,1623.6905371603541,0,0,0,0,86.072749475541286,0,0,0,0,39.060462839645879,71.350305149691081,24.338018513795674,null,null,1639.3027239999999,null,35119.346100000024,9.61853255518119,7302.4332762864915,92.280680645908816,6467.118533400002,77.558236320058612,-14.722444325850205,null,null,null,null,null,null,null,null,null,1576.6782505244587,0,0,0,0,13.356928703506128]
[0,0,0,0,1616.685457440982,1616.685457440982,1491.2919039999999,"2013-01-07T08:00:00",31,29,"OFF",-27.448220200310022,-69.579997033272008,-8.8484060000000007,"OFF",-7.9813849569850008,-108.59479340106,-8.8484060000000007,"OFF",-3.7616133500007191E-2,-46.444647297834003,-3.2905009999999999,"OFF",-3.0244300933700017,-166.99199929652002,-3.9817830000000001,"ON",34142.171941034991,71752.127109645997,1516.261,null,0,0,0,0,1602.3669947638073,1602.3669947638073,0,0,0,0,1653.2595549153687,1653.2595549153687,0,0,0,0,-86.105994763807303,0,0,0,0,-136.99855491536869,-94.611830627237111,-145.50439077879849,null,null,1491.2919039999999,null,32487.155900000012,9.650503523722751,6732.738000694053,82.046094062066885,6219.6926546000013,73.540258198637076,-8.5058358634298088,null,null,null,null,null,null,null,null,null,1602.3669947638073,0,0,0,0,14.318462677174693]
[0,0,0,0,1702.037380391778,1702.037380391778,1875.5059039999999,"2013-01-07T09:00:00",38,34,"OFF",-27.760689218700008,-70.971595690604005,-8.8484060000000007,"OFF",-9.0857789423249837,-109.19058095058001,-8.8484060000000007,"OFF",-0.51917759349999992,-62.100144224070007,-3.2905009999999999,"OFF",-2.6204841334699975,-160.83416440970004,-3.9817830000000001,"ON",37847.534664524981,72668.699894162011,1900.4749999999999,null,0,0,0,0,1684.5327263472745,1684.5327263472745,0,0,0,0,1743.9797749366089,1743.9797749366089,0,0,0,0,215.94227365272536,0,0,0,0,156.49522506339099,216.45090242646916,157.00385383713478,null,null,1875.5059039999999,null,28563.352800000052,9.820988249508714,5816.798080667475,67.332979086408727,5850.8551632000053,67.841607860152536,0.50862877374380844,null,null,null,null,null,null,null,null,null,1684.5327263472745,0,0,0,0,17.504654044503468]
[0,0,0,0,1673.5032132720582,1673.5032132720582,1519.9843000000001,"2013-01-07T10:00:00",40,36,"OFF",-27.664738396820013,-71.667395019270003,-8.8484060000000007,"OFF",-7.506234900239976,-105.76159420724001,-8.8484060000000007,"OFF",-0.15266834377799968,-62.100144224070007,-1.7696810000000001,"OFF",-3.1958897385799978,-158.64239131086001,-5.6132070000000001,"ON",36631.287878759991,71326.429365930017,1545.0640000000001,null,0,0,0,0,1657.0809665384586,1657.0809665384586,0,0,0,0,1716.7042173554162,1716.7042173554162,0,0,0,0,-112.01696653845852,0,0,0,0,-171.6402173554161,-110.79194013140027,-170.41519094835786,null,null,1519.9843000000001,null,28829.600000000006,9.9517575034576407,5793.8710805570663,66.992245885587849,5875.8824000000004,68.217272292646101,1.2250264070582517,null,null,null,null,null,null,null,null,null,1657.0809665384586,0,0,0,0,16.42224673359965]
[0,0,0,0,1664.8424363917595,1664.8424363917595,1928.9217239999998,"2013-01-07T11:00:00",49,41,"OFF",-28.42833183974999,-72.363194347936002,-8.8484060000000007,"OFF",-6.7487299198799997,-107.20317870206,-8.8484060000000007,"OFF",0.26738840600000424,-62.100144224070007,-1.7696810000000001,"OFF",-2.6736848440399963,-160.83416440970004,-3.9817830000000001,"ON",36257.791162409994,72533.613007934007,1952.37,null,0,0,0,0,1648.7453969515914,1648.7453969515914,0,0,0,0,1703.7785384837093,1703.7785384837093,0,0,0,0,303.62460304840852,0,0,0,0,248.59146151629056,297.60317876853026,242.57003723641228,null,null,1928.9217239999998,null,36544.120100000058,10.518954739638612,6948.241722590692,85.819920685504087,6601.047289400005,79.798496405625798,-6.0214242798782891,null,null,null,null,null,null,null,null,null,1648.7453969515914,0,0,0,0,16.097039440168146]
[0,0,0,0,1668.6621553624886,1668.6621553624886,1705.0604010000002,"2013-01-07T12:00:00",51,42,"OFF",-27.731781529829998,-70.971595690604005,-8.8484060000000007,"OFF",-8.3584498085400245,-109.19058095058001,-8.8484060000000007,"OFF",-1.0451827728750034,-33.398399859304,-1.7696810000000001,"OFF",-1.5483014127699966,-158.64239131086001,-3.401106,"ON",36422.77093536,71032.177049806007,1727.9280000000001,null,0,0,0,0,1652.4218822843063,1652.4218822843063,0,0,0,0,1712.2392198541322,1712.2392198541322,0,0,0,0,75.50611771569379,0,0,0,0,15.688780145867895,66.005949629311587,6.1886120594856919,null,null,1705.0604010000002,null,39527.769900000014,10.681504515347623,7401.1614830485532,94.138804861646676,6881.5103706000009,84.638636775264473,-9.5001680863822031,null,null,null,null,null,null,null,null,null,1652.4218822843063,0,0,0,0,16.240273078182327]
[0,0,0,0,1662.8308996633348,1662.8308996633348,1910.232724,"2013-01-07T13:00:00",54,44,"OFF",-27.414727742609983,-73.058993676602014,-8.8484060000000007,"OFF",-8.9167475247299706,-108.41063505242002,-8.8484060000000007,"OFF",-0.23038125099999898,-62.100144224070007,-1.7696810000000001,"OFF",-3.6121148124600055,-158.64239131086001,-3.9817830000000001,"ON",36170.747442080014,72454.198730500008,1933.681,null,0,0,0,0,1646.8091655521237,1646.8091655521237,0,0,0,0,1701.8039910487553,1701.8039910487553,0,0,0,0,286.87183444787638,0,0,0,0,231.87700895124476,271.4348010381093,216.43997554147768,null,null,1910.232724,null,44737.413600000087,10.980778046217896,8148.3139740555944,109.00962639333079,7371.2168784000078,93.572592983563723,-15.437033409767068,null,null,null,null,null,null,null,null,null,1646.8091655521237,0,0,0,0,16.021734111211117]
[0,0,0,0,1731.1061750207823,1731.1061750207823,1812.817724,"2013-01-07T14:00:00",54,43,"OFF",-27.35970473591998,-72.363194347936002,-8.8484060000000007,"OFF",-8.5580255369999847,-101.02505110522002,-8.8484060000000007,"OFF",-0.1065990611520008,-75.14639166260001,-1.7696810000000001,"OFF",-2.3764301556100063,-164.80022619768002,-3.9817830000000001,"ON",39064.893215039985,71566.557094222007,1836.2660000000001,null,0,0,0,0,1712.4821528042116,1712.4821528042116,0,0,0,0,1779.3197856365655,1779.3197856365655,0,0,0,0,123.78384719578844,0,0,0,0,56.946214363434592,107.39707942349278,40.559446591138936,null,null,1812.817724,null,44737.413600000087,10.919931168938236,8193.7171412317584,109.95936075585938,7371.2168784000078,93.572592983563723,-16.386767772295656,null,null,null,null,null,null,null,null,null,1712.4821528042116,0,0,0,0,18.624022216570665]
[0,0,0,0,2105.6708325954346,2105.6708325954346,2681.815826,"2013-01-07T15:00:00",55,44,"OFF",-27.091045543659977,-69.579997033272008,-8.8484060000000007,"OFF",-7.2625055465599813,-102.14844911526001,-8.8484060000000007,"OFF",0.12249836750000574,-46.444647297834003,-1.7696810000000001,"OFF",-2.7505478815500166,-158.64239131086001,-1.7696810000000001,"ON",53181.040592120007,72442.977583734013,2703.0520000000001,null,0,0,0,0,2071.3936117092394,2071.3936117092394,0,0,0,0,2189.2985809188194,2189.2985809188194,0,0,0,0,631.65838829076074,0,0,0,0,513.75341908118071,613.31375579383473,495.4087865842547,null,null,2681.815826,null,46654.737500000047,11.046133369707222,8447.2522535252756,115.35977041240044,7551.4453250000042,97.015137915474455,-18.344632496925982,null,null,null,null,null,null,null,null,null,2071.3936117092394,0,0,0,0,34.277220886195209]
[0,0,0,0,0,0,3501.6911300000002,"2013-01-07T16:00:00",54,43,"OFF",-26.565863095729984,-70.971595690604005,-8.8484060000000007,"check",-5095.9692829199976,34668.346527358008,1008.683,"OFF",0.2543296099079998,-46.444647297834003,-1.7696810000000001,"OFF",-3.977924346494996,-158.64239131086001,-3.9817830000000001,"check",17990.490914949998,32039.486100522001,2507.6080000000002,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-16.386767772295656,-16.386767772295656,null,null,3501.6911300000002,null,44737.413600000087,10.919931168938236,8193.7171412317584,109.95936075585938,7371.2168784000078,93.572592983563723,-16.386767772295656,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,2118.7138720650878,0,0,0,2118.7138720650878,2243.6387719999993,"2013-01-07T17:00:00",52,42,"OFF",-26.013622325760014,-70.971595690604005,-8.8484060000000007,"ON",44034.349347450006,77154.038496136011,2260.5889999999999,"OFF",2.0813128461250043,-33.398399859304,-1.7696810000000001,"OFF",-2.7430908230600086,-166.99199929652002,-2.3503579999999999,"OFF",-0.10867924480001818,-117.59015873206,-3.9817830000000001,null,0,2094.152646443365,0,0,0,2094.152646443365,0,2159.7866574726409,0,0,0,2159.7866574726409,0,166.43635355663491,0,0,0,0,100.80234252735909,0,0,0,154.52986980895582,88.895858779680012,null,null,2243.6387719999993,null,41170.179200000071,10.73748889602706,7668.4929965763786,99.295404593332435,7035.8968448000069,87.388920845653359,-11.906483747679076,null,null,null,null,null,null,null,null,null,2094.152646443365,0,24.56122562172277,0,0,0]
[0,1833.2836833378115,0,0,0,1833.2836833378115,1851.7444860000001,"2013-01-07T18:00:00",49,41,"OFF",-25.875413255790001,-73.754793005267999,-8.8484060000000007,"ON",36717.425384150003,76124.035077192006,1870.575,"OFF",0.54847882824999739,-75.14639166260001,-1.7696810000000001,"OFF",-3.0473019194099971,-160.83416440970004,-3.9817830000000001,"OFF",-1.3913915032500073,-117.59015873206,-4.2306439999999998,null,0,1816.2478597741042,0,0,0,1816.2478597741042,0,1864.4557744479087,0,0,0,1864.4557744479087,0,54.327140225895846,0,0,0,0,6.1192255520913932,0,0,0,48.305715946017557,9.7801272213104085E-2,null,null,1851.7444860000001,null,36544.120100000058,10.518954739638612,6948.241722590692,85.819920685504087,6601.047289400005,79.798496405625798,-6.0214242798782891,null,null,null,null,null,null,null,null,null,1816.2478597741042,0,17.035823563707254,0,0,0]
[0,1824.2058876842148,0,0,0,1824.2058876842148,2123.4591629999995,"2013-01-07T19:00:00",47,40,"OFF",-25.494640220609998,-71.046012988456013,-8.8484060000000007,"ON",36467.166976900007,77311.270905038007,2141.7089999999998,"OFF",-0.63354844025000545,-46.444647297834003,-1.7696810000000001,"OFF",-3.5740653691400039,-164.80022619768002,-3.401106,"OFF",-1.3448207487400057,-121.06919547956002,-4.2306439999999998,null,0,1807.4013255572172,0,0,0,1807.4013255572172,0,1851.8845982452876,0,0,0,1851.8845982452876,0,334.30767444278263,0,0,0,0,289.8244017547122,0,0,0,331.107281838414,286.62400915034357,null,null,2123.4591629999995,null,33987.03270000004,10.370945086044795,6554.2787890629543,79.0109701692935,6360.681073800004,75.810577564924898,-3.2003926043686022,null,null,null,null,null,null,null,null,null,1807.4013255572172,0,16.804562126997553,0,0,0]
[0,1835.8076157108967,0,0,0,1835.8076157108967,1913.3093470000001,"2013-01-07T20:00:00",48,41,"OFF",-25.138692770870016,-70.897178392752011,-8.8484060000000007,"ON",36786.786414105009,76557.817821580014,1931.8910000000001,"OFF",-1.1781391750003329E-2,-46.444647297834003,-1.7696810000000001,"OFF",-3.7219680875300125,-164.80022619768002,-3.9817830000000001,"OFF",-1.6063301815399995,-121.06919547956002,-3.9817830000000001,null,0,1818.7073949674723,0,0,0,1818.7073949674723,0,1865.9451033698479,0,0,0,1865.9451033698479,0,113.18360503252779,0,0,0,0,65.94589663015222,0,0,0,108.99294954145198,61.755241139076404,null,null,1913.3093470000001,null,35210.380800000043,10.473491913351447,6723.713751115688,81.890658056886011,6475.6757952000044,77.700002565810195,-4.190655491075816,null,null,null,null,null,null,null,null,null,1818.7073949674723,0,17.100220743424416,0,0,0]
[0,1816.8044338379102,0,0,0,1816.8044338379102,2028.1670239999999,"2013-01-07T21:00:00",46,40,"OFF",-25.534312554880003,-70.971595690604005,-8.8484060000000007,"ON",36262.200146445022,77241.626003416008,2046.1679999999999,"OFF",7.9813977462001473E-2,-46.444647297834003,-1.7696810000000001,"OFF",-2.5808800383800086,-160.83416440970004,-3.401106,"OFF",-2.0775843210849985,-120.37338813006001,-3.9817830000000001,null,0,1800.1880128564512,0,0,0,1800.1880128564512,0,1844.3481057366705,0,0,0,1844.3481057366705,0,245.97998714354867,0,0,0,0,201.81989426332939,0,0,0,244.24903044883129,200.08893756861201,null,null,2028.1670239999999,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,1800.1880128564512,0,16.616420981458987,0,0,0]
[0,1789.1595911365296,0,0,0,1789.1595911365296,1887.737486,"2013-01-07T22:00:00",46,40,"OFF",-25.238348584330009,-70.945503917602011,-8.8484060000000007,"ON",35489.141693429992,77264.581630324014,1906.568,"OFF",-4.1691605000002685E-3,-75.14639166260001,-1.7696810000000001,"OFF",-3.2693272721899982,-160.83416440970004,-3.9817830000000001,"OFF",-2.8889575343299922,-120.37338813006001,-4.2306439999999998,null,0,1773.2425295416592,0,0,0,1773.2425295416592,0,1815.4865074410095,0,0,0,1815.4865074410095,0,133.32547045834076,0,0,0,0,91.081492558990476,0,0,0,131.59451376362338,89.350535864273098,null,null,1887.737486,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,1773.2425295416592,0,15.917061594870347,0,0,0]
[0,1739.9045333368258,0,0,0,1739.9045333368258,1836.2243470000001,"2013-01-07T23:00:00",45,39,"OFF",-25.945089561990009,-70.997687463605999,-8.8484060000000007,"ON",34081.111000440003,76893.393474472017,1854.806,"OFF",-1.9191604454996359E-3,-33.398399859304,-1.7696810000000001,"OFF",-3.1973653402599984,-166.99199929652002,-3.9817830000000001,"OFF",-2.6584811202600149,-116.89443159090001,-3.9817830000000001,null,0,1725.2198839560458,0,0,0,1725.2198839560458,0,1765.0198068325674,0,0,0,1765.0198068325674,0,129.58611604395423,0,0,0,0,89.786193167432657,0,0,0,128.54692287234263,88.746999995821056,null,null,1836.2243470000001,null,31886.51250000007,10.238498320417181,6228.747908550873,73.684544650594404,6163.2321750000065,72.645351478982803,-1.0391931716116005,null,null,null,null,null,null,null,null,null,1725.2198839560458,0,14.684649380780002,0,0,0]
[0,1775.1863562406729,0,0,0,1775.1863562406729,1818.223532,"2013-01-08",46,40,"OFF",-26.06958663071001,-70.971595690604005,-8.8484060000000007,"ON",35093.777246500009,76715.435230514006,1837.1369999999999,"OFF",7.120364000000047E-2,-46.444647297834003,-1.7696810000000001,"OFF",-4.2609813308699955,-166.99199929652002,-2.3503579999999999,"OFF",-2.7275094218399953,-117.59457019076001,-5.9450229999999999,null,0,1759.6207290867665,0,0,0,1759.6207290867665,0,1802.2362167933256,0,0,0,1802.2362167933256,0,77.516270913233484,0,0,0,0,34.900783206674305,0,0,0,75.785314218516106,33.169826511956927,null,null,1818.223532,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,1759.6207290867665,0,15.565627153906462,0,0,0]
[0,1656.4630766586999,0,0,0,1656.4630766586999,1805.1754860000001,"2013-01-08T01:00:00",45,39,"OFF",-26.556113535750008,-71.667395019270003,-8.8484060000000007,"ON",31597.657434969995,77030.333173354011,1824.0060000000001,"OFF",2.143135874999582E-2,-62.100144224070007,-1.7696810000000001,"OFF",-3.9530455246150149,-164.80022619768002,-3.9817830000000001,"OFF",-3.4042499848700003,-114.1067907342,-4.2306439999999998,null,0,1643.8231392994103,0,0,0,1643.8231392994103,0,1677.8113868565247,0,0,0,1677.8113868565247,0,180.1828607005898,0,0,0,0,146.19461314347541,0,0,0,179.1436675289782,145.15541997186381,null,null,1805.1754860000001,null,31886.51250000007,10.238498320417181,6228.747908550873,73.684544650594404,6163.2321750000065,72.645351478982803,-1.0391931716116005,null,null,null,null,null,null,null,null,null,1643.8231392994103,0,12.639937359289661,0,0,0]
[0,1620.5908257178751,0,0,0,1620.5908257178751,1801.9033469999999,"2013-01-08T02:00:00",45,40,"OFF",-26.749601854920019,-73.754793005267999,-8.8484060000000007,"ON",30488.069079825007,76651.228454344004,1820.4849999999999,"OFF",-4.5544565124994121E-2,-33.398399859304,-1.7696810000000001,"OFF",-3.3740159413799948,-164.80022619768002,-3.9817830000000001,"OFF",-3.2728584760200126,-114.53734910332001,-3.9817830000000001,null,0,1608.8117841637027,0,0,0,1608.8117841637027,0,1641.1669094185063,0,0,0,1641.1669094185063,0,211.67321583629723,0,0,0,0,179.31809058149361,0,0,0,211.21906242814964,178.86393717334602,null,null,1801.9033469999999,null,31886.51250000007,10.299345197696841,6191.9494662885154,73.099504887130408,6163.2321750000065,72.645351478982803,-0.45415340814760441,null,null,null,null,null,null,null,null,null,1608.8117841637027,0,11.779041554172409,0,0,0]
[0,1654.107142333665,0,0,0,1654.107142333665,1854.2057419999999,"2013-01-08T03:00:00",47,41,"OFF",-27.361380158550002,-70.971595690604005,-8.8484060000000007,"ON",31525.599356475002,76910.325455045997,1870.202,"OFF",-0.72742481825000471,-33.398399859304,-1.147527,"OFF",-3.2957300022499907,-158.64239131086001,-1.7696810000000001,"OFF",-4.3949966520249726,-117.16401182164,-4.2306439999999998,null,0,1641.5240950689629,0,0,0,1641.5240950689629,0,1675.5897774512919,0,0,0,1675.5897774512919,0,228.67790493103712,0,0,0,0,194.61222254870813,0,0,0,226.11710094911962,192.05141856679063,null,null,1854.2057419999999,null,33987.03270000004,10.431791963324457,6516.0487899854324,78.3713815468424,6360.681073800004,75.810577564924898,-2.5608039819175019,null,null,null,null,null,null,null,null,null,1641.5240950689629,0,12.583047264702145,0,0,0]
[0,1698.9778194897788,0,0,0,1698.9778194897788,1917.607107,"2013-01-08T04:00:00",47,41,"OFF",-27.051652248809997,-71.667395019270003,-8.8484060000000007,"ON",32879.25748836001,77517.903630546003,1938.152,"OFF",4.8870520452000313E-2,-33.398399859304,-1.7696810000000001,"OFF",-4.0304478887400075,-164.80022619768002,-3.9817830000000001,"OFF",-2.5311226302600098,-116.20303570010002,-5.9450229999999999,null,0,1685.3031449773514,0,0,0,1685.3031449773514,0,1721.0666244582374,0,0,0,1721.0666244582374,0,252.84885502264865,0,0,0,0,217.08537554176269,0,0,0,250.28805104073115,214.52457155984519,null,null,1917.607107,null,33987.03270000004,10.431791963324457,6516.0487899854324,78.3713815468424,6360.681073800004,75.810577564924898,-2.5608039819175019,null,null,null,null,null,null,null,null,null,1685.3031449773514,0,13.674674512427373,0,0,0]
[0,1648.3330366353728,0,0,0,1648.3330366353728,1956.316347,"2013-01-08T05:00:00",47,41,"OFF",-27.832950775799983,-72.363194347936002,-8.8484060000000007,"ON",31348.517917919995,77446.486124610019,1974.8979999999999,"OFF",-0.58883536500000067,-46.444647297834003,-1.7696810000000001,"OFF",-5.0493771988100118,-164.80022619768002,-3.9817830000000001,"OFF",-2.1355896131500072,-119.67316932186,-3.9817830000000001,null,0,1635.8892149936912,0,0,0,1635.8892149936912,0,1668.564461796246,0,0,0,1668.564461796246,0,339.0087850063087,0,0,0,0,306.33353820375396,0,0,0,336.4479810243912,303.77273422183646,null,null,1956.316347,null,33987.03270000004,10.431791963324457,6516.0487899854324,78.3713815468424,6360.681073800004,75.810577564924898,-2.5608039819175019,null,null,null,null,null,null,null,null,null,1635.8892149936912,0,12.443821641681552,0,0,0]
[0,1765.5711717547895,0,0,0,1765.5711717547895,1994.7377720000002,"2013-01-08T06:00:00",48,42,"OFF",-27.303061160874979,-73.754793005267999,-8.8484060000000007,"ON",34819.869987139988,77391.503307539999,2011.6880000000001,"OFF",-0.79110991599999847,-33.398399859304,-1.7696810000000001,"OFF",-3.8846795227800031,-158.64239131086001,-2.3503579999999999,"OFF",-4.5005943196200171,-115.50281689190001,-3.9817830000000001,null,0,1750.2465491234841,0,0,0,1750.2465491234841,0,1790.6221124856161,0,0,0,1790.6221124856161,0,261.441450876516,0,0,0,0,221.06588751438403,0,0,0,257.91734632096382,217.54178295883187,null,null,1994.7377720000002,null,35210.380800000043,10.534338790631107,6684.877238107244,81.224107121362351,6475.6757952000044,77.700002565810195,-3.5241045555521566,null,null,null,null,null,null,null,null,null,1750.2465491234841,0,15.324622631305374,0,0,0]
[0,1752.96617889753,0,0,0,1752.96617889753,2022.996347,"2013-01-08T07:00:00",48,43,"OFF",-27.977669746290005,-74.450592333934011,-8.8484060000000007,"ON",34458.460283999993,77216.079647126011,2041.578,"OFF",-0.24083928562499829,-33.398399859304,-1.7696810000000001,"OFF",-3.7941671697300126,-166.99199929652002,-3.9817830000000001,"OFF",-3.2880990419899936,-118.28596608156001,-3.9817830000000001,null,0,1737.9564672575787,0,0,0,1737.9564672575787,0,1777.9001635587713,0,0,0,1777.9001635587713,0,303.62153274242132,0,0,0,0,263.67783644122869,0,0,0,300.75252836355025,260.80883206235762,null,null,2022.996347,null,35210.380800000043,10.595185667910767,6646.4867919474727,80.569006944681234,6475.6757952000044,77.700002565810195,-2.8690043788710398,null,null,null,null,null,null,null,null,null,1737.9564672575787,0,15.00971163995132,0,0,0]
[0,1787.9149329528909,0,0,0,1787.9149329528909,2042.2971629999997,"2013-01-08T08:00:00",49,43,"OFF",-27.863839223499983,-71.667395019270003,-8.8484060000000007,"ON",35454.052577045004,77036.733798886009,2060.547,"OFF",-7.0126216499999658E-2,-33.398399859304,-1.7696810000000001,"OFF",-4.5607952887199943,-160.83416440970004,-3.401106,"OFF",-1.8578207464599805,-116.62477115182,-4.2306439999999998,null,0,1772.0292320571236,0,0,0,1772.0292320571236,0,1814.7402791018021,0,0,0,1814.7402791018021,0,288.51776794287639,0,0,0,0,245.80672089819791,0,0,0,283.90174196257959,241.19069491790111,null,null,2042.2971629999997,null,36544.120100000058,10.640648494197933,6868.7768644790049,84.414522385922595,6601.047289400005,79.798496405625798,-4.6160259802967971,null,null,null,null,null,null,null,null,null,1772.0292320571236,0,15.885700895767286,0,0,0]
[0,1798.3540601445,0,0,0,1798.3540601445,2082.0011629999999,"2013-01-08T09:00:00",48,43,"OFF",-28.586758754200009,-73.058993676602014,-8.8484060000000007,"ON",35747.58564469,77306.963717180013,2100.2510000000002,"OFF",6.4393615314000327E-2,-75.14639166260001,-1.7696810000000001,"OFF",-3.5500604918100049,-164.80022619768002,-3.401106,"OFF",-3.0107547036000111,-117.85981917114,-4.2306439999999998,null,0,1782.2049916264746,0,0,0,1782.2049916264746,0,1824.9617055207725,0,0,0,1824.9617055207725,0,318.04600837352564,0,0,0,0,275.28929447922769,0,0,0,315.17700399465457,272.42029010035662,null,null,2082.0011629999999,null,35210.380800000043,10.595185667910767,6646.4867919474727,80.569006944681234,6475.6757952000044,77.700002565810195,-2.8690043788710398,null,null,null,null,null,null,null,null,null,1782.2049916264746,0,16.149068518025388,0,0,0]
[0,1793.2743737069979,0,0,0,1793.2743737069979,2106.4300846999995,"2013-01-08T10:00:00",49,45,"OFF",-28.278983946149985,-71.667395019270003,-8.8484060000000007,"ON",35604.968588699994,76966.415147208012,2123.643,"OFF",-0.11480041763399855,-62.100144224070007,-0.4009433,"OFF",-3.542287232960009,-166.99199929652002,-3.9817830000000001,"OFF",-5.2445739973250047,-117.59015873206,-3.9817830000000001,null,0,1777.253556574743,0,0,0,1777.253556574743,0,1820.5002892039927,0,0,0,1820.5002892039927,0,346.38944342525701,0,0,0,0,303.14271079600735,0,0,0,343.13141173188245,299.88467910263279,null,null,2106.4300846999995,null,36544.120100000058,10.762342248757253,6791.1090830102294,83.05652809900036,6601.047289400005,79.798496405625798,-3.2580316933745621,null,null,null,null,null,null,null,null,null,1777.253556574743,0,16.020817132254933,0,0,0]
[0,1834.9685295309819,0,0,0,1834.9685295309819,2222.8632459999999,"2013-01-08T11:00:00",49,46,"OFF",-28.684910848230007,-71.667395019270003,-8.8484060000000007,"ON",36763.73773162999,76837.359928147998,2243.6570000000002,"OFF",-0.57417303649999829,-46.444647297834003,-1.7696810000000001,"OFF",-3.8170126457399998,-166.99199929652002,-3.9817830000000001,"OFF",-3.4906718949999926,-115.50281689190001,-6.1938839999999997,null,0,1817.8897224983771,0,0,0,1817.8897224983771,0,1864.3333189455209,0,0,0,1864.3333189455209,0,425.76727750162308,0,0,0,0,379.32368105447927,0,0,0,423.17112987492499,376.72753342778117,null,null,2222.8632459999999,null,36544.120100000058,10.823189126036914,6752.9301529227332,82.394644032323896,6601.047289400005,79.798496405625798,-2.5961476266980981,null,null,null,null,null,null,null,null,null,1817.8897224983771,0,17.0788070326048,0,0,0]
[0,1880.9480532374816,0,0,0,1880.9480532374816,2209.2607719999992,"2013-01-08T12:00:00",49,46,"OFF",-28.249748295750006,-72.363194347936002,-8.8484060000000007,"ON",38011.653064199993,77028.977652407993,2226.2109999999998,"OFF",5.4497715533999465E-2,-62.100144224070007,-1.7696810000000001,"OFF",-3.3574417725099952,-164.80022619768002,-2.3503579999999999,"OFF",-3.8652452658399983,-115.50281689190001,-3.9817830000000001,null,0,1862.68900962202,0,0,0,1862.68900962202,0,1911.8108744979506,0,0,0,1911.8108744979506,0,363.52199037797982,0,0,0,0,314.40012550204915,0,0,0,360.92584275128172,311.80397787535105,null,null,2209.2607719999992,null,36544.120100000058,10.823189126036914,6752.9301529227332,82.394644032323896,6601.047289400005,79.798496405625798,-2.5961476266980981,null,null,null,null,null,null,null,null,null,1862.68900962202,0,18.259043615461678,0,0,0]
[0,1856.1967850486828,0,0,0,1856.1967850486828,2227.9913469999992,"2013-01-08T13:00:00",48,47,"OFF",-28.489285310669988,-73.754793005267999,-8.8484060000000007,"ON",37343.667028980002,76938.566811560013,2246.5729999999999,"OFF",1.9316038560004E-3,-62.100144224070007,-1.7696810000000001,"OFF",-4.4825880535099945,-160.83416440970004,-3.9817830000000001,"OFF",-3.6729339459399788,-116.19862424140001,-3.9817830000000001,null,0,1838.5747886802512,0,0,0,1838.5747886802512,0,1886.2241795390335,0,0,0,1886.2241795390335,0,407.99821131974863,0,0,0,0,360.34882046096641,0,0,0,407.64020663413208,359.99081577534986,null,null,2227.9913469999992,null,35210.380800000043,10.83857317702941,6497.2354247923904,78.058007251426758,6475.6757952000044,77.700002565810195,-0.35800468561656373,null,null,null,null,null,null,null,null,null,1838.5747886802512,0,17.62199636843161,0,0,0]
[0,1880.4315761490836,0,0,0,1880.4315761490836,2252.6597719999995,"2013-01-08T14:00:00",48,47,"OFF",-28.257851222089979,-73.829210303120007,-8.8484060000000007,"ON",37997.802435579993,76917.832955670005,2269.61,"OFF",-0.31590010206500058,-46.444647297834003,-1.7696810000000001,"OFF",-4.182013261299999,-164.80022619768002,-2.3503579999999999,"OFF",-4.9863820533100114,-117.59015873206,-3.9817830000000001,null,0,1862.1858656498418,0,0,0,1862.1858656498418,0,1911.581762453754,0,0,0,1911.581762453754,0,407.42413435015828,0,0,0,0,358.02823754624615,0,0,0,407.06612966454173,357.6702328606296,null,null,2252.6597719999995,null,35210.380800000043,10.83857317702941,6497.2354247923904,78.058007251426758,6475.6757952000044,77.700002565810195,-0.35800468561656373,null,null,null,null,null,null,null,null,null,1862.1858656498418,0,18.245710499241795,0,0,0]
[0,1889.4441493251957,0,0,0,1889.4441493251957,2264.3827839999999,"2013-01-08T15:00:00",49,48,"OFF",-28.264698896219993,-70.897178392752011,-8.8484060000000007,"ON",38238.96739665002,77133.649536108001,2284.3470000000002,"OFF",0.32670627156999887,-33.398399859304,-1.7696810000000001,"OFF",-4.2285737643100054,-158.64239131086001,-3.401106,"OFF",-5.1035986800500073,-118.98177343106001,-5.9450229999999999,null,0,1870.9655330362059,0,0,0,1870.9655330362059,0,1920.3840504531283,0,0,0,1920.3840504531283,0,413.38146696379431,0,0,0,0,363.96294954687187,0,0,0,412.07612393485635,362.65760651793391,null,null,2264.3827839999999,null,36544.120100000058,10.944882880596234,6677.8458022219202,81.103839434563753,6601.047289400005,79.798496405625798,-1.3053430289379548,null,null,null,null,null,null,null,null,null,1870.9655330362059,0,18.47861628898977,0,0,0]
[0,1862.3556747753248,0,0,0,1862.3556747753248,2174.0213469999994,"2013-01-08T16:00:00",48,47,"OFF",-27.471302826589987,-72.262685277082014,-8.8484060000000007,"ON",37510.695408165004,77004.032858668012,2192.6030000000001,"OFF",-0.64527127637499848,-33.398399859304,-1.7696810000000001,"OFF",-4.2470451353399898,-158.64239131086001,-3.9817830000000001,"OFF",-5.0857641283400046,-118.98177343106001,-3.9817830000000001,null,0,1844.5755302413284,0,0,0,1844.5755302413284,0,1892.4751744000773,0,0,0,1892.4751744000773,0,348.02746975867171,0,0,0,0,300.12782559992274,0,0,0,347.66946507305516,299.76982091430619,null,null,2174.0213469999994,null,35210.380800000043,10.83857317702941,6497.2354247923904,78.058007251426758,6475.6757952000044,77.700002565810195,-0.35800468561656373,null,null,null,null,null,null,null,null,null,1844.5755302413284,0,17.780144533996463,0,0,0]
[0,1836.2941653554303,0,0,0,1836.2941653554303,1976.5973470000001,"2013-01-08T17:00:00",48,47,"OFF",-27.374598216489996,-70.376305432792009,-8.8484060000000007,"ON",36800.146549660007,76760.111275894014,1995.1790000000001,"OFF",1.2782691845999748E-2,-62.100144224070007,-1.7696810000000001,"OFF",-4.3904419986000089,-166.99199929652002,-3.9817830000000001,"OFF",-3.3458932106600234,-115.50281689190001,-3.9817830000000001,null,0,1819.1815255691145,0,0,0,1819.1815255691145,0,1865.9201743169119,0,0,0,1865.9201743169119,0,175.99747443088563,0,0,0,0,129.25882568308816,0,0,0,175.63946974526908,128.90082099747161,null,null,1976.5973470000001,null,35210.380800000043,10.83857317702941,6497.2354247923904,78.058007251426758,6475.6757952000044,77.700002565810195,-0.35800468561656373,null,null,null,null,null,null,null,null,null,1819.1815255691145,0,17.112639786315867,0,0,0]
[0,1890.0260504145213,0,0,0,1890.0260504145213,1982.215209,"2013-01-08T18:00:00",47,46,"OFF",-27.165721528680013,-71.667395019270003,-8.8484060000000007,"ON",38254.499869095001,76601.026054337999,2000.548,"OFF",-0.98730639312499768,-33.398399859304,-1.7696810000000001,"OFF",-4.3986895579899876,-166.99199929652002,-1.7696810000000001,"OFF",-3.711481115579998,-114.11120219290001,-5.9450229999999999,null,0,1871.5323788958381,0,0,0,1871.5323788958381,0,1922.5010154344441,0,0,0,1922.5010154344441,0,129.01562110416194,0,0,0,0,78.046984565555931,0,0,0,129.49133530122023,78.522698762614226,null,null,1982.215209,null,33987.03270000004,10.736026349722758,6331.3988980434469,75.334863367866603,6360.681073800004,75.810577564924898,0.47571419705829499,null,null,null,null,null,null,null,null,null,1871.5323788958381,0,18.493671518683186,0,0,0]
[0,1918.3760437057092,0,0,0,1918.3760437057092,2081.9376659999998,"2013-01-08T19:00:00",47,46,"OFF",-27.80858503071002,-70.275796361938006,-8.8484060000000007,"ON",39005.688075689999,77277.54329806802,2102.2890000000002,"OFF",-0.14750161937500367,-62.100144224070007,-3.2905009999999999,"OFF",-4.8111992776399948,-166.99199929652002,-3.9817830000000001,"OFF",-4.8745744708799998,-116.89443159090001,-4.2306439999999998,null,0,1899.1463469905968,0,0,0,1899.1463469905968,0,1950.1556638018865,0,0,0,1950.1556638018865,0,203.14265300940338,0,0,0,0,152.13333619811374,0,0,0,203.61836720646167,152.60905039517203,null,null,2081.9376659999998,null,33987.03270000004,10.736026349722758,6331.3988980434469,75.334863367866603,6360.681073800004,75.810577564924898,0.47571419705829499,null,null,null,null,null,null,null,null,null,1899.1463469905968,0,19.229696715112368,0,0,0]
[0,1878.5559394651843,0,0,0,1878.5559394651843,1974.3287720000001,"2013-01-08T20:00:00",47,46,"OFF",-27.764066657970005,-73.058993676602014,-8.8484060000000007,"ON",37947.471324400001,75492.458566364003,1991.279,"OFF",-0.33131943737500125,-62.100144224070007,-1.7696810000000001,"OFF",-4.9337269171399996,-166.99199929652002,-2.3503579999999999,"OFF",-4.9344845774750006,-116.89443159090001,-3.9817830000000001,null,0,1860.3586352480577,0,0,0,1860.3586352480577,0,1913.6696789229136,0,0,0,1913.6696789229136,0,130.92036475194232,0,0,0,0,77.609321077086406,0,0,0,131.39607894900061,78.085035274144701,null,null,1974.3287720000001,null,33987.03270000004,10.736026349722758,6331.3988980434469,75.334863367866603,6360.681073800004,75.810577564924898,0.47571419705829499,null,null,null,null,null,null,null,null,null,1860.3586352480577,0,18.197304217126657,0,0,0]
[0,1796.175747053569,0,0,0,1796.175747053569,2122.6732089999991,"2013-01-08T21:00:00",46,45,"OFF",-28.059409146160014,-73.654283934414011,-8.8484060000000007,"ON",35686.477421700001,76350.110304316011,2141.0059999999999,"OFF",-7.1918018625002564E-2,-46.444647297834003,-1.7696810000000001,"OFF",-4.9265597089799904,-160.83416440970004,-1.7696810000000001,"OFF",-4.5022924328200125,-118.28596608156001,-5.9450229999999999,null,0,1780.0816986776383,0,0,0,1780.0816986776383,0,1825.0544484600161,0,0,0,1825.0544484600161,0,360.92430132236154,0,0,0,0,315.95155153998371,0,0,0,362.11588512509059,317.14313534271275,null,null,2122.6732089999991,null,32877.826400000049,10.637370244407659,6181.5703777509816,72.93511978891317,6256.415681600005,74.126703591642183,1.1915838027290135,null,null,null,null,null,null,null,null,null,1780.0816986776383,0,16.094048375930697,0,0,0]
[0,1806.7306629077757,0,0,0,1806.7306629077757,1831.535486,"2013-01-08T22:00:00",47,46,"OFF",-27.909187625130016,-71.767904090124006,-8.8484060000000007,"ON",35981.880005174993,76224.151127180012,1850.366,"OFF",-0.37001299437500096,-33.398399859304,-1.7696810000000001,"OFF",-4.4831150541099927,-166.99199929652002,-3.9817830000000001,"OFF",-5.0410451643499767,-118.28596608156001,-4.2306439999999998,null,0,1790.3697065517842,0,0,0,1790.3697065517842,0,1836.4098703819195,0,0,0,1836.4098703819195,0,59.996293448215738,0,0,0,0,13.956129618080467,0,0,0,60.472007645274033,14.431843815138762,null,null,1831.535486,null,33987.03270000004,10.736026349722758,6331.3988980434469,75.334863367866603,6360.681073800004,75.810577564924898,0.47571419705829499,null,null,null,null,null,null,null,null,null,1790.3697065517842,0,16.360956355991448,0,0,0]
[0,1776.8432249616199,0,0,0,1776.8432249616199,1972.5935320000001,"2013-01-08T23:00:00",47,46,"OFF",-28.071055859419982,-70.971595690604005,-8.8484060000000007,"ON",35140.822914880016,74490.431816412005,1991.5070000000001,"OFF",0.11215242223799887,-33.398399859304,-1.7696810000000001,"OFF",-4.7975236120699973,-158.64239131086001,-2.3503579999999999,"OFF",-6.3468678963199814,-116.89443159090001,-5.9450229999999999,null,0,1761.236000286,0,0,0,1761.236000286,0,1809.4688087275119,0,0,0,1809.4688087275119,0,230.27099971400003,0,0,0,0,182.03819127248812,0,0,0,230.74671391105832,182.51390546954642,null,null,1972.5935320000001,null,33987.03270000004,10.736026349722758,6331.3988980434469,75.334863367866603,6360.681073800004,75.810577564924898,0.47571419705829499,null,null,null,null,null,null,null,null,null,1761.236000286,0,15.607224675619818,0,0,0]
[0,1751.8151094699681,0,0,0,1751.8151094699681,1996.937449,"2013-01-09",48,47,"OFF",-28.791207106200019,-72.363194347936002,-8.8484060000000007,"ON",34425.323334674998,76654.091892081997,2013.307,"OFF",7.7410536250023462E-3,-46.444647297834003,-1.7696810000000001,"OFF",-5.4107415102299994,-160.83416440970004,-1.7696810000000001,"OFF",-5.128174505510013,-117.59015873206,-3.9817830000000001,null,0,1736.8340959918132,0,0,0,1736.8340959918132,0,1777.9886615338528,0,0,0,1777.9886615338528,0,276.47290400818679,0,0,0,0,235.31833846614722,0,0,0,276.11489932257024,234.96033378053068,null,null,1996.937449,null,35210.380800000043,10.83857317702941,6497.2354247923904,78.058007251426758,6475.6757952000044,77.700002565810195,-0.35800468561656373,null,null,null,null,null,null,null,null,null,1736.8340959918132,0,14.981013478154864,0,0,0]
[0,1822.2365057581007,0,0,0,{"$f":"SUM(A196:E196)","v":1822.2365057581007},{"$f":"N196+R196+V196+Z196+AD196","v":1865.9703469999999},"2013-01-09T01:00:00",49,48,"OFF",-28.614103627690014,-73.058993676602014,-8.8484060000000007,"ON",36412.71065898001,76033.985173874011,1884.5519999999999,"OFF",9.2974355381999094E-2,-33.398399859304,-1.7696810000000001,"OFF",-4.8923573700400116,-166.99199929652002,-3.9817830000000001,"OFF",-5.2859083938149807,-117.59015873206,-3.9817830000000001,null,0,1805.4820408477249,0,0,0,{"$f":"SUM(AF196:AJ196)","v":1805.4820408477249},0,1853.1288283484037,0,0,0,{"$f":"SUM(AL196:AP196)","v":1853.1288283484037},{"$f":"IF($K196=\"ON\",$N196-AF196,0)","v":0},{"$f":"IF($O196=\"ON\",$R196-AG196,0)","v":79.069959152275032},{"$f":"IF($S196=\"ON\",$V196-AH196,0)","v":0},{"$f":"IF($W196=\"ON\",$Z196-AI196,0)","v":0},{"$f":"IF($AA196=\"ON\",$AD196-AJ196,0)","v":0},{"$f":"IF($K196=\"ON\",$N196-AL196,0)","v":0},{"$f":"IF($O196=\"ON\",$R196-AM196,0)","v":31.423171651596249},{"$f":"IF($S196=\"ON\",$V196-AN196,0)","v":0},{"$f":"IF($W196=\"ON\",$Z196-AO196,0)","v":0},{"$f":"IF($AA196=\"ON\",$AD196-AP196,0)","v":0},{"$f":"SUM(AR196:AV196)+BN196","v":77.764616123337078},{"$f":"SUM(AW196:BA196)+BN196","v":30.117828622658294},null,null,{"$f":"N196+R196+V196+Z196+AD196","v":1865.9703469999999},null,36544.120100000058,{"$f":"19.5285952781395+42*-0.3035722016559+BH196*0.0000340867411548605+J196*0.0608468772796604","v":10.944882880596234},{"$f":"BH196*1000/(500*BI196)","v":6677.8458022219202},{"$f":"0.00000128*BJ196^2+0*BJ196+24.024","v":81.103839434563753},{"$f":"0.094*BH196 + 3165.9","v":6601.047289400005},{"$f":"0.00000128*BL196^2+0*BL196+24.024","v":79.798496405625798},{"$f":"BM196-BK196","v":-1.3053430289379548},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF196:AJ196)","v":1805.4820408477249},{"$f":"A196-AF196","v":0},{"$f":"B196-AG196","v":16.754464910375873},{"$f":"C196-AH196","v":0},{"$f":"D196-AI196","v":0},{"$f":"E196-AJ196","v":0}]
[0,1748.1384147325452,0,0,0,1748.1384147325452,1862.168287,"2013-01-09T02:00:00",48,47,"OFF",-28.613497577000004,-74.450592333934011,-8.8484060000000007,"ON",34319.327599249984,76348.90717921601,1884.2339999999999,"OFF",-0.60253738124999778,-46.444647297834003,-3.2905009999999999,"OFF",-6.4407468065249827,-166.99199929652002,-3.9817830000000001,"OFF",-5.2921273349700195,-118.29037754026001,-5.9450229999999999,null,0,1733.2490009039821,0,0,0,1733.2490009039821,0,1774.8544404166305,0,0,0,1774.8544404166305,0,150.98499909601787,0,0,0,0,109.37955958336943,0,0,0,150.62699441040132,109.02155489775286,null,null,1862.168287,null,{"$f":" -0.6251*I197^3 + 145.21*I197^2 - 8340.3*I197 + 170112","v":35210.380800000043},10.83857317702941,6497.2354247923904,78.058007251426758,6475.6757952000044,77.700002565810195,-0.35800468561656373,null,null,null,null,null,null,null,null,null,1733.2490009039821,0,14.889413828563193,0,0,0]
[0,1762.4478188688774,0,0,0,1762.4478188688774,1957.4034489999999,"2013-01-09T03:00:00",49,48,"OFF",-28.876128326010015,-72.363194347936002,-8.8484060000000007,"ON",34730.565673440004,74839.225803736001,1973.7729999999999,"OFF",-0.19870265787500416,-33.398399859304,-1.7696810000000001,"OFF",-5.3742203686499961,-166.99199929652002,-1.7696810000000001,"OFF",-5.0389073190400033,-118.28596608156001,-3.9817830000000001,null,0,1747.2013369572626,0,0,0,1747.2013369572626,0,1793.4536066137991,0,0,0,1793.4536066137991,0,226.57166304273733,0,0,0,0,180.31939338620077,0,0,0,225.26632001379937,179.01405035726282,null,null,1957.4034489999999,null,36544.120100000058,10.944882880596234,6677.8458022219202,81.103839434563753,6601.047289400005,79.798496405625798,-1.3053430289379548,null,null,null,null,null,null,null,null,null,1747.2013369572626,0,15.246481911614865,0,0,0]
[0,1742.3652289638619,0,0,0,1742.3652289638619,1984.6927839999998,"2013-01-09T04:00:00",49,48,"OFF",-28.693628018229997,-70.971595690604005,-8.8484060000000007,"ON",34152.424560900006,75815.818489074009,2004.6569999999999,"OFF",-6.1339035636000509E-2,-33.398399859304,-1.7696810000000001,"OFF",-4.7290135340700079,-160.83416440970004,-3.401106,"OFF",-5.4705141266299924,-116.89002013220001,-5.9450229999999999,null,0,1727.6194397183756,0,0,0,1727.6194397183756,0,1770.0524738148658,0,0,0,1770.0524738148658,0,277.03756028162434,0,0,0,0,234.60452618513409,0,0,0,275.73221725268638,233.29918315619614,null,null,1984.6927839999998,null,36544.120100000058,10.944882880596234,6677.8458022219202,81.103839434563753,6601.047289400005,79.798496405625798,-1.3053430289379548,null,null,null,null,null,null,null,null,null,1727.6194397183756,0,14.745789245486321,0,0,0]
[0,1863.7090109490191,0,0,0,1863.7090109490191,1884.4437720000001,"2013-01-09T05:00:00",50,49,"OFF",-28.682587355659994,-73.754793005267999,-8.8484060000000007,"ON",37547.324968749999,75401.871267168011,1901.394,"OFF",-8.7681192875004921E-2,-75.14639166260001,-1.7696810000000001,"OFF",-5.1645795299700135,-158.64239131086001,-2.3503579999999999,"OFF",-4.9878620133499805,-116.19862424140001,-3.9817830000000001,null,0,1845.8940823995238,0,0,0,1845.8940823995238,0,1898.3402495937446,0,0,0,1898.3402495937446,0,55.499917600476238,0,0,0,0,3.0537504062554035,0,0,0,53.138318901679796,0.6921517074589616,null,null,1884.4437720000001,null,37984.500000000058,11.05482761469186,6872.0203197956125,84.471568992875262,6736.4430000000057,82.109970294078821,-2.3615986987964419,null,null,null,null,null,null,null,null,null,1845.8940823995238,0,17.814928549495335,0,0,0]
[0,1827.4922839885651,0,0,0,1827.4922839885651,2192.8214859999994,"2013-01-09T06:00:00",51,50,"OFF",-29.526142255190006,-72.363194347936002,-8.8484060000000007,"ON",36557.910079159999,75653.08378804801,2211.652,"OFF",-0.29513206112500656,-33.398399859304,-1.7696810000000001,"OFF",-5.6590641929499972,-160.83416440970004,-3.9817830000000001,"OFF",-5.469169529899979,-118.28596608156001,-4.2306439999999998,null,0,1810.6040636543266,0,0,0,1810.6040636543266,0,1859.6446487804899,0,0,0,1859.6446487804899,0,401.04793634567341,0,0,0,0,352.00735121951016,0,0,0,397.52654876010979,348.48596363394654,null,null,2192.8214859999994,null,39527.769900000014,11.168279533584904,7078.5781786949956,88.160024360828118,6881.5103706000009,84.638636775264473,-3.5213875855636445,null,null,null,null,null,null,null,null,null,1810.6040636543266,0,16.88822033423844,0,0,0]
[0,1854.2092822525283,0,0,0,1854.2092822525283,1937.072502,"2013-01-09T07:00:00",51,50,"OFF",-28.893545695839986,-72.363194347936002,-8.8484060000000007,"ON",37289.649755085011,76319.238114250009,1957.7280000000001,"OFF",-0.63038643650000026,-33.398399859304,-2.460963,"OFF",-4.6602136057400001,-160.83416440970004,-3.401106,"OFF",-6.3554635268600235,-116.89443159090001,-5.9450229999999999,null,0,1836.638268269734,0,0,0,1836.638268269734,0,1885.8279328348681,0,0,0,1885.8279328348681,0,121.08973173026607,0,0,0,0,71.900067165131986,0,0,0,117.56834414470242,68.378679579568342,null,null,1937.072502,null,39527.769900000014,11.168279533584904,7078.5781786949956,88.160024360828118,6881.5103706000009,84.638636775264473,-3.5213875855636445,null,null,null,null,null,null,null,null,null,1836.638268269734,0,17.571013982794284,0,0,0]
[0,1927.2109885224679,0,0,0,1927.2109885224679,2133.3687719999994,"2013-01-09T08:00:00",51,50,"OFF",-29.011198579789994,-72.363194347936002,-8.8484060000000007,"ON",39237.604682325007,74361.946076566004,2150.319,"OFF",7.1426151375004535E-2,-75.14639166260001,-1.7696810000000001,"OFF",-7.8693436237800114,-160.83416440970004,-2.3503579999999999,"OFF",-5.2333301654199982,-116.89443159090001,-3.9817830000000001,null,0,1907.7509157648731,0,0,0,1907.7509157648731,0,1968.3197052445362,0,0,0,1968.3197052445362,0,242.56808423512689,0,0,0,0,181.99929475546378,0,0,0,239.04669664956324,178.47790716990013,null,null,2133.3687719999994,null,39527.769900000014,11.168279533584904,7078.5781786949956,88.160024360828118,6881.5103706000009,84.638636775264473,-3.5213875855636445,null,null,null,null,null,null,null,null,null,1907.7509157648731,0,19.460072757594844,0,0,0]
[0,1878.6478634175101,0,0,0,1878.6478634175101,2178.8425879999991,"2013-01-09T09:00:00",52,51,"OFF",-28.964506326630019,-74.450592333934011,-8.8484060000000007,"ON",37949.939167079996,76108.827575928008,2195.4609999999998,"OFF",2.2144271593500554E-2,-62.100144224070007,-1.7696810000000001,"OFF",-5.717719359729986,-166.99199929652002,-1.7696810000000001,"OFF",-4.725466960129995,-118.28596608156001,-4.2306439999999998,null,0,1860.4481873546354,0,0,0,1860.4481873546354,0,1911.9972992853513,0,0,0,1911.9972992853513,0,335.01281264536442,0,0,0,0,283.46370071464844,0,0,0,330.23432994238783,278.68521801167185,null,null,2178.8425879999991,null,41170.179200000071,11.285110791544003,7296.3712914274829,92.167403548629963,7035.8968448000069,87.388920845653359,-4.7784827029766035,null,null,null,null,null,null,null,null,null,1860.4481873546354,0,18.199676062874687,0,0,0]
[0,1837.164185915701,0,0,0,1837.164185915701,2037.2432449999999,"2013-01-09T10:00:00",53,52,"OFF",-29.041474764259981,-73.133410974454009,-8.8484060000000007,"ON",36824.027624730006,75312.687613922011,2058.0369999999998,"OFF",-8.1439163249995755E-2,-62.100144224070007,-3.9817830000000001,"OFF",-5.4771172358000042,-164.80022619768002,-3.9817830000000001,"OFF",-6.2663553566599823,-120.37338813006001,-3.9817830000000001,null,0,1820.0293351472349,0,0,0,1820.0293351472349,0,1870.7144764052396,0,0,0,1870.7144764052396,0,238.00766485276495,0,0,0,0,187.32252359476024,0,0,0,231.88196508632564,181.19682382832093,null,null,2037.2432449999999,null,42907.977300000086,11.405193542837774,7524.2874465633977,96.491074020494764,7199.249866200008,90.365374254055467,-6.1256997664392969,null,null,null,null,null,null,null,null,null,1820.0293351472349,0,17.134850768466094,0,0,0]
[0,1851.2407123594371,0,0,0,1851.2407123594371,2310.3657839999996,"2013-01-09T11:00:00",54,53,"OFF",-29.323868035769987,-72.288777050083993,-8.8484060000000007,"ON",37208.862198149996,75155.278746672004,2330.33,"OFF",3.9324588941999694E-2,-62.100144224070007,-1.7696810000000001,"OFF",-8.2872113588249974,-164.80022619768002,-3.401106,"OFF",-3.7490094172999946,-118.28596608156001,-5.9450229999999999,null,0,1833.7457984050202,0,0,0,1833.7457984050202,0,1885.9383623563665,0,0,0,1885.9383623563665,0,496.58420159497973,0,0,0,0,444.39163764363343,0,0,0,489.02937544184033,436.83681149049403,null,null,2310.3657839999996,null,44737.413600000087,11.52839994173484,7761.2528756992124,101.1274191367031,7371.2168784000078,93.572592983563723,-7.5548261531393734,null,null,null,null,null,null,null,null,null,1833.7457984050202,0,17.494913954416916,0,0,0]
[0,1879.548126855487,0,0,0,1879.548126855487,2012.283107,"2013-01-09T12:00:00",54,53,"OFF",-29.251484503360025,-73.754793005267999,-8.8484060000000007,"ON",37974.101928299984,75895.433287358013,2032.828,"OFF",-9.630058087500315E-2,-33.398399859304,-1.7696810000000001,"OFF",-5.6085775354699985,-166.99199929652002,-3.9817830000000001,"OFF",-4.9791226193799991,-116.89443159090001,-5.9450229999999999,null,0,1861.3252191256352,0,0,0,1861.3252191256352,0,1913.5501057912279,0,0,0,1913.5501057912279,0,171.50278087436482,0,0,0,0,119.27789420877207,0,0,0,163.94795472122544,111.72306805563269,null,null,2012.283107,null,44737.413600000087,11.52839994173484,7761.2528756992124,101.1274191367031,7371.2168784000078,93.572592983563723,-7.5548261531393734,null,null,null,null,null,null,null,null,null,1861.3252191256352,0,18.22290772985184,0,0,0]
[0,1898.3036153715723,0,0,0,1898.3036153715723,2258.7587719999992,"2013-01-09T13:00:00",56,54,"OFF",-29.535906727179988,-72.363194347936002,-8.8484060000000007,"ON",38474.949071790004,74284.087840928012,2275.7089999999998,"OFF",-0.28561091650000503,-62.100144224070007,-1.7696810000000001,"OFF",-6.0225166524049953,-158.64239131086001,-2.3503579999999999,"OFF",-6.2329808794999746,-116.89443159090001,-3.9817830000000001,null,0,1879.5955536949748,0,0,0,1879.5955536949748,0,1938.0592117817889,0,0,0,1938.0592117817889,0,396.11344630502504,0,0,0,0,337.64978821821092,0,0,0,384.58423874498214,326.12058065816802,null,null,2258.7587719999992,null,48656.198400000052,11.722825422133701,8301.104323900101,112.22666623522937,7739.5826496000045,100.69745867518647,-11.529207560042906,null,null,null,null,null,null,null,null,null,1879.5955536949748,0,18.708061676597481,0,0,0]
[0,1930.9990701882148,0,0,0,1930.9990701882148,2245.6190239999996,"2013-01-09T14:00:00",56,55,"OFF",-29.159839099020012,-70.871086619750002,-8.8484060000000007,"ON",39336.729981569995,75596.248158324015,2263.62,"OFF",7.2620686125000916E-2,-46.444647297834003,-1.7696810000000001,"OFF",-5.1645531799399862,-164.80022619768002,-3.401106,"OFF",-5.905144741549984,-119.67758078056001,-3.9817830000000001,null,0,1911.4400775531838,0,0,0,1911.4400775531838,0,1968.4238520230369,0,0,0,1968.4238520230369,0,352.17992244681614,0,0,0,0,295.19614797696295,0,0,0,341.55926026383929,284.5754857939861,null,null,2245.6190239999996,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1911.4400775531838,0,19.558992635031018,0,0,0]
[0,1947.1934129097892,0,0,0,1947.1934129097892,2152.5873469999992,"2013-01-09T15:00:00",56,55,"OFF",-29.673992769645007,-71.072104761458007,-8.8484060000000007,"ON",39758.418032399997,75235.543232509997,2171.1689999999999,"OFF",-0.28621541014999935,-46.444647297834003,-1.7696810000000001,"OFF",-5.872710236189997,-158.64239131086001,-3.9817830000000001,"OFF",-6.868740535509998,-119.67758078056001,-3.9817830000000001,null,0,1927.2105692840059,0,0,0,1927.2105692840059,0,1986.57980995445,0,0,0,1986.57980995445,0,243.95843071599393,0,0,0,0,184.58919004554991,0,0,0,233.33776853301708,173.96852786257307,null,null,2152.5873469999992,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1927.2105692840059,0,19.982843625783289,0,0,0]
[0,1969.1069218829437,0,0,0,1969.1069218829437,2413.0800239999999,"2013-01-09T16:00:00",57,55,"OFF",-29.018559297689997,-73.754793005267999,-8.8484060000000007,"ON",40323.762807404994,74660.032351342015,2431.0810000000001,"OFF",-1.103242971600087E-2,-33.398399859304,-1.7696810000000001,"OFF",-6.2534154696299824,-166.99199929652002,-3.401106,"OFF",-6.3930990281899964,-118.98177343106001,-3.9817830000000001,null,0,1948.5481004032267,0,0,0,1948.5481004032267,0,2011.541234437738,0,0,0,2011.541234437738,0,482.5328995967734,0,0,0,0,419.53976556226212,0,0,0,469.34175454775789,406.3486205132466,null,null,2413.0800239999999,null,50738.045700000075,11.854635689452406,8560.0345770463373,117.81496570909295,7935.2762958000076,104.62382066007743,-13.191145049015518,null,null,null,null,null,null,null,null,null,1948.5481004032267,0,20.558821479716926,0,0,0]
[0,1989.4059743821319,0,0,0,1989.4059743821319,2150.7495879999992,"2013-01-09T17:00:00",57,55,"OFF",-29.427149667330006,-72.363194347936002,-8.8484060000000007,"ON",40842.194400350003,75178.426873596007,2167.3679999999999,"OFF",-0.75289651512500155,-75.14639166260001,-1.7696810000000001,"OFF",-5.7217509143200109,-160.83416440970004,-1.7696810000000001,"OFF",-4.8711226198599862,-119.67758078056001,-4.2306439999999998,null,0,1968.3111597153586,0,0,0,1968.3111597153586,0,2031.1824036202727,0,0,0,2031.1824036202727,0,199.05684028464134,0,0,0,0,136.18559637972726,0,0,0,185.86569523562582,122.99445133071174,null,null,2150.7495879999992,null,50738.045700000075,11.854635689452406,8560.0345770463373,117.81496570909295,7935.2762958000076,104.62382066007743,-13.191145049015518,null,null,null,null,null,null,null,null,null,1968.3111597153586,0,21.094814666773345,0,0,0]
[0,1938.5103187641803,0,0,0,1938.5103187641803,2302.2053479999995,"2013-01-09T18:00:00",56,55,"OFF",-29.000579517700011,-73.058993676602014,-8.8484060000000007,"ON",39532.734113760009,74644.367662539997,2320.7869999999998,"OFF",5.5268280660000335E-2,-46.444647297834003,-1.7696810000000001,"OFF",-9.0879353849250091,-166.99199929652002,-1.7696810000000001,"OFF",-5.7926462006700143,-116.19862424140001,-6.1938839999999997,null,0,1918.754928679361,0,0,0,1918.754928679361,0,1979.3328531670586,0,0,0,1979.3328531670586,0,402.03207132063881,0,0,0,0,341.45414683294121,0,0,0,391.41140913766196,330.83348464996436,null,null,2302.2053479999995,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1918.754928679361,0,19.755390084819282,0,0,0]
[0,1906.949499000101,0,0,0,1906.949499000101,2296.7002089999992,"2013-01-09T19:00:00",57,55,"OFF",-28.887801389299995,-74.450592333934011,-8.8484060000000007,"ON",38704.216559810011,75523.3708606,2315.0329999999999,"OFF",-6.5218163160000717E-2,-46.444647297834003,-1.7696810000000001,"OFF",-6.0773972692299996,-166.99199929652002,-1.7696810000000001,"OFF",-6.2153065761500006,-120.37338813006001,-5.9450229999999999,null,0,1888.0170540515733,0,0,0,1888.0170540515733,0,1943.3918626486702,0,0,0,1943.3918626486702,0,427.01594594842663,0,0,0,0,371.64113735132969,0,0,0,413.82480089941112,358.44999230231417,null,null,2296.7002089999992,null,50738.045700000075,11.854635689452406,8560.0345770463373,117.81496570909295,7935.2762958000076,104.62382066007743,-13.191145049015518,null,null,null,null,null,null,null,null,null,1888.0170540515733,0,18.932444948527746,0,0,0]
[0,1932.3311922414268,0,0,0,1932.3311922414268,2096.6641629999999,"2013-01-09T20:00:00",56,54,"OFF",-29.158496978309991,-73.058993676602014,-8.8484060000000007,"ON",39371.544371444994,75336.509490901997,2114.9140000000002,"OFF",5.0091688458001181E-2,-33.398399859304,-1.7696810000000001,"OFF",-6.4519365956499932,-166.99199929652002,-3.401106,"OFF",-5.4734748325999965,-119.67758078056001,-4.2306439999999998,null,0,1912.7373929370001,0,0,0,1912.7373929370001,0,1970.6326818371444,0,0,0,1970.6326818371444,0,202.17660706300012,0,0,0,0,144.28131816285577,0,0,0,190.64739950295723,132.75211060281288,null,null,2096.6641629999999,null,48656.198400000052,11.722825422133701,8301.104323900101,112.22666623522937,7739.5826496000045,100.69745867518647,-11.529207560042906,null,null,null,null,null,null,null,null,null,1912.7373929370001,0,19.593799304426739,0,0,0]
[0,1937.8822064981862,0,0,0,1937.8822064981862,2413.6196709999999,"2013-01-09T21:00:00",56,54,"OFF",-29.235858953399983,-73.754793005267999,-8.8484060000000007,"ON",39516.371449654987,74722.017356494005,2432.7820000000002,"OFF",7.053024428999269E-3,-46.444647297834003,-1.7696810000000001,"OFF",-6.0527072911200079,-166.99199929652002,-2.3503579999999999,"OFF",-5.6654253094799998,-119.67758078056001,-6.1938839999999997,null,0,1918.1432525615028,0,0,0,1918.1432525615028,0,1978.4215236733064,0,0,0,1978.4215236733064,0,514.63874743849738,0,0,0,0,454.36047632669374,0,0,0,503.10953987845448,442.83126876665085,null,null,2413.6196709999999,null,48656.198400000052,11.722825422133701,8301.104323900101,112.22666623522937,7739.5826496000045,100.69745867518647,-11.529207560042906,null,null,null,null,null,null,null,null,null,1918.1432525615028,0,19.738953936683401,0,0,0]
[0,1908.2817000324292,0,0,0,1908.2817000324292,2066.8570909999999,"2013-01-09T22:00:00",56,55,"OFF",-29.067851144290021,-73.058993676602014,-8.8484060000000007,"ON",38739.454012049995,75288.66521609202,2085.5770000000002,"OFF",-0.41204422199999496,-46.444647297834003,-3.2905009999999999,"OFF",-6.5156773182200052,-166.99199929652002,-2.3503579999999999,"OFF",-6.3892782734899898,-119.67758078056001,-4.2306439999999998,null,0,1889.3146400756577,0,0,0,1889.3146400756577,0,1945.5003952188504,0,0,0,1945.5003952188504,0,196.26235992434249,0,0,0,0,140.07660478114985,0,0,0,185.64169774136565,129.45594259817301,null,null,2066.8570909999999,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1889.3146400756577,0,18.967059956771436,0,0,0]
[0,1857.4624950300681,0,0,0,1857.4624950300681,2218.7055879999994,"2013-01-09T23:00:00",56,55,"OFF",-28.586594196370005,-73.754793005267999,-8.8484060000000007,"ON",37378.037400800014,74093.336366740012,2235.3240000000001,"OFF",-6.190500674999469E-2,-33.398399859304,-1.7696810000000001,"OFF",-8.0392603069500002,-160.83416440970004,-1.7696810000000001,"OFF",-5.9973288699500031,-118.28596608156001,-4.2306439999999998,null,0,1839.8080178801952,0,0,0,1839.8080178801952,0,1895.5289166996417,0,0,0,1895.5289166996417,0,395.5159821198049,0,0,0,0,339.79508330035833,0,0,0,384.89531993682806,329.17442111738148,null,null,2218.7055879999994,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1839.8080178801952,0,17.654477149872946,0,0,0]
[0,1827.4375609847382,0,0,0,1827.4375609847382,2201.1153889999996,"2013-01-10",56,55,"OFF",-28.817578559350004,-73.754793005267999,-8.8484060000000007,"ON",36556.400415755001,75114.581034956005,2220.9690000000001,"OFF",-1.6980038659999277E-2,-75.14639166260001,-3.2905009999999999,"OFF",-5.734003678270005,-160.83416440970004,-1.7696810000000001,"OFF",-5.8202205353500203,-119.67758078056001,-5.9450229999999999,null,0,1810.5507342742503,0,0,0,1810.5507342742503,0,1861.0369953247382,0,0,0,1861.0369953247382,0,410.41826572574973,0,0,0,0,359.93200467526185,0,0,0,399.79760354277289,349.31134249228501,null,null,2201.1153889999996,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1810.5507342742503,0,16.886826710487867,0,0,0]
[0,1795.3929023135483,0,0,0,1795.3929023135483,1996.4054490000001,"2013-01-10T01:00:00",56,55,"OFF",-29.037866548950007,-71.667395019270003,-8.8484060000000007,"ON",35664.497957199994,74947.426854396006,2012.7750000000001,"OFF",-1.132959954000093E-2,-33.398399859304,-1.7696810000000001,"OFF",-6.3373666652100056,-166.99199929652002,-1.7696810000000001,"OFF",-5.9075235586500092,-117.59015873206,-3.9817830000000001,null,0,1779.3186189613002,0,0,0,1779.3186189613002,0,1827.8047453825113,0,0,0,1827.8047453825113,0,233.45638103869987,0,0,0,0,184.97025461748876,0,0,0,222.83571885572303,174.34959243451192,null,null,1996.4054490000001,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1779.3186189613002,0,16.074283352248131,0,0,0]
[0,1798.0693989789263,0,0,0,1798.0693989789263,2300.7061629999998,"2013-01-10T02:00:00",56,55,"OFF",-28.98329564042999,-71.641303246267995,-8.8484060000000007,"ON",35739.604297995,74277.719298732001,2318.9560000000001,"OFF",5.9609626249948443E-3,-75.14639166260001,-1.7696810000000001,"OFF",-6.3426630212400017,-166.99199929652002,-3.401106,"OFF",-8.0590754358799845,-120.37338813006001,-4.2306439999999998,null,0,1781.9275223730388,0,0,0,1781.9275223730388,0,1832.3773636507833,0,0,0,1832.3773636507833,0,537.02847762696138,0,0,0,0,486.57863634921682,0,0,0,526.40781544398453,475.95797416623998,null,null,2300.7061629999998,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1781.9275223730388,0,16.141876605887546,0,0,0]
[0,1802.9548252834747,0,0,0,1802.9548252834747,1982.562449,"2013-01-10T03:00:00",56,55,"OFF",-30.018148565549989,-71.693486792272012,-8.8484060000000007,"ON",35876.4054407,74929.676748754006,1998.932,"OFF",4.9095959589000093E-2,-46.444647297834003,-1.7696810000000001,"OFF",-6.4578390023700134,-164.80022619768002,-1.7696810000000001,"OFF",-6.0897613298199929,-118.98618488976001,-3.9817830000000001,null,0,1786.6894402987139,0,0,0,1786.6894402987139,0,1835.7993813422327,0,0,0,1835.7993813422327,0,212.24255970128615,0,0,0,0,163.13261865776735,0,0,0,201.62189751830931,152.51195647479051,null,null,1982.562449,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1786.6894402987139,0,16.265384984760885,0,0,0]
[0,1800.5271121987848,0,0,0,1800.5271121987848,2217.0484489999994,"2013-01-10T04:00:00",56,55,"OFF",-29.089589919039994,-72.363194347936002,-8.8484060000000007,"ON",35808.471760000015,74043.005633389999,2233.4180000000001,"OFF",-0.31286270437500102,-46.444647297834003,-1.7696810000000001,"OFF",-5.6504213831100056,-160.83416440970004,-1.7696810000000001,"OFF",-6.0949579400000111,-118.97736197236,-3.9817830000000001,null,0,1784.3231231322902,0,0,0,1784.3231231322902,0,1835.5941101563117,0,0,0,1835.5941101563117,0,449.0948768677099,0,0,0,0,397.82388984368845,0,0,0,438.47421468473306,387.2032276607116,null,null,2217.0484489999994,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1784.3231231322902,0,16.203989066494614,0,0,0]
[0,1851.7722116790674,0,0,0,1851.7722116790674,2212.1885319999992,"2013-01-10T05:00:00",56,55,"OFF",-29.654475264809996,-74.450592333934011,-8.8484060000000007,"ON",37223.335968210005,74919.442164570006,2231.1019999999999,"OFF",-0.76492384049999962,-46.444647297834003,-1.7696810000000001,"OFF",-5.9312600028500082,-166.99199929652002,-2.3503579999999999,"OFF",-6.6142782724899787,-119.67758078056001,-5.9450229999999999,null,0,1834.2636768568912,0,0,0,1834.2636768568912,0,1887.1614848427939,0,0,0,1887.1614848427939,0,396.83832314310871,0,0,0,0,343.94051515720594,0,0,0,386.21766096013187,333.31985297422909,null,null,2212.1885319999992,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1834.2636768568912,0,17.508534822176216,0,0,0]
[0,1833.3974515394893,0,0,0,1833.3974515394893,2125.8407719999996,"2013-01-10T06:00:00",56,55,"OFF",-30.731211831360007,-75.842190991265994,-8.8484060000000007,"ON",36720.553929289992,74389.834516383999,2142.7910000000002,"OFF",-0.68111903000000185,-33.398399859304,-1.7696810000000001,"OFF",-6.3686178007900027,-164.80022619768002,-2.3503579999999999,"OFF",-7.1597971379899894,-118.98177343106001,-3.9817830000000001,null,0,1816.3587261439689,0,0,0,1816.3587261439689,0,1869.3024697058524,0,0,0,1869.3024697058524,0,326.43227385603132,0,0,0,0,273.48853029414772,0,0,0,315.81161167305447,262.86786811117088,null,null,2125.8407719999996,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,1816.3587261439689,0,17.038725395520487,0,0,0]
[0,1915.9522227783359,0,0,0,1915.9522227783359,2138.0483469999995,"2013-01-10T07:00:00",57,55,"OFF",-30.07487024080001,-74.450592333934011,-8.8484060000000007,"ON",38941.883906724979,74428.174102903999,2156.63,"OFF",-0.60200160319000151,-46.444647297834003,-1.7696810000000001,"OFF",-7.2013841489099857,-164.80022619768002,-3.9817830000000001,"OFF",-7.4755612875300104,-116.19862424140001,-3.9817830000000001,null,0,1896.7856461120969,0,0,0,1896.7856461120969,0,1956.2315379225945,0,0,0,1956.2315379225945,0,259.84435388790325,0,0,0,0,200.39846207740561,0,0,0,246.65320883888774,187.20731702839009,null,null,2138.0483469999995,null,50738.045700000075,11.854635689452406,8560.0345770463373,117.81496570909295,7935.2762958000076,104.62382066007743,-13.191145049015518,null,null,null,null,null,null,null,null,null,1896.7856461120969,0,19.166576666239052,0,0,0]
[0,1909.3449944994313,0,0,0,1909.3449944994313,2054.4530846999996,"2013-01-10T08:00:00",54,52,"OFF",-30.001101591150007,-71.667395019270003,-8.8484060000000007,"ON",38767.561729325011,74952.471958982002,2071.6660000000002,"OFF",3.6060014686500053E-2,-75.14639166260001,-0.4009433,"OFF",-6.8969359022899974,-164.80022619768002,-3.9817830000000001,"OFF",-5.0914103547299865,-118.98177343106001,-3.9817830000000001,null,0,1890.3502988154464,0,0,0,1890.3502988154464,0,1947.6437841034417,0,0,0,1947.6437841034417,0,181.31570118455375,0,0,0,0,124.02221589655846,0,0,0,172.94048225546686,115.64699696747157,null,null,2054.4530846999996,null,44737.413600000087,11.46755306445518,7802.4341110167852,101.94781191265062,7371.2168784000078,93.572592983563723,-8.3752189290868984,null,null,null,null,null,null,null,null,null,1890.3502988154464,0,18.994695683984901,0,0,0]
[0,1909.3784746592742,0,0,0,1909.3784746592742,2363.5475879999995,"2013-01-10T09:00:00",56,53,"OFF",-30.146911222819995,-71.667395019270003,-8.8484060000000007,"ON",38768.44651758,74087.160324560013,2380.1660000000002,"OFF",-6.4735262196000135E-2,-62.100144224070007,-1.7696810000000001,"OFF",-8.6127237285000131,-166.99199929652002,-1.7696810000000001,"OFF",-5.3771542368999832,-118.28596608156001,-4.2306439999999998,null,0,1890.3829086913579,0,0,0,1890.3829086913579,0,1950.3628282377647,0,0,0,1950.3628282377647,0,489.78309130864227,0,0,0,0,429.80317176223548,0,0,0,477.33108017951747,417.35116063311068,null,null,2363.5475879999995,null,48656.198400000052,11.661978544854041,8344.4156946198564,113.14946980431128,7739.5826496000045,100.69745867518647,-12.452011129124813,null,null,null,null,null,null,null,null,null,1890.3829086913579,0,18.995565967916264,0,0,0]
[0,1948.5813913049369,0,0,0,1948.5813913049369,2162.7441069999995,"2013-01-10T10:00:00",57,53,"OFF",-29.966518917440013,-73.754793005267999,-8.8484060000000007,"ON",39794.404570515006,74646.300683534006,2183.2890000000002,"OFF",-0.37989419230999794,-46.444647297834003,-1.7696810000000001,"OFF",-5.9612199869600069,-160.83416440970004,-3.9817830000000001,"OFF",-6.8605046864900077,-117.59015873206,-5.9450229999999999,null,0,1928.5621485537993,0,0,0,1928.5621485537993,0,1989.944132678301,0,0,0,1989.944132678301,0,254.72685144620095,0,0,0,0,193.34486732169921,0,0,0,239.58002188000208,178.19803775550034,null,null,2162.7441069999995,null,50738.045700000075,11.732941934893086,8648.8190228075855,119.7706502262763,7935.2762958000076,104.62382066007743,-15.146829566198875,null,null,null,null,null,null,null,null,null,1928.5621485537993,0,20.019242751137654,0,0,0]
[0,1949.9947029687517,0,0,0,1949.9947029687517,2032.7004490000002,"2013-01-10T11:00:00",57,52,"OFF",-30.484155188789973,-72.363194347936002,-8.8484060000000007,"ON",39831.022951230014,74489.709941352005,2049.0700000000002,"OFF",-0.36751852474999969,-75.14639166260001,-1.7696810000000001,"OFF",-5.9943419746699984,-158.64239131086001,-1.7696810000000001,"OFF",-6.9716461954299929,-118.28596608156001,-3.9817830000000001,null,0,1929.9383851627483,0,0,0,1929.9383851627483,0,1991.9464378437053,0,0,0,1991.9464378437053,0,119.13161483725185,0,0,0,0,57.123562156294838,0,0,0,102.98392469252562,40.975872011568612,null,null,2032.7004490000002,null,50738.045700000075,11.672095057613426,8693.9054984657414,120.77151080480365,7935.2762958000076,104.62382066007743,-16.147690144726226,null,null,null,null,null,null,null,null,null,1929.9383851627483,0,20.056317806003335,0,0,0]
[0,2029.3068446302714,0,0,0,2029.3068446302714,2258.3954489999992,"2013-01-10T12:00:00",57,51,"OFF",-30.510409886669986,-71.566885948416015,-8.8484060000000007,"ON",41847.027407839989,74383.546182528007,2274.7649999999999,"OFF",-0.59051005587499972,-46.444647297834003,-1.7696810000000001,"OFF",-6.8880559421800065,-166.99199929652002,-1.7696810000000001,"OFF",-6.5671131783599996,-118.98177343106001,-3.9817830000000001,null,0,2007.1517885590399,0,0,0,2007.1517885590399,0,2076.0448077682649,0,0,0,2076.0448077682649,0,267.61321144095996,0,0,0,0,198.72019223173493,0,0,0,250.44888497992895,181.55586577070392,null,null,2258.3954489999992,null,50738.045700000075,11.611248180333764,8739.4645109620978,121.78814712110845,7935.2762958000076,104.62382066007743,-17.164326461031024,null,null,null,null,null,null,null,null,null,2007.1517885590399,0,22.155056071231456,0,0,0]
[0,2229.2028943256955,0,0,0,2229.2028943256955,2414.4674489999993,"2013-01-10T13:00:00",57,50,"OFF",-30.552438184519996,-71.767904090124006,-8.8484060000000007,"ON",46626.036095880008,74242.68429582,2430.837,"OFF",-3.4628329777500168E-2,-33.398399859304,-1.7696810000000001,"OFF",-7.1575376989899988,-160.83416440970004,-1.7696810000000001,"OFF",-8.0807263791799802,-120.37338813006001,-3.9817830000000001,null,0,2201.6143261609473,0,0,0,2201.6143261609473,0,2288.0761236242092,0,0,0,2288.0761236242092,0,229.22267383905273,0,0,0,0,142.76087637579076,0,0,0,211.02560202700084,124.56380456373887,null,null,2414.4674489999993,null,50738.045700000075,11.550401303054105,8785.5035281906876,122.82089247212932,7935.2762958000076,104.62382066007743,-18.197071812051888,null,null,null,null,null,null,null,null,null,2201.6143261609473,0,27.588568164748267,0,0,0]
[0,2161.3597978110743,0,0,0,2161.3597978110743,2317.8247719999995,"2013-01-10T14:00:00",58,51,"OFF",-30.525824654219992,-70.971595690604005,-8.8484060000000007,"ON",45048.519179999988,74384.66107845401,2334.7750000000001,"OFF",0.44582473598000022,-33.398399859304,-1.7696810000000001,"OFF",-7.4733686278900002,-166.99199929652002,-2.3503579999999999,"OFF",-6.5687100724000107,-116.89884304960002,-3.9817830000000001,null,0,2135.6368531162052,0,0,0,2135.6368531162052,0,2215.6408229915746,0,0,0,2215.6408229915746,0,199.13814688379489,0,0,0,0,119.13417700842547,0,0,0,178.98714253365387,98.983172658284445,null,null,2317.8247719999995,null,52896.528800000029,11.684823835050604,9053.8855436276153,128.94923959949966,8138.1737072000033,108.79823524935864,-20.151004350141022,null,null,null,null,null,null,null,null,null,2135.6368531162052,0,25.722944694869057,0,0,0]
[0,2235.2082846961944,0,0,0,2235.2082846961944,2270.4803469999993,"2013-01-10T15:00:00",56,50,"OFF",-30.610504605170011,-74.450592333934011,-8.8484060000000007,"ON",46763.645213430013,74159.452101401999,2289.0619999999999,"OFF",4.4973643941000133E-2,-33.398399859304,-1.7696810000000001,"OFF",-7.1859957313899887,-164.80022619768002,-3.9817830000000001,"OFF",-6.223202802530003,-121.06478402086002,-3.9817830000000001,null,0,2207.4535736452267,0,0,0,2207.4535736452267,0,2294.8181579855413,0,0,0,2294.8181579855413,0,81.608426354773201,0,0,0,0,-5.7561579855414493,0,0,0,66.299416328915399,-21.065168011399251,null,null,2270.4803469999993,null,48656.198400000052,11.479437913015058,8477.1046751052236,116.00646870104427,7739.5826496000045,100.69745867518647,-15.309010025857802,null,null,null,null,null,null,null,null,null,2207.4535736452267,0,27.754711050967671,0,0,0]
[0,2095.5527861478981,0,0,0,2095.5527861478981,2269.0609109999996,"2013-01-10T16:00:00",55,49,"OFF",-30.001669857459991,-75.14639166260001,-8.8484060000000007,"ON",43475.872451009993,74127.336682066001,2286.2600000000002,"OFF",0.11938425213499938,-75.14639166260001,-1.7696810000000001,"OFF",-7.6563174168599977,-164.80022619768002,-2.3503579999999999,"OFF",-6.2397979377299864,-119.67758078056001,-4.2306439999999998,null,0,2071.6187825771231,0,0,0,2071.6187825771231,0,2147.0629526603489,0,0,0,2147.0629526603489,0,214.64121742287716,0,0,0,0,139.19704733965136,0,0,0,201.12727867758042,125.68310859435464,null,null,2269.0609109999996,null,46654.737500000047,11.350367756105523,8220.8327522962954,110.52907666077118,7551.4453250000042,97.015137915474455,-13.513938745296727,null,null,null,null,null,null,null,null,null,2071.6187825771231,0,23.934003570775076,0,0,0]
[0,2104.5771059424969,0,0,0,2104.5771059424969,2375.1173479999998,"2013-01-10T17:00:00",54,49,"OFF",-30.186699768120004,-73.754793005267999,-8.8484060000000007,"ON",43694.130717140004,74136.705016178006,2393.6990000000001,"OFF",0.1159635597500035,-62.100144224070007,-1.7696810000000001,"OFF",-7.0096086305700007,-166.99199929652002,-1.7696810000000001,"OFF",-5.8763631814300128,-118.98177343106001,-6.1938839999999997,null,0,2080.3990322307204,0,0,0,2080.3990322307204,0,2156.5765312033172,0,0,0,2156.5765312033172,0,313.29996776927965,0,0,0,0,237.12246879668282,0,0,0,302.38344830257262,226.20594932997579,null,null,2375.1173479999998,null,44737.413600000087,11.285012432616197,7928.6423239905353,104.48911245027077,7371.2168784000078,93.572592983563723,-10.916519466707044,null,null,null,null,null,null,null,null,null,2080.3990322307204,0,24.178073711776506,0,0,0]
[0,2026.2769612773434,0,0,0,2026.2769612773434,2111.9260239999999,"2013-01-10T18:00:00",54,49,"OFF",-30.406063767870005,-72.363194347936002,-8.8484060000000007,"ON",41771.370282130018,74321.890031570001,2129.9270000000001,"OFF",-0.33239686087500214,-62.100144224070007,-1.7696810000000001,"OFF",-7.6510210608300016,-166.99199929652002,-3.401106,"OFF",-6.6065943102599833,-118.98177343106001,-3.9817830000000001,null,0,2004.2027186373841,0,0,0,2004.2027186373841,0,2073.0673850044163,0,0,0,2073.0673850044163,0,125.72428136261601,0,0,0,0,56.859614995583797,0,0,0,114.80776189590897,45.943095528876754,null,null,2111.9260239999999,null,44737.413600000087,11.285012432616197,7928.6423239905353,104.48911245027077,7371.2168784000078,93.572592983563723,-10.916519466707044,null,null,null,null,null,null,null,null,null,2004.2027186373841,0,22.074242639959266,0,0,0]
[0,2041.1959410365009,0,0,0,2041.1959410365009,2289.3286709999998,"2013-01-10T19:00:00",51,48,"OFF",-30.653833099959996,-71.667395019270003,-8.8484060000000007,"ON",42142.900132080009,73982.504482528006,2308.491,"OFF",-0.34276120649999664,-33.398399859304,-1.7696810000000001,"OFF",-6.9228643318100076,-164.80022619768002,-2.3503579999999999,"OFF",-7.2069622321199986,-120.37338813006001,-6.1938839999999997,null,0,2018.7233039727273,0,0,0,2018.7233039727273,0,2090.0916990911846,0,0,0,2090.0916990911846,0,289.76769602727268,0,0,0,0,218.39930090881535,0,0,0,284.82542690213654,213.45703178367921,null,null,2289.3286709999998,null,39527.769900000014,11.046585779025584,7156.5587215286623,89.580905900400595,6881.5103706000009,84.638636775264473,-4.9422691251361215,null,null,null,null,null,null,null,null,null,2018.7233039727273,0,22.472637063773618,0,0,0]
[0,2029.6681650725318,0,0,0,2029.6681650725318,2342.9429109999992,"2013-01-10T20:00:00",51,48,"OFF",-30.705584558880023,-71.667395019270003,-8.8484060000000007,"ON",41856.042737355012,74484.528482588008,2360.1419999999998,"OFF",0.11071697574999409,-46.444647297834003,-1.7696810000000001,"OFF",-6.8301912763000052,-164.80022619768002,-2.3503579999999999,"OFF",-8.258161502499993,-117.59457019076001,-4.2306439999999998,null,0,2007.5034685326771,0,0,0,2007.5034685326771,0,2076.0599898438099,0,0,0,2076.0599898438099,0,352.63853146732276,0,0,0,0,284.08201015618988,0,0,0,347.69626234218663,279.13974103105375,null,null,2342.9429109999992,null,39527.769900000014,11.046585779025584,7156.5587215286623,89.580905900400595,6881.5103706000009,84.638636775264473,-4.9422691251361215,null,null,null,null,null,null,null,null,null,2007.5034685326771,0,22.164696539854731,0,0,0]
[0,1821.7691538492188,0,0,0,1821.7691538492188,1704.5890239999999,"2013-01-10T21:00:00",48,46,"OFF",-30.882393260179992,-73.754793005267999,-8.8484060000000007,"ON",36399.779051940008,61391.102498470005,1722.59,"OFF",-9.9790688220002151E-3,-62.100144224070007,-1.7696810000000001,"OFF",-6.7233682546799871,-166.99199929652002,-3.401106,"OFF",53.274891072599921,1732.5466648372001,-3.9817830000000001,null,0,1805.0265735739229,0,0,0,1805.0265735739229,0,1900.3878363214228,0,0,0,1900.3878363214228,0,-82.436573573922942,0,0,0,0,-177.79783632142289,0,0,0,-83.406410726283383,-178.76767347378333,null,null,1704.5890239999999,null,35210.380800000043,10.777726299749748,6533.9163049292883,78.669839718170635,6475.6757952000044,77.700002565810195,-0.96983715236044077,null,null,null,null,null,null,null,null,null,1805.0265735739229,0,16.74258027529595,0,0,0]
[0,2107.8530374984139,0,0,0,2107.8530374984139,2477.2581669999995,"2013-01-10T22:00:00",49,47,"OFF",-31.036145685230021,-74.450592333934011,-8.8484060000000007,"ON",43773.152449859997,74031.014486560001,2494.319,"OFF",-0.10775406112499393,-46.444647297834003,-2.460963,"OFF",-6.6067957219600002,-160.83416440970004,-1.7696810000000001,"OFF",24.085018760880008,-118.98177343106001,-3.9817830000000001,null,0,2083.586263313543,0,0,0,2083.586263313543,0,2160.4679554636264,0,0,0,2160.4679554636264,0,410.73273668645697,0,0,0,0,333.85104453637359,0,0,0,408.78740345558765,331.90571130550427,null,null,2477.2581669999995,null,36544.120100000058,10.884036003316574,6715.1780991654878,81.743829636495121,6601.047289400005,79.798496405625798,-1.9453332308693234,null,null,null,null,null,null,null,null,null,2083.586263313543,0,24.266774184870883,0,0,0]
[0,2035.2723599871847,0,0,0,2035.2723599871847,2091.7615319999995,"2013-01-10T23:00:00",48,46,"OFF",-31.003629748209999,-72.363194347936002,-8.8484060000000007,"ON",41995.684359264997,73986.298337009997,2110.6750000000002,"OFF",0.13036824349999906,-62.100144224070007,-1.7696810000000001,"OFF",-6.7154105456200082,-164.80022619768002,-2.3503579999999999,"OFF",20.075051797569984,-120.37338813006001,-5.9450229999999999,null,0,2012.9580473875144,0,0,0,2012.9580473875144,0,2083.8087216449462,0,0,0,2083.8087216449462,0,97.716952612485784,0,0,0,0,26.866278355053964,0,0,0,96.747115460125343,25.896441202693524,null,null,2091.7615319999995,null,35210.380800000043,10.777726299749748,6533.9163049292883,78.669839718170635,6475.6757952000044,77.700002565810195,-0.96983715236044077,null,null,null,null,null,null,null,null,null,2012.9580473875144,0,22.314312599670302,0,0,0]
[0,2010.0798549571834,0,0,0,2010.0798549571834,2178.8391069999993,"2013-01-11",50,47,"OFF",-31.024130071550029,-73.754793005267999,-8.8484060000000007,"ON",41365.141213670002,73418.190685624009,2199.384,"OFF",0.2016889947500034,-46.444647297834003,-1.7696810000000001,"OFF",-9.1339224114749857,-166.99199929652002,-3.9817830000000001,"OFF",18.108042372349974,-116.20303570010002,-5.9450229999999999,null,0,1988.4367831326899,0,0,0,1988.4367831326899,0,2059.2067880422137,0,0,0,2059.2067880422137,0,210.94721686731009,0,0,0,0,140.17721195778631,0,0,0,207.23247806211089,136.46247315258711,null,null,2178.8391069999993,null,37984.500000000058,10.933133860132539,6948.5109184494313,85.824709099278039,6736.4430000000057,82.109970294078821,-3.7147388051992181,null,null,null,null,null,null,null,null,null,1988.4367831326899,0,21.643071824493518,0,0,0]
[0,1939.6271435133476,0,0,0,1939.6271435133476,2283.1304489999993,"2013-01-11T01:00:00",49,46,"OFF",-31.334717875159999,-73.133410974454009,-8.8484060000000007,"ON",39561.815536289992,73971.355523268008,2299.5,"OFF",6.9861441660004032E-3,-33.398399859304,-1.7696810000000001,"OFF",-7.3795103517099836,-166.99199929652002,-1.7696810000000001,"OFF",17.01093056924001,-118.28155462286001,-3.9817830000000001,null,0,1919.8425231178444,0,0,0,1919.8425231178444,0,1982.6972639905132,0,0,0,1982.6972639905132,0,379.65747688215561,0,0,0,0,316.80273600948681,0,0,0,377.06132925545751,314.20658838278871,null,null,2283.1304489999993,null,36544.120100000058,10.823189126036914,6752.9301529227332,82.394644032323896,6601.047289400005,79.798496405625798,-2.5961476266980981,null,null,null,null,null,null,null,null,null,1919.8425231178444,0,19.784620395503225,0,0,0]
[0,1938.5461489115637,0,0,0,1938.5461489115637,1995.3165879999999,"2013-01-11T02:00:00",47,45,"OFF",-31.780534032729982,-73.680375707416005,-8.8484060000000007,"ON",39533.667356219994,74175.790540260001,2011.9349999999999,"OFF",-0.4657397301249967,-33.398399859304,-1.7696810000000001,"OFF",-7.5637761115000002,-164.80022619768002,-1.7696810000000001,"OFF",16.205571394349995,-119.67758078056001,-4.2306439999999998,null,0,1918.7898211698218,0,0,0,1918.7898211698218,0,1980.8868787079336,0,0,0,1980.8868787079336,0,93.145178830178111,0,0,0,0,31.048121292066298,0,0,0,93.034298005497845,30.937240467386033,null,null,1995.3165879999999,null,33987.03270000004,10.675179472443098,6367.4868956974724,75.921458389605164,6360.681073800004,75.810577564924898,-0.11088082468026528,null,null,null,null,null,null,null,null,null,1918.7898211698218,0,19.75632774174187,0,0,0]
[0,1961.4715917495973,0,0,0,1961.4715917495973,2259.6796399999994,"2013-01-11T03:00:00",48,45,"OFF",-32.290872446159987,-74.450592333934011,-8.8484060000000007,"ON",40127.457492149988,73533.915278576009,2277.8879999999999,"OFF",-0.35627584475000096,-46.444647297834003,-1.147527,"OFF",-7.7869345155700049,-160.83416440970004,-3.9817830000000001,"OFF",14.687536640520008,-116.62035969312001,-4.2306439999999998,null,0,1941.113773337479,0,0,0,1941.113773337479,0,2007.2779742941007,0,0,0,2007.2779742941007,0,336.77422666252096,0,0,0,0,270.61002570589926,0,0,0,335.18210614290069,269.01790518627899,null,null,2259.6796399999994,null,35210.380800000043,10.71687942247009,6571.0137087433131,79.292123085430461,6475.6757952000044,77.700002565810195,-1.5921205196202664,null,null,null,null,null,null,null,null,null,1941.113773337479,0,20.357818412118377,0,0,0]
[0,1927.2850690259827,0,0,0,1927.2850690259827,2088.9804489999992,"2013-01-11T04:00:00",48,46,"OFF",-32.748499800855015,-73.058993676602014,-8.8484060000000007,"ON",39239.544982185005,73875.169681940009,2105.35,"OFF",-0.32346127250000334,-46.444647297834003,-1.7696810000000001,"OFF",-7.4736326588699962,-166.99199929652002,-1.7696810000000001,"OFF",12.692504660570027,-117.86423062984001,-3.9817830000000001,null,0,1907.823062594149,0,0,0,1907.823062594149,0,1969.9619138296391,0,0,0,1969.9619138296391,0,197.52693740585096,0,0,0,0,135.38808617036079,0,0,0,196.55710025349052,134.41824901800035,null,null,2088.9804489999992,null,35210.380800000043,10.777726299749748,6533.9163049292883,78.669839718170635,6475.6757952000044,77.700002565810195,-0.96983715236044077,null,null,null,null,null,null,null,null,null,1907.823062594149,0,19.462006431833743,0,0,0]
[0,1920.3177468767169,0,0,0,1920.3177468767169,2011.103347,"2013-01-11T05:00:00",46,44,"OFF",-32.540350853970004,-72.363194347936002,-8.8484060000000007,"ON",39056.745274949986,73565.493302033996,2029.6849999999999,"OFF",-0.1938191187500018,-46.444647297834003,-1.7696810000000001,"OFF",-9.4701217319099786,-166.99199929652002,-3.9817830000000001,"OFF",12.760683905550009,-117.59015873206,-3.9817830000000001,null,0,1901.0374595371404,0,0,0,1901.0374595371404,0,1963.5916994934091,0,0,0,1963.5916994934091,0,128.64754046285952,0,0,0,0,66.093300506590822,0,0,0,129.27473282257833,66.720492866309627,null,null,2011.103347,null,32877.826400000049,10.576523367127997,6217.1330329935945,73.499511231923378,6256.415681600005,74.126703591642183,0.62719235971880494,null,null,null,null,null,null,null,null,null,1901.0374595371404,0,19.280287339576489,0,0,0]
[0,1965.4656215463544,0,0,0,1965.4656215463544,2317.9439109999994,"2013-01-11T06:00:00",49,46,"OFF",-32.688266216199999,-73.058993676602014,-8.8484060000000007,"ON",40230.234199250001,73597.496429694002,2335.143,"OFF",-9.5258320639998145E-2,-33.398399859304,-1.7696810000000001,"OFF",-8.1470076755200136,-164.80022619768002,-2.3503579999999999,"OFF",12.64512730229001,-119.67758078056001,-4.2306439999999998,null,0,1945.002700457452,0,0,0,1945.002700457452,0,2011.2909481563579,0,0,0,2011.2909481563579,0,390.14029954254806,0,0,0,0,323.85205184364213,0,0,0,387.54415191584997,321.25590421694403,null,null,2317.9439109999994,null,36544.120100000058,10.823189126036914,6752.9301529227332,82.394644032323896,6601.047289400005,79.798496405625798,-2.5961476266980981,null,null,null,null,null,null,null,null,null,1945.002700457452,0,20.462921088902476,0,0,0]
[0,1985.2323924146408,0,0,0,1985.2323924146408,2019.0593470000001,"2013-01-11T07:00:00",51,47,"OFF",-33.609811574389994,-75.246908754288015,-8.8484060000000007,"ON",40736.008665239991,73441.699750078013,2037.6410000000001,"OFF",-0.43115325355999989,-75.14639166260001,-1.7696810000000001,"OFF",-8.9037541870899997,-158.64239131086001,-3.9817830000000001,"OFF",11.025042403830017,-118.70778174162001,-3.9817830000000001,null,0,1964.2479702380567,0,0,0,1964.2479702380567,0,2032.7774560767832,0,0,0,2032.7774560767832,0,73.393029761943353,0,0,0,0,4.8635439232168665,0,0,0,67.722547482361549,-0.80693835636493816,null,null,2019.0593470000001,null,39527.769900000014,10.985738901745924,7196.1968609536143,90.309119054846278,6881.5103706000009,84.638636775264473,-5.6704822795818046,null,null,null,null,null,null,null,null,null,1964.2479702380567,0,20.984422176584076,0,0,0]
[0,1937.9629722696354,0,0,0,1937.9629722696354,2218.6891069999992,"2013-01-11T08:00:00",48,45,"OFF",-33.529488461909992,-75.120299889598002,-8.8484060000000007,"ON",39518.475724665004,73300.829842536012,2239.2339999999999,"OFF",-4.2906546641999825E-2,-46.444647297834003,-1.7696810000000001,"OFF",-7.6952627612000022,-164.80022619768002,-3.9817830000000001,"OFF",11.319139140574991,-119.25584532884001,-5.9450229999999999,null,0,1918.2219050228105,0,0,0,1918.2219050228105,0,1983.1527679064382,0,0,0,1983.1527679064382,0,321.01209497718946,0,0,0,0,256.08123209356177,0,0,0,319.4199744575692,254.4891115739415,null,null,2218.6891069999992,null,35210.380800000043,10.71687942247009,6571.0137087433131,79.292123085430461,6475.6757952000044,77.700002565810195,-1.5921205196202664,null,null,null,null,null,null,null,null,null,1918.2219050228105,0,19.741067246824969,0,0,0]
[0,2066.4220513910968,0,0,0,2066.4220513910968,2299.4661669999996,"2013-01-11T09:00:00",52,48,"OFF",-33.340591208879985,-72.288777050083993,-8.8484060000000007,"ON",42765.479850129988,73517.167777184004,2316.527,"OFF",5.2577091198000407E-2,-75.14639166260001,-2.460963,"OFF",-8.7892896567699896,-166.99199929652002,-1.7696810000000001,"OFF",11.324716930799999,-119.67758078056001,-3.9817830000000001,null,0,2043.2731104171407,0,0,0,2043.2731104171407,0,2118.5910330447082,0,0,0,2118.5910330447082,0,273.2538895828593,0,0,0,0,197.93596695529186,0,0,0,266.21625500786206,190.89833238029462,null,null,2299.4661669999996,null,41170.179200000071,11.102570159705023,7416.3330846438703,94.426555420650587,7035.8968448000069,87.388920845653359,-7.0376345749972273,null,null,null,null,null,null,null,null,null,2043.2731104171407,0,23.148940973956087,0,0,0]
[0,2049.4878346949604,0,0,0,2049.4878346949604,2275.7004489999995,"2013-01-11T10:00:00",57,50,"OFF",-32.994601201400023,-74.450592333934011,-8.8484060000000007,"ON",42348.316897994999,73198.467959027999,2292.0700000000002,"OFF",-0.35333820161499696,-46.444647297834003,-1.7696810000000001,"OFF",-7.6813235953300154,-164.80022619768002,-1.7696810000000001,"OFF",8.6270246426499906,-120.09939644062001,-3.9817830000000001,null,0,2026.7932617957481,0,0,0,2026.7932617957481,0,2101.8503759594932,0,0,0,2101.8503759594932,0,265.27673820425207,0,0,0,0,190.21962404050691,0,0,0,247.07966639220018,172.02255222845503,null,null,2275.7004489999995,null,50738.045700000075,11.550401303054105,8785.5035281906876,122.82089247212932,7935.2762958000076,104.62382066007743,-18.197071812051888,null,null,null,null,null,null,null,null,null,2026.7932617957481,0,22.694572899212289,0,0,0]
[0,2093.1459040254517,0,0,0,2093.1459040254517,2631.0477719999994,"2013-01-11T11:00:00",62,53,"OFF",-33.486118774570009,-73.754793005267999,-8.8484060000000007,"ON",43417.51742405002,73202.486396862005,2647.998,"OFF",0.1344879184739998,-62.100144224070007,-1.7696810000000001,"OFF",-7.7532855272600152,-164.80022619768002,-2.3503579999999999,"OFF",8.3157343739000034,-119.25584532884001,-3.9817830000000001,null,0,2069.2769278044616,0,0,0,2069.2769278044616,0,2148.2094173605847,0,0,0,2148.2094173605847,0,578.72107219553845,0,0,0,0,499.78858263941538,0,0,0,547.89592377979079,468.96343422366778,null,null,2631.0477719999994,null,62221.807200000039,12.124385940627738,10263.91068458161,158.8692640525677,9014.7498768000041,128.0441156368201,-30.825148415747606,null,null,null,null,null,null,null,null,null,2069.2769278044616,0,23.868976220990135,0,0,0]
[0,2197.537226505428,0,0,0,2197.537226505428,2424.9643469999992,"2013-01-11T12:00:00",67,55,"OFF",-33.400981827639981,-73.754793005267999,-8.8484060000000007,"ON",45895.051734860011,69371.639828454005,2443.5459999999998,"OFF",-0.16750030195799998,-33.398399859304,-1.7696810000000001,"OFF",-7.8705958608199929,-166.99199929652002,-3.9817830000000001,"OFF",8.3655408169000083,-116.89443159090001,-3.9817830000000001,null,0,2170.8220475857925,0,0,0,2170.8220475857925,0,2277.5200984275998,0,0,0,2277.5200984275998,0,272.72395241420736,0,0,0,0,166.02590157240002,0,0,0,227.02638771812249,120.32833687631515,null,null,2424.9643469999992,null,75152.638700000127,12.686849601444678,11847.328700332719,203.68377258717098,10230.248037800013,157.98620789108611,-45.697564696084868,null,null,null,null,null,null,null,null,null,2170.8220475857925,0,26.715178919635491,0,0,0]
[0,2306.4068297081335,0,0,0,2306.4068297081335,2829.4300239999998,"2013-01-11T13:00:00",69,57,"OFF",-33.497133087109987,-73.058993676602014,-8.8484060000000007,"ON",46955.323194660014,64299.103990174008,2847.431,"OFF",-0.63050354774999595,-62.100144224070007,-1.7696810000000001,"OFF",-6.738545871960012,-164.80022619768002,-3.401106,"OFF",8.3672829816799918,-117.59457019076001,-3.9817830000000001,null,0,2278.3099524870445,0,0,0,2278.3099524870445,0,2419.7023905138026,0,0,0,2419.7023905138026,0,569.12104751295556,0,0,0,0,427.72860948619746,0,0,0,519.80957045319769,378.41713242643959,null,null,2829.4300239999998,null,80625.134100000141,12.995082890174963,12408.560188709134,221.10862842472611,10744.662605400013,171.79715136496822,-49.311477059757891,null,null,null,null,null,null,null,null,null,2278.3099524870445,0,28.096877221089017,0,0,0]
[0,2400.8526159486537,0,0,0,2400.8526159486537,2656.2454489999991,"2013-01-11T14:00:00",68,58,"OFF",-33.448069331250011,-70.971595690604005,-8.8484060000000007,"ON",48317.218496949994,64348.327848432004,2672.6149999999998,"OFF",-0.51290955777000191,-33.398399859304,-1.7696810000000001,"OFF",-9.0421232725999943,-160.83416440970004,-1.7696810000000001,"OFF",6.961075440759986,-118.97736197236,-3.9817830000000001,null,0,2371.0095157108208,0,0,0,2371.0095157108208,0,2520.8970839474309,0,0,0,2520.8970839474309,0,301.605484289179,0,0,0,0,151.71791605256885,0,0,0,257.55497719529774,107.66740895868759,null,null,2656.2454489999991,null,77871.196800000151,12.962057019552809,12015.252931310852,208.81286784431873,10485.792499200013,164.76236075043747,-44.050507093881265,null,null,null,null,null,null,null,null,null,2371.0095157108208,0,29.843100237832914,0,0,0]
[0,2534.4917465097856,0,0,0,2534.4917465097856,2964.6020239999998,"2013-01-11T15:00:00",69,59,"OFF",-32.886655592069992,-73.754793005267999,-8.8484060000000007,"ON",50418.151714720028,63756.069465872002,2982.6030000000001,"OFF",-0.35662717850000425,-62.100144224070007,-1.7696810000000001,"OFF",-7.7374491592300068,-166.99199929652002,-3.401106,"OFF",6.0348525376000071,-116.62035969312001,-3.9817830000000001,null,0,2501.8690531768689,0,0,0,2501.8690531768689,0,2670.0839644658308,0,0,0,2670.0839644658308,0,480.73394682313119,0,0,0,0,312.51903553416923,0,0,0,435.06249669957253,266.84758541061058,null,null,2964.6020239999998,null,80625.134100000141,13.116776644734284,12293.437066699922,217.46860148852684,10744.662605400013,171.79715136496822,-45.671450123558628,null,null,null,null,null,null,null,null,null,2501.8690531768689,0,32.622693332916697,0,0,0]
[0,2560.5265857846894,0,0,0,2560.5265857846894,2798.8855879999992,"2013-01-11T16:00:00",71,59,"OFF",-33.572801979284989,-75.14639166260001,-8.8484060000000007,"ON",50946.960009110022,64482.997651292004,2815.5039999999999,"OFF",-0.15583994037500418,-33.398399859304,-1.7696810000000001,"OFF",-8.0306195930099911,-166.99199929652002,-1.7696810000000001,"OFF",5.7941745025500166,-115.50281689190001,-4.2306439999999998,null,0,2527.198236359297,0,0,0,2527.198236359297,0,2693.6699878512177,0,0,0,2693.6699878512177,0,288.30576364070293,0,0,0,0,121.83401214878222,0,0,0,235.96571916423218,69.49396767231147,null,null,2798.8855879999992,null,86224.143900000025,13.307628642510409,12958.603852915199,238.96852968548947,11270.969526600002,186.62848520901872,-52.340044476470752,null,null,null,null,null,null,null,null,null,2527.198236359297,0,33.328349425392389,0,0,0]
[0,2608.0291274467672,0,0,0,{"$f":"SUM(A260:E260)","v":2608.0291274467672},{"$f":"N260+R260+V260+Z260+AD260","v":3019.0397719999992},"2013-01-11T17:00:00",70,58,"OFF",-32.585738249470019,-73.654283934414011,-8.8484060000000007,"ON",52596.788849919983,66696.418981098017,3035.99,"OFF",-0.33357968449999476,-46.444647297834003,-1.7696810000000001,"OFF",-7.5874911385000194,-166.99199929652002,-2.3503579999999999,"OFF",3.7883207378799848,-119.25584532884001,-3.9817830000000001,null,0,2572.5144323592153,0,0,0,{"$f":"SUM(AF260:AJ260)","v":2572.5144323592153},0,2733.2253409682962,0,0,0,{"$f":"SUM(AL260:AP260)","v":2733.2253409682962},{"$f":"IF($K260=\"ON\",$N260-AF260,0)","v":0},{"$f":"IF($O260=\"ON\",$R260-AG260,0)","v":463.47556764078445},{"$f":"IF($S260=\"ON\",$V260-AH260,0)","v":0},{"$f":"IF($W260=\"ON\",$Z260-AI260,0)","v":0},{"$f":"IF($AA260=\"ON\",$AD260-AJ260,0)","v":0},{"$f":"IF($K260=\"ON\",$N260-AL260,0)","v":0},{"$f":"IF($O260=\"ON\",$R260-AM260,0)","v":302.76465903170356},{"$f":"IF($S260=\"ON\",$V260-AN260,0)","v":0},{"$f":"IF($W260=\"ON\",$Z260-AO260,0)","v":0},{"$f":"IF($AA260=\"ON\",$AD260-AP260,0)","v":0},{"$f":"SUM(AR260:AV260)+BN260","v":412.56889520522543},{"$f":"SUM(AW260:BA260)+BN260","v":251.85798659614454},null,null,{"$f":"N260+R260+V260+Z260+AD260","v":3019.0397719999992},null,83410.700000000012,{"$f":"19.5285952781395+42*-0.3035722016559+BH260*0.0000340867411548605+J260*0.0608468772796604","v":13.150880631257724},{"$f":"BH260*1000/(500*BI260)","v":12685.188519123953},{"$f":"0.00000128*BJ260^2+0*BJ260+24.024","v":229.9939299401141},{"$f":"0.094*BH260 + 3165.9","v":11006.505800000001},{"$f":"0.00000128*BL260^2+0*BL260+24.024","v":179.08725750455508},{"$f":"BM260-BK260","v":-50.906672435559017},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF260:AJ260)","v":2572.5144323592153},{"$f":"A260-AF260","v":0},{"$f":"B260-AG260","v":35.5146950875519},{"$f":"C260-AH260","v":0},{"$f":"D260-AI260","v":0},{"$f":"E260-AJ260","v":0}]
[0,2528.5153766984822,0,0,0,2528.5153766984822,2913.0537719999993,"2013-01-11T18:00:00",66,58,"OFF",-32.646620517929989,-73.855302076122015,-8.8484060000000007,"ON",50987.831349,65599.890764958007,2930.0039999999999,"OFF",-0.12235171512599924,-62.100144224070007,-1.7696810000000001,"OFF",-7.9549423068500102,-160.83416440970004,-2.3503579999999999,"OFF",3.1525688938800118,-120.37338813006001,-3.9817830000000001,null,0,2495.1970366921682,0,0,0,2495.1970366921682,0,2653.569578529999,0,0,0,2653.569578529999,0,434.80696330783167,0,0,0,0,276.43442147000087,0,0,0,397.5534894221463,239.18094758431548,null,null,2913.0537719999993,null,{"$f":" -0.6251*I261^3 + 145.21*I261^2 - 8340.3*I261 + 170112","v":72473.210400000098},12.778057254378549,11343.384828733071,188.72464559709647,9978.3817776000087,151.47117171141107,-37.253473885685395,null,null,null,null,null,null,null,null,null,2495.1970366921682,0,33.318340006313974,0,0,0]
[0,2759.0751799016252,0,0,0,2759.0751799016252,3013.8487839999998,"2013-01-11T19:00:00",66,60,"OFF",-32.480407955429989,-72.363194347936002,-8.8484060000000007,"ON",54153.848745765004,68318.624636764012,3033.8130000000001,"OFF",-6.6433375475999951E-2,-33.398399859304,-1.7696810000000001,"OFF",-11.41975251307502,-164.80022619768002,-3.401106,"OFF",4.9862122419899872,-119.67758078056001,-5.9450229999999999,null,0,2721.2138303240968,0,0,0,2721.2138303240968,0,2880.2585439813265,0,0,0,2880.2585439813265,0,312.59916967590334,0,0,0,0,153.55445601867359,0,0,0,278.43854600837682,119.39383235114707,null,null,3013.8487839999998,null,72473.210400000098,12.899751008937869,11236.373531517853,185.6317953789376,9978.3817776000087,151.47117171141107,-34.160623667526522,null,null,null,null,null,null,null,null,null,2721.2138303240968,0,37.861349577528472,0,0,0]
[0,2505.9393198184393,0,0,0,2505.9393198184393,2767.5607719999994,"2013-01-11T20:00:00",65,60,"OFF",-32.321668309739998,-73.058993676602014,-8.8484060000000007,"ON",49153.886435550005,65272.079279378006,2784.511,"OFF",-0.22101388424000182,-46.444647297834003,-1.7696810000000001,"OFF",-8.6190948130000038,-166.99199929652002,-2.3503579999999999,"OFF",2.8059622516799818,-117.59015873206,-3.9817830000000001,null,0,2474.9096949656787,0,0,0,2474.9096949656787,0,2624.5350579385772,0,0,0,2624.5350579385772,0,309.60130503432129,0,0,0,0,159.97594206142276,0,0,0,278.61999748581422,128.99463451291567,null,null,2767.5607719999994,null,69836.662499999977,12.809879683128177,10903.56259816889,176.20022698520003,9730.5462749999988,145.21891943669294,-30.98130754850709,null,null,null,null,null,null,null,null,null,2474.9096949656787,0,31.029624852760662,0,0,0]
[0,2570.9758126846286,0,0,0,2570.9758126846286,2745.5825319999994,"2013-01-11T21:00:00",65,61,"OFF",-32.56234410023999,-75.14639166260001,-8.8484060000000007,"ON",49802.758064999995,67929.076791886007,2764.4960000000001,"OFF",0.14155236787499587,-33.398399859304,-1.7696810000000001,"OFF",-8.1544120339500239,-164.80022619768002,-2.3503579999999999,"OFF",3.0182282369499887,-114.80700954240001,-5.9450229999999999,null,0,2539.0400813548686,0,0,0,2539.0400813548686,0,2675.5653297415652,0,0,0,2675.5653297415652,0,225.45591864513153,0,0,0,0,88.93067025843493,0,0,0,195.91004847586717,59.384800089170568,null,null,2745.5825319999994,null,69836.662499999977,12.870726560407837,10852.0155676102,174.7647896059573,9730.5462749999988,145.21891943669294,-29.545870169264361,null,null,null,null,null,null,null,null,null,2539.0400813548686,0,31.935731329760074,0,0,0]
[0,2530.3709229543797,0,0,0,2530.3709229543797,2718.9545879999991,"2013-01-11T22:00:00",64,60,"OFF",-32.036314582439992,-74.450592333934011,-8.8484060000000007,"ON",49653.316752710016,68159.491290204009,2735.5729999999999,"OFF",-0.11608067099999907,-33.398399859304,-1.7696810000000001,"OFF",-8.2558596494500023,-166.99199929652002,-1.7696810000000001,"OFF",2.2781462162899797,-118.98177343106001,-4.2306439999999998,null,0,2498.6926050461843,0,0,0,2498.6926050461843,0,2632.6761300420826,0,0,0,2632.6761300420826,0,236.88039495381554,0,0,0,0,102.89686995791726,0,0,0,209.02312680366245,75.039601807764171,null,null,2718.9545879999991,null,67246.745600000082,12.72159785614528,10572.059635970329,167.08760953153674,9487.0940864000077,139.23034138138365,-27.857268150153089,null,null,null,null,null,null,null,null,null,2498.6926050461843,0,31.678317908195368,0,0,0]
[0,2435.6993633610823,0,0,0,2435.6993633610823,3724.4807279999995,"2013-01-11T23:00:00",64,62,"OFF",-31.940549552429996,-73.058993676602014,-8.8484060000000007,"ON",46379.451878899992,67543.186447312008,2788.748,"check",4130.8478353249902,71378.644995270006,952.54470000000003,"OFF",-7.7106248286899737,-166.99199929652002,-3.9817830000000001,"OFF",3.9711650766899851,-118.28596608156001,-3.9817830000000001,null,0,2408.0321930460295,0,0,0,2408.0321930460295,0,2528.3792554401016,0,0,0,2528.3792554401016,0,380.71580695397051,0,0,0,0,260.36874455989846,0,0,0,355.55682928338291,235.20976688931086,null,null,3724.4807279999995,null,67246.745600000082,12.843291610704602,10471.886435086686,164.38931905197126,9487.0940864000077,139.23034138138365,-25.158977670587603,null,null,null,null,null,null,null,null,null,2408.0321930460295,0,27.667170315052772,0,0,0]
[0,2514.4216154304004,2158.7417093400895,0,0,4673.1633247704904,4969.5667049999993,"2013-01-12",65,63,"OFF",-32.704328419875004,-72.363194347936002,-8.8484060000000007,"ON",47353.597420480015,64850.335806824005,2655.2660000000001,"ON",48293.18199667499,68442.450272056012,2330.5320000000002,"OFF",-7.5389807332700123,-164.80022619768002,-3.401106,"OFF",2.7351933840699911,-116.89443159090001,-3.9817830000000001,null,0,2485.5015271542957,2129.7550247717718,0,0,4615.2565519260679,0,2627.5504260941575,2250.7202843420791,0,0,4878.2707104362362,0,169.7644728457044,200.77697522822837,0,0,0,27.715573905842575,79.811715657921013,0,0,343.80618616696188,80.792027656792726,null,null,4969.5667049999993,null,69836.662499999977,12.992420314967157,10750.369955249789,171.95418134366381,9730.5462749999988,145.21891943669294,-26.735261906970862,null,null,null,null,null,null,null,null,null,4615.2565519260679,0,28.920088276104707,28.986684568317742,0,0]
[0,2412.6314946970997,2126.9368435219012,0,0,4539.5683382190009,5034.7674529999995,"2013-01-12T01:00:00",66,63,"OFF",-32.304293579040014,-72.363194347936002,-8.8484060000000007,"ON",45256.298940454995,61000.945070208007,2722.8719999999998,"ON",47503.55996749999,63049.642532156009,2327.076,"OFF",-7.7392146112400049,-164.80022619768002,-2.3503579999999999,"OFF",2.6961792333000054,-116.19862424140001,-3.9817830000000001,null,0,2386.2590556245591,2098.9013189148627,0,0,4485.1603745394223,0,2539.2280510603414,2247.8881418549613,0,0,4787.1161929153022,0,336.61294437544075,228.17468108513731,0,0,0,183.64394893965846,79.187858145038717,0,0,535.10544935515122,233.14963097927028,null,null,5034.7674529999995,null,72473.210400000098,13.082291640776852,11079.58947713789,181.15334781683796,9978.3817776000087,151.47117171141107,-29.68217610542689,null,null,null,null,null,null,null,null,null,4485.1603745394223,0,26.372439072540601,28.035524607038496,0,0]
[0,2433.8265957644167,2160.0950547235134,0,0,4593.9216504879296,5038.9101300000002,"2013-01-12T02:00:00",66,64,"OFF",-32.62401560943001,-71.667395019270003,-8.8484060000000007,"ON",45067.770679890011,64127.843142606005,2657.9290000000001,"ON",47689.663774659995,63321.011408878003,2395.5810000000001,"OFF",-8.2171778054100066,-158.64239131086001,-1.7696810000000001,"OFF",1.4215754653799959,-118.98177343106001,-3.9817830000000001,null,0,2407.6263146721326,2131.7918260314113,0,0,4539.4181407035439,0,2540.4296524475717,2280.4452556640854,0,0,4820.8749081116566,0,250.30268532786749,263.78917396858878,0,0,0,117.49934755242839,115.13574433591475,0,0,485.86119326040773,204.40442585229459,null,null,5038.9101300000002,null,72473.210400000098,13.143138518056512,11028.295912796448,179.70183774745962,9978.3817776000087,151.47117171141107,-28.230666036048547,null,null,null,null,null,null,null,null,null,4539.4181407035439,0,26.200281092284058,28.303228692102039,0,0]
[0,2436.1705152273394,2125.2960799341504,0,0,4561.4665951614897,4967.5011299999996,"2013-01-12T03:00:00",66,64,"OFF",-32.90821270910002,-73.058993676602014,-8.8484060000000007,"ON",45116.329915889997,67152.788394030009,2655.3850000000002,"ON",46831.718938609985,77109.595054942009,2326.7159999999999,"OFF",-8.2562548998999947,-166.99199929652002,-1.7696810000000001,"OFF",0.97067692345000656,-118.98618488976001,-3.9817830000000001,null,0,2409.9128589870643,2098.0131421098454,0,0,4507.9260010969101,0,2526.1706013437692,2171.1156512758303,0,0,4697.2862526195995,0,245.47214101293594,228.70285789015452,0,0,0,129.21439865623097,155.60034872416963,0,0,445.94433286704191,256.58408134435206,null,null,4967.5011299999996,null,72473.210400000098,13.143138518056512,11028.295912796448,179.70183774745962,9978.3817776000087,151.47117171141107,-28.230666036048547,null,null,null,null,null,null,null,null,null,4507.9260010969101,0,26.257656240275082,27.282937824305009,0,0]
[0,2433.7173526276092,2148.5264810876974,0,0,4582.2438337153071,4980.5501300000005,"2013-01-12T04:00:00",65,63,"OFF",-32.911319220149991,-73.754793005267999,-8.8484060000000007,"ON",45696.400674854995,65499.141069084006,2671.6,"ON",48040.478555200003,70183.083541732005,2323.5500000000002,"OFF",-8.8420424168299974,-166.99199929652002,-1.7696810000000001,"OFF",1.0598773537799941,-119.67316932186,-3.9817830000000001,null,0,2406.820980588871,2119.846052197141,0,0,4526.667032786012,0,2535.1440889956948,2230.0595820862854,0,0,4765.2036710819802,0,264.77901941112896,203.70394780285915,0,0,0,136.45591100430511,93.490417913714737,0,0,441.74770530701721,203.21106701104898,null,null,4980.5501300000005,null,69836.662499999977,12.992420314967157,10750.369955249789,171.95418134366381,9730.5462749999988,145.21891943669294,-26.735261906970862,null,null,null,null,null,null,null,null,null,4526.667032786012,0,26.896372038738264,28.680428890556414,0,0]
[0,2464.3349748806745,2107.8560272475288,0,0,4572.1910021282038,5014.65913,"2013-01-12T05:00:00",64,63,"OFF",-33.542716586890009,-73.058993676602014,-8.8484060000000007,"ON",46330.118309085003,65643.299518566011,2708.7370000000001,"ON",47025.777085750015,69356.985764736004,2320.5219999999999,"OFF",-11.719596841274992,-164.80022619768002,-1.7696810000000001,"OFF",2.3713384082850117,-118.98177343106001,-3.9817830000000001,null,0,2436.6742379888506,2080.3877620550702,0,0,4517.0620000439212,0,2567.8094865788162,2190.1768292329507,0,0,4757.9863158117669,0,272.06276201114952,240.13423794492974,0,0,0,140.9275134211839,130.34517076704924,0,0,488.35863042313599,247.43431465528988,null,null,5014.65913,null,67246.745600000082,12.904138487984262,10422.50835460533,163.06871091432691,9487.0940864000077,139.23034138138365,-23.838369532943261,null,null,null,null,null,null,null,null,null,4517.0620000439212,0,27.660736891823944,27.468265192458603,0,0]
[0,2513.8544044772675,2057.0343959394872,0,0,4570.8888004167547,5109.15013,"2013-01-12T06:00:00",63,62,"OFF",-33.128445296069998,-73.058993676602014,-8.8484060000000007,"ON",47989.335752200001,65480.083567500005,2738.1779999999999,"ON",46370.84395427999,70091.493638286003,2385.5720000000001,"OFF",-8.8076029276199996,-158.64239131086001,-1.7696810000000001,"OFF",0.45142365074999014,-118.98177343106001,-3.9817830000000001,null,0,2484.193910411761,2030.375982632158,0,0,4514.5698930439194,0,2625.8730663089032,2133.2525582931275,0,0,4759.1256246020312,0,253.98408958823893,355.19601736784216,0,0,0,112.30493369109672,252.31944170687257,0,0,586.92802849414852,342.37229693603672,null,null,5109.15013,null,64707.210300000093,12.756727128279872,10144.79805820308,155.75766738140285,9248.3777682000091,133.50558891947031,-22.252078461932541,null,null,null,null,null,null,null,null,null,4514.5698930439194,0,29.660494065506555,26.658413307329283,0,0]
[0,2464.4785945709991,2105.3768911949901,0,0,4569.8554857659892,5061.5444529999995,"2013-01-12T07:00:00",63,62,"OFF",-33.225357296015005,-74.450592333934011,-8.8484060000000007,"ON",46976.951475079994,65909.944124062007,2686.7429999999999,"ON",47605.317227045001,71201.208105522004,2389.982,"OFF",-9.3398471835899866,-158.64239131086001,-2.3503579999999999,"OFF",-0.63691980849000418,-119.68199223926001,-3.9817830000000001,null,0,2436.0805025144255,2077.2646360284834,0,0,4513.3451385429089,0,2569.1257074312712,2180.0759046634121,0,0,4749.2016120946828,0,250.66249748557448,312.71736397151653,0,0,0,117.61729256872877,209.9060953365879,0,0,541.12778299515844,305.2713094433841,null,null,5061.5444529999995,null,64707.210300000093,12.756727128279872,10144.79805820308,155.75766738140285,9248.3777682000091,133.50558891947031,-22.252078461932541,null,null,null,null,null,null,null,null,null,4513.3451385429089,0,28.39809205657366,28.112255166506657,0,0]
[0,2745.8185174545874,0,0,0,2745.8185174545874,3107.8424489999993,"2013-01-12T08:00:00",63,62,"OFF",-32.585606499320015,-74.350083263080009,-8.8484060000000007,"ON",52548.178933850009,59215.972630180011,3124.212,"check",3755.6524948799943,70406.961060340007,-1.7696810000000001,"OFF",-8.5727714602600162,-158.64239131086001,-1.7696810000000001,"OFF",-0.58750471437000462,-118.28155462286001,-3.9817830000000001,null,0,2710.0952857420452,0,0,0,2710.0952857420452,0,2933.8234876667816,0,0,0,2933.8234876667816,0,414.11671425795475,0,0,0,0,190.38851233321839,0,0,0,391.86463579602218,168.13643387128585,null,null,3107.8424489999993,null,64707.210300000093,12.756727128279872,10144.79805820308,155.75766738140285,9248.3777682000091,133.50558891947031,-22.252078461932541,null,null,null,null,null,null,null,null,null,2710.0952857420452,0,35.723231712542201,0,0,0]
[0,2634.9568649848857,0,0,0,2634.9568649848857,3441.4097719999995,"2013-01-12T09:00:00",64,63,"OFF",-32.619255487629999,-74.551109425622002,-8.8484060000000007,"ON",49753.218591719982,60413.130229684,3458.36,"OFF",-0.10414322458999632,-46.444647297834003,-1.7696810000000001,"OFF",-8.899511832259984,-158.64239131086001,-2.3503579999999999,"OFF",-1.1524245231799897,-119.67758078056001,-3.9817830000000001,null,0,2602.9626685714434,0,0,0,2602.9626685714434,0,2793.3822269058869,0,0,0,2793.3822269058869,0,855.39733142855675,0,0,0,0,664.97777309411322,0,0,0,831.55896189561349,641.13940356116996,null,null,3441.4097719999995,null,67246.745600000082,12.904138487984262,10422.50835460533,163.06871091432691,9487.0940864000077,139.23034138138365,-23.838369532943261,null,null,null,null,null,null,null,null,null,2602.9626685714434,0,31.994196413442296,0,0,0]
[0,2901.887351524425,0,0,0,2901.887351524425,3115.6314489999995,"2013-01-12T10:00:00",65,64,"OFF",-33.330454884434992,-70.971595690604005,-8.8484060000000007,"ON",54124.236925659985,56832.774307096006,3132.0010000000002,"OFF",-0.29572932850000477,-75.14639166260001,-1.7696810000000001,"OFF",-8.5740626117300121,-160.83416440970004,-1.7696810000000001,"OFF",0.28698113079999471,-119.67758078056001,-3.9817830000000001,null,0,2863.7754749594374,0,0,0,2863.7754749594374,0,3127.4372381688272,0,0,0,3127.4372381688272,0,268.22552504056284,0,0,0,0,4.5637618311729966,0,0,0,242.86618082350418,-20.795582385885666,null,null,3115.6314489999995,null,69836.662499999977,13.053267192246818,10700.257869766197,170.57826365375161,9730.5462749999988,145.21891943669294,-25.359344217058663,null,null,null,null,null,null,null,null,null,2863.7754749594374,0,38.111876564987597,0,0,0]
[0,2823.3370878288029,0,0,0,2823.3370878288029,3058.7241629999999,"2013-01-12T11:00:00",64,63,"OFF",-32.950238214460029,-75.14639166260001,-8.8484060000000007,"ON",53340.689707874997,57477.408735676006,3076.9740000000002,"OFF",-1.7777123400000042E-2,-103.84814404820001,-1.7696810000000001,"OFF",-8.4160414818199953,-166.99199929652002,-3.401106,"OFF",-0.21502358394998902,-119.67758078056001,-4.2306439999999998,null,0,2786.4247961391661,0,0,0,2786.4247961391661,0,3035.017672736541,0,0,0,3035.017672736541,0,290.54920386083404,0,0,0,0,41.956327263459116,0,0,0,266.71083432789078,18.117957730515855,null,null,3058.7241629999999,null,67246.745600000082,12.904138487984262,10422.50835460533,163.06871091432691,9487.0940864000077,139.23034138138365,-23.838369532943261,null,null,null,null,null,null,null,null,null,2786.4247961391661,0,36.912291689636731,0,0,0]
[0,2371.7425753777466,0,0,0,2371.7425753777466,2600.1213889999995,"2013-01-12T12:00:00",56,55,"OFF",-33.117467464979988,-73.754793005267999,-8.8484060000000007,"ON",49809.573056910005,61662.695958544005,2619.9749999999999,"OFF",0.43347558074999909,-46.444647297834003,-3.2905009999999999,"OFF",-12.681721215000005,-166.99199929652002,-1.7696810000000001,"OFF",-1.0289716935400179,-117.59015873206,-5.9450229999999999,null,0,2340.1692053723164,0,0,0,2340.1692053723164,0,2518.3655250538982,0,0,0,2518.3655250538982,0,279.80579462768355,0,0,0,0,101.60947494610173,0,0,0,269.18513244470671,90.988812763124869,null,null,2600.1213889999995,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,2340.1692053723164,0,31.573370005430206,0,0,0]
[0,2279.1101672941145,0,0,0,2279.1101672941145,2416.4463059999994,"2013-01-12T13:00:00",53,50,"OFF",-32.917195276840019,-74.450592333934011,-8.8484060000000007,"ON",47760.015514920007,67651.427602142008,2433.7559999999999,"OFF",0.29501494987499438,-33.398399859304,-2.460963,"OFF",-9.257608739960002,-166.99199929652002,-1.7696810000000001,"OFF",-2.5118490454399853,-117.59457019076001,-4.2306439999999998,null,0,2250.1361081988475,0,0,0,2250.1361081988475,0,2375.564539623098,0,0,0,2375.564539623098,0,183.61989180115233,0,0,0,0,58.191460376901887,0,0,0,175.92263245032225,50.494201026071806,null,null,2416.4463059999994,null,42907.977300000086,11.283499788278451,7605.4376931125289,98.062633604885548,7199.249866200008,90.365374254055467,-7.6972593508300804,null,null,null,null,null,null,null,null,null,2250.1361081988475,0,28.974059095266966,0,0,0]
[0,2251.5905056520164,0,0,0,2251.5905056520164,2309.5174859999993,"2013-01-12T14:00:00",53,49,"OFF",-33.280648310339991,-73.058993676602014,-8.8484060000000007,"ON",47137.40739652999,66762.558778261999,2328.348,"OFF",4.0539801258000822E-2,-33.398399859304,-1.7696810000000001,"OFF",-8.9784038220799918,-160.83416440970004,-3.9817830000000001,"OFF",-1.4751509368399887,-116.89002013220001,-4.2306439999999998,null,0,2223.3817646659659,0,0,0,2223.3817646659659,0,2350.5526287299695,0,0,0,2350.5526287299695,0,104.96623533403408,0,0,0,0,-22.2046287299695,0,0,0,96.463955579207948,-30.706908484795633,null,null,2309.5174859999993,null,42907.977300000086,11.222652910998791,7646.6727858879085,98.867654008881601,7199.249866200008,90.365374254055467,-8.5022797548261337,null,null,null,null,null,null,null,null,null,2223.3817646659659,0,28.208740986050543,0,0,0]
[0,2241.9886516796096,0,0,0,2241.9886516796096,2440.0841629999995,"2013-01-12T15:00:00",52,48,"OFF",-33.347631201235004,-71.667395019270003,-8.8484060000000007,"ON",46918.627052580006,67003.905673322006,2458.3339999999998,"OFF",3.0345814974000254E-2,-33.398399859304,-1.7696810000000001,"OFF",-9.056347210820018,-166.99199929652002,-3.401106,"OFF",-1.3642216920500103,-120.37338813006001,-4.2306439999999998,null,0,2214.046166599644,0,0,0,2214.046166599644,0,2338.6371361332208,0,0,0,2338.6371361332208,0,244.28783340035579,0,0,0,0,119.69686386677904,0,0,0,237.25019882535855,112.65922929178181,null,null,2440.0841629999995,null,41170.179200000071,11.102570159705023,7416.3330846438703,94.426555420650587,7035.8968448000069,87.388920845653359,-7.0376345749972273,null,null,null,null,null,null,null,null,null,2214.046166599644,0,27.942485079965536,0,0,0]
[0,2157.3697335450247,0,0,0,2157.3697335450247,2402.9815879999992,"2013-01-12T16:00:00",50,46,"OFF",-33.091579775380012,-73.058993676602014,-8.8484060000000007,"ON",44954.389243169979,66726.072004396003,2419.6,"OFF",0.10848821217599902,-75.14639166260001,-1.7696810000000001,"OFF",-8.5341159662499901,-160.83416440970004,-1.7696810000000001,"OFF",-1.9291415008599953,-119.67758078056001,-4.2306439999999998,null,0,2131.7558504914209,0,0,0,2131.7558504914209,0,2247.3853507987792,0,0,0,2247.3853507987792,0,287.84414950857899,0,0,0,0,172.21464920122071,0,0,0,283.43573830981654,167.80623800245826,null,null,2402.9815879999992,null,37984.500000000058,10.872286982852879,6987.3983385293168,86.518381492841286,6736.4430000000057,82.109970294078821,-4.4084111987624652,null,null,null,null,null,null,null,null,null,2131.7558504914209,0,25.613883053603786,0,0,0]
[0,2070.823941000931,0,0,0,2070.823941000931,2129.2854489999995,"2013-01-12T17:00:00",44,41,"OFF",-32.944283107679993,-73.133410974454009,-8.8484060000000007,"ON",42873.406705699992,66664.913145145998,2145.6550000000002,"OFF",2.8902418686000228E-2,-46.444647297834003,-1.7696810000000001,"OFF",-9.4286731347199844,-160.83416440970004,-1.7696810000000001,"OFF",-2.5732782904499976,-119.67758078056001,-3.9817830000000001,null,0,2047.5566482084755,0,0,0,2047.5566482084755,0,2152.8545919345711,0,0,0,2152.8545919345711,0,98.098351791524692,0,0,0,0,-7.1995919345708899,0,0,0,99.283468703452812,-6.0144750226427703,null,null,2129.2854489999995,null,31016.841600000043,10.330547828118286,6004.8783696788278,70.178962220334924,6081.4831104000041,71.364079132263043,1.1851169119281195,null,null,null,null,null,null,null,null,null,2047.5566482084755,0,23.267292792455464,0,0,0]
[0,2011.0536533091108,0,0,0,2011.0536533091108,2425.5247719999993,"2013-01-12T18:00:00",42,39,"OFF",-33.972278728409989,-74.376175036082017,-8.8484060000000007,"ON",41389.649927150014,67317.977470259997,2442.4749999999999,"OFF",-2.7822524771998692E-2,-62.100144224070007,-1.7696810000000001,"OFF",-8.7947177629500288,-164.80022619768002,-2.3503579999999999,"OFF",-3.0736273448299989,-119.67758078056001,-3.9817830000000001,null,0,1989.3846990063464,0,0,0,1989.3846990063464,0,2084.5568282269951,0,0,0,2084.5568282269951,0,453.0903009936535,0,0,0,0,357.91817177300481,0,0,0,454.85703214498312,359.68490292433444,null,null,2425.5247719999993,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1989.3846990063464,0,21.668954302764405,0,0,0]
[0,1982.3995084702904,0,0,0,1982.3995084702904,2055.0654489999993,"2013-01-12T19:00:00",39,36,"OFF",-34.058309676020002,-75.14639166260001,-8.8484060000000007,"ON",40663.814329474997,66985.27327594001,2071.4349999999999,"OFF",-5.4058553000000495E-2,-62.100144224070007,-1.7696810000000001,"OFF",-8.4160414818200309,-166.99199929652002,-1.7696810000000001,"OFF",-1.8076550566549934,-118.98177343106001,-3.9817830000000001,null,0,1961.4899612352847,0,0,0,1961.4899612352847,0,2054.7228829393439,0,0,0,2054.7228829393439,0,109.94503876471526,0,0,0,0,16.712117060656055,0,0,0,111.43027578503833,18.197354080979125,null,null,2055.0654489999993,null,28624.403100000054,9.9447630098415623,5756.678780916689,66.442368750920267,5856.5938914000053,67.927605771243336,1.4852370203230691,null,null,null,null,null,null,null,null,null,1961.4899612352847,0,20.909547235005675,0,0,0]
[0,1960.7814663038093,0,0,0,1960.7814663038093,2090.5933469999995,"2013-01-12T20:00:00",38,36,"OFF",-35.093825238075006,-73.058993676602014,-8.8484060000000007,"ON",40109.678770199993,67781.260842100004,2109.1750000000002,"OFF",0.22322575362499941,-46.444647297834003,-1.7696810000000001,"OFF",-8.0392624028500013,-160.83416440970004,-3.9817830000000001,"OFF",-3.0327480813500083,-120.37338813006001,-3.9817830000000001,null,0,1940.4417992013766,0,0,0,1940.4417992013766,0,2027.8806848648755,0,0,0,2027.8806848648755,0,168.73320079862356,0,0,0,0,81.294315135124634,0,0,0,170.29550471999741,82.856619056498488,null,null,2090.5933469999995,null,28563.352800000052,9.9426820040680362,5745.6032061195147,66.279303938778682,5850.8551632000053,67.841607860152536,1.5623039213738537,null,null,null,null,null,null,null,null,null,1940.4417992013766,0,20.339667102432713,0,0,0]
[0,1936.9182175706735,0,0,0,1936.9182175706735,2226.2345319999995,"2013-01-12T21:00:00",38,35,"OFF",-35.068217880509991,-72.363194347936002,-8.8484060000000007,"ON",39491.249187040019,66551.033344014009,2245.1480000000001,"OFF",0.17465971824999485,-46.444647297834003,-1.7696810000000001,"OFF",-9.2607443935299667,-160.83416440970004,-2.3503579999999999,"OFF",-3.6044150783199789,-119.67758078056001,-5.9450229999999999,null,0,1917.2044843024239,0,0,0,1917.2044843024239,0,2006.8401863915994,0,0,0,2006.8401863915994,0,327.94351569757623,0,0,0,0,238.30781360840069,0,0,0,328.98384794539419,239.34814585621865,null,null,2226.2345319999995,null,28563.352800000052,9.8818351267883742,5780.9814540557363,66.801275612334564,5850.8551632000053,67.841607860152536,1.0403322478179717,null,null,null,null,null,null,null,null,null,1917.2044843024239,0,19.713733268249598,0,0,0]
[0,1821.0428734541952,0,0,0,1821.0428734541952,1928.850784,"2013-01-12T22:00:00",38,35,"OFF",-35.838948601095005,-72.363194347936002,-8.8484060000000007,"ON",36379.676319479993,67110.261932162015,1948.8150000000001,"OFF",-0.3483591242500011,-75.14639166260001,-1.7696810000000001,"OFF",-9.0127906112300114,-160.83416440970004,-3.401106,"OFF",-3.2728584760200126,-118.29037754026001,-5.9450229999999999,null,0,1804.3187593378022,0,0,0,1804.3187593378022,0,1878.4239837858015,0,0,0,1878.4239837858015,0,144.49624066219781,0,0,0,0,70.391016214198544,0,0,0,145.53657291001576,71.431348462016516,null,null,1928.850784,null,28563.352800000052,9.8818351267883742,5780.9814540557363,66.801275612334564,5850.8551632000053,67.841607860152536,1.0403322478179717,null,null,null,null,null,null,null,null,null,1804.3187593378022,0,16.724114116392911,0,0,0]
[0,1690.7914036293478,0,0,0,1690.7914036293478,1877.150347,"2013-01-12T23:00:00",37,35,"OFF",-36.026921918075011,-72.363194347936002,-8.8484060000000007,"ON",32635.179506974986,67094.958180889997,1895.732,"OFF",0.19411189687499486,-62.100144224070007,-1.7696810000000001,"OFF",-9.2903091271899907,-166.99199929652002,-3.9817830000000001,"OFF",-1.6978160301899901,-116.89443159090001,-3.9817830000000001,null,0,1677.3171443633119,0,0,0,1677.3171443633119,0,1737.0345029993741,0,0,0,1737.0345029993741,0,218.41485563668812,0,0,0,0,158.69749700062584,0,0,0,219.34279942797014,159.62544079190786,null,null,1877.150347,null,28650.199700000056,9.8847954545887777,5796.8219639183117,67.036025448148166,5859.0187718000052,67.963969239430199,0.92794379128203275,null,null,null,null,null,null,null,null,null,1677.3171443633119,0,13.474259266035915,0,0,0]
[0,1580.1975819701991,0,0,0,1580.1975819701991,1589.4453470000001,"2013-01-13",36,33,"OFF",-36.017908707059995,-73.754793005267999,-8.8484060000000007,"ON",29205.272229210001,66555.87792775,1608.027,"OFF",6.0150356340013464E-3,-33.398399859304,-1.7696810000000001,"OFF",-8.7037047593299715,-158.64239131086001,-3.9817830000000001,"OFF",-2.21612263165999,-117.58582748170001,-3.9817830000000001,null,0,1569.3736876727914,0,0,0,1569.3736876727914,0,1618.5094013630769,0,0,0,1618.5094013630769,0,38.653312327208596,0,0,0,0,-10.48240136307686,0,0,0,38.176660783448085,-10.959052906837371,null,null,1589.4453470000001,null,28888.694400000008,9.7712312071351608,5913.0100982371323,68.777521179973519,5881.4372736000005,68.300869636213008,-0.47665154376051078,null,null,null,null,null,null,null,null,null,1569.3736876727914,0,10.823894297407605,0,0,0]
[0,1557.4284716415937,0,0,0,1557.4284716415937,1623.226107,"2013-01-13T01:00:00",35,32,"OFF",-36.52871191058999,-71.667395019270003,-8.8484060000000007,"ON",28465.53283212001,66982.337650696005,1643.771,"OFF",-0.28459204862499787,-62.100144224070007,-1.7696810000000001,"OFF",-7.767725343700012,-158.64239131086001,-3.9817830000000001,"OFF",-3.2550198854499914,-120.37338813006001,-5.9450229999999999,null,0,1547.1359330287416,0,0,0,1547.1359330287416,0,1592.9614082926403,0,0,0,1592.9614082926403,0,96.635066971258311,0,0,0,0,50.809591707359687,0,0,0,95.039336078585592,49.213860814686967,null,null,1623.226107,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1547.1359330287416,0,10.292538612852013,0,0,0]
[0,1562.3584807036823,0,0,0,1562.3584807036823,1692.535486,"2013-01-13T02:00:00",35,32,"OFF",-36.478507231460007,-70.275796361938006,-8.8484060000000007,"ON",28626.76195732499,66320.402283178002,1711.366,"OFF",-0.36633570112499869,-75.14639166260001,-1.7696810000000001,"OFF",-7.816868149649995,-164.80022619768002,-3.9817830000000001,"OFF",-4.4675660178800003,-118.70778174162001,-4.2306439999999998,null,0,1551.9513383568112,0,0,0,1551.9513383568112,0,1599.6954681695197,0,0,0,1599.6954681695197,0,159.41466164318877,0,0,0,0,111.67053183048029,0,0,0,157.81893075051605,110.07480093780757,null,null,1692.535486,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1551.9513383568112,0,10.407142346871069,0,0,0]
[0,1567.1303884763909,0,0,0,1567.1303884763909,1645.251107,"2013-01-13T03:00:00",35,31,"OFF",-36.516398574599997,-71.667395019270003,-8.8484060000000007,"ON",28782.257771639983,66439.198855552007,1665.796,"OFF",-0.3710904178750018,-33.398399859304,-1.7696810000000001,"OFF",-12.476822637900003,-158.64239131086001,-3.9817830000000001,"OFF",-3.3955896075499963,-117.86423062984001,-5.9450229999999999,null,0,1556.6120807694278,0,0,0,1556.6120807694278,0,1604.6097931191232,0,0,0,1604.6097931191232,0,109.1839192305722,0,0,0,0,61.186206880876853,0,0,0,107.00159247685539,59.003880127160045,null,null,1645.251107,null,29282.587499999994,9.6629639847182247,6060.7878796422701,71.042431644183864,5918.4632249999995,68.860104890467056,-2.1823267537168078,null,null,null,null,null,null,null,null,null,1556.6120807694278,0,10.518307706963014,0,0,0]
[0,1570.0583576550123,0,0,0,1570.0583576550123,1659.989431,"2013-01-13T04:00:00",35,31,"OFF",-38.500900184924987,-70.275796361938006,-8.8484060000000007,"ON",28877.395971060007,66604.86918182201,1681.115,"OFF",-0.59371890412499462,-46.444647297834003,-1.7696810000000001,"OFF",-8.4532213741500009,-158.64239131086001,-4.5624589999999996,"OFF",-4.2030424341499844,-118.98177343106001,-5.9450229999999999,null,0,1559.4717261464798,0,0,0,1559.4717261464798,0,1607.4220708021987,0,0,0,1607.4220708021987,0,121.64327385352021,0,0,0,0,73.692929197801277,0,0,0,119.46094709980341,71.510602444084469,null,null,1659.989431,null,29282.587499999994,9.6629639847182247,6060.7878796422701,71.042431644183864,5918.4632249999995,68.860104890467056,-2.1823267537168078,null,null,null,null,null,null,null,null,null,1559.4717261464798,0,10.586631508532491,0,0,0]
[0,1592.5396073224476,0,0,0,1592.5396073224476,1634.198486,"2013-01-13T05:00:00",34,30,"OFF",-37.795903331339993,-70.971595690604005,-8.8484060000000007,"ON",29601.137503200007,66523.217091701998,1653.029,"OFF",-6.2065230755000228E-2,-75.14639166260001,-1.7696810000000001,"OFF",-8.2161765042699884,-160.83416440970004,-3.9817830000000001,"OFF",-4.0757263969800235,-118.70778174162001,-4.2306439999999998,null,0,1581.4255318341466,0,0,0,1581.4255318341466,0,1631.9556422815886,0,0,0,1631.9556422815886,0,71.603468165853428,0,0,0,0,21.073357718411444,0,0,0,67.992415041976201,17.462304594534217,null,null,1634.198486,null,29835.629600000044,9.620968510349007,6202.2091784016739,73.26227032659196,5970.4491824000042,69.651217202714733,-3.6110531238772268,null,null,null,null,null,null,null,null,null,1581.4255318341466,0,11.114075488301069,0,0,0]
[0,1591.8227419147806,0,0,0,1591.8227419147806,1629.7671069999999,"2013-01-13T06:00:00",34,30,"OFF",-38.062934535360007,-73.133410974454009,-8.8484060000000007,"ON",29578.240324300001,66061.152886630007,1650.3119999999999,"OFF",-0.32270004937500307,-62.100144224070007,-1.7696810000000001,"OFF",-9.1303907951200056,-158.64239131086001,-3.9817830000000001,"OFF",-4.0876980950399924,-119.25584532884001,-5.9450229999999999,null,0,1580.7255617677574,0,0,0,1580.7255617677574,0,1632.2381467075047,0,0,0,1632.2381467075047,0,69.586438232242472,0,0,0,0,18.073853292495187,0,0,0,65.975385108365245,14.46280016861796,null,null,1629.7671069999999,null,29835.629600000044,9.620968510349007,6202.2091784016739,73.26227032659196,5970.4491824000042,69.651217202714733,-3.6110531238772268,null,null,null,null,null,null,null,null,null,1580.7255617677574,0,11.097180147023209,0,0,0]
[0,1582.6168030671331,0,0,0,1582.6168030671331,1631.792246,"2013-01-13T07:00:00",33,29,"OFF",-37.659357475880007,-73.680375707416005,-8.8484060000000007,"ON",29283.145946249992,66420.381978988007,1652.586,"OFF",-0.34489263124999919,-33.398399859304,-1.7696810000000001,"OFF",-12.980376863999997,-164.80022619768002,-3.9817830000000001,"OFF",-4.3290848864199942,-116.89443159090001,-6.1938839999999997,null,0,1571.7361467091346,0,0,0,1571.7361467091346,0,1621.4328087622346,0,0,0,1621.4328087622346,0,80.84985329086544,0,0,0,0,31.153191237765441,0,0,0,75.48843231692662,25.791770263826621,null,null,1631.792246,null,30551.57130000004,9.5845257524792178,6375.1868561879128,76.047049537678248,6037.7477022000039,70.685628563739428,-5.3614209739388201,null,null,null,null,null,null,null,null,null,1571.7361467091346,0,10.880656357998532,0,0,0]
[0,1598.7709692119224,0,0,0,1598.7709692119224,1675.0324860000001,"2013-01-13T08:00:00",32,28,"OFF",-38.059139809170013,-74.450592333934011,-8.8484060000000007,"ON",29799.679167265014,66557.008865344003,1693.8630000000001,"OFF",-0.16893297812499947,-33.398399859304,-1.7696810000000001,"OFF",-10.037675028079995,-164.80022619768002,-3.9817830000000001,"OFF",-4.2174763963499808,-120.37338813006001,-4.2306439999999998,null,0,1587.5098218133865,0,0,0,1587.5098218133865,0,1638.6319197928606,0,0,0,1638.6319197928606,0,106.3531781866136,0,0,0,0,55.231080207139485,0,0,0,98.878519386082999,47.756421406608879,null,null,1675.0324860000001,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1587.5098218133865,0,11.261147398535968,0,0,0]
[0,1561.574127699573,0,0,0,1561.574127699573,1681.1167720000001,"2013-01-13T09:00:00",32,28,"OFF",-38.027730895279994,-72.363194347936002,-8.8484060000000007,"ON",28601.150463809994,66461.272190720003,1698.067,"OFF",-0.2258815965750037,-33.398399859304,-1.7696810000000001,"OFF",-9.0579809126800139,-160.83416440970004,-2.3503579999999999,"OFF",-5.5999952581300079,-118.98177343106001,-3.9817830000000001,null,0,1551.1852352353671,0,0,0,1551.1852352353671,0,1598.5441033055772,0,0,0,1598.5441033055772,0,146.88176476463286,0,0,0,0,99.522896694422798,0,0,0,139.40710596410224,92.048237893892193,null,null,1681.1167720000001,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1551.1852352353671,0,10.38889246420581,0,0,0]
[0,1555.1328854397082,0,0,0,1555.1328854397082,1574.6964309999998,"2013-01-13T10:00:00",34,29,"OFF",-37.892107290870008,-71.667395019270003,-8.8484060000000007,"ON",28390.255486600003,66468.859899684001,1595.8219999999999,"OFF",-0.73933503237499898,-62.100144224070007,-1.7696810000000001,"OFF",-9.1177164306900274,-160.83416440970004,-4.5624589999999996,"OFF",-5.2871603538600107,-117.59015873206,-5.9450229999999999,null,0,1544.8936248654409,0,0,0,1544.8936248654409,0,1591.5530994925259,0,0,0,1591.5530994925259,0,50.928375134559019,0,0,0,0,4.2689005074739725,0,0,0,46.688558205190148,2.9083578105101537E-2,null,null,1574.6964309999998,null,29835.629600000044,9.5601216330693468,6241.6841009210257,73.891034132083604,5970.4491824000042,69.651217202714733,-4.239816929368871,null,null,null,null,null,null,null,null,null,1544.8936248654409,0,10.239260574267291,0,0,0]
[0,1617.2697156689121,0,0,0,1617.2697156689121,1595.0863469999999,"2013-01-13T11:00:00",34,29,"OFF",-39.859749354919998,-72.363194347936002,-8.8484060000000007,"ON",30383.966163950008,67493.657797362001,1613.6679999999999,"OFF",-0.78575793187499732,-75.14639166260001,-1.7696810000000001,"OFF",-9.2972918851399964,-164.80022619768002,-3.9817830000000001,"OFF",-4.3407594146699893,-118.98177343106001,-3.9817830000000001,null,0,1605.5697879912016,0,0,0,1605.5697879912016,0,1656.473081925797,0,0,0,1656.473081925797,0,8.0982120087983276,0,0,0,0,-42.80508192579714,0,0,0,3.8583950794294566,-47.044898855166011,null,null,1595.0863469999999,null,29835.629600000044,9.5601216330693468,6241.6841009210257,73.891034132083604,5970.4491824000042,69.651217202714733,-4.239816929368871,null,null,null,null,null,null,null,null,null,1605.5697879912016,0,11.699927677710548,0,0,0]
[0,1633.7520300070923,0,0,0,1633.7520300070923,1878.120246,"2013-01-13T12:00:00",37,31,"OFF",-39.022498405989992,-73.058993676602014,-8.8484060000000007,"ON",30898.291956270015,66145.965185346009,1898.914,"OFF",-0.1510852236250011,-62.100144224070007,-1.7696810000000001,"OFF",-8.7131907701300264,-164.80022619768002,-3.9817830000000001,"OFF",-5.4700170600950191,-120.37338813006001,-6.1938839999999997,null,0,1621.6584741437323,0,0,0,1621.6584741437323,0,1677.5931518013022,0,0,0,1677.5931518013022,0,277.2555258562677,0,0,0,0,221.32084819869783,0,0,0,275.98447044934852,220.04979279177866,null,null,1878.120246,null,28650.199700000056,9.6414079454701351,5943.1568215015532,69.235024646349373,5859.0187718000052,67.963969239430199,-1.2710554069191744,null,null,null,null,null,null,null,null,null,1621.6584741437323,0,12.093555863360052,0,0,0]
[0,1677.1785785760719,0,0,0,1677.1785785760719,1582.570287,"2013-01-13T13:00:00",39,32,"OFF",-38.544349583459983,-72.363194347936002,-8.8484060000000007,"ON",32226.49782878501,66781.022738130006,1604.636,"OFF",-0.33280675024999906,-33.398399859304,-3.2905009999999999,"OFF",-8.0875883578699881,-166.99199929652002,-3.9817830000000001,"OFF",-4.3748490371600113,-120.37338813006001,-5.9450229999999999,null,0,1664.0363570613536,0,0,0,1664.0363570613536,0,1723.1155441754788,0,0,0,1723.1155441754788,0,-59.400357061353589,0,0,0,0,-118.47954417547885,0,0,0,-60.070197187721973,-119.14938430184723,null,null,1582.570287,null,28624.403100000054,9.7013755007229214,5901.1019824698133,68.597445897611721,5856.5938914000053,67.927605771243336,-0.66984012636838486,null,null,null,null,null,null,null,null,null,1664.0363570613536,0,13.142221514718358,0,0,0]
[0,1683.6369077352151,0,0,0,1683.6369077352151,1838.9334859999999,"2013-01-13T14:00:00",42,34,"OFF",-38.782026854059993,-71.667395019270003,-8.8484060000000007,"ON",32420.831001405004,67154.962040044018,1857.7639999999999,"OFF",-2.41397415959986E-2,-75.14639166260001,-1.7696810000000001,"OFF",-7.8408466769499672,-164.80022619768002,-3.9817830000000001,"OFF",-5.5597397296399871,-118.98177343106001,-4.2306439999999998,null,0,1670.3373497080872,0,0,0,1670.3373497080872,0,1729.1178998623088,0,0,0,1729.1178998623088,0,187.42665029191267,0,0,0,0,128.64610013769106,0,0,0,186.46049398723918,127.67994383301757,null,null,1838.9334859999999,null,29657.431200000021,9.8582818167326369,6016.7545930086799,70.361709865588551,5953.6985328000019,69.395553560915062,-0.96615630467348979,null,null,null,null,null,null,null,null,null,1670.3373497080872,0,13.299558027127887,0,0,0]
[0,1731.1908920998719,0,0,0,1731.1908920998719,1768.5281070000001,"2013-01-13T15:00:00",43,35,"OFF",-38.697954523380005,-73.058993676602014,-8.8484060000000007,"ON",33827.732566874991,66516.760320332003,1789.0730000000001,"OFF",-0.38798957124999861,-62.100144224070007,-1.7696810000000001,"OFF",-7.8892253320300076,-164.80022619768002,-3.9817830000000001,"OFF",-4.1315035119500232,-118.28596608156001,-5.9450229999999999,null,0,1716.7223737533038,0,0,0,1716.7223737533038,0,1782.5600415293825,0,0,0,1782.5600415293825,0,72.350626246696265,0,0,0,0,6.5129584706176047,0,0,0,71.119399155250221,5.2817313791715605,null,null,1768.5281070000001,null,30272.564300000085,9.9400965767677878,6091.0000353022297,71.512360230466271,6011.521044200008,70.281133139020227,-1.2312270914460441,null,null,null,null,null,null,null,null,null,1716.7223737533038,0,14.468518346568089,0,0,0]
[0,1712.4905488139048,0,0,0,1712.4905488139048,1916.055347,"2013-01-13T16:00:00",43,35,"OFF",-39.008891688299983,-71.046012988456013,-8.8484060000000007,"ON",33279.415790879983,67189.363397070003,1934.6369999999999,"OFF",-0.43062977737500285,-33.398399859304,-1.7696810000000001,"OFF",-8.7763781420700102,-158.64239131086001,-3.9817830000000001,"OFF",-3.7567782851899874,-119.67758078056001,-3.9817830000000001,null,0,1698.4838757302027,0,0,0,1698.4838757302027,0,1760.2995620944992,0,0,0,1760.2995620944992,0,236.15312426979722,0,0,0,0,174.33743790550079,0,0,0,234.92189717835117,173.10621081405475,null,null,1916.055347,null,30272.564300000085,9.9400965767677878,6091.0000353022297,71.512360230466271,6011.521044200008,70.281133139020227,-1.2312270914460441,null,null,null,null,null,null,null,null,null,1698.4838757302027,0,14.006673083702026,0,0,0]
[0,1713.1247395345381,0,0,0,1713.1247395345381,1793.4611070000001,"2013-01-13T17:00:00",40,33,"OFF",-39.774294649425002,-72.984576378750006,-8.8484060000000007,"ON",33298.114108600006,66009.089653136005,1814.0060000000001,"OFF",-0.85183209912500057,-46.444647297834003,-1.7696810000000001,"OFF",-10.695176061350036,-164.80022619768002,-3.9817830000000001,"OFF",-4.6631462056900022,-118.98177343106001,-5.9450229999999999,null,0,1699.1024488902342,0,0,0,1699.1024488902342,0,1764.3788929351315,0,0,0,1764.3788929351315,0,114.90355110976589,0,0,0,0,49.627107064868596,0,0,0,114.50782747604886,49.231383431151571,null,null,1793.4611070000001,null,28829.600000000006,9.76921687161866,5902.1312309598125,68.612995926363126,5875.8824000000004,68.217272292646101,-0.39572363371702579,null,null,null,null,null,null,null,null,null,1699.1024488902342,0,14.022290644303894,0,0,0]
[0,1670.565401971917,0,0,0,1670.565401971917,1771.050107,"2013-01-13T18:00:00",38,32,"OFF",-38.347752009630021,-73.058993676602014,-8.8484060000000007,"ON",32026.667301195008,67141.430893086013,1791.595,"OFF",-0.46627844187500128,-33.398399859304,-1.7696810000000001,"OFF",-8.5886868783800114,-160.83416440970004,-3.9817830000000001,"OFF",-4.6939669602700107,-117.59015873206,-5.9450229999999999,null,0,1657.5839261668825,0,0,0,1657.5839261668825,0,1714.9910874243128,0,0,0,1714.9910874243128,0,134.01107383311751,0,0,0,0,76.603912575687218,0,0,0,133.42611885477231,76.018957597342009,null,null,1771.050107,null,28563.352800000052,9.6992944949493936,5889.7794710478229,68.426562838497745,5850.8551632000053,67.841607860152536,-0.58495497834520904,null,null,null,null,null,null,null,null,null,1657.5839261668825,0,12.981475805034506,0,0,0]
[0,1647.7131073298488,0,0,0,1647.7131073298488,1791.7292459999999,"2013-01-13T19:00:00",36,30,"OFF",-38.659863417550014,-71.566885948416015,-8.8484060000000007,"ON",31329.465391494996,66592.428868288014,1812.5229999999999,"OFF",-0.35751722399999558,-46.444647297834003,-1.7696810000000001,"OFF",-9.2979242858600095,-166.99199929652002,-3.9817830000000001,"OFF",-5.169353750609992,-118.98177343106001,-6.1938839999999997,null,0,1635.284216071437,0,0,0,1635.284216071437,0,1691.6288386507592,0,0,0,1691.6288386507592,0,177.23878392856295,0,0,0,0,120.89416134924068,0,0,0,175.0419608756313,118.69733829630903,null,null,1791.7292459999999,null,28888.694400000008,9.5886905752961802,6025.5765212462666,70.497692689144657,5881.4372736000005,68.300869636213008,-2.1968230529316486,null,null,null,null,null,null,null,null,null,1635.284216071437,0,12.428891258411795,0,0,0]
[0,1680.3121841660309,0,0,0,1680.3121841660309,1584.8120650000001,"2013-01-13T20:00:00",35,30,"OFF",-38.027098494560001,-70.376305432792009,-8.8484060000000007,"ON",32320.889405999991,67601.521972994,1604.085,"OFF",-0.30919712224999413,-62.100144224070007,-2.460963,"OFF",-8.9369552248900188,-166.99199929652002,-3.9817830000000001,"OFF",-3.4561697959600104,-119.67758078056001,-3.9817830000000001,null,0,1667.0936659292281,0,0,0,1667.0936659292281,0,1724.3342753069717,0,0,0,1724.3342753069717,0,-63.008665929228073,0,0,0,0,-120.24927530697164,0,0,0,-65.788775294638228,-123.02938467238179,null,null,1584.8120650000001,null,29282.587499999994,9.6021171074385645,6099.1939948983481,71.640214255877211,5918.4632249999995,68.860104890467056,-2.780109365410155,null,null,null,null,null,null,null,null,null,1667.0936659292281,0,13.218518236802765,0,0,0]
[0,1649.2660772857027,0,0,0,1649.2660772857027,1866.536347,"2013-01-13T21:00:00",35,30,"OFF",-38.575835620200003,-73.058993676602014,-8.8484060000000007,"ON",31377.178599254996,66844.194826714011,1885.1179999999999,"OFF",7.5886192455000404E-2,-75.14639166260001,-1.7696810000000001,"OFF",-9.3344717774700019,-160.83416440970004,-3.9817830000000001,"OFF",-4.7016024805400001,-118.28596608156001,-3.9817830000000001,null,0,1636.7997779090936,0,0,0,1636.7997779090936,0,1692.6738989625539,0,0,0,1692.6738989625539,0,248.31822209090637,0,0,0,0,192.44410103744599,0,0,0,245.53811272549621,189.66399167203582,null,null,1866.536347,null,29282.587499999994,9.6021171074385645,6099.1939948983481,71.640214255877211,5918.4632249999995,68.860104890467056,-2.780109365410155,null,null,null,null,null,null,null,null,null,1636.7997779090936,0,12.466299376609186,0,0,0]
[0,1633.120120186727,0,0,0,1633.120120186727,1536.198431,"2013-01-13T22:00:00",32,28,"OFF",-38.292195819245009,-73.058993676602014,-8.8484060000000007,"ON",30878.679914000011,66303.245719252009,1557.3240000000001,"OFF",2.6533015312500834E-2,-46.444647297834003,-1.7696810000000001,"OFF",-8.6498716480399978,-166.99199929652002,-4.5624589999999996,"OFF",-5.3463007406800127,-120.37338813006001,-5.9450229999999999,null,0,1621.0417010928054,0,0,0,1621.0417010928054,0,1676.5127430731161,0,0,0,1676.5127430731161,0,-63.717701092805328,0,0,0,0,-119.18874307311603,0,0,0,-71.192359893335933,-126.66340187364663,null,null,1536.198431,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1621.0417010928054,0,12.078419093921639,0,0,0]
[0,1583.973855489789,0,0,0,1583.973855489789,1710.2104859999999,"2013-01-13T23:00:00",31,27,"OFF",-38.097980075260011,-75.14639166260001,-8.8484060000000007,"ON",29326.769154215006,67576.705512598011,1729.0409999999999,"OFF",7.0711772750002455E-2,-33.398399859304,-1.7696810000000001,"OFF",-8.7040209596899984,-160.83416440970004,-3.9817830000000001,"OFF",-4.5808131909050074,-120.37338813006001,-4.2306439999999998,null,0,1573.0613334069915,0,0,0,1573.0613334069915,0,1620.3521798511804,0,0,0,1620.3521798511804,0,155.97966659300846,0,0,0,0,108.68882014881956,0,0,0,145.98235074774115,98.69150430355225,null,null,1710.2104859999999,null,32487.155900000012,9.5288097691634306,6818.7227338996781,83.537574043904385,6219.6926546000013,73.540258198637076,-9.997315845267309,null,null,null,null,null,null,null,null,null,1573.0613334069915,0,10.912522082797523,0,0,0]
[0,0,0,0,0,0,490.30783100000002,"2013-01-14",31,27,"OFF",-38.065841499690002,-73.058993676602014,-8.8484060000000007,"OFF",11076.391035159999,24012.532204180003,511.43340000000001,"OFF",7.1717122140004447E-2,-33.398399859304,-1.7696810000000001,"OFF",-9.1669119366999894,-160.83416440970004,-4.5624589999999996,"OFF",1438.1338994250048,27279.048934016002,-5.9450229999999999,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-9.997315845267309,-9.997315845267309,null,null,490.30783100000002,null,32487.155900000012,9.5288097691634306,6818.7227338996781,83.537574043904385,6219.6926546000013,73.540258198637076,-9.997315845267309,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,0,1391.9032914044737,1391.9032914044737,1423.8190480000001,"2013-01-14T01:00:00",30,26,"OFF",-38.288194017299979,-72.363194347936002,-8.8484060000000007,"OFF",0.77595703124998383,-148.20536127670002,-8.8484060000000007,"OFF",-0.17966036862500109,-166.99199929652002,-1.7696810000000001,"OFF",-10.171754634029986,-164.80022619768002,-4.5624589999999996,"ON",23201.416876290008,49753.03278115001,1447.848,null,0,0,0,0,1385.0832343668126,1385.0832343668126,0,0,0,0,1447.4937844679428,1447.4937844679428,0,0,0,0,62.76476563318738,0,0,0,0,0.35421553205719647,49.78359751436642,-12.626952586763764,null,null,1423.8190480000001,null,33714.300000000047,9.5097922351801838,7090.4388163767808,88.375132939241695,6335.0442000000039,75.393964820420734,-12.98116811882096,null,null,null,null,null,null,null,null,null,1385.0832343668126,0,0,0,0,6.8200570376611722]
[0,0,0,0,1421.6395938876494,1421.6395938876494,1506.665442,"2013-01-14T02:00:00",29,25,"OFF",-38.550942836099992,-68.884197704605995,-8.8484060000000007,"OFF",-9.0061298080023278E-2,-138.22415523876001,-8.8484060000000007,"OFF",-0.25108652000000564,-166.99199929652002,-2.460963,"OFF",-8.845546970819985,-158.64239131086001,-3.9817830000000001,"ON",24769.489840649996,60593.294202992009,1530.8050000000001,null,0,0,0,0,1413.9176261561381,1413.9176261561381,0,0,0,0,1459.3114324343455,1459.3114324343455,0,0,0,0,116.88737384386195,0,0,0,0,71.49356756565453,100.40442127962497,55.010615001417548,null,null,1506.665442,null,35119.346100000024,9.4968388006218696,7396.0076268116391,94.041188884295593,6467.118533400002,77.558236320058612,-16.482952564236982,null,null,null,null,null,null,null,null,null,1413.9176261561381,0,0,0,0,7.7219677315113131]
[0,0,0,0,1440.3156961490647,1440.3156961490647,1376.340048,"2013-01-14T03:00:00",29,25,"OFF",-38.477383804440016,-72.363194347936002,-8.8484060000000007,"OFF",0.13602384553501753,-108.41063505242002,-8.8484060000000007,"OFF",-0.12202992249999851,-62.100144224070007,-1.7696810000000001,"OFF",-8.2161765042700239,-166.99199929652002,-4.5624589999999996,"ON",25732.72842000001,69075.566783012007,1400.3689999999999,null,0,0,0,0,1432.0112820053328,1432.0112820053328,0,0,0,0,1465.565563243294,1465.565563243294,0,0,0,0,-31.642282005332845,0,0,0,0,-65.196563243294122,-48.125234569569827,-81.679515807531104,null,null,1376.340048,null,35119.346100000024,9.4968388006218696,7396.0076268116391,94.041188884295593,6467.118533400002,77.558236320058612,-16.482952564236982,null,null,null,null,null,null,null,null,null,1432.0112820053328,0,0,0,0,8.3044141437319468]
[0,0,0,0,1478.4096541936092,1478.4096541936092,1418.3990480000002,"2013-01-14T04:00:00",30,26,"OFF",-39.021199088625011,-74.450592333934011,-8.8484060000000007,"OFF",-0.55639366804000789,-107.98304439188001,-8.8484060000000007,"OFF",-0.46502535150000296,-75.14639166260001,-1.7696810000000001,"OFF",-9.322976186590024,-164.80022619768002,-4.5624589999999996,"ON",27649.513814240017,68458.868919254004,1442.4280000000001,null,0,0,0,0,1468.8815702392342,1468.8815702392342,0,0,0,0,1508.5146632046785,1508.5146632046785,0,0,0,0,-26.453570239234068,0,0,0,0,-66.086663204678416,-39.434738358055029,-79.067831323499377,null,null,1418.3990480000002,null,33714.300000000047,9.5097922351801838,7090.4388163767808,88.375132939241695,6335.0442000000039,75.393964820420734,-12.98116811882096,null,null,null,null,null,null,null,null,null,1468.8815702392342,0,0,0,0,9.5280839543750062]
[0,0,0,0,1419.9076343101979,1419.9076343101979,1453.0990179999999,"2013-01-14T05:00:00",29,25,"OFF",-39.069330707265024,-72.363194347936002,-8.8484060000000007,"OFF",0.10643197028998976,-107.71490791126001,-8.8484060000000007,"OFF",-4.6501770852000406E-2,-75.14639166260001,-2.460963,"OFF",-7.9257464736100305,-166.99199929652002,-5.6132070000000001,"ON",24679.338787749992,70621.454203168003,1478.87,null,0,0,0,0,1412.2390701428017,1412.2390701428017,0,0,0,0,1441.0202474934536,1441.0202474934536,0,0,0,0,66.630929857198225,0,0,0,0,37.849752506546338,50.147977292961244,21.366799942309356,null,null,1453.0990179999999,null,35119.346100000024,9.4968388006218696,7396.0076268116391,94.041188884295593,6467.118533400002,77.558236320058612,-16.482952564236982,null,null,null,null,null,null,null,null,null,1412.2390701428017,0,0,0,0,7.6685641673961982]
[0,0,0,0,1455.5615654534665,1455.5615654534665,1359.941724,"2013-01-14T06:00:00",29,25,"OFF",-38.93538584465999,-73.133410974454009,-8.8484060000000007,"OFF",-1.2295178887500138,-106.50737135256001,-8.8484060000000007,"OFF",-0.27655821687500243,-33.398399859304,-1.7696810000000001,"OFF",-9.2059363311299816,-166.99199929652002,-3.9817830000000001,"ON",26507.363660260005,68915.334582194002,1383.39,null,0,0,0,0,1446.7730044675079,1446.7730044675079,0,0,0,0,1482.5545923379391,1482.5545923379391,0,0,0,0,-63.383004467507817,0,0,0,0,-99.164592337938984,-79.865957031744799,-115.64754490217597,null,null,1359.941724,null,35119.346100000024,9.4968388006218696,7396.0076268116391,94.041188884295593,6467.118533400002,77.558236320058612,-16.482952564236982,null,null,null,null,null,null,null,null,null,1446.7730044675079,0,0,0,0,8.7885609859586111]
[0,0,0,0,1451.9555806827675,1451.9555806827675,1481.6900480000002,"2013-01-14T07:00:00",29,25,"OFF",-38.39573541426001,-73.680375707416005,-8.8484060000000007,"OFF",-1.1326178379999909,-108.5447433969,-8.8484060000000007,"OFF",-8.3674531871999552E-2,-46.444647297834003,-1.7696810000000001,"OFF",-8.8676809960199723,-160.83416440970004,-4.5624589999999996,"ON",26325.069471420007,72059.260885174008,1505.7190000000001,null,0,0,0,0,1443.2822183810142,1443.2822183810142,0,0,0,0,1473.6213582715473,1473.6213582715473,0,0,0,0,62.436781618985833,0,0,0,0,32.0976417284528,45.953829054748851,15.614689164215818,null,null,1481.6900480000002,null,35119.346100000024,9.4968388006218696,7396.0076268116391,94.041188884295593,6467.118533400002,77.558236320058612,-16.482952564236982,null,null,null,null,null,null,null,null,null,1443.2822183810142,0,0,0,0,8.6733623017532864]
[0,0,0,0,1491.6365413909375,1491.6365413909375,1372.446623,"2013-01-14T08:00:00",30,26,"OFF",-38.517301413450014,-71.667395019270003,-8.8484060000000007,"OFF",-1.0171787542800101,-107.98304439188001,-8.8484060000000007,"OFF",-0.46466230662500424,-46.444647297834003,-1.7696810000000001,"OFF",-9.6782844097500025,-158.64239131086001,-6.1938839999999997,"ON",28300.853969250002,70170.731457372007,1398.107,null,0,0,0,0,1481.6729871650384,1481.6729871650384,0,0,0,0,1519.902255033961,1519.902255033961,0,0,0,0,-83.56598716503845,0,0,0,0,-121.79525503396098,-96.547155283859411,-134.77642315278194,null,null,1372.446623,null,33714.300000000047,9.5097922351801838,7090.4388163767808,88.375132939241695,6335.0442000000039,75.393964820420734,-12.98116811882096,null,null,null,null,null,null,null,null,null,1481.6729871650384,0,0,0,0,9.9635542258990881]
[0,0,0,0,1456.1430746633064,{"$f":"SUM(A324:E324)","v":1456.1430746633064},{"$f":"N324+R324+V324+Z324+AD324","v":1455.0063},"2013-01-14T09:00:00",31,26,"OFF",-38.702213773660013,-69.479479941584003,-8.8484060000000007,"OFF",-2.4466389327549893,-106.40735155258001,-8.8484060000000007,"OFF",-0.12561262328400116,-75.14639166260001,-1.7696810000000001,"OFF",-8.1304598566800035,-164.80022619768002,-5.6132070000000001,"ON",26536.707924489998,71876.76284917201,1480.086,null,0,0,0,0,1447.3358971051105,{"$f":"SUM(AF324:AJ324)","v":1447.3358971051105},0,0,0,0,1478.4246135064511,{"$f":"SUM(AL324:AP324)","v":1478.4246135064511},{"$f":"IF($K324=\"ON\",$N324-AF324,0)","v":0},{"$f":"IF($O324=\"ON\",$R324-AG324,0)","v":0},{"$f":"IF($S324=\"ON\",$V324-AH324,0)","v":0},{"$f":"IF($W324=\"ON\",$Z324-AI324,0)","v":0},{"$f":"IF($AA324=\"ON\",$AD324-AJ324,0)","v":32.750102894889551},{"$f":"IF($K324=\"ON\",$N324-AL324,0)","v":0},{"$f":"IF($O324=\"ON\",$R324-AM324,0)","v":0},{"$f":"IF($S324=\"ON\",$V324-AN324,0)","v":0},{"$f":"IF($W324=\"ON\",$Z324-AO324,0)","v":0},{"$f":"IF($AA324=\"ON\",$AD324-AP324,0)","v":1.6613864935488891},{"$f":"SUM(AR324:AV324)+BN324","v":21.985388351251714},{"$f":"SUM(AW324:BA324)+BN324","v":-9.1033280500889475},null,null,{"$f":"N324+R324+V324+Z324+AD324","v":1455.0063},null,32487.155900000012,{"$f":"19.5285952781395+42*-0.3035722016559+BH324*0.0000340867411548605+J324*0.0608468772796604","v":9.4679628918837686},{"$f":"BH324*1000/(500*BI324)","v":6862.5439856442645},{"$f":"0.00000128*BJ324^2+0*BJ324+24.024","v":84.304972742274913},{"$f":"0.094*BH324 + 3165.9","v":6219.6926546000013},{"$f":"0.00000128*BL324^2+0*BL324+24.024","v":73.540258198637076},{"$f":"BM324-BK324","v":-10.764714543637837},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF324:AJ324)","v":1447.3358971051105},{"$f":"A324-AF324","v":0},{"$f":"B324-AG324","v":0},{"$f":"C324-AH324","v":0},{"$f":"D324-AI324","v":0},{"$f":"E324-AJ324","v":8.8071775581959173}]
[0,0,0,0,1437.7095514023158,1437.7095514023158,1440.2990480000001,"2013-01-14T10:00:00",34,29,"OFF",-37.790422525099991,-72.363194347936002,-8.8484060000000007,"OFF",-3.1919922255200102,-110.63216544540002,-8.8484060000000007,"OFF",-8.556102959400072E-2,-62.100144224070007,-1.7696810000000001,"OFF",-7.3787989009000192,-164.80022619768002,-4.5624589999999996,"ON",25599.274683045005,70264.486985997995,1464.328,null,0,0,0,0,1429.4871272998553,1429.4871272998553,0,0,0,0,1460.8854381631963,1460.8854381631963,0,0,0,0,34.840872700144701,0,0,0,0,3.4425618368036339,30.60105577077583,-0.79725509256523708,null,null,1440.2990480000001,null,{"$f":" -0.6251*I325^3 + 145.21*I325^2 - 8340.3*I325 + 170112","v":29835.629600000044},9.5601216330693468,6241.6841009210257,73.891034132083604,5970.4491824000042,69.651217202714733,-4.239816929368871,null,null,null,null,null,null,null,null,null,1429.4871272998553,0,0,0,0,8.2224241024605362]
[0,0,0,0,1283.1178097300001,1283.1178097300001,1375.9267239999999,"2013-01-14T11:00:00",36,30,"OFF",-37.400731931429995,-73.855302076122015,-8.8484060000000007,"OFF",-2.4265165122800161,-106.45732134840001,-8.8484060000000007,"OFF",-0.19601465021999856,-46.444647297834003,-1.7696810000000001,"OFF",-7.1631766054099906,-166.99199929652002,-3.9817830000000001,"ON",17045.606617600006,51199.670401390002,1399.375,null,0,0,0,0,1279.2891276157593,1279.2891276157593,0,0,0,0,1312.2850410971535,1312.2850410971535,0,0,0,0,120.0858723842407,0,0,0,0,87.089958902846547,117.88904933130905,84.893135849914898,null,null,1375.9267239999999,null,28888.694400000008,9.5886905752961802,6025.5765212462666,70.497692689144657,5881.4372736000005,68.300869636213008,-2.1968230529316486,null,null,null,null,null,null,null,null,null,1279.2891276157593,0,0,0,0,3.8286821142407916]
[0,0,1601.7533629233001,0,0,1601.7533629233001,1789.9767610000001,"2013-01-14T12:00:00",39,32,"OFF",-38.217626935940011,-72.363194347936002,-8.8484060000000007,"OFF",-2.9009907763199925,-109.10644240192002,-8.8484060000000007,"ON",37621.59679286999,68229.52921269201,1815.886,"OFF",-8.0131231730900172,-158.64239131086001,-3.9817830000000001,"OFF",-0.65903773291999634,-118.98177343106001,-4.2306439999999998,null,0,0,1584.4156469521199,0,0,1584.4156469521199,0,0,1657.3941630502284,0,0,1657.3941630502284,0,0,231.47035304788005,0,0,0,0,158.4918369497716,0,0,230.80051292151165,157.8219968234032,null,null,1789.9767610000001,null,28624.403100000054,9.7013755007229214,5901.1019824698133,68.597445897611721,5856.5938914000053,67.927605771243336,-0.66984012636838486,null,null,null,null,null,null,null,null,null,1584.4156469521199,0,0,17.33771597118016,0,0]
[0,0,1639.6106379415692,0,0,1639.6106379415692,1698.9623820000002,"2013-01-14T13:00:00",42,33,"OFF",-37.6853319855,-70.275796361938006,-8.8484060000000007,"OFF",-3.9792178698500087,-132.29780162118001,-8.8484060000000007,"ON",38876.00803248,68594.565388866016,1726.586,"OFF",-7.5196398112500136,-158.64239131086001,-3.9817830000000001,"OFF",-2.0547842218750119,-118.28596608156001,-5.9450229999999999,null,0,0,1621.1017279526648,0,0,1621.1017279526648,0,0,1697.7090121849988,0,0,1697.7090121849988,0,0,105.48427204733525,0,0,0,0,28.876987815001257,0,0,103.94076866814166,27.333484435807662,null,null,1698.9623820000002,null,29657.431200000021,9.7974349394529767,6054.1215906570533,70.939056940108657,5953.6985328000019,69.395553560915062,-1.543503379193595,null,null,null,null,null,null,null,null,null,1621.1017279526648,0,0,18.508909988904406,0,0]
[0,0,1540.0932608114783,0,0,1540.0932608114783,1642.4856220000001,"2013-01-14T14:00:00",44,35,"OFF",-37.286604725479989,-72.363194347936002,-8.8484060000000007,"OFF",-4.5323220134000088,-119.62672869300002,-8.8484060000000007,"ON",35517.701041479995,74158.794393014017,1668.146,"OFF",-7.4279680568799744,-164.80022619768002,-3.9817830000000001,"OFF",-2.2502547069800252,-116.89443159090001,-3.9817830000000001,null,0,0,1524.6292270631161,0,0,1524.6292270631161,0,0,1573.2608950067684,0,0,1573.2608950067684,0,0,143.51677293688385,0,0,0,0,94.885104993231607,0,0,141.25820472611315,92.626536782460917,null,null,1642.4856220000001,null,31016.841600000043,9.9654665644403231,6224.8649171484121,73.622647343033734,6081.4831104000041,71.364079132263043,-2.2585682107706901,null,null,null,null,null,null,null,null,null,1524.6292270631161,0,0,15.464033748362226,0,0]
[0,0,1568.2045718578447,0,0,1568.2045718578447,1631.5217610000002,"2013-01-14T15:00:00",45,36,"OFF",-36.623887683480014,-70.971595690604005,-8.8484060000000007,"OFF",-6.2602625818500197,-108.49477360108,-8.8484060000000007,"ON",36486.604412160006,74827.282781910006,1657.431,"OFF",-6.9478968603099966,-160.83416440970004,-3.9817830000000001,"OFF",-0.43870754522001215,-118.29037754026001,-4.2306439999999998,null,0,0,1551.8917108775202,0,0,1551.8917108775202,0,0,1601.4159110879957,0,0,1601.4159110879957,0,0,105.53928912247989,0,0,0,0,56.01508891200433,0,0,102.68080747844678,53.156607267971225,null,null,1631.5217610000002,null,31886.51250000007,10.0559576885782,6341.8151681798627,75.503833123015909,6163.2321750000065,72.645351478982803,-2.8584816440331053,null,null,null,null,null,null,null,null,null,1551.8917108775202,0,0,16.312860980324558,0,0]
[0,0,1603.9354120997918,0,0,1603.9354120997918,1717.766521,"2013-01-14T16:00:00",45,36,"OFF",-35.98552452018999,-70.971595690604005,-8.8484060000000007,"OFF",-4.8745771405649956,-109.29060075056002,-8.8484060000000007,"ON",37694.643119399982,77809.140113086018,1745.6389999999999,"OFF",-7.3496821177499889,-160.83416440970004,-3.9817830000000001,"OFF",-3.1876556462099956,-117.58582748170001,-6.1938839999999997,null,0,0,1586.5306064001275,0,0,1586.5306064001275,0,0,1631.301275395977,0,0,1631.301275395977,0,0,159.10839359987244,0,0,0,0,114.33772460402292,0,0,156.24991195583934,111.47924295998982,null,null,1717.766521,null,31886.51250000007,10.0559576885782,6341.8151681798627,75.503833123015909,6163.2321750000065,72.645351478982803,-2.8584816440331053,null,null,null,null,null,null,null,null,null,1586.5306064001275,0,0,17.404805699664394,0,0]
[0,0,1636.1667643541443,0,0,1636.1667643541443,1613.6590470000003,"2013-01-14T17:00:00",44,36,"OFF",-35.612671595689996,-73.058993676602014,-8.8484060000000007,"OFF",-4.955011306769987,-106.9690505576,-8.8484060000000007,"ON",38763.006607985008,75739.484211895993,1637.6880000000001,"OFF",-8.1974679829700037,-158.64239131086001,-2.3503579999999999,"OFF",-2.0550990474700077,-118.98177343106001,-3.9817830000000001,null,0,0,1617.7650221888277,0,0,1617.7650221888277,0,0,1670.9562577649317,0,0,1670.9562577649317,0,0,19.922977811172359,0,0,0,0,-33.268257764931604,0,0,18.264583405680384,-34.92665217042358,null,null,1613.6590470000003,null,31016.841600000043,10.026313441719985,6187.0879621491649,73.022473537755019,6081.4831104000041,71.364079132263043,-1.6583944054919755,null,null,null,null,null,null,null,null,null,1617.7650221888277,0,0,18.401742165316591,0,0]
[0,0,1589.8930151663899,0,0,1589.8930151663899,1645.7346220000002,"2013-01-14T18:00:00",41,35,"OFF",-35.463266925590013,-72.363194347936002,-8.8484060000000007,"OFF",-5.3023524070399919,-109.37465909088,-8.8484060000000007,"ON",37222.924678880008,76751.079816810001,1671.395,"OFF",-6.7525377378899964,-158.64239131086001,-3.9817830000000001,"OFF",-1.9628065950500027,-117.59015873206,-3.9817830000000001,null,0,0,1572.9190468954441,0,0,1572.9190468954441,0,0,1619.302688317443,0,0,1619.302688317443,0,0,98.475953104555856,0,0,0,0,52.09231168255701,0,0,98.71750068307324,52.333859261074394,null,null,1645.7346220000002,null,29175.192900000024,9.9026907619052373,5892.3768501858849,68.465734329096364,5908.3681326000024,68.707281907613748,0.24154757851738395,null,null,null,null,null,null,null,null,null,1572.9190468954441,0,0,16.973968270945761,0,0]
[0,0,1552.354250030894,0,0,1552.354250030894,1521.4006220000001,"2013-01-14T19:00:00",37,32,"OFF",-35.352596799590003,-71.667395019270003,-8.8484060000000007,"OFF",-4.8444041769000066,-106.50737135256001,-8.8484060000000007,"ON",35942.357537240008,75971.438710342016,1547.0609999999999,"OFF",-7.8037458347100239,-164.80022619768002,-3.9817830000000001,"OFF",-3.4358773432199947,-118.98177343106001,-3.9817830000000001,null,0,0,1536.5211340166645,0,0,1536.5211340166645,0,0,1581.7004362567898,0,0,1581.7004362567898,0,0,10.539865983335403,0,0,0,0,-34.63943625678985,0,0,9.8341066943595621,-35.345195545765691,null,null,1521.4006220000001,null,28650.199700000056,9.7022548227497971,5905.8848120173498,68.66972852840604,5859.0187718000052,67.963969239430199,-0.70575928897584106,null,null,null,null,null,null,null,null,null,1536.5211340166645,0,0,15.833116014229518,0,0]
[0,0,1507.0294735875632,0,0,1507.0294735875632,1554.9696220000003,"2013-01-14T20:00:00",36,32,"OFF",-35.131599097980001,-72.363194347936002,-8.8484060000000007,"OFF",-6.6389903946500137,-107.79896625158001,-8.8484060000000007,"ON",34356.060294930001,76409.536663422012,1580.63,"OFF",-6.1358152857400068,-166.99199929652002,-3.9817830000000001,"OFF",-0.5179245259999995,-117.59015873206,-3.9817830000000001,null,0,0,1492.5516413942466,0,0,1492.5516413942466,0,0,1532.8700433115255,0,0,1532.8700433115255,0,0,88.078358605753465,0,0,0,0,47.759956688474631,0,0,87.039083863193198,46.720681945914365,null,null,1554.9696220000003,null,28888.694400000008,9.7103843298555006,5950.0619993338405,69.340144378773275,5881.4372736000005,68.300869636213008,-1.0392747425602664,null,null,null,null,null,null,null,null,null,1492.5516413942466,0,0,14.477832193316544,0,0]
[0,0,1449.8848433349726,0,0,1449.8848433349726,1551.1676220000002,"2013-01-14T21:00:00",37,32,"OFF",-35.780898017910005,-73.058993676602014,-8.8484060000000007,"OFF",-5.7014071450000268,-105.06578685774001,-8.8484060000000007,"ON",32287.944241995003,76132.946223766005,1576.828,"OFF",-7.2466211129400033,-158.64239131086001,-3.9817830000000001,"OFF",-2.2890565936000038,-116.89443159090001,-3.9817830000000001,null,0,0,1437.0783755363891,0,0,1437.0783755363891,0,0,1473.2883669916014,0,0,1473.2883669916014,0,0,139.74962446361087,0,0,0,0,103.5396330083986,0,0,139.04386517463502,102.83387371942275,null,null,1551.1676220000002,null,28650.199700000056,9.7022548227497971,5905.8848120173498,68.66972852840604,5859.0187718000052,67.963969239430199,-0.70575928897584106,null,null,null,null,null,null,null,null,null,1437.0783755363891,0,0,12.806467798583526,0,0]
[0,0,1492.8231837732797,0,0,1492.8231837732797,1592.6166220000002,"2013-01-14T22:00:00",37,32,"OFF",-35.828615973020007,-73.058993676602014,-8.8484060000000007,"OFF",-5.1526411731549748,-121.86582471244,-8.8484060000000007,"ON",33849.286494939995,76237.578003296003,1618.277,"OFF",-6.7118269415400311,-160.83416440970004,-3.9817830000000001,"OFF",-2.7273396105200023,-116.89443159090001,-3.9817830000000001,null,0,0,1478.7648785167241,0,0,1478.7648785167241,0,0,1518.2892545392549,0,0,1518.2892545392549,0,0,139.51212148327591,0,0,0,0,99.987745460745145,0,0,138.80636219430005,99.281986171769304,null,null,1592.6166220000002,null,28650.199700000056,9.7022548227497971,5905.8848120173498,68.66972852840604,5859.0187718000052,67.963969239430199,-0.70575928897584106,null,null,null,null,null,null,null,null,null,1478.7648785167241,0,0,14.058305256555514,0,0]
[0,0,1424.5313782781736,0,0,1424.5313782781736,1358.4097610000001,"2013-01-14T23:00:00",34,29,"OFF",-34.882538614420007,-72.363194347936002,-8.8484060000000007,"OFF",-6.1355952173000006,-136.04754151618002,-8.8484060000000007,"ON",31343.967246374992,73411.509330902001,1384.319,"OFF",-6.0237749581799793,-164.80022619768002,-3.9817830000000001,"OFF",-1.1103962214800123,-121.06919547956002,-4.2306439999999998,null,0,0,1412.4520893290533,0,0,1412.4520893290533,0,0,1451.9281026299313,0,0,1451.9281026299313,0,0,-28.133089329053291,0,0,0,0,-67.609102629931385,0,0,-32.372906258422162,-71.848919559300256,null,null,1358.4097610000001,null,29835.629600000044,9.5601216330693468,6241.6841009210257,73.891034132083604,5970.4491824000042,69.651217202714733,-4.239816929368871,null,null,null,null,null,null,null,null,null,1412.4520893290533,0,0,12.079288949120382,0,0]
[0,0,1432.8853313453085,0,0,1432.8853313453085,1647.9466220000002,"2013-01-15",33,29,"OFF",-35.505795721049999,-72.363194347936002,-8.8484060000000007,"OFF",-5.4572002616400042,-107.10315890208001,-8.8484060000000007,"ON",31656.890207850003,79195.172311622009,1673.607,"OFF",-5.8684942313900077,-166.99199929652002,-3.9817830000000001,"OFF",0.52095772493998804,-117.59015873206,-3.9817830000000001,null,0,0,1420.5674562022548,0,0,1420.5674562022548,0,0,1449.7367862806605,0,0,1449.7367862806605,0,0,253.03954379774518,0,0,0,0,223.87021371933952,0,0,247.67812282380635,218.50879274540068,null,null,1647.9466220000002,null,30551.57130000004,9.5845257524792178,6375.1868561879128,76.047049537678248,6037.7477022000039,70.685628563739428,-5.3614209739388201,null,null,null,null,null,null,null,null,null,1420.5674562022548,0,0,12.317875143053698,0,0]
[0,0,1392.211774793642,0,0,1392.211774793642,1262.9447610000002,"2013-01-15T01:00:00",32,28,"OFF",-35.099968396720001,-70.971595690604005,-8.8484060000000007,"OFF",-5.3319786417300232,-157.11161514196002,-8.8484060000000007,"ON",30115.194890260009,78817.599571906016,1288.854,"OFF",-6.4444531871299766,-158.64239131086001,-3.9817830000000001,"OFF",-0.31601886652001154,-119.67758078056001,-4.2306439999999998,null,0,0,1381.0457443813971,0,0,1381.0457443813971,0,0,1408.0957803024953,0,0,1408.0957803024953,0,0,-92.191744381397029,0,0,0,0,-119.24178030249527,0,0,-99.666403181927635,-126.71643910302588,null,null,1262.9447610000002,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1381.0457443813971,0,0,11.166030412244936,0,0]
[0,0,1354.8960752068369,0,0,1354.8960752068369,1508.6250850000001,"2013-01-15T02:00:00",34,29,"OFF",-35.063312777749992,-72.363194347936002,-8.8484060000000007,"OFF",-6.0927757950850143,-110.49805710092001,-8.8484060000000007,"ON",28658.54130165001,72824.424386272003,1535.115,"OFF",-6.3057466292099864,-164.80022619768002,-4.5624589999999996,"OFF",-0.29207547040001303,-121.06919547956002,-4.2306439999999998,null,0,0,1344.7641383753628,0,0,1344.7641383753628,0,0,1378.8758121923738,0,0,1378.8758121923738,0,0,190.35086162463722,0,0,0,0,156.23918780762619,0,0,186.11104469526833,151.99937087825731,null,null,1508.6250850000001,null,29835.629600000044,9.5601216330693468,6241.6841009210257,73.891034132083604,5970.4491824000042,69.651217202714733,-4.239816929368871,null,null,null,null,null,null,null,null,null,1344.7641383753628,0,0,10.13193683147415,0,0]
[0,0,1347.8220372676249,0,0,1347.8220372676249,1338.8739460000002,"2013-01-15T03:00:00",34,29,"OFF",-35.551355075879982,-71.667395019270003,-8.8484060000000007,"OFF",-6.8221177672500266,-143.56980047473999,-8.8484060000000007,"ON",28377.549712500015,78083.09971919001,1365.115,"OFF",-5.2976998815299909,-166.99199929652002,-4.5624589999999996,"OFF",-2.6510879401650085,-119.67758078056001,-3.9817830000000001,null,0,0,1337.8835487982269,0,0,1337.8835487982269,0,0,1363.0294817563063,0,0,1363.0294817563063,0,0,27.231451201773098,0,0,0,0,2.0855182436937412,0,0,22.991634272404227,-2.1542986856751298,null,null,1338.8739460000002,null,29835.629600000044,9.5601216330693468,6241.6841009210257,73.891034132083604,5970.4491824000042,69.651217202714733,-4.239816929368871,null,null,null,null,null,null,null,null,null,1337.8835487982269,0,0,9.9384884693979529,0,0]
[0,0,1391.8050653343832,0,0,1391.8050653343832,1341.6666220000002,"2013-01-15T04:00:00",33,29,"OFF",-35.762287066029984,-70.971595690604005,-8.8484060000000007,"OFF",-5.6879938145399995,-125.61564481578002,-8.8484060000000007,"ON",30099.542940319992,78302.277029074015,1367.327,"OFF",-6.5533051610600035,-158.64239131086001,-3.9817830000000001,"OFF",-0.99106131634999017,-120.37338813006001,-3.9817830000000001,null,0,0,1380.6504257059469,0,0,1380.6504257059469,0,0,1408.514701740429,0,0,1408.514701740429,0,0,-13.323425705946875,0,0,0,0,-41.18770174042902,0,0,-18.684846679885695,-46.54912271436784,null,null,1341.6666220000002,null,30551.57130000004,9.5845257524792178,6375.1868561879128,76.047049537678248,6037.7477022000039,70.685628563739428,-5.3614209739388201,null,null,null,null,null,null,null,null,null,1380.6504257059469,0,0,11.154639628436371,0,0]
[0,0,1387.3435506284311,0,0,1387.3435506284311,1567.2187060000001,"2013-01-15T05:00:00",33,29,"OFF",-36.225030721500005,-71.667395019270003,-8.8484060000000007,"OFF",-6.111359897264971,-105.71154420308001,-8.8484060000000007,"ON",29927.527565100005,77534.899777792001,1595.423,"OFF",-5.8629343750600018,-158.64239131086001,-4.5624589999999996,"OFF",1.9783018780005171E-2,-118.98177343106001,-5.9450229999999999,null,0,0,1376.3136955069579,0,0,1376.3136955069579,0,0,1405.1263334785424,0,0,1405.1263334785424,0,0,219.10930449304215,0,0,0,0,190.29666652145761,0,0,213.74788351910331,184.93524554751878,null,null,1567.2187060000001,null,30551.57130000004,9.5845257524792178,6375.1868561879128,76.047049537678248,6037.7477022000039,70.685628563739428,-5.3614209739388201,null,null,null,null,null,null,null,null,null,1376.3136955069579,0,0,11.029855121473247,0,0]
[0,0,1417.9315833482356,0,0,1417.9315833482356,1233.9378450000002,"2013-01-15T06:00:00",33,29,"OFF",-35.675727217479988,-74.450592333934011,-8.8484060000000007,"OFF",-6.3258923342200069,-160.72476023394,-8.8484060000000007,"ON",31095.414097770004,76336.996240726003,1262.3910000000001,"OFF",-5.5362467031199936,-164.80022619768002,-4.5624589999999996,"OFF",3.5660377200007379E-2,-119.67758078056001,-6.1938839999999997,null,0,0,1406.0400602089521,0,0,1406.0400602089521,0,0,1439.2826138150801,0,0,1439.2826138150801,0,0,-143.64906020895205,0,0,0,0,-176.89161381508006,0,0,-149.01048118289089,-182.2530347890189,null,null,1233.9378450000002,null,30551.57130000004,9.5845257524792178,6375.1868561879128,76.047049537678248,6037.7477022000039,70.685628563739428,-5.3614209739388201,null,null,null,null,null,null,null,null,null,1406.0400602089521,0,0,11.891523139283436,0,0]
[0,0,1404.977505669825,0,0,1404.977505669825,1461.2033820000001,"2013-01-15T07:00:00",30,29,"OFF",-36.423608194169979,-74.450592333934011,-8.8484060000000007,"OFF",-5.9225009276199989,-109.93635809590002,-8.8484060000000007,"ON",30604.053522659993,71022.985174042013,1488.827,"OFF",-5.2812311127800058,-158.64239131086001,-3.9817830000000001,"OFF",0.12256132020999036,-121.06919547956002,-5.9450229999999999,null,0,0,1393.4526427250937,0,0,1393.4526427250937,0,0,1435.8975353092042,0,0,1435.8975353092042,0,0,95.374357274906288,0,0,0,0,52.929464690795839,0,0,84.794278939737694,42.349386355627246,null,null,1461.2033820000001,null,33714.300000000047,9.6923328670191662,6956.9009778279988,85.974043155589328,6335.0442000000039,75.393964820420734,-10.580078335168594,null,null,null,null,null,null,null,null,null,1393.4526427250937,0,0,11.52486294473124,0,0]
[0,0,1426.5160805599983,0,0,1426.5160805599983,1483.5873820000002,"2013-01-15T08:00:00",30,29,"OFF",-35.600313431620002,-70.275796361938006,-8.8484060000000007,"OFF",-7.2083129826000141,-130.49375563789999,-8.8484060000000007,"ON",31418.480672039997,76896.417328890006,1511.211,"OFF",-5.1379923496999993,-166.99199929652002,-3.9817830000000001,"OFF",0.86043395844000348,-120.37338813006001,-5.9450229999999999,null,0,0,1414.380201163418,0,0,1414.380201163418,0,0,1447.2603140565479,0,0,1447.2603140565479,0,0,96.830798836582062,0,0,0,0,63.950685943452072,0,0,86.250720501413468,53.370607608283478,null,null,1483.5873820000002,null,33714.300000000047,9.6923328670191662,6956.9009778279988,85.974043155589328,6335.0442000000039,75.393964820420734,-10.580078335168594,null,null,null,null,null,null,null,null,null,1414.380201163418,0,0,12.135879396580322,0,0]
[0,0,1373.0715779865347,0,0,1373.0715779865347,1310.586706,"2013-01-15T09:00:00",31,30,"OFF",-36.015682674780017,-70.971595690604005,-8.8484060000000007,"OFF",-6.2589861383199796,-133.63182673206001,-8.8484060000000007,"ON",29373.310552040013,73180.316811686003,1338.7909999999999,"OFF",-5.3848394307400156,-158.64239131086001,-4.5624589999999996,"OFF",1.4376017610500018,-118.98177343106001,-5.9450229999999999,null,0,0,1362.4387783527948,0,0,1362.4387783527948,0,0,1397.5960532705935,0,0,1397.5960532705935,0,0,-23.64777835279483,0,0,0,0,-58.805053270593589,0,0,-31.428812214833528,-66.586087132632287,null,null,1310.586706,null,32487.155900000012,9.7113504010024112,6690.5537455731528,81.321292060675773,6219.6926546000013,73.540258198637076,-7.7810338620386972,null,null,null,null,null,null,null,null,null,1362.4387783527948,0,0,10.632799633739978,0,0]
[0,0,1383.7409622940158,0,0,1383.7409622940158,1562.365706,"2013-01-15T10:00:00",33,31,"OFF",-35.789585697109978,-71.667395019270003,-8.8484060000000007,"OFF",-6.1018879466999811,-110.63216544540002,-8.8484060000000007,"ON",29788.201952820003,77007.834733984011,1590.57,"OFF",-5.5286051944200025,-166.99199929652002,-4.5624589999999996,"OFF",1.7089827171899821,-116.89884304960002,-5.9450229999999999,null,0,0,1372.811639723576,0,0,1372.811639723576,0,0,1402.2337660268549,0,0,1402.2337660268549,0,0,217.7583602764239,0,0,0,0,188.336233973145,0,0,213.69326128463226,184.27113498135336,null,null,1562.365706,null,30551.57130000004,9.7062195070385382,6295.2566192935019,74.750727555531071,6037.7477022000039,70.685628563739428,-4.0650989917916434,null,null,null,null,null,null,null,null,null,1372.811639723576,0,0,10.929322570439808,0,0]
[0,0,1409.0024651971059,0,0,1409.0024651971059,1260.842521,"2013-01-15T11:00:00",35,32,"OFF",-36.429223463124998,-72.363194347936002,-8.8484060000000007,"OFF",-5.7974758911999844,-136.65511969168003,-8.8484060000000007,"ON",30757.226184320003,73588.408824772006,1288.7149999999999,"OFF",-5.8175859734299875,-160.83416440970004,-3.9817830000000001,"OFF",1.9287169725599811,-118.97736197236,-6.1938839999999997,null,0,0,1397.3639476421804,0,0,1397.3639476421804,0,0,1435.0524912331352,0,0,1435.0524912331352,0,0,-108.64894764218047,0,0,0,0,-146.33749123313532,0,0,-110.24467853485319,-147.93322212580804,null,null,1260.842521,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1397.3639476421804,0,0,11.638517554925556,0,0]
[0,0,1497.0839732527825,0,0,1497.0839732527825,1647.6423820000002,"2013-01-15T12:00:00",35,32,"OFF",-35.92701824544001,-70.971595690604005,-8.8484060000000007,"OFF",-6.9193162300199917,-108.5447433969,-8.8484060000000007,"ON",34001.775810990002,77260.667463332007,1675.2660000000001,"OFF",-5.0644494159699844,-166.99199929652002,-3.9817830000000001,"OFF",0.32385534177501124,-120.37338813006001,-5.9450229999999999,null,0,0,1482.9001142096872,0,0,1482.9001142096872,0,0,1520.5483208390704,0,0,1520.5483208390704,0,0,192.36588579031286,0,0,0,0,154.71767916092972,0,0,190.77015489764014,153.121948268257,null,null,1647.6423820000002,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1482.9001142096872,0,0,14.183859043095254,0,0]
[0,0,1465.4342504050114,0,0,1465.4342504050114,1366.7189460000002,"2013-01-15T13:00:00",36,33,"OFF",-36.561125819880004,-73.754793005267999,-8.8484060000000007,"OFF",-5.511849019969997,-146.39626216799999,-8.8484060000000007,"ON",32858.639212220012,77004.706608723995,1392.96,"OFF",-4.5570532382900213,-158.64239131086001,-4.5624589999999996,"OFF",0.80566980773999541,-119.67758078056001,-3.9817830000000001,null,0,0,1452.1773265217955,0,0,1452.1773265217955,0,0,1487.8786698611036,0,0,1487.8786698611036,0,0,-59.217326521795485,0,0,0,0,-94.918669861103581,0,0,-59.693978065555996,-95.395321404864092,null,null,1366.7189460000002,null,28888.694400000008,9.7712312071351608,5913.0100982371323,68.777521179973519,5881.4372736000005,68.300869636213008,-0.47665154376051078,null,null,null,null,null,null,null,null,null,1452.1773265217955,0,0,13.256923883215904,0,0]
[0,0,1494.5222746200384,0,0,1494.5222746200384,1576.8686220000002,"2013-01-15T14:00:00",37,33,"OFF",-35.919702145249992,-73.754793005267999,-8.8484060000000007,"OFF",-6.530010987014971,-106.45732134840001,-8.8484060000000007,"ON",33910.146606844988,71191.29435469801,1602.529,"OFF",-6.083879376609997,-158.64239131086001,-3.9817830000000001,"OFF",0.6524424392300141,-121.06919547956002,-3.9817830000000001,null,0,0,1480.4139299372011,0,0,1480.4139299372011,0,0,1531.964727960557,0,0,1531.964727960557,0,0,122.11507006279885,0,0,0,0,70.56427203944304,0,0,121.96407052525329,70.413272501897481,null,null,1576.8686220000002,null,28650.199700000056,9.7631017000294555,5869.0773855021125,68.114968776975758,5859.0187718000052,67.963969239430199,-0.15099953754555884,null,null,null,null,null,null,null,null,null,1480.4139299372011,0,0,14.108344682837242,0,0]
[0,0,1476.4188725506287,0,0,1476.4188725506287,1416.242845,"2013-01-15T15:00:00",38,34,"OFF",-35.595596776249998,-73.754793005267999,-8.8484060000000007,"OFF",-5.6522271401849853,-107.20317870206,-8.8484060000000007,"ON",33258.144744179997,76228.714981726007,1444.6959999999999,"OFF",-5.4220193230699838,-166.99199929652002,-4.5624589999999996,"OFF",3.2621179100300117,-118.98177343106001,-6.1938839999999997,null,0,0,1462.8417442265159,0,0,1462.8417442265159,0,0,1501.030523225344,0,0,1501.030523225344,0,0,-18.145744226515944,0,0,0,0,-56.334523225344128,0,0,-17.637115452772136,-55.82589445160032,null,null,1416.242845,null,28563.352800000052,9.820988249508714,5816.798080667475,67.332979086408727,5850.8551632000053,67.841607860152536,0.50862877374380844,null,null,null,null,null,null,null,null,null,1462.8417442265159,0,0,13.577128324112891,0,0]
[0,0,1496.0879305853002,0,0,1496.0879305853002,1682.2066220000002,"2013-01-15T16:00:00",39,34,"OFF",-36.056770420229988,-70.971595690604005,-8.8484060000000007,"OFF",-6.0480940405500005,-101.53678031442,-8.8484060000000007,"ON",33966.166807529997,75598.574200184012,1707.867,"OFF",-4.9707487092899738,-158.64239131086001,-3.9817830000000001,"OFF",3.9884858313299931,-118.98177343106001,-3.9817830000000001,null,0,0,1481.9334431820059,0,0,1481.9334431820059,0,0,1523.1492094496596,0,0,1523.1492094496596,0,0,225.93355681799403,0,0,0,0,184.7177905503404,0,0,226.36127797928057,185.14551171162694,null,null,1682.2066220000002,null,28624.403100000054,9.8230692552822418,5827.9957834172064,67.499884609956794,5856.5938914000053,67.927605771243336,0.42772116128654147,null,null,null,null,null,null,null,null,null,1481.9334431820059,0,0,14.154487403294297,0,0]
[0,0,1517.4608600201582,0,0,1517.4608600201582,1503.2335210000001,"2013-01-15T17:00:00",38,33,"OFF",-35.576440304439991,-73.058993676602014,-8.8484060000000007,"OFF",-6.9519580231949902,-128.30551170602001,-8.8484060000000007,"ON",34725.201648390001,74985.662170074007,1531.106,"OFF",-5.3247613623400056,-160.83416440970004,-3.9817830000000001,"OFF",4.4807688480099976,-118.98177343106001,-6.1938839999999997,null,0,0,1502.6733475076414,0,0,1502.6733475076414,0,0,1547.1826460660184,0,0,1547.1826460660184,0,0,28.432652492358557,0,0,0,0,-16.076646066018384,0,0,28.399602555823236,-16.109696002553704,null,null,1503.2335210000001,null,28563.352800000052,9.7601413722290538,5853.0612848032251,67.874657796687856,5850.8551632000053,67.841607860152536,-3.3049936535320512E-2,null,null,null,null,null,null,null,null,null,1502.6733475076414,0,0,14.787512512516741,0,0]
[0,0,1495.9676604553738,0,0,1495.9676604553738,1660.2093820000002,"2013-01-15T18:00:00",38,33,"OFF",-35.461475123550024,-69.579997033272008,-8.8484060000000007,"OFF",-5.6183922966249931,-126.45815321914,-8.8484060000000007,"ON",33961.865512459997,70356.076889443997,1687.8330000000001,"OFF",-6.3334313624999927,-164.80022619768002,-3.9817830000000001,"OFF",4.0024952652300056,-118.28596608156001,-5.9450229999999999,null,0,0,1481.8167187527665,0,0,1481.8167187527665,0,0,1535.6641554385751,0,0,1535.6641554385751,0,0,206.01628124723356,0,0,0,0,152.16884456142498,0,0,205.98323131069824,152.13579462488966,null,null,1660.2093820000002,null,28563.352800000052,9.7601413722290538,5853.0612848032251,67.874657796687856,5850.8551632000053,67.841607860152536,-3.3049936535320512E-2,null,null,null,null,null,null,null,null,null,1481.8167187527665,0,0,14.15094170260727,0,0]
[0,0,1502.2368233460857,0,0,1502.2368233460857,1624.8573369999999,"2013-01-15T19:00:00",38,33,"OFF",-35.642467639700023,-73.058993676602014,-8.8484060000000007,"OFF",-5.9599288652399736,-134.37768408572001,-8.8484060000000007,"ON",34185.621223979993,75848.543491794015,1652.3979999999999,"OFF",-4.6566563516899953,-160.83416440970004,-5.6132070000000001,"OFF",4.0955518685899817,-117.59015873206,-4.2306439999999998,null,0,0,1487.9008118735785,0,0,1487.9008118735785,0,0,1529.0799819629917,0,0,1529.0799819629917,0,0,164.49718812642141,0,0,0,0,123.31801803700819,0,0,164.46413818988609,123.28496810047287,null,null,1624.8573369999999,null,28563.352800000052,9.7601413722290538,5853.0612848032251,67.874657796687856,5850.8551632000053,67.841607860152536,-3.3049936535320512E-2,null,null,null,null,null,null,null,null,null,1487.9008118735785,0,0,14.336011472507153,0,0]
[0,0,1429.0534248976514,0,0,1429.0534248976514,1365.7794200000001,"2013-01-15T20:00:00",37,32,"OFF",-34.613346707939989,-71.667395019270003,-8.8484060000000007,"OFF",-5.9847489978750117,-101.58675011024,-8.8484060000000007,"ON",31513.587432919994,76712.202834412004,1395.864,"OFF",-5.0831579372700064,-158.64239131086001,-6.1938839999999997,"OFF",5.6055794477199985,-118.98177343106001,-6.1938839999999997,null,0,0,1416.8451136831354,0,0,1416.8451136831354,0,0,1450.2665427333391,0,0,1450.2665427333391,0,0,-20.981113683135391,0,0,0,0,-54.402542733339033,0,0,-21.686872972111232,-55.108302022314874,null,null,1365.7794200000001,null,28650.199700000056,9.7022548227497971,5905.8848120173498,68.66972852840604,5859.0187718000052,67.963969239430199,-0.70575928897584106,null,null,null,null,null,null,null,null,null,1416.8451136831354,0,0,12.208311214516016,0,0]
[0,0,1459.3791158110362,0,0,1459.3791158110362,1500.1915210000002,"2013-01-15T21:00:00",36,32,"OFF",-34.610026604159991,-71.741812317122012,-8.8484060000000007,"OFF",-6.4351076522699993,-101.58675011024,-8.8484060000000007,"ON",32637.131931600004,75676.071498292004,1528.0640000000001,"OFF",-4.4038014638100185,-164.80022619768002,-3.9817830000000001,"OFF",3.9880833948300207,-120.37338813006001,-6.1938839999999997,null,0,0,1446.2980011049885,0,0,1446.2980011049885,0,0,1484.2242609501066,0,0,1484.2242609501066,0,0,81.765998895011535,0,0,0,0,43.839739049893524,0,0,80.726724152451268,42.800464307333257,null,null,1500.1915210000002,null,28888.694400000008,9.7103843298555006,5950.0619993338405,69.340144378773275,5881.4372736000005,68.300869636213008,-1.0392747425602664,null,null,null,null,null,null,null,null,null,1446.2980011049885,0,0,13.081114706047629,0,0]
[0,0,1419.0768456300061,0,0,1419.0768456300061,1393.610085,"2013-01-15T22:00:00",33,29,"OFF",-34.528341511160015,-69.505571714585997,-8.8484060000000007,"OFF",-5.526590825745016,-108.5447433969,-8.8484060000000007,"ON",31138.630997249988,76168.959768425993,1420.1,"OFF",-6.4150416188250317,-160.83416440970004,-4.5624589999999996,"OFF",4.7179528092199927,-120.37338813006001,-4.2306439999999998,null,0,0,1407.1527856034677,0,0,1407.1527856034677,0,0,1440.7981536371299,0,0,1440.7981536371299,0,0,12.947214396532218,0,0,0,0,-20.698153637129963,0,0,7.5857934225933974,-26.059574611068783,null,null,1393.610085,null,30551.57130000004,9.5845257524792178,6375.1868561879128,76.047049537678248,6037.7477022000039,70.685628563739428,-5.3614209739388201,null,null,null,null,null,null,null,null,null,1407.1527856034677,0,0,11.924060026538427,0,0]
[0,0,1466.6009518542305,0,0,1466.6009518542305,1629.7106220000003,"2013-01-15T23:00:00",33,29,"OFF",-34.698986645670011,-73.754793005267999,-8.8484060000000007,"OFF",-5.9811036480600226,-108.5447433969,-8.8484060000000007,"ON",32901.213565760001,76083.377469646002,1655.3710000000001,"OFF",-4.23073446676998,-166.99199929652002,-3.9817830000000001,"OFF",3.2909075918399888,-118.98177343106001,-3.9817830000000001,null,0,0,1453.3100956616834,0,0,1453.3100956616834,0,0,1490.994190011658,0,0,1490.994190011658,0,0,202.06090433831673,0,0,0,0,164.37680998834207,0,0,196.6994833643779,159.01538901440324,null,null,1629.7106220000003,null,30551.57130000004,9.5845257524792178,6375.1868561879128,76.047049537678248,6037.7477022000039,70.685628563739428,-5.3614209739388201,null,null,null,null,null,null,null,null,null,1453.3100956616834,0,0,13.290856192547153,0,0]
[0,0,1425.5216235827857,0,0,1425.5216235827857,1258.4915210000001,"2013-01-16",32,28,"OFF",-34.096174669129979,-71.667395019270003,-8.8484060000000007,"OFF",-7.4267258291199987,-105.71154420308001,-8.8484060000000007,"ON",31381.158232620011,76072.677677090003,1286.364,"OFF",-6.3507415033499983,-158.64239131086001,-3.9817830000000001,"OFF",5.0091067975000181,-121.06919547956002,-6.1938839999999997,null,0,0,1413.4141066547504,0,0,1413.4141066547504,0,0,1447.7597143424621,0,0,1447.7597143424621,0,0,-127.05010665475038,0,0,0,0,-161.39571434246204,0,0,-134.524765455281,-168.87037314299266,null,null,1258.4915210000001,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1413.4141066547504,0,0,12.107516928035238,0,0]
[0,0,1409.4416180150326,0,0,1409.4416180150326,1497.5378450000001,"2013-01-16T01:00:00",31,27,"OFF",-34.742294449404994,-71.667395019270003,-8.8484060000000007,"OFF",-5.3257212058700123,-107.1531286979,-8.8484060000000007,"ON",30773.910900749994,71649.47647611401,1525.991,"OFF",-5.4251690150250269,-166.99199929652002,-4.5624589999999996,"OFF",3.4794339468000048,-120.37338813006001,-6.1938839999999997,null,0,0,1397.7906850766376,0,0,1397.7906850766376,0,0,1439.4006256604698,0,0,1439.4006256604698,0,0,128.20031492336238,0,0,0,0,86.590374339530172,0,0,118.20299907809508,76.593058494262863,null,null,1497.5378450000001,null,32487.155900000012,9.5288097691634306,6818.7227338996781,83.537574043904385,6219.6926546000013,73.540258198637076,-9.997315845267309,null,null,null,null,null,null,null,null,null,1397.7906850766376,0,0,11.650932938395044,0,0]
[0,0,1393.262734584529,0,0,1393.262734584529,1371.3780850000001,"2013-01-16T02:00:00",30,27,"OFF",-34.068138237210015,-72.437611645787996,-8.8484060000000007,"OFF",-5.3996603446799858,-110.63216544540002,-8.8484060000000007,"ON",30155.618142499985,76656.369808938005,1397.8679999999999,"OFF",-3.8766164135999897,-166.99199929652002,-4.5624589999999996,"OFF",3.2156745140099905,-120.37338813006001,-4.2306439999999998,null,0,0,1382.067257816833,0,0,1382.067257816833,0,0,1412.8094024196896,0,0,1412.8094024196896,0,0,15.800742183166903,0,0,0,0,-14.941402419689666,0,0,3.6352183539812017,-27.106926248875368,null,null,1371.3780850000001,null,33714.300000000047,9.570639112459844,7045.3602113380284,87.559488649606436,6335.0442000000039,75.393964820420734,-12.165523829185702,null,null,null,null,null,null,null,null,null,1382.067257816833,0,0,11.195476767695936,0,0]
[0,0,1393.4329727708309,0,0,1393.4329727708309,1392.5866220000003,"2013-01-16T03:00:00",30,27,"OFF",-34.528710411579993,-70.275796361938006,-8.8484060000000007,"OFF",-6.5725173288000036,-103.72414195456,-8.8484060000000007,"ON",30162.163027499995,70723.455149146001,1418.2470000000001,"OFF",-3.9989596028899923,-164.80022619768002,-3.9817830000000001,"OFF",3.364896211459997,-120.09939644062001,-3.9817830000000001,null,0,0,1382.2327245598731,0,0,1382.2327245598731,0,0,1424.0856116053044,0,0,1424.0856116053044,0,0,36.014275440126994,0,0,0,0,-5.8386116053043224,0,0,23.848751610941292,-18.004135434490024,null,null,1392.5866220000003,null,33714.300000000047,9.570639112459844,7045.3602113380284,87.559488649606436,6335.0442000000039,75.393964820420734,-12.165523829185702,null,null,null,null,null,null,null,null,null,1382.2327245598731,0,0,11.200248210957852,0,0]
[0,0,1336.4743428777838,0,0,1336.4743428777838,1482.107706,"2013-01-16T04:00:00",29,25,"OFF",-34.715528119889981,-70.897178392752011,-8.8484060000000007,"OFF",-6.1264181063499885,-110.58211544124002,-8.8484060000000007,"ON",27923.433816915,75750.432650306015,1510.3119999999999,"OFF",-4.3313652313399809,-158.64239131086001,-4.5624589999999996,"OFF",4.2142924340999963,-119.25584532884001,-5.9450229999999999,null,0,0,1326.844380759228,0,0,1326.844380759228,0,0,1354.6424066733894,0,0,1354.6424066733894,0,0,183.46761924077191,0,0,0,0,155.66959332661054,0,0,166.98466667653491,139.18664076237354,null,null,1482.107706,null,35119.346100000024,9.4968388006218696,7396.0076268116391,94.041188884295593,6467.118533400002,77.558236320058612,-16.482952564236982,null,null,null,null,null,null,null,null,null,1326.844380759228,0,0,9.6299621185557953,0,0]
[0,0,1412.9380302859272,0,0,1412.9380302859272,1274.0049460000002,"2013-01-16T05:00:00",28,24,"OFF",-34.672286259629985,-72.363194347936002,-8.8484060000000007,"OFF",-5.5705388259850128,-113.00296355912,-8.8484060000000007,"ON",30906.557653619999,71285.48300836001,1300.2460000000001,"OFF",-5.3695079635450238,-160.83416440970004,-4.5624589999999996,"OFF",3.8100990396699896,-117.59015873206,-3.9817830000000001,null,0,0,1401.1881459929436,0,0,1401.1881459929436,0,0,1443.9108993962645,0,0,1443.9108993962645,0,0,-100.94214599294355,0,0,0,0,-143.66489939626445,0,0,-121.50606022369183,-164.22881362701273,null,null,1274.0049460000002,null,36706.044800000032,9.4900773112198635,7735.6682345682184,100.61992068519396,6616.268211200003,80.056006454445679,-20.563914230748281,null,null,null,null,null,null,null,null,null,1401.1881459929436,0,0,11.749884292983552,0,0]
[0,0,1371.6327052754739,0,0,1371.6327052754739,1490.1820850000001,"2013-01-16T06:00:00",27,24,"OFF",-35.361638888849996,-70.971595690604005,-8.8484060000000007,"OFF",-5.7965563359000152,-103.80828050322,-8.8484060000000007,"ON",29317.095995954991,72433.817791306006,1516.672,"OFF",-3.1808438714500338,-158.64239131086001,-4.5624589999999996,"OFF",5.1731473820250011,-114.80700954240001,-4.2306439999999998,null,0,0,1361.039754440158,0,0,1361.039754440158,0,0,1397.4159318850784,0,0,1397.4159318850784,0,0,155.63224555984198,0,0,0,0,119.25606811492162,0,0,131.41228382032094,95.036106375400578,null,null,1490.1820850000001,null,38478.146700000041,9.5504824899852014,8057.8435153090704,107.1329179100268,6782.8457898000033,82.912956170505765,-24.21996173952104,null,null,null,null,null,null,null,null,null,1361.039754440158,0,0,10.592950835315833,0,0]
[0,0,1384.7537700813507,0,0,1384.7537700813507,1343.8518450000001,"2013-01-16T07:00:00",28,24,"OFF",-34.558248795209991,-72.363194347936002,-8.8484060000000007,"OFF",-6.4802478667499956,-105.11575665356001,-8.8484060000000007,"ON",29827.409733649987,76618.262826604012,1372.3050000000001,"OFF",-4.2411427286199883,-164.80022619768002,-4.5624589999999996,"OFF",3.1892264009199813,-115.50281689190001,-6.1938839999999997,null,0,0,1373.7962051895086,0,0,1373.7962051895086,0,0,1403.9487140370279,0,0,1403.9487140370279,0,0,-1.4912051895084915,0,0,0,0,-31.643714037027848,0,0,-22.055119420256773,-52.20762826777613,null,null,1343.8518450000001,null,36706.044800000032,9.4900773112198635,7735.6682345682184,100.61992068519396,6616.268211200003,80.056006454445679,-20.563914230748281,null,null,null,null,null,null,null,null,null,1373.7962051895086,0,0,10.957564891842139,0,0]
[0,0,1371.8143643361907,0,0,1371.8143643361907,1380.0750850000002,"2013-01-16T08:00:00",28,24,"OFF",-34.643543842319986,-69.579997033272008,-8.8484060000000007,"OFF",-5.7768642316800047,-111.32797279490001,-8.8484060000000007,"ON",29324.196606849986,71016.472256834008,1406.5650000000001,"OFF",-4.001647305950021,-160.83416440970004,-4.5624589999999996,"OFF",3.919268739294993,-120.37338813006001,-4.2306439999999998,null,0,0,1361.2163844055067,0,0,1361.2163844055067,0,0,1400.2550833304842,0,0,1400.2550833304842,0,0,45.348615594493367,0,0,0,0,6.3099166695158146,0,0,24.784701363745086,-14.253997561232467,null,null,1380.0750850000002,null,36706.044800000032,9.4900773112198635,7735.6682345682184,100.61992068519396,6616.268211200003,80.056006454445679,-20.563914230748281,null,null,null,null,null,null,null,null,null,1361.2163844055067,0,0,10.597979930684005,0,0]
[0,0,1370.8757305121344,0,0,1370.8757305121344,1492.5738450000001,"2013-01-16T09:00:00",32,27,"OFF",-34.863698342969975,-68.958615002458004,-8.8484060000000007,"OFF",-5.8916782285899885,-106.40735155258001,-8.8484060000000007,"ON",29287.496882599989,77909.849704790002,1521.027,"OFF",-5.5623871701750316,-166.99199929652002,-4.5624589999999996,"OFF",5.4014433722199984,-117.59015873206,-6.1938839999999997,null,0,0,1360.3037301820023,0,0,1360.3037301820023,0,0,1387.3260780600667,0,0,1387.3260780600667,0,0,160.72326981799779,0,0,0,0,133.70092193993332,0,0,152.53578582852305,125.51343795045857,null,null,1492.5738450000001,null,31434.163200000039,9.4929166795605724,6622.6565050721856,80.164261355743918,6120.7113408000041,71.976777366269161,-8.1874839894747566,null,null,null,null,null,null,null,null,null,1360.3037301820023,0,0,10.572000330132141,0,0]
[0,0,1421.5424585336018,0,0,1421.5424585336018,1262.4608450000001,"2013-01-16T10:00:00",36,29,"OFF",-34.43495700484003,-70.897178392752011,-8.8484060000000007,"OFF",-5.9232453298200198,-107.8489360474,-8.8484060000000007,"ON",31231.549745834996,71775.251174068006,1290.914,"OFF",-4.5389715251999894,-166.99199929652002,-4.5624589999999996,"OFF",4.8093537522100167,-120.37338813006001,-6.1938839999999997,null,0,0,1409.5482846354791,0,0,1409.5482846354791,0,0,1452.1200998843706,0,0,1452.1200998843706,0,0,-118.63428463547916,0,0,0,0,-161.20609988437059,0,0,-121.42658523214193,-163.99840048103334,null,null,1262.4608450000001,null,28888.694400000008,9.52784369801652,6064.0571603864519,71.093170232875778,5881.4372736000005,68.300869636213008,-2.7923005966627699,null,null,null,null,null,null,null,null,null,1409.5482846354791,0,0,11.994173898122654,0,0]
[0,0,1509.0776563188886,0,0,1509.0776563188886,1649.495097,"2013-01-16T11:00:00",40,31,"OFF",-34.617799863010021,-72.363194347936002,-8.8484060000000007,"OFF",-6.7557703568999905,-102.28255745974,-8.8484060000000007,"ON",34428.737060840002,70668.400144569998,1678.999,"OFF",-2.9728367346299889,-158.64239131086001,-5.6132070000000001,"OFF",3.9169631112849888,-119.67758078056001,-6.1938839999999997,null,0,0,1494.5391269243421,0,0,1494.5391269243421,0,0,1549.0354187364346,0,0,1549.0354187364346,0,0,184.45987307565792,0,0,0,0,129.9635812635654,0,0,182.9321645190895,128.43587270699697,null,null,1649.495097,null,28829.600000000006,9.6475231170593378,5976.5806518818808,69.744980849214528,5875.8824000000004,68.217272292646101,-1.5277085565684274,null,null,null,null,null,null,null,null,null,1494.5391269243421,0,0,14.538529394546458,0,0]
[0,0,1540.2629767444914,0,0,1540.2629767444914,1490.6656220000002,"2013-01-16T12:00:00",43,33,"OFF",-35.415954961900013,-70.971595690604005,-8.8484060000000007,"OFF",-6.0719673826949858,-105.81156400306001,-8.8484060000000007,"ON",35523.601236264978,76948.071499850004,1516.326,"OFF",-3.0437710153899999,-164.80022619768002,-3.9817830000000001,"OFF",4.7944952617100061,-118.98177343106001,-3.9817830000000001,null,0,0,1524.7938464057524,0,0,1524.7938464057524,0,0,1566.5935953071835,0,0,1566.5935953071835,0,0,-8.4678464057524252,0,0,0,0,-50.267595307183456,0,0,-10.883553491855594,-52.683302393286624,null,null,1490.6656220000002,null,30272.564300000085,9.8184028222084656,6166.4946627624395,72.696840225123395,6011.521044200008,70.281133139020227,-2.4157070861031684,null,null,null,null,null,null,null,null,null,1524.7938464057524,0,0,15.469130338738978,0,0]
[0,0,1600.2404114870496,0,0,1600.2404114870496,1739.3896220000001,"2013-01-16T13:00:00",45,35,"OFF",-34.698720805139978,-71.667395019270003,-8.8484060000000007,"OFF",-5.6876491999400089,-107.1531286979,-8.8484060000000007,"ON",37570.894638025005,72497.214463241995,1765.05,"OFF",-2.6387974043200062,-166.99199929652002,-3.9817830000000001,"OFF",3.8721650771299929,-116.89443159090001,-3.9817830000000001,null,0,0,1582.949182540618,0,0,1582.949182540618,0,0,1642.18244486138,0,0,1642.18244486138,0,0,182.10081745938191,0,0,0,0,122.86755513861999,0,0,178.61364412639276,119.38038180563083,null,null,1739.3896220000001,null,31886.51250000007,9.9951108112985398,6380.4220087195717,76.132524811971962,6163.2321750000065,72.645351478982803,-3.4871733329891583,null,null,null,null,null,null,null,null,null,1582.949182540618,0,0,17.291228946431602,0,0]
[0,0,1577.8128133892055,0,0,1577.8128133892055,1633.6097610000002,"2013-01-16T14:00:00",47,36,"OFF",-34.059161359080015,-71.667395019270003,-8.8484060000000007,"OFF",-6.6698562524750216,-110.40469459316,-8.8484060000000007,"ON",36813.981551849982,77748.598858054014,1659.519,"OFF",-3.1871415286199736,-166.99199929652002,-3.9817830000000001,"OFF",4.277782529800005,-118.28596608156001,-4.2306439999999998,null,0,0,1561.2077294702424,0,0,1561.2077294702424,0,0,1604.0694332063676,0,0,1604.0694332063676,0,0,98.311270529757621,0,0,0,0,55.449566793632357,0,0,92.436204435202825,49.574500699077561,null,null,1633.6097610000002,null,33987.03270000004,10.127557576926154,6711.7925406681416,81.685643659479695,6360.681073800004,75.810577564924898,-5.8750660945547963,null,null,null,null,null,null,null,null,null,1561.2077294702424,0,0,16.605083918963146,0,0]
[0,0,1660.8392526648486,0,0,1660.8392526648486,1609.3315210000001,"2013-01-16T15:00:00",48,37,"OFF",-34.114503493889991,-70.971595690604005,-8.8484060000000007,"OFF",-6.440452980089999,-120.13332456844002,-8.8484060000000007,"ON",39567.805876349994,72895.914079713999,1637.204,"OFF",-5.8999720629750261,-158.64239131086001,-3.9817830000000001,"OFF",2.618999988360001,-119.67758078056001,-6.1938839999999997,null,0,0,1641.6670589750124,0,0,1641.6670589750124,0,0,1706.0430878331847,0,0,1706.0430878331847,0,0,-4.4630589750124727,0,0,0,0,-68.839087833184749,0,0,-11.439914843699881,-75.815943701872158,null,null,1609.3315210000001,null,35210.380800000043,10.230104404232804,6883.6796593065865,84.676858434497603,6475.6757952000044,77.700002565810195,-6.9768558686874087,null,null,null,null,null,null,null,null,null,1641.6670589750124,0,0,19.172193689836149,0,0]
[0,0,1633.8825489735286,0,0,1633.8825489735286,1925.7036220000002,"2013-01-16T16:00:00",49,37,"OFF",-33.955684066169972,-71.667395019270003,-8.8484060000000007,"OFF",-7.0874530244649936,-107.71490791126001,-8.8484060000000007,"ON",38687.935569100009,75529.691277792008,1951.364,"OFF",-4.1844111140299924,-166.99199929652002,-3.9817830000000001,"OFF",4.7668584693799811,-116.19862424140001,-3.9817830000000001,null,0,0,1615.5518200476863,0,0,1615.5518200476863,0,0,1669.146655441632,0,0,1669.146655441632,0,0,335.81217995231373,0,0,0,0,282.21734455836804,0,0,326.82868494587473,273.23384955192904,null,null,1925.7036220000002,null,36544.120100000058,10.27556723051997,7112.8180625315881,88.781991412064798,6601.047289400005,79.798496405625798,-8.983495006439,null,null,null,null,null,null,null,null,null,1615.5518200476863,0,0,18.330728925842322,0,0]
[0,0,1637.3960471406051,0,0,1637.3960471406051,1563.4716220000003,"2013-01-16T17:00:00",49,37,"OFF",-32.967260333839981,-72.363194347936002,-8.8484060000000007,"OFF",-7.1627801598599863,-129.74709620083999,-8.8484060000000007,"ON",38803.36726776501,78869.269784534001,1589.1320000000001,"OFF",-3.3237137341099987,-158.64239131086001,-3.9817830000000001,"OFF",4.546273564700007,-116.19862424140001,-3.9817830000000001,null,0,0,1618.9560657663028,0,0,1618.9560657663028,0,0,1663.5094301319034,0,0,1663.5094301319034,0,0,-29.824065766302738,0,0,0,0,-74.377430131903338,0,0,-38.807560772741738,-83.360925138342338,null,null,1563.4716220000003,null,36544.120100000058,10.27556723051997,7112.8180625315881,88.781991412064798,6601.047289400005,79.798496405625798,-8.983495006439,null,null,null,null,null,null,null,null,null,1618.9560657663028,0,0,18.439981374302306,0,0]
[0,0,1615.5399435008221,0,0,1615.5399435008221,1781.1156220000003,"2013-01-16T18:00:00",45,34,"OFF",-32.982689022299986,-68.087881284252006,-8.8484060000000007,"OFF",-5.7867980986200109,-101.02505110522002,-8.8484060000000007,"ON",38081.568432810011,72798.853967479998,1806.7760000000001,"OFF",-3.5919833895399997,-164.80022619768002,-3.9817830000000001,"OFF",4.1362216797299807,-118.98177343106001,-3.9817830000000001,null,0,0,1597.7774764959772,0,0,1597.7774764959772,0,0,1657.7068037662061,0,0,1657.7068037662061,0,0,208.99852350402284,0,0,0,0,149.06919623379395,0,0,204.87107102290503,144.94174375267613,null,null,1781.1156220000003,null,31886.51250000007,9.9342639340188796,6419.5017792527015,76.772803960100603,6163.2321750000065,72.645351478982803,-4.1274524811177997,null,null,null,null,null,null,null,null,null,1597.7774764959772,0,0,17.762467004844893,0,0]
[0,0,1573.4077088060355,0,0,1573.4077088060355,1665.4216220000003,"2013-01-16T19:00:00",43,33,"OFF",-32.347217777910004,-73.159502747456003,-8.8484060000000007,"OFF",-6.7223549526000239,-117.08444514836002,-8.8484060000000007,"ON",36664.123370820009,76415.792913942016,1691.0820000000001,"OFF",-2.7347378635500159,-158.64239131086001,-3.9817830000000001,"OFF",3.1851509292399847,-115.50281689190001,-3.9817830000000001,null,0,0,1556.9367313034127,0,0,1556.9367313034127,0,0,1602.7968195495473,0,0,1602.7968195495473,0,0,134.14526869658744,0,0,0,0,88.285180450452799,0,0,131.72956161048427,85.869473364349631,null,null,1665.4216220000003,null,30272.564300000085,9.8184028222084656,6166.4946627624395,72.696840225123395,6011.521044200008,70.281133139020227,-2.4157070861031684,null,null,null,null,null,null,null,null,null,1556.9367313034127,0,0,16.470977502622873,0,0]
[0,0,1598.5680802875418,0,0,1598.5680802875418,1499.9155210000001,"2013-01-16T20:00:00",41,32,"OFF",-31.986617617360018,-69.579997033272008,-8.8484060000000007,"OFF",-6.5617297118999849,-128.20460961430001,-8.8484060000000007,"ON",37514.799192420011,72463.045710402002,1527.788,"OFF",-3.47722900889001,-158.64239131086001,-3.9817830000000001,"OFF",3.1041084767699911,-117.31616704262001,-6.1938839999999997,null,0,0,1581.3282063487,0,0,1581.3282063487,0,0,1640.4869727972844,0,0,1640.4869727972844,0,0,-53.54020634869994,0,0,0,0,-112.69897279728434,0,0,-54.983529110533283,-114.14229555911768,null,null,1499.9155210000001,null,29175.192900000024,9.7201501300662567,6003.0333913785244,70.150604669447091,5908.3681326000024,68.707281907613748,-1.4433227618333433,null,null,null,null,null,null,null,null,null,1581.3282063487,0,0,17.239873938841811,0,0]
[0,0,1535.5143253690098,0,0,1535.5143253690098,1834.1636220000003,"2013-01-16T21:00:00",43,33,"OFF",-32.179603108319988,-71.667395019270003,-8.8484060000000007,"OFF",-6.749104960299996,-125.04985518542001,-8.8484060000000007,"ON",35358.277025774994,78955.373437524002,1859.8240000000001,"OFF",-3.805155132239999,-164.80022619768002,-3.9817830000000001,"OFF",4.5562499797500058,-117.86864208854,-3.9817830000000001,null,0,0,1520.1876669088267,0,0,1520.1876669088267,0,0,1557.0203864772059,0,0,1557.0203864772059,0,0,339.63633309117336,0,0,0,0,302.80361352279419,0,0,337.22062600507019,300.38790643669103,null,null,1834.1636220000003,null,30272.564300000085,9.8184028222084656,6166.4946627624395,72.696840225123395,6011.521044200008,70.281133139020227,-2.4157070861031684,null,null,null,null,null,null,null,null,null,1520.1876669088267,0,0,15.326658460183125,0,0]
[0,0,1860.2078855154919,0,0,1860.2078855154919,2082.9696219999996,"2013-01-16T22:00:00",43,34,"OFF",-32.09301301176,-72.363194347936002,-8.8484060000000007,"OFF",-6.7244219899999988,-136.36436445918002,-8.8484060000000007,"ON",45706.636984549994,75958.132146735996,2108.63,"OFF",-4.5553002091300092,-158.64239131086001,-3.9817830000000001,"OFF",5.9492546905400134,-117.58582748170001,-3.9817830000000001,null,0,0,1834.6018781633245,0,0,1834.6018781633245,0,0,1907.7713953747316,0,0,1907.7713953747316,0,0,274.02812183667561,0,0,0,0,200.85860462526853,0,0,272.21012613994054,199.04060892853346,null,null,2082.9696219999996,null,30272.564300000085,9.8792496994881276,6128.5148611171544,72.09912883575528,6011.521044200008,70.281133139020227,-1.8179956967350535,null,null,null,null,null,null,null,null,null,1834.6018781633245,0,0,25.606007352167353,0,0]
[0,0,1775.8451463346826,0,0,1775.8451463346826,1883.9635210000001,"2013-01-16T23:00:00",43,34,"OFF",-32.134020975180015,-68.884197704605995,-8.8484060000000007,"OFF",-6.8866550692050001,-133.66094235948,-8.8484060000000007,"ON",43182.888292080002,76380.565411014017,1911.836,"OFF",-4.0130568689400103,-160.83416440970004,-3.9817830000000001,"OFF",3.1074622503400002,-119.67758078056001,-6.1938839999999997,null,0,0,1753.0041803466265,0,0,1753.0041803466265,0,0,1816.7531078340476,0,0,1816.7531078340476,0,0,158.83181965337349,0,0,0,0,95.082892165952444,0,0,157.01382395663842,93.264896469217391,null,null,1883.9635210000001,null,30272.564300000085,9.8792496994881276,6128.5148611171544,72.09912883575528,6011.521044200008,70.281133139020227,-1.8179956967350535,null,null,null,null,null,null,null,null,null,1753.0041803466265,0,0,22.840965988056041,0,0]
[0,0,1833.8039056198013,0,0,1833.8039056198013,2016.0536220000001,"2013-01-17",42,34,"OFF",-32.089077098280015,-67.492591026439996,-8.8484060000000007,"OFF",-7.7162315091599778,-125.06653852014001,-8.8484060000000007,"ON",44927.492838615006,73376.017140452008,2041.7139999999999,"OFF",-2.7378735171200002,-158.64239131086001,-3.9817830000000001,"OFF",3.6144339462000219,-118.28596608156001,-3.9817830000000001,null,0,0,1809.0695640271713,0,0,1809.0695640271713,0,0,1890.1450951053098,0,0,1890.1450951053098,0,0,232.64443597282866,0,0,0,0,151.56890489469015,0,0,231.67827966815517,150.60274859001666,null,null,2016.0536220000001,null,29657.431200000021,9.8582818167326369,6016.7545930086799,70.361709865588551,5953.6985328000019,69.395553560915062,-0.96615630467348979,null,null,null,null,null,null,null,null,null,1809.0695640271713,0,0,24.734341592630017,0,0]
[0,0,1692.4659374652722,0,0,{"$f":"SUM(A388:E388)","v":1692.4659374652722},{"$f":"N388+R388+V388+Z388+AD388","v":1927.3486220000002},"2013-01-17T01:00:00",39,33,"OFF",-32.234659548585,-73.754793005267999,-8.8484060000000007,"OFF",-7.2801849386699944,-112.75784687208001,-8.8484060000000007,"ON",40583.69788983,75527.862527639998,1953.009,"OFF",-2.9408741482399914,-164.80022619768002,-3.9817830000000001,"OFF",3.7795330020700009,-118.28596608156001,-3.9817830000000001,null,0,0,1672.2972290586788,0,0,{"$f":"SUM(AF388:AJ388)","v":1672.2972290586788},0,0,1731.2798676410025,0,0,{"$f":"SUM(AL388:AP388)","v":1731.2798676410025},{"$f":"IF($K388=\"ON\",$N388-AF388,0)","v":0},{"$f":"IF($O388=\"ON\",$R388-AG388,0)","v":0},{"$f":"IF($S388=\"ON\",$V388-AH388,0)","v":280.71177094132122},{"$f":"IF($W388=\"ON\",$Z388-AI388,0)","v":0},{"$f":"IF($AA388=\"ON\",$AD388-AJ388,0)","v":0},{"$f":"IF($K388=\"ON\",$N388-AL388,0)","v":0},{"$f":"IF($O388=\"ON\",$R388-AM388,0)","v":0},{"$f":"IF($S388=\"ON\",$V388-AN388,0)","v":221.7291323589975},{"$f":"IF($W388=\"ON\",$Z388-AO388,0)","v":0},{"$f":"IF($AA388=\"ON\",$AD388-AP388,0)","v":0},{"$f":"SUM(AR388:AV388)+BN388","v":280.59584212802537},{"$f":"SUM(AW388:BA388)+BN388","v":221.61320354570165},null,null,{"$f":"N388+R388+V388+Z388+AD388","v":1927.3486220000002},null,28624.403100000054,{"$f":"19.5285952781395+42*-0.3035722016559+BH388*0.0000340867411548605+J388*0.0608468772796604","v":9.7622223780025799},{"$f":"BH388*1000/(500*BI388)","v":5864.3210514237044},{"$f":"0.00000128*BJ388^2+0*BJ388+24.024","v":68.043534584539174},{"$f":"0.094*BH388 + 3165.9","v":5856.5938914000053},{"$f":"0.00000128*BL388^2+0*BL388+24.024","v":67.927605771243336},{"$f":"BM388-BK388","v":-0.11592881329583804},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF388:AJ388)","v":1672.2972290586788},{"$f":"A388-AF388","v":0},{"$f":"B388-AG388","v":0},{"$f":"C388-AH388","v":20.168708406593396},{"$f":"D388-AI388","v":0},{"$f":"E388-AJ388","v":0}]
[0,0,1672.1754452584516,0,0,1672.1754452584516,1615.6911860000002,"2013-01-17T02:00:00",41,33,"OFF",-31.686385375539999,-70.275796361938006,-8.8484060000000007,"OFF",-7.2050365463999935,-133.59356735387999,-8.8484060000000007,"ON",39933.936250829989,77139.079640726006,1639.9690000000001,"OFF",-3.7951684708700122,-158.64239131086001,-2.3503579999999999,"OFF",3.7642924360999892,-117.59015873206,-4.2306439999999998,null,0,0,1652.6471945828669,0,0,1652.6471945828669,0,0,1704.8609634372535,0,0,1704.8609634372535,0,0,-12.678194582866809,0,0,0,0,-64.89196343725348,0,0,-13.549401876872508,-65.76317073125918,null,null,1615.6911860000002,null,{"$f":" -0.6251*I389^3 + 145.21*I389^2 - 8340.3*I389 + 170112","v":29175.192900000024},9.7809970073459169,5965.6889534038901,69.578489201619448,5908.3681326000024,68.707281907613748,-0.87120729400569985,null,null,null,null,null,null,null,null,null,1652.6471945828669,0,0,19.528250675584786,0,0]
[0,0,1660.4889211602094,0,0,1660.4889211602094,1823.3246220000001,"2013-01-17T03:00:00",40,33,"OFF",-32.24422655262002,-68.884197704605995,-8.8484060000000007,"OFF",-6.4528835715600152,-103.67417215874002,-8.8484060000000007,"ON",39556.454927974984,72739.87677507801,1848.9849999999999,"OFF",-4.3890717970399864,-164.80022619768002,-3.9817830000000001,"OFF",4.0644763970299822,-117.59015873206,-3.9817830000000001,null,0,0,1641.3277105564277,0,0,1641.3277105564277,0,0,1706.1784997482093,0,0,1706.1784997482093,0,0,207.65728944357215,0,0,0,0,142.80650025179057,0,0,207.26156580985514,142.41077661807356,null,null,1823.3246220000001,null,28829.600000000006,9.76921687161866,5902.1312309598125,68.612995926363126,5875.8824000000004,68.217272292646101,-0.39572363371702579,null,null,null,null,null,null,null,null,null,1641.3277105564277,0,0,19.161210603781683,0,0]
[0,0,1729.8791820517097,0,0,1729.8791820517097,1763.7367610000001,"2013-01-17T04:00:00",38,32,"OFF",-32.236477979120011,-68.783680612918019,-8.8484060000000007,"OFF",-6.7478868831400112,-118.80435258298002,-8.8484060000000007,"ON",41763.684745010018,74622.19807736401,1789.646,"OFF",-4.4105863823449853,-166.99199929652002,-3.9817830000000001,"OFF",4.8013301673400042,-116.19862424140001,-4.2306439999999998,null,0,0,1708.5192471217722,0,0,1708.5192471217722,0,0,1774.1037233995673,0,0,1774.1037233995673,0,0,81.126752878227762,0,0,0,0,15.542276600432615,0,0,80.541797899882553,14.957321622087406,null,null,1763.7367610000001,null,28563.352800000052,9.6992944949493936,5889.7794710478229,68.426562838497745,5850.8551632000053,67.841607860152536,-0.58495497834520904,null,null,null,null,null,null,null,null,null,1708.5192471217722,0,0,21.359934929937481,0,0]
[0,0,1698.1880202893196,0,0,1698.1880202893196,1657.6106220000001,"2013-01-17T05:00:00",39,33,"OFF",-32.361738174625003,-70.971595690604005,-8.8484060000000007,"OFF",-7.2126368616300027,-116.70939095052,-8.8484060000000007,"ON",40765.668420699985,72998.725129925995,1683.271,"OFF",-4.1622243887699897,-158.64239131086001,-3.9817830000000001,"OFF",5.0862508427000206,-117.59015873206,-3.9817830000000001,null,0,0,1677.8379776727818,0,0,1677.8379776727818,0,0,1745.8193771357837,0,0,1745.8193771357837,0,0,5.4330223272181684,0,0,0,0,-62.548377135783767,0,0,5.3170935139223303,-62.664305949079605,null,null,1657.6106220000001,null,28624.403100000054,9.7622223780025799,5864.3210514237044,68.043534584539174,5856.5938914000053,67.927605771243336,-0.11592881329583804,null,null,null,null,null,null,null,null,null,1677.8379776727818,0,0,20.350042616537849,0,0]
[0,0,1729.619929260753,0,0,1729.619929260753,1973.6637610000002,"2013-01-17T06:00:00",36,31,"OFF",-32.448612693350007,-71.146522059310001,-8.8484060000000007,"OFF",-6.9621548011500041,-106.40735155258001,-8.8484060000000007,"ON",41755.586552605004,76569.480114216014,1999.5730000000001,"OFF",-3.7989628751899809,-166.99199929652002,-3.9817830000000001,"OFF",3.472429229849983,-118.98177343106001,-4.2306439999999998,null,0,0,1708.2682936754641,0,0,1708.2682936754641,0,0,1767.2296849574304,0,0,1767.2296849574304,0,0,291.30470632453603,0,0,0,0,232.34331504256966,0,0,289.69213169953275,230.73074041756638,null,null,1973.6637610000002,null,28888.694400000008,9.6495374525758404,5987.581175155392,69.913444261216284,5881.4372736000005,68.300869636213008,-1.6125746250032762,null,null,null,null,null,null,null,null,null,1708.2682936754641,0,0,21.351635585288932,0,0]
[0,0,1540.9714468148522,0,0,1540.9714468148522,1464.4388630000001,"2013-01-17T07:00:00",36,32,"OFF",-32.684524511939998,-71.667395019270003,-8.8484060000000007,"OFF",-7.1408427223000075,-111.46208113938002,-8.8484060000000007,"ON",35548.224530369997,76136.339036548001,1488.136,"OFF",-4.6626114584700122,-160.83416440970004,-1.7696810000000001,"OFF",3.4833697639499843,-118.98177343106001,-4.2306439999999998,null,0,0,1525.4810373034718,0,0,1525.4810373034718,0,0,1569.2813597975216,0,0,1569.2813597975216,0,0,-37.345037303471827,0,0,0,0,-81.145359797521678,0,0,-38.384312046032093,-82.184634540081944,null,null,1464.4388630000001,null,28888.694400000008,9.7103843298555006,5950.0619993338405,69.340144378773275,5881.4372736000005,68.300869636213008,-1.0392747425602664,null,null,null,null,null,null,null,null,null,1525.4810373034718,0,0,15.490409511380449,0,0]
[0,0,1535.0204116521095,0,0,1535.0204116521095,1744.9884380000001,"2013-01-17T08:00:00",37,34,"OFF",-32.567556728770015,-70.871086619750002,-8.8484060000000007,"OFF",-6.893656286859982,-107.1531286979,-8.8484060000000007,"ON",35341.053146439997,76774.572839596003,1770.317,"OFF",-5.5219720773750307,-166.99199929652002,-3.401106,"OFF",4.9366911439299894,-118.28596608156001,-4.2306439999999998,null,0,0,1519.7085562790387,0,0,1519.7085562790387,0,0,1561.489875129492,0,0,1561.489875129492,0,0,250.6084437209613,0,0,0,0,208.82712487050799,0,0,251.00192779584916,209.22060894539584,null,null,1744.9884380000001,null,28650.199700000056,9.8239485773091175,5832.7259094525198,67.570485164542362,5859.0187718000052,67.963969239430199,0.39348407488783721,null,null,null,null,null,null,null,null,null,1519.7085562790387,0,0,15.311855373070784,0,0]
[0,0,1456.0270011501411,0,0,1456.0270011501411,1341.3220590000001,"2013-01-17T09:00:00",42,37,"OFF",-33.249001438440018,-69.606088806274002,-8.8484060000000007,"OFF",-6.6583289413799784,-136.93344263148003,-8.8484060000000007,"ON",32514.107806129989,76709.082729985996,1368.365,"OFF",-5.6258700687000163,-166.99199929652002,-3.401106,"OFF",2.6426886675000092,-119.67758078056001,-5.9450229999999999,null,0,0,1443.0429978042528,0,0,1443.0429978042528,0,0,1478.5964908989492,0,0,1478.5964908989492,0,0,-74.677997804252755,0,0,0,0,-110.23149089894923,0,0,-73.974643942752294,-109.52813703744877,null,null,1341.3220590000001,null,29657.431200000021,10.040822448571618,5907.3709055016725,68.692199699414601,5953.6985328000019,69.395553560915062,0.7033538615004602,null,null,null,null,null,null,null,null,null,1443.0429978042528,0,0,12.984003345888368,0,0]
[0,0,1495.387774346294,0,0,1495.387774346294,1623.2948070000002,"2013-01-17T10:00:00",48,41,"OFF",-32.616488734479987,-69.55390526027,-8.8484060000000007,"OFF",-6.7401566439899971,-106.32329321226001,-8.8484060000000007,"ON",33941.121903000014,73407.587143076002,1649.287,"OFF",-3.6577267143899732,-158.64239131086001,-2.3503579999999999,"OFF",3.2085901504500098,-119.67758078056001,-5.9450229999999999,null,0,0,1481.2539257290452,0,0,1481.2539257290452,0,0,1527.4638674170728,0,0,1527.4638674170728,0,0,168.03307427095478,0,0,0,0,121.8231325829272,0,0,163.84241877987898,117.63247709185138,null,null,1623.2948070000002,null,35210.380800000043,10.473491913351447,6723.713751115688,81.890658056886011,6475.6757952000044,77.700002565810195,-4.190655491075816,null,null,null,null,null,null,null,null,null,1481.2539257290452,0,0,14.133848617248759,0,0]
[0,0,1586.0764211378664,0,0,1586.0764211378664,1751.8053820000002,"2013-01-17T11:00:00",51,42,"OFF",-32.715406747099991,-69.606088806274002,-8.8484060000000007,"OFF",-7.2985673606999875,-102.97836480924001,-8.8484060000000007,"ON",37094.040980744998,77733.728231818008,1779.4290000000001,"OFF",-4.078589393550029,-166.99199929652002,-3.9817830000000001,"OFF",2.9820141376899985,-118.70778174162001,-5.9450229999999999,null,0,0,1569.2191739529108,0,0,1569.2191739529108,0,0,1612.7700359857729,0,0,1612.7700359857729,0,0,210.20982604708934,0,0,0,0,166.65896401422719,0,0,200.70965796070715,157.15879592784501,null,null,1751.8053820000002,null,39527.769900000014,10.681504515347623,7401.1614830485532,94.138804861646676,6881.5103706000009,84.638636775264473,-9.5001680863822031,null,null,null,null,null,null,null,null,null,1569.2191739529108,0,0,16.857247184955668,0,0]
[0,0,1608.6651436624634,0,0,1608.6651436624634,1531.6866220000002,"2013-01-17T12:00:00",54,44,"OFF",-32.406821545770015,-71.667395019270003,-8.8484060000000007,"OFF",-6.2769696977100109,-102.97836480924001,-8.8484060000000007,"ON",37852.658158524988,78096.149616108014,1557.347,"OFF",-3.4726441036700146,-166.99199929652002,-3.9817830000000001,"OFF",3.0039197979699832,-117.86423062984001,-3.9817830000000001,null,0,0,1591.1147391209188,0,0,1591.1147391209188,0,0,1635.5100727173096,0,0,1635.5100727173096,0,0,-33.767739120918804,0,0,0,0,-78.16307271730966,0,0,-49.204772530685872,-93.600106127076728,null,null,1531.6866220000002,null,44737.413600000087,10.980778046217896,8148.3139740555944,109.00962639333079,7371.2168784000078,93.572592983563723,-15.437033409767068,null,null,null,null,null,null,null,null,null,1591.1147391209188,0,0,17.550404541544594,0,0]
[0,0,1684.8509384262913,0,0,1684.8509384262913,1984.9323820000002,"2013-01-17T13:00:00",57,45,"OFF",-32.396281533770001,-70.971595690604005,-8.8484060000000007,"OFF",-7.0200925984200149,-110.07046644038,-8.8484060000000007,"ON",40340.670599459998,75719.905356102012,2012.556,"OFF",-2.9857218992999974,-158.64239131086001,-3.9817830000000001,"OFF",2.2923626435000108,-116.62035969312001,-5.9450229999999999,null,0,0,1664.9230627375782,0,0,1664.9230627375782,0,0,1722.5938129511032,0,0,1722.5938129511032,0,0,347.63293726242182,0,0,0,0,289.96218704889679,0,0,324.01820219607276,266.34745198254774,null,null,1984.9323820000002,null,50738.045700000075,11.246166916655802,9023.1713749252649,128.23855572642648,7935.2762958000076,104.62382066007743,-23.614735066349056,null,null,null,null,null,null,null,null,null,1664.9230627375782,0,0,19.927875688713129,0,0]
[0,0,1715.2954668674338,0,0,1715.2954668674338,1733.0436220000001,"2013-01-17T14:00:00",59,46,"OFF",-32.214176476440016,-70.971595690604005,-8.8484060000000007,"OFF",-7.2145775337500098,-106.45732134840001,-8.8484060000000007,"ON",41306.455783679987,75504.906900732007,1758.704,"OFF",-4.6588170541500071,-166.99199929652002,-3.9817830000000001,"OFF",4.3872452635199943,-116.47261593084001,-3.9817830000000001,null,0,0,1694.4014315886252,0,0,1694.4014315886252,0,0,1755.5847266900121,0,0,1755.5847266900121,0,0,64.30256841137475,0,0,0,0,3.1192733099878751,0,0,34.954053443603101,-26.229241657783774,null,null,1733.0436220000001,null,55127.89710000006,11.456649522315564,9623.738073268365,142.57290816368015,8347.9223274000051,113.2243931959085,-29.348514967771649,null,null,null,null,null,null,null,null,null,1694.4014315886252,0,0,20.894035278808587,0,0]
[0,0,1696.2937603570922,0,0,1696.2937603570922,1852.4546220000002,"2013-01-17T15:00:00",60,46,"OFF",-32.283319747320014,-73.754793005267999,-8.8484060000000007,"OFF",-7.8020101941149811,-105.76159420724001,-8.8484060000000007,"ON",40705.489201600001,77213.705480262011,1878.115,"OFF",-4.6920707920100018,-164.80022619768002,-3.9817830000000001,"OFF",3.3119150796200119,-116.62035969312001,-3.9817830000000001,null,0,0,1676.0037820008729,0,0,1676.0037820008729,0,0,1730.0265950576993,0,0,1730.0265950576993,0,0,202.11121799912712,0,0,0,0,148.08840494230071,0,0,169.0865099153466,115.0636968585202,null,null,1852.4546220000002,null,57428.400000000081,11.535066169193872,9957.1860547053057,150.93030928386281,8564.1696000000084,117.9056012000823,-33.02470808378051,null,null,null,null,null,null,null,null,null,1676.0037820008729,0,0,20.289978356219308,0,0]
[0,0,1707.5687193704791,0,0,1707.5687193704791,2053.5496219999995,"2013-01-17T16:00:00",60,46,"OFF",-31.34815639045998,-73.058993676602014,-8.8484060000000007,"OFF",-7.5625038748499751,-105.81156400306001,-8.8484060000000007,"ON",41062.803222000002,75561.269301250009,2079.21,"OFF",-4.3216420702700029,-166.99199929652002,-3.9817830000000001,"OFF",3.7951131906799986,-116.47261593084001,-3.9817830000000001,null,0,0,1686.9207254789762,0,0,1686.9207254789762,0,0,1747.1975469824856,0,0,1747.1975469824856,0,0,392.2892745210238,0,0,0,0,332.01245301751442,0,0,359.26456643724327,298.98774493373389,null,null,2053.5496219999995,null,57428.400000000081,11.535066169193872,9957.1860547053057,150.93030928386281,8564.1696000000084,117.9056012000823,-33.02470808378051,null,null,null,null,null,null,null,null,null,1686.9207254789762,0,0,20.647993891502892,0,0]
[0,0,1685.2649255363087,0,0,1685.2649255363087,1684.7910470000002,"2013-01-17T17:00:00",58,45,"OFF",-30.76653038697,-71.046012988456013,-8.8484060000000007,"OFF",-7.8325696414750086,-109.75227995560002,-8.8484060000000007,"ON",40353.908091975005,78932.16114392801,1708.82,"OFF",-4.0914482081899921,-160.83416440970004,-2.3503579999999999,"OFF",2.5816839507900111,-114.80700954240001,-3.9817830000000001,null,0,0,1665.3239714703318,0,0,1665.3239714703318,0,0,1713.3255353863635,0,0,1713.3255353863635,0,0,43.496028529668138,0,0,0,0,-4.5055353863635901,0,0,16.467843001661038,-31.53372091437069,null,null,1684.7910470000002,null,52896.528800000029,11.319742571372641,9345.8890017117683,135.82642077736574,8138.1737072000033,108.79823524935864,-27.0281855280071,null,null,null,null,null,null,null,null,null,1665.3239714703318,0,0,19.940954065976939,0,0]
[0,0,1701.6016936712124,0,0,1701.6016936712124,1895.4396220000001,"2013-01-17T18:00:00",53,43,"OFF",-30.118268740210002,-72.363194347936002,-8.8484060000000007,"OFF",-7.6405373895399791,-105.19989520222002,-8.8484060000000007,"ON",40873.966546390002,72327.100594936011,1921.1,"OFF",-3.7347478520800061,-166.99199929652002,-3.9817830000000001,"OFF",2.4526718558000002,-116.89443159090001,-3.9817830000000001,null,0,0,1681.1433220169761,0,0,1681.1433220169761,0,0,1751.8498228846859,0,0,1751.8498228846859,0,0,239.95667798302384,0,0,0,0,169.25017711531405,0,0,226.33660652762921,155.63010565991942,null,null,1895.4396220000001,null,42907.977300000086,10.85757164732083,7903.788930665336,103.9854457094501,7199.249866200008,90.365374254055467,-13.620071455394637,null,null,null,null,null,null,null,null,null,1681.1433220169761,0,0,20.458371654236316,0,0]
[0,0,1684.059568923951,0,0,1684.059568923951,1851.8465210000002,"2013-01-17T19:00:00",50,41,"OFF",-29.97616302842,-70.897178392752011,-8.8484060000000007,"OFF",-8.0272439315200064,-110.54810710508001,-8.8484060000000007,"ON",40315.357914660002,76005.094129806006,1879.7190000000001,"OFF",-4.8619494354200024,-164.80022619768002,-3.9817830000000001,"OFF",3.1270754578000113,-117.31616704262001,-6.1938839999999997,null,0,0,1664.1566889689618,0,0,1664.1566889689618,0,0,1720.8611324742349,0,0,1720.8611324742349,0,0,215.56231103103823,0,0,0,0,158.85786752576519,0,0,207.50391549595449,150.79947199068144,null,null,1851.8465210000002,null,37984.500000000058,10.568052596454578,7188.5524136666936,90.168365829162568,6736.4430000000057,82.109970294078821,-8.0583955350837471,null,null,null,null,null,null,null,null,null,1664.1566889689618,0,0,19.902879954989203,0,0]
[0,0,1706.120524116697,0,0,1706.120524116697,1650.6426220000003,"2013-01-17T20:00:00",48,40,"OFF",-29.804703383209983,-72.363194347936002,-8.8484060000000007,"OFF",-7.7483244848999808,-104.50408785272002,-8.8484060000000007,"ON",41017.026892560003,75385.396474132009,1676.3030000000001,"OFF",-4.2773740198699937,-166.99199929652002,-3.9817830000000001,"OFF",2.2548396126199721,-119.95165267834001,-3.9817830000000001,null,0,0,1685.5185824118139,0,0,1685.5185824118139,0,0,1746.2374416696221,0,0,1746.2374416696221,0,0,-9.2155824118137843,0,0,0,0,-69.934441669621947,0,0,-14.084508030386615,-74.803367288194778,null,null,1650.6426220000003,null,35210.380800000043,10.412645036071787,6763.0041508230079,82.568928184383026,6475.6757952000044,77.700002565810195,-4.8689256185728311,null,null,null,null,null,null,null,null,null,1685.5185824118139,0,0,20.601941704883075,0,0]
[0,0,1605.1569866607936,0,0,1605.1569866607936,1943.0406220000002,"2013-01-17T21:00:00",47,40,"OFF",-30.250314058859992,-71.667395019270003,-8.8484060000000007,"OFF",-7.9275205200450136,-109.75227995560002,-8.8484060000000007,"ON",37735.49610923999,76236.02196150001,1968.701,"OFF",-4.6469068405900078,-166.99199929652002,-3.9817830000000001,"OFF",2.1315141414699807,-114.11120219290001,-3.9817830000000001,null,0,0,1587.7145995601311,0,0,1587.7145995601311,0,0,1636.77036586033,0,0,1636.77036586033,0,0,380.98640043986893,0,0,0,0,331.93063413967002,0,0,377.7860078355003,328.73024153530139,null,null,1943.0406220000002,null,33987.03270000004,10.370945086044795,6554.2787890629543,79.0109701692935,6360.681073800004,75.810577564924898,-3.2003926043686022,null,null,null,null,null,null,null,null,null,1587.7145995601311,0,0,17.442387100662472,0,0]
[0,0,1657.1315446798055,0,0,1657.1315446798055,1609.3592990000002,"2013-01-17T22:00:00",46,39,"OFF",-29.984147087509989,-73.058993676602014,-8.8484060000000007,"OFF",-7.6918094016499916,-103.85825029904001,-8.8484060000000007,"ON",39447.563237000009,77490.536544938004,1634.4390000000001,"OFF",-4.7935974575999873,-164.80022619768002,-3.401106,"OFF",2.7836320630999825,-115.50281689190001,-3.9817830000000001,null,0,0,1638.0755271360117,0,0,1638.0755271360117,0,0,1688.0104599414888,0,0,1688.0104599414888,0,0,-3.6365271360116367,0,0,0,0,-53.571459941488683,0,0,-5.9833655152393419,-55.918298320716389,null,null,1609.3592990000002,null,32877.826400000049,10.272288980729696,6401.2658642445167,76.473541970869888,6256.415681600005,74.126703591642183,-2.3468383792277052,null,null,null,null,null,null,null,null,null,1638.0755271360117,0,0,19.056017543793814,0,0]
[0,0,1588.4247567184395,0,0,1588.4247567184395,1625.8396220000002,"2013-01-17T23:00:00",42,37,"OFF",-30.038811897329996,-72.363194347936002,-8.8484060000000007,"OFF",-7.3216777526400101,-102.92831480508001,-8.8484060000000007,"ON",37173.377065439992,71895.266913210013,1651.5,"OFF",-5.0852659396700011,-160.83416440970004,-3.9817830000000001,"OFF",4.1760848870999947,-116.19862424140001,-3.9817830000000001,null,0,0,1571.4957106954005,0,0,1571.4957106954005,0,0,1631.2600120317743,0,0,1631.2600120317743,0,0,80.004289304599524,0,0,0,0,20.239987968225705,0,0,80.707643166099984,20.943341829726165,null,null,1625.8396220000002,null,29657.431200000021,10.040822448571618,5907.3709055016725,68.692199699414601,5953.6985328000019,69.395553560915062,0.7033538615004602,null,null,null,null,null,null,null,null,null,1571.4957106954005,0,0,16.929046023039064,0,0]
[0,0,1558.6169512525803,0,0,1558.6169512525803,1751.5273820000002,"2013-01-18",40,36,"OFF",-30.262630513980007,-73.058993676602014,-8.8484060000000007,"OFF",-7.7984185230000183,-105.76159420724001,-8.8484060000000007,"ON",36158.027555285007,77589.433428157994,1779.1510000000001,"OFF",-4.4807962514700055,-164.80022619768002,-3.9817830000000001,"OFF",2.189801877059991,-114.80700954240001,-5.9450229999999999,null,0,0,1542.5946298936171,0,0,1542.5946298936171,0,0,1584.333048555784,0,0,1584.333048555784,0,0,236.55637010638293,0,0,0,0,194.81795144421608,0,0,237.78139651344117,196.04297785127432,null,null,1751.5273820000002,null,28829.600000000006,9.9517575034576407,5793.8710805570663,66.992245885587849,5875.8824000000004,68.217272292646101,1.2250264070582517,null,null,null,null,null,null,null,null,null,1542.5946298936171,0,0,16.022321358963154,0,0]
[0,0,1500.7994825793792,0,0,1500.7994825793792,1395.4766220000001,"2013-01-18T01:00:00",41,37,"OFF",-29.690344253010007,-70.971595690604005,-8.8484060000000007,"OFF",-7.4883471349399819,-107.1531286979,-8.8484060000000007,"ON",34134.401638479998,75336.870428431997,1421.1369999999999,"OFF",-6.9143240290500421,-166.99199929652002,-3.9817830000000001,"OFF",2.904452817279993,-118.98177343106001,-3.9817830000000001,null,0,0,1486.5059468488676,0,0,1486.5059468488676,0,0,1528.7217962790269,0,0,1528.7217962790269,0,0,-65.368946848867608,0,0,0,0,-107.58479627902693,0,0,-64.054923679389788,-106.27077310954911,null,null,1395.4766220000001,null,29175.192900000024,10.024384516464558,5820.8447315805197,67.393258738135927,5908.3681326000024,68.707281907613748,1.3140231694778208,null,null,null,null,null,null,null,null,null,1486.5059468488676,0,0,14.293535730511621,0,0]
[0,0,1507.5552908404459,0,0,1507.5552908404459,1726.6146220000003,"2013-01-18T02:00:00",41,37,"OFF",-30.076070105340015,-72.363194347936002,-8.8484060000000007,"OFF",-9.052815426480004,-106.32329321226001,-8.8484060000000007,"ON",34374.727370774999,77372.862889324009,1752.2750000000001,"OFF",-4.7814500937700259,-166.99199929652002,-3.9817830000000001,"OFF",2.8109827834499765,-115.50281689190001,-3.9817830000000001,null,0,0,1493.0618812906716,0,0,1493.0618812906716,0,0,1531.2864810187521,0,0,1531.2864810187521,0,0,259.21311870932846,0,0,0,0,220.98851898124803,0,0,260.52714187880628,222.30254215072586,null,null,1726.6146220000003,null,29175.192900000024,10.024384516464558,5820.8447315805197,67.393258738135927,5908.3681326000024,68.707281907613748,1.3140231694778208,null,null,null,null,null,null,null,null,null,1493.0618812906716,0,0,14.493409549774242,0,0]
[0,0,1540.3240331571781,0,0,1540.3240331571781,1464.9917610000002,"2013-01-18T03:00:00",40,37,"OFF",-29.84156707518002,-74.450592333934011,-8.8484060000000007,"OFF",-9.5602217553500104,-135.89418317010001,-8.8484060000000007,"ON",35525.723716789995,76938.951811592007,1490.9010000000001,"OFF",-4.6551543999800051,-166.99199929652002,-3.9817830000000001,"OFF",3.2420377214400027,-116.19862424140001,-4.2306439999999998,null,0,0,1524.8530692023614,0,0,1524.8530692023614,0,0,1566.679349474181,0,0,1566.679349474181,0,0,-33.952069202361372,0,0,0,0,-75.778349474180914,0,0,-32.206391156584687,-74.032671428404228,null,null,1464.9917610000002,null,28829.600000000006,10.012604380737301,5758.6615637113737,66.471594246869415,5875.8824000000004,68.217272292646101,1.7456780457766854,null,null,null,null,null,null,null,null,null,1524.8530692023614,0,0,15.470963954816625,0,0]
[0,0,1525.8016928212244,0,0,1525.8016928212244,1547.6546220000002,"2013-01-18T04:00:00",37,34,"OFF",-29.971999723680025,-72.437611645787996,-8.8484060000000007,"OFF",-7.7987718237299797,-103.78421800122001,-8.8484060000000007,"ON",35018.589219915004,73799.236446462004,1573.3150000000001,"OFF",-4.7030851045500155,-158.64239131086001,-3.9817830000000001,"OFF",2.1013301793399921,-115.92455234362001,-3.9817830000000001,null,0,0,1510.7655877513264,0,0,1510.7655877513264,0,0,1558.9447413541182,0,0,1558.9447413541182,0,0,62.549412248673661,0,0,0,0,14.370258645881904,0,0,62.942896323561499,14.763742720769741,null,null,1547.6546220000002,null,28650.199700000056,9.8239485773091175,5832.7259094525198,67.570485164542362,5859.0187718000052,67.963969239430199,0.39348407488783721,null,null,null,null,null,null,null,null,null,1510.7655877513264,0,0,15.036105069897985,0,0]
[0,0,1516.9182862501964,0,0,1516.9182862501964,1668.9067610000002,"2013-01-18T05:00:00",38,35,"OFF",-30.592305779909996,-70.897178392752011,-8.8484060000000007,"OFF",-8.6307927487249962,-110.96134047276,-8.8484060000000007,"ON",34706.062412140003,75891.599328705997,1694.816,"OFF",-4.4369498015500177,-158.64239131086001,-3.9817830000000001,"OFF",1.8894905576399881,-116.47261593084001,-4.2306439999999998,null,0,0,1502.146914902492,0,0,1502.146914902492,0,0,1544.4781368923561,0,0,1544.4781368923561,0,0,192.66908509750806,0,0,0,0,150.3378631076439,0,0,193.70941734532602,151.37819535546186,null,null,1668.9067610000002,null,28563.352800000052,9.8818351267883742,5780.9814540557363,66.801275612334564,5850.8551632000053,67.841607860152536,1.0403322478179717,null,null,null,null,null,null,null,null,null,1502.146914902492,0,0,14.771371347704417,0,0]
[0,0,1543.4222237583792,0,0,1543.4222237583792,1407.4906220000003,"2013-01-18T06:00:00",39,35,"OFF",-30.709645799579992,-73.652719871784015,-8.8484060000000007,"OFF",-7.6514612967000035,-143.33823899716003,-8.8484060000000007,"ON",35633.318854100005,73387.759641427998,1433.1510000000001,"OFF",-4.6883027377200044,-158.64239131086001,-3.9817830000000001,"OFF",3.8965330015500053,-115.50281689190001,-3.9817830000000001,null,0,0,1527.8581578878757,0,0,1527.8581578878757,0,0,1578.8033693481241,0,0,1578.8033693481241,0,0,-94.70715788787561,0,0,0,0,-145.65236934812401,0,0,-93.745796188500421,-144.69100764874884,null,null,1407.4906220000003,null,28624.403100000054,9.883916132561902,5792.1177630592929,66.966244071868147,5856.5938914000053,67.927605771243336,0.961361699375189,null,null,null,null,null,null,null,null,null,1527.8581578878757,0,0,15.564065870503555,0,0]
[0,0,1541.4319628023316,2001.3995496407149,0,3542.8315124430464,3889.6334049999996,"2013-01-18T07:00:00",31,29,"OFF",-30.078506544939984,-72.46526748142,-8.8484060000000007,"OFF",-8.7649147086449837,-115.67670857302001,-8.8484060000000007,"ON",35564.224196069998,65710.786815842017,1827.5360000000001,"ON",36015.587151950014,54251.525550884005,2083.7759999999998,"OFF",3.0326179110499831,-117.59015873206,-3.9817830000000001,null,0,0,1525.9277182907335,1984.8812079732691,0,3510.8089262640024,0,0,1599.0924697964074,2111.3430682925873,0,3710.4355380889947,0,0,301.60828170926652,98.894792026730784,0,0,0,228.44353020359267,-27.567068292587464,0,391.9972378725675,192.3706260475754,null,null,3889.6334049999996,null,32487.155900000012,9.650503523722751,6732.738000694053,82.046094062066885,6219.6926546000013,73.540258198637076,-8.5058358634298088,null,null,null,null,null,null,null,null,null,3510.8089262640024,0,0,15.504244511598017,16.518341667445839,0]
[0,0,1519.149604858603,1840.3140893331251,0,3359.4636941917279,3147.2121649999999,"2013-01-18T08:00:00",32,30,"OFF",-31.285694883380007,-70.971595690604005,-8.8484060000000007,"OFF",-7.863739330110004,-107.15609640648,-8.8484060000000007,"ON",34784.729345415013,78613.036221570001,1447.5989999999999,"ON",30508.570259549997,72574.246552978017,1723.2550000000001,"OFF",3.6025437656249997,-115.50281689190001,-5.9450229999999999,null,0,0,1504.3118300193839,1828.3539174645616,0,3332.6657474839458,0,0,1540.7087319000775,1869.1403326583195,0,3409.849064558397,0,0,-56.712830019384,-105.09891746456151,0,0,0,-93.109731900077577,-145.88533265831938,0,-167.90088957949945,-245.0842066539509,null,null,3147.2121649999999,null,31434.163200000039,9.675457311399553,6497.7111031154127,78.065919461823114,6120.7113408000041,71.976777366269161,-6.089142095553953,null,null,null,null,null,null,null,null,null,3332.6657474839458,0,0,14.837774839219037,11.960171868563521,0]
[0,0,1526.6982879094894,1960.321240539188,0,3487.0195284486772,3631.7397610000003,"2013-01-18T09:00:00",41,38,"OFF",-31.36488865950999,-74.450592333934011,-8.8484060000000007,"OFF",-8.2967983769799911,-107.01581201982002,-8.8484060000000007,"ON",35050.034098420001,79728.549751788014,1757.17,"ON",34664.583325710009,72637.266245716004,1896.4880000000001,"OFF",3.0860578589000145,-116.61634927612,-4.2214270000000003,null,0,0,1511.6354094301853,1944.9929633517299,0,3456.6283727819155,0,0,1546.1606884685505,1997.1187255550064,0,3543.2794140235569,0,0,245.53459056981478,-48.504963351729884,0,0,0,211.00931153144961,-100.63072555500639,0,198.86538822734454,112.21434698570286,null,null,3631.7397610000003,null,29175.192900000024,10.08523139374422,5785.7260306584812,66.871520898354106,5908.3681326000024,68.707281907613748,1.8357610092596417,null,null,null,null,null,null,null,null,null,3456.6283727819155,0,0,15.062878479304118,15.32827718745807,0]
[0,0,1441.369064136403,1718.4488942998591,0,3159.8179584362624,3093.1614049999998,"2013-01-18T10:00:00",48,41,"OFF",-31.744338946649979,-73.754793005267999,-8.8484060000000007,"OFF",-8.505796575420014,-104.5058524362,-8.8484060000000007,"ON",31972.769424524999,78329.395468828006,1421.8409999999999,"ON",25903.303353610008,72766.024693918007,1692.999,"OFF",4.0312293419399952,-118.56260464622001,-3.9817830000000001,null,0,0,1428.8078661566819,1709.7131682900779,0,3138.5210344467596,0,0,1460.1387829714481,1739.2042700651507,0,3199.3430530365986,0,0,-6.9668661566820447,-16.714168290077851,0,0,0,-38.297782971448214,-46.205270065150671,0,-27.871689937835711,-88.693708527674701,null,null,3093.1614049999998,null,35210.380800000043,10.473491913351447,6723.713751115688,81.890658056886011,6475.6757952000044,77.700002565810195,-4.190655491075816,null,null,null,null,null,null,null,null,null,3138.5210344467596,0,0,12.561197979721101,8.7357260097812741,0]
[0,0,1383.4469501079004,1826.5262761405975,0,3209.9732262484977,3402.8424049999999,"2013-01-18T11:00:00",53,44,"OFF",-31.474083183830015,-70.971595690604005,-8.8484060000000007,"OFF",-9.4614717088299916,-108.405581927,-8.8484060000000007,"ON",29776.814477520016,78918.581871966016,1578.5,"ON",30008.804109549983,73404.298601136004,1846.021,"OFF",2.3166933859300283,-116.89852221624001,-3.9817830000000001,null,0,0,1372.5258230734644,1814.9416459909244,0,3187.4674690643888,0,0,1398.8218684554263,1852.811012155862,0,3251.6328806112883,0,0,205.97417692653562,31.079354009075587,0,0,0,179.67813154457372,-6.7900121558620867,0,224.32220488626314,160.15679333936356,null,null,3402.8424049999999,null,42907.977300000086,10.91841852460049,7859.7421784708704,103.09670030340355,7199.249866200008,90.365374254055467,-12.731326049348084,null,null,null,null,null,null,null,null,null,3187.4674690643888,0,0,10.92112703443604,11.584630149673103,0]
[0,0,2176.7410284010375,2245.7878042580301,0,4422.5288326590671,4474.9154049999997,"2013-01-18T12:00:00",57,46,"OFF",-31.317669405749999,-72.363194347936002,-8.8484060000000007,"OFF",-9.4712870259200201,-109.93491434578002,-8.8484060000000007,"ON",54399.355303735014,79584.319114800019,2252.0349999999999,"ON",43449.612722999991,72468.676335870012,2244.5590000000002,"OFF",2.0471179154300083,-116.89034096556001,-3.9817830000000001,null,0,0,2140.2990921559704,2221.8675315165428,0,4362.1666236725132,0,0,2224.6572767860052,2303.9724137844632,0,4528.6296905704685,0,0,111.7359078440295,22.691468483457356,0,0,0,27.377723213994614,-59.413413784463046,0,111.93125109245318,-54.531815805502106,null,null,4474.9154049999997,null,50738.045700000075,11.307013793935463,8974.6146285261493,127.1199458951111,7935.2762958000076,104.62382066007743,-22.496125235033674,null,null,null,null,null,null,null,null,null,4362.1666236725132,0,0,36.441936245067154,23.920272741487224,0]
[0,0,1946.6942543082696,1971.540778679562,0,3918.2350329878318,3836.231405,"2013-01-18T13:00:00",59,46,"OFF",-31.162019778540007,-70.971595690604005,-8.8484060000000007,"OFF",-7.5777555065600142,-111.32797279490001,-8.8484060000000007,"ON",48195.082357975014,80930.134851660012,2042.673,"ON",35036.920135359993,72815.665635544006,1815.2370000000001,"OFF",3.1891839480899979,-118.28596608156001,-3.9817830000000001,null,0,0,1918.1956294415706,1955.8892162934517,0,3874.0848457350221,0,0,1978.753306823824,2008.6374978243068,0,3987.3908046481311,0,0,124.47737055842936,-140.6522162934516,0,0,0,63.919693176175997,-193.40049782430674,0,-45.523360702793894,-158.82931961590239,null,null,3836.231405,null,55127.89710000006,11.456649522315564,9623.738073268365,142.57290816368015,8347.9223274000051,113.2243931959085,-29.348514967771649,null,null,null,null,null,null,null,null,null,3874.0848457350221,0,0,28.498624866698947,15.651562386110299,0]
[0,0,1778.8475155987294,1852.5836967953076,0,3631.4312123940372,3593.0445439999999,"2013-01-18T14:00:00",61,47,"OFF",-30.66231780962001,-70.971595690604005,-8.8484060000000007,"OFF",-10.061925987080011,-109.28947783380001,-8.8484060000000007,"ON",43274.463365099997,77638.232182214007,1870.595,"ON",30949.167872385013,73549.636113216009,1744.377,"OFF",3.3102169664199859,-118.28596608156001,-4.2306439999999998,null,0,0,1755.9091657514687,1840.2872275219511,0,3596.1963932734197,0,0,1815.5213603745797,1880.1869749259083,0,3695.7083353004882,0,0,114.68583424853136,-95.910227521951128,0,0,0,55.073639625420356,-135.80997492590836,0,-16.667686483287682,-116.17962851035593,null,null,3593.0445439999999,null,59794.286900000065,11.676558420835505,10241.765551963306,158.2880148753693,8786.5629686000066,122.84472166550138,-35.443293209867917,null,null,null,null,null,null,null,null,null,3596.1963932734197,0,0,22.938349847260724,12.296469273356479,0]
[0,0,1782.8302563020866,1837.4200962610771,0,3620.2503525631637,3703.7937610000004,"2013-01-18T15:00:00",62,47,"OFF",-29.574693971339997,-73.754793005267999,-8.8484060000000007,"OFF",-9.523500749124997,-106.27396508316001,-8.8484060000000007,"ON",43395.733366649998,79016.957400976011,1927.441,"ON",30404.084163099989,73406.857247181993,1798.271,"OFF",3.5355402975000048,-118.2900567069,-4.2214270000000003,null,0,0,1759.7626037836585,1825.5389584761581,0,3585.3015622598168,0,0,1815.0157366126282,1864.3737783105107,0,3679.3895149231389,0,0,167.67839621634153,-27.267958476158128,0,0,0,112.42526338737184,-66.102778310510757,0,101.08246131868904,6.9945086553667295,null,null,3703.7937610000004,null,62221.807200000039,11.759304676949775,10582.565705940982,167.37209205831445,9014.7498768000041,128.0441156368201,-39.327976421494355,null,null,null,null,null,null,null,null,null,3585.3015622598168,0,0,23.067652518428076,11.881137784919019,0]
[0,0,1723.0222585310128,1656.2126624301509,0,3379.2349209611639,3534.501949,"2013-01-18T16:00:00",62,48,"OFF",-29.082791611300006,-73.133410974454009,-8.8484060000000007,"OFF",-9.7262166735800122,-110.07223102386001,-8.8484060000000007,"ON",41549.134380389994,77578.701552266008,1793.701,"ON",23364.413440175002,73098.624617395995,1764.452,"OFF",1.9929905571799911,-118.97768280572001,-5.9542390000000003,null,0,0,1701.8816235349616,1649.0305135777537,0,3350.9121371127153,0,0,1757.005435598554,1672.8653298172603,0,3429.8707654158143,0,0,91.819376465038431,115.42148642224629,0,0,0,36.695564401446063,91.586670182739681,0,169.38492068993727,90.426292386838298,null,null,3534.501949,null,62221.807200000039,11.820151554229435,10528.089578976016,165.90005783416754,9014.7498768000041,128.0441156368201,-37.855942197347446,null,null,null,null,null,null,null,null,null,3350.9121371127153,0,0,21.140634996051176,7.1821488523971766,0]
[0,0,1687.9519222423571,1600.3478082817985,0,3288.2997305241556,3532.4915439999995,"2013-01-18T17:00:00",60,47,"OFF",-29.179027554029989,-70.795105259267999,-8.8484060000000007,"OFF",-8.6664274818799889,-107.15609640648,-8.8484060000000007,"ON",40439.755342749988,78594.259449175996,1800.4159999999999,"ON",20953.732151189997,74016.28021450201,1754.0029999999999,"OFF",2.6681179126699965,-118.98177343106001,-4.2306439999999998,null,0,0,1667.9260421604338,1594.4956786464634,0,3262.4217208068972,0,0,1717.1195831504149,1613.0156620318273,0,3330.1352451822422,0,0,132.48995783956616,159.50732135353655,0,0,0,83.296416849585057,140.9873379681726,0,260.30090002597535,192.58737565063029,null,null,3532.4915439999995,null,57428.400000000081,11.595913046473532,9904.9380190833363,149.60198036720965,8564.1696000000084,117.9056012000823,-31.696379167127347,null,null,null,null,null,null,null,null,null,3262.4217208068972,0,0,20.025880081923333,5.8521296353351318,0]
[0,0,1656.5946850682826,1661.9764616322821,0,3318.5711467005649,3468.9979490000001,"2013-01-18T18:00:00",54,44,"OFF",-28.62361165518001,-70.377869495422004,-8.8484060000000007,"OFF",-8.903828630399989,-106.45732134840001,-8.8484060000000007,"ON",39430.132331655012,76521.708026912005,1754.51,"ON",23605.676975100003,74018.429798014011,1738.1389999999999,"OFF",3.1498301746800248,-120.37338813006001,-5.9542390000000003,null,0,0,1637.5554778432415,1654.6534513735032,0,3292.2089292167448,0,0,1690.2637127118767,1677.8305670557406,0,3368.0942797676171,0,0,116.95452215675846,83.485548626496666,0,0,0,64.246287288123312,60.308432944259266,0,185.00303737348804,109.11768682261551,null,null,3468.9979490000001,null,44737.413600000087,10.980778046217896,8148.3139740555944,109.00962639333079,7371.2168784000078,93.572592983563723,-15.437033409767068,null,null,null,null,null,null,null,null,null,3292.2089292167448,0,0,19.039207225041082,7.3230102587788224,0]
[0,0,1636.9627799470877,1615.4037816115699,0,3252.3665615586578,3299.784165,"2013-01-18T19:00:00",51,43,"OFF",-29.135280407579991,-73.754793005267999,-8.8484060000000007,"OFF",-8.5268135246450072,-108.5447433969,-8.8484060000000007,"ON",38789.145119920009,76975.735356316014,1665.0350000000001,"ON",21616.910090099998,73593.477991860011,1658.3910000000001,"OFF",2.8648018740600163,-116.89587534102002,-5.9450229999999999,null,0,0,1618.5362779719526,1609.1997589574701,0,3227.7360369294229,0,0,1668.2597199866784,1629.2696251212874,0,3297.529345107966,0,0,46.498722028047496,49.19124104253001,0,0,0,-3.2247199866783376,29.121374878712686,0,86.981834690739973,17.188526512196816,null,null,3299.784165,null,39527.769900000014,10.742351392627283,7359.2397893684265,93.346765155102005,6881.5103706000009,84.638636775264473,-8.7081283798375324,null,null,null,null,null,null,null,null,null,3227.7360369294229,0,0,18.426501975135125,6.2040226540998447,0]
[0,0,1552.7620494331627,1645.7845521959564,0,3198.5466016291193,3236.2084049999999,"2013-01-18T20:00:00",49,42,"OFF",-28.992094808039997,-73.058993676602014,-8.8484060000000007,"OFF",-7.8734522831849869,-106.45732134840001,-8.8484060000000007,"ON",35956.426287900009,78782.372068978017,1594.335,"ON",22924.516361949994,73447.009542186017,1663.5519999999999,"OFF",2.6631509315599886,-117.59015873206,-3.9817830000000001,null,0,0,1536.9166271983845,1638.8555946937056,0,3175.7722218920899,0,0,1575.3958527558166,1661.4427716401212,0,3236.8386243959376,0,0,57.418372801615533,24.696405306294309,0,0,0,18.939147244183459,2.1092283598786707,0,76.802114988112237,15.735712484264525,null,null,3236.2084049999999,null,36544.120100000058,10.579801616918271,6908.2807831787659,85.111159525423403,6601.047289400005,79.798496405625798,-5.3126631197976053,null,null,null,null,null,null,null,null,null,3175.7722218920899,0,0,15.845422234778198,6.9289575022507961,0]
[0,0,1547.2252110412956,1486.1290830315359,0,3033.3542940728312,3293.8249489999998,"2013-01-18T21:00:00",52,44,"OFF",-29.195596089729996,-71.667395019270003,-8.8484060000000007,"OFF",-8.9371446783900055,-107.8489360474,-8.8484060000000007,"ON",35765.107206359993,77594.711136930011,1608.3879999999999,"ON",15533.756481180008,73422.233185960009,1709.088,"OFF",3.5151367768299955,-119.67758078056001,-5.9542390000000003,null,0,0,1531.5467073170435,1482.7597905153282,0,3014.3064978323719,0,0,1572.3760716752645,1493.7503519570664,0,3066.1264236323309,0,0,76.841292682956464,226.32820948467179,0,0,0,36.011928324735436,215.33764804293355,0,292.94062784728828,241.12070204732902,null,null,3293.8249489999998,null,41170.179200000071,10.859182650586382,7582.5558008782436,97.617795165993343,7035.8968448000069,87.388920845653359,-10.228874320339983,null,null,null,null,null,null,null,null,null,3014.3064978323719,0,0,15.678503724252096,3.369292516207679,0]
[0,0,1543.0548302231471,1550.9099650666601,0,3093.9647952898072,3417.8254049999996,"2013-01-18T22:00:00",46,40,"OFF",-29.675112216569993,-70.971595690604005,-8.8484060000000007,"OFF",-8.7516778021200015,-106.37037550784001,-8.8484060000000007,"ON",35620.570726174985,77322.748718492003,1692.4369999999999,"ON",18698.256189385003,74112.818972526016,1747.067,"OFF",2.5382031970800121,-119.67758078056001,-3.9817830000000001,null,0,0,1527.5018106770933,1546.1757364634564,0,3073.6775471405499,0,0,1568.6420415323096,1561.0800127499567,0,3129.7220542822661,0,0,164.93518932290658,200.89126353654365,0,0,0,123.79495846769032,185.98698725004328,0,364.09549616473282,308.0509890230162,null,null,3417.8254049999996,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,3073.6775471405499,0,0,15.553019546053747,4.7342286032037464,0]
[0,0,1735.4542233901209,0,0,1735.4542233901209,1985.6690820000001,"2013-01-18T23:00:00",45,40,"OFF",-29.376120145259986,-70.971595690604005,-8.8484060000000007,"OFF",-8.7815461019499885,-108.6317694458,-8.8484060000000007,"ON",41937.571063924981,74113.548868419995,2010.758,"OFF",5.9589275343500097,-158.64239131086001,-3.410323,"OFF",3.0566886656599919,-115.50281689190001,-3.9817830000000001,null,0,0,1713.9156685737294,0,0,1713.9156685737294,0,0,1781.8466692301799,0,0,1781.8466692301799,0,0,296.84233142627068,0,0,0,0,228.9113307698201,0,0,296.38817801812309,228.45717736167251,null,null,1985.6690820000001,null,31886.51250000007,10.299345197696841,6191.9494662885154,73.099504887130408,6163.2321750000065,72.645351478982803,-0.45415340814760441,null,null,null,null,null,null,null,null,null,1713.9156685737294,0,0,21.538554816391525,0,0]
[0,0,1746.2982329092274,0,0,1746.2982329092274,1850.0911630000001,"2013-01-19",45,40,"OFF",-29.860463158904984,-72.363194347936002,-8.8484060000000007,"OFF",-9.9744966294800115,-109.15360490584001,-8.8484060000000007,"ON",42274.38882842999,78366.724430264017,1876.3230000000001,"OFF",4.58530047045,-158.64239131086001,-2.3411409999999999,"OFF",1.5612028232500035,-120.37338813006001,-6.1938839999999997,null,0,0,1724.4114371386083,0,0,1724.4114371386083,0,0,1778.913902969203,0,0,1778.913902969203,0,0,151.91156286139176,0,0,0,0,97.409097030797057,0,0,151.45740945324417,96.954943622649452,null,null,1850.0911630000001,null,31886.51250000007,10.299345197696841,6191.9494662885154,73.099504887130408,6163.2321750000065,72.645351478982803,-0.45415340814760441,null,null,null,null,null,null,null,null,null,1724.4114371386083,0,0,21.886795770619074,0,0]
[0,0,1626.1916949931731,0,0,1626.1916949931731,1695.6576220000002,"2013-01-19T01:00:00",43,39,"OFF",-29.72401959134999,-72.366089869010011,-8.8484060000000007,"OFF",-10.151555591320014,-108.49004130902001,-8.8484060000000007,"ON",38434.461990270007,76921.137539278003,1721.318,"OFF",3.3383380007599976,-166.99199929652002,-3.9817830000000001,"OFF",1.2079750781499905,-119.67902453068001,-3.9817830000000001,null,0,0,1608.0996640203732,0,0,1608.0996640203732,0,0,1657.0705107638446,0,0,1657.0705107638446,0,0,113.21833597962677,0,0,0,0,64.247489236155388,0,0,114.22994706824015,65.259100324768767,null,null,1695.6576220000002,null,30272.564300000085,10.183484085886429,5945.4237949771377,69.269522050406849,6011.521044200008,70.281133139020227,1.0116110886133782,null,null,null,null,null,null,null,null,null,1608.0996640203732,0,0,18.092030972799876,0,0]
[0,0,1636.8321936890284,0,0,1636.8321936890284,1687.7126220000002,"2013-01-19T02:00:00",43,39,"OFF",-30.582685995840013,-69.579997033272008,-8.8484060000000007,"OFF",-10.589908287199981,-104.41601909540002,-8.8484060000000007,"ON",38784.857901600008,74132.229390806009,1713.373,"OFF",2.0647883507999993,-166.99199929652002,-3.9817830000000001,"OFF",1.7130565961599709,-117.59015873206,-3.9817830000000001,null,0,0,1618.4097540083305,0,0,1618.4097540083305,0,0,1676.4410670316413,0,0,1676.4410670316413,0,0,94.96324599166951,0,0,0,0,36.931932968358751,0,0,95.974857080282888,37.943544056972129,null,null,1687.7126220000002,null,30272.564300000085,10.183484085886429,5945.4237949771377,69.269522050406849,6011.521044200008,70.281133139020227,1.0116110886133782,null,null,null,null,null,null,null,null,null,1618.4097540083305,0,0,18.422439680697835,0,0]
[0,0,1563.0722137379576,0,0,1563.0722137379576,1676.3620820000001,"2013-01-19T03:00:00",46,41,"OFF",-30.633728027069999,-73.058993676602014,-8.8484060000000007,"OFF",-10.514729804879979,-108.68069653320001,-8.8484060000000007,"ON",36310.95199862001,77380.747369146004,1701.451,"OFF",1.3021921325700085,-164.83503661724001,-3.410323,"OFF",1.8435559414500118,-117.59015873206,-3.9817830000000001,null,0,0,1546.9150140094773,0,0,1546.9150140094773,0,0,1589.5134612007203,0,0,1589.5134612007203,0,0,154.5359859905227,0,0,0,0,111.93753879927976,0,0,153.41012646732617,110.81167927608324,null,null,1676.3620820000001,null,32877.826400000049,10.393982735289017,6326.3192247520783,75.252563114838708,6256.415681600005,74.126703591642183,-1.1258595231965245,null,null,null,null,null,null,null,null,null,1546.9150140094773,0,0,16.157199728480236,0,0]
[0,0,1600.452962460537,0,0,1600.452962460537,1603.2331660000002,"2013-01-19T04:00:00",44,40,"OFF",-30.663767061270001,-70.275796361938006,-8.8484060000000007,"OFF",-10.006735442384979,-107.80000896,-8.8484060000000007,"ON",37578.020366759985,77079.083802406007,1630.866,"OFF",1.8150722410799898,-160.79935399013999,-3.9817830000000001,"OFF",3.215504702689997,-118.28740983168001,-5.9542390000000003,null,0,0,1583.1552041718105,0,0,1583.1552041718105,0,0,1629.5563419982452,0,0,1629.5563419982452,0,0,47.710795828189475,0,0,0,0,1.3096580017547694,0,0,48.347366092742604,1.946228266307898,null,null,1603.2331660000002,null,31016.841600000043,10.269700950838626,6040.4566303300589,70.727508867709915,6081.4831104000041,71.364079132263043,0.6365702645531286,null,null,null,null,null,null,null,null,null,1583.1552041718105,0,0,17.297758288726527,0,0]
[0,0,1664.8532549942934,0,0,1664.8532549942934,1710.5266220000001,"2013-01-19T05:00:00",43,39,"OFF",-31.534483097029987,-70.971595690604005,-8.8484060000000007,"OFF",-9.0651651879800124,-107.89786313480001,-8.8484060000000007,"ON",39697.706763189999,76514.368963802001,1736.1869999999999,"OFF",0.42310243170999973,-160.79935399013999,-3.9817830000000001,"OFF",2.1086745189300005,-118.28596608156001,-3.9817830000000001,null,0,0,1645.5551324050421,0,0,1645.5551324050421,0,0,1699.0030175532013,0,0,1699.0030175532013,0,0,90.631867594957839,0,0,0,0,37.183982446798609,0,0,91.643478683571217,38.195593535411987,null,null,1710.5266220000001,null,30272.564300000085,10.183484085886429,5945.4237949771377,69.269522050406849,6011.521044200008,70.281133139020227,1.0116110886133782,null,null,null,null,null,null,null,null,null,1645.5551324050421,0,0,19.298122589251307,0,0]
[0,0,1645.8041020676892,0,0,1645.8041020676892,1635.25962,"2013-01-19T06:00:00",41,38,"OFF",-31.480951871609992,-70.275796361938006,-8.8484060000000007,"OFF",-8.9567679983900099,-108.5447433969,-8.8484060000000007,"ON",39078.682859580003,77403.11747517201,1659.519,"OFF",0.27809821662001283,-164.83503661724001,-2.3411409999999999,"OFF",1.3839198051699884,-116.61779302624001,-4.2214270000000003,null,0,0,1627.1021534757169,0,0,1627.1021534757169,0,0,1676.3549805032887,0,0,1676.3549805032887,0,0,32.416846524283073,0,0,0,0,-16.835980503288738,0,0,34.252607533542715,-15.000219494029096,null,null,1635.25962,null,29175.192900000024,10.08523139374422,5785.7260306584812,66.871520898354106,5908.3681326000024,68.707281907613748,1.8357610092596417,null,null,null,null,null,null,null,null,null,1627.1021534757169,0,0,18.701948591972268,0,0]
[0,0,1719.790792612961,0,0,1719.790792612961,1910.7946220000001,"2013-01-19T07:00:00",40,38,"OFF",-31.448365554550016,-71.667395019270003,-8.8484060000000007,"OFF",-10.749088690649987,-111.2790457075,-8.8484060000000007,"ON",41447.760314799991,77256.264025466007,1936.4549999999999,"OFF",-0.33712228382000631,-164.83503661724001,-3.9817830000000001,"OFF",1.8902547085799892,-115.08356789872001,-3.9817830000000001,null,0,0,1698.7533568982512,0,0,1698.7533568982512,0,0,1754.6329477138806,0,0,1754.6329477138806,0,0,237.70164310174869,0,0,0,0,181.82205228611929,0,0,239.95856660073883,184.07897578510944,null,null,1910.7946220000001,null,28829.600000000006,10.073451258016961,5723.8774004204279,65.960348793655953,5875.8824000000004,68.217272292646101,2.2569234989901474,null,null,null,null,null,null,null,null,null,1698.7533568982512,0,0,21.037435714709773,0,0]
[0,0,1618.2280685743565,0,0,1618.2280685743565,1612.3696260000002,"2013-01-19T08:00:00",42,40,"OFF",-31.659060394430014,-69.579997033272008,-8.8484060000000007,"OFF",-9.8746498499099751,-109.2405507464,-8.8484060000000007,"ON",38170.829081294993,76620.444493452,1639.431,"OFF",-0.73142413274000107,-158.64239131086001,-3.410323,"OFF",2.8935848927999825,-118.28596608156001,-5.9542390000000003,null,0,0,1600.382545009945,0,0,1600.382545009945,0,0,1649.5098576753292,0,0,1649.5098576753292,0,0,39.048454990055006,0,0,0,0,-10.078857675329118,0,0,41.332691314054244,-7.7946213513298801,null,null,1612.3696260000002,null,29657.431200000021,10.2233630804106,5801.893362630899,67.111317236915824,5953.6985328000019,69.395553560915062,2.284236323999238,null,null,null,null,null,null,null,null,null,1600.382545009945,0,0,17.845523564411451,0,0]
[0,0,1582.8530699622436,0,0,1582.8530699622436,1678.8636220000001,"2013-01-19T09:00:00",46,43,"OFF",-31.631366512900023,-73.058993676602014,-8.8484060000000007,"OFF",-11.137510920269985,-106.45732134840001,-8.8484060000000007,"ON",36984.963283500001,75931.952144560011,1704.5239999999999,"OFF",-1.7055583918099972,-160.79935399013999,-3.9817830000000001,"OFF",1.0469292406299866,-114.11120219290001,-3.9817830000000001,null,0,0,1566.0942743107662,0,0,1566.0942743107662,0,0,1614.0223438124956,0,0,1614.0223438124956,0,0,138.42972568923369,0,0,0,0,90.501656187504295,0,0,138.48270107063001,90.554631568900618,null,null,1678.8636220000001,null,32877.826400000049,10.515676489848337,6253.1072407447627,74.073728210245861,6256.415681600005,74.126703591642183,5.2975381396322518E-2,null,null,null,null,null,null,null,null,null,1566.0942743107662,0,0,16.758795651477385,0,0]
[0,0,1596.345965032494,0,0,1596.345965032494,1632.5066220000001,"2013-01-19T10:00:00",50,45,"OFF",-32.01166264813002,-73.058993676602014,-8.8484060000000007,"OFF",-10.411891842935024,-102.97836480924001,-8.8484060000000007,"ON",37440.177229349996,75772.995256348018,1658.1669999999999,"OFF",-1.8025792022699938,-166.99199929652002,-3.9817830000000001,"OFF",2.2137028203500062,-116.62188365158002,-3.9817830000000001,null,0,0,1579.1742817713935,0,0,1579.1742817713935,0,0,1628.7144634445233,0,0,1628.7144634445233,0,0,78.992718228606464,0,0,0,0,29.452536555476627,0,0,73.878889726895792,24.338708053765956,null,null,1632.5066220000001,null,37984.500000000058,10.811440105573219,7026.7234760740748,87.223798795789492,6736.4430000000057,82.109970294078821,-5.113828501710671,null,null,null,null,null,null,null,null,null,1579.1742817713935,0,0,17.171683261100497,0,0]
[0,0,1677.2617369125671,0,0,1677.2617369125671,1929.586082,"2013-01-19T11:00:00",56,49,"OFF",-31.652736387229989,-70.173723228454008,-8.8484060000000007,"OFF",-10.082880928590026,-107.1531286979,-8.8484060000000007,"ON",40097.479942469996,75980.237565240008,1954.675,"OFF",-1.6818960648700132,-164.83503661724001,-3.410323,"OFF",3.2139339479799811,-113.68794278272001,-3.9817830000000001,null,0,0,1657.5733179150636,0,0,1657.5733179150636,0,0,1713.7426934184111,0,0,1713.7426934184111,0,0,297.10168208493633,0,0,0,0,240.93230658158882,0,0,280.80975602702711,224.64038052367962,null,null,1929.586082,null,48656.198400000052,11.418591035735398,8522.2770914076118,116.98938473309566,7739.5826496000045,100.69745867518647,-16.291926057909194,null,null,null,null,null,null,null,null,null,1657.5733179150636,0,0,19.688418997503504,0,0]
[0,0,1746.1450006336045,0,0,1746.1450006336045,1869.275981,"2013-01-19T12:00:00",61,51,"OFF",-31.984746765229985,-73.856866138752011,-8.8484060000000007,"OFF",-9.6199660061299976,-106.45732134840001,-8.8484060000000007,"ON",42269.64225102499,75972.513502098009,1896.577,"OFF",-1.8651868735500015,-160.79935399013999,-3.410323,"OFF",4.4106792256800116,-118.9858640564,-6.1938839999999997,null,0,0,1724.2631330930885,0,0,1724.2631330930885,0,0,1786.7262761823815,0,0,1786.7262761823815,0,0,172.31386690691147,0,0,0,0,109.85072381761847,0,0,142.29753862720207,79.83439553790906,null,null,1869.275981,null,59794.286900000065,11.919945929954146,10032.643982006733,152.86104994521079,8786.5629686000066,122.84472166550138,-30.016328279709413,null,null,null,null,null,null,null,null,null,1724.2631330930885,0,0,21.881867540515941,0,0]
[0,0,1732.3610442756415,0,0,1732.3610442756415,1935.4806220000003,"2013-01-19T13:00:00",64,52,"OFF",-31.578086752240001,-71.667395019270003,-8.8484060000000007,"OFF",-8.4999253313450005,-117.97283272220001,-8.8484060000000007,"ON",41841.155510880002,75094.143949924008,1961.1410000000001,"OFF",-2.3960872779899924,-166.99199929652002,-3.9817830000000001,"OFF",2.1174198019100015,-118.28187545622001,-3.9817830000000001,null,0,0,1710.9216274780151,0,0,1710.9216274780151,0,0,1775.1128293523507,0,0,1775.1128293523507,0,0,250.21937252198495,0,0,0,0,186.0281706476494,0,0,210.7517790797759,146.56057720544035,null,null,1935.4806220000003,null,67246.745600000082,12.234822837907998,10992.679908963592,178.6979348235927,9487.0940864000077,139.23034138138365,-39.467593442209051,null,null,null,null,null,null,null,null,null,1710.9216274780151,0,0,21.439416797626336,0,0]
[0,0,1700.304529657664,0,0,1700.304529657664,2057.4146219999993,"2013-01-19T14:00:00",65,52,"OFF",-31.249743548670015,-73.058993676602014,-8.8484060000000007,"OFF",-9.4066347351200008,-131.12347131524001,-8.8484060000000007,"ON",40832.837212089995,66387.80135128001,2083.0749999999998,"OFF",-2.3263650986099917,-166.99199929652002,-3.9817830000000001,"OFF",1.9633584818399969,-116.89443159090001,-3.9817830000000001,null,0,0,1679.8873350885881,0,0,1679.8873350885881,0,0,1773.4202103176176,0,0,1773.4202103176176,0,0,403.18766491141173,0,0,0,0,309.65478968238222,0,0,359.9466845356734,266.41380930664388,null,null,2057.4146219999993,null,69836.662499999977,12.323104664890893,11334.264278216822,188.45989981243125,9730.5462749999988,145.21891943669294,-43.240980375738303,null,null,null,null,null,null,null,null,null,1679.8873350885881,0,0,20.417194569075946,0,0]
[0,0,1828.7931924494123,0,0,1828.7931924494123,1938.9359810000001,"2013-01-19T15:00:00",66,53,"OFF",-31.57929652059001,-73.754793005267999,-8.8484060000000007,"OFF",-10.170383959639976,-106.5932744847,-8.8484060000000007,"ON",44778.554825029998,65420.713354232008,1966.2370000000001,"OFF",-3.4472831222499978,-164.83503661724001,-3.410323,"OFF",2.5994716865599861,-119.67758078056001,-6.1938839999999997,null,0,0,1804.2236371345521,0,0,1804.2236371345521,0,0,1921.830980589393,0,0,1921.830980589393,0,0,162.01336286544802,0,0,0,0,44.406019410607087,0,0,116.62787391996841,-0.97946953487252131,null,null,1938.9359810000001,null,72473.210400000098,12.473822867980248,11620.048026501261,196.85666065689068,9978.3817776000087,151.47117171141107,-45.385488945479608,null,null,null,null,null,null,null,null,null,1804.2236371345521,0,0,24.569555314860281,0,0]
[0,0,1743.7516924216759,0,0,1743.7516924216759,2214.6931659999996,"2013-01-19T16:00:00",65,53,"OFF",-31.295059741709998,-70.971595690604005,-8.8484060000000007,"OFF",-9.7569919001699894,-143.16410669102001,-8.8484060000000007,"ON",42195.45864294999,67088.405159512011,2242.326,"OFF",-2.5003806967299949,-160.79935399013999,-3.9817830000000001,"OFF",2.1918211628000086,-118.98177343106001,-5.9542390000000003,null,0,0,1721.9467706899777,0,0,1721.9467706899777,0,0,1818.7299928883026,0,0,1818.7299928883026,0,0,520.37922931002231,0,0,0,0,423.59600711169742,0,0,478.75014653624476,381.96692433791986,null,null,2214.6931659999996,null,69836.662499999977,12.383951542170553,11278.574897872961,186.8480022104705,9730.5462749999988,145.21891943669294,-41.629082773777554,null,null,null,null,null,null,null,null,null,1721.9467706899777,0,0,21.804921731698187,0,0]
[0,0,1811.8170345451717,0,0,{"$f":"SUM(A452:E452)","v":1811.8170345451717},{"$f":"N452+R452+V452+Z452+AD452","v":2018.8246220000001},"2013-01-19T17:00:00",62,52,"OFF",-30.395629155990004,-72.363194347936002,-8.8484060000000007,"OFF",-10.150268089725019,-123.93608217618001,-8.8484060000000007,"ON",44271.343261779999,67446.840189304014,2044.4849999999999,"OFF",-3.9290452247799781,-160.79935399013999,-3.9817830000000001,"OFF",1.7963065957900017,-116.19862424140001,-3.9817830000000001,null,0,0,1787.8042472662785,0,0,{"$f":"SUM(AF452:AJ452)","v":1787.8042472662785},0,0,1892.6824344597792,0,0,{"$f":"SUM(AL452:AP452)","v":1892.6824344597792},{"$f":"IF($K452=\"ON\",$N452-AF452,0)","v":0},{"$f":"IF($O452=\"ON\",$R452-AG452,0)","v":0},{"$f":"IF($S452=\"ON\",$V452-AH452,0)","v":256.68075273372142},{"$f":"IF($W452=\"ON\",$Z452-AI452,0)","v":0},{"$f":"IF($AA452=\"ON\",$AD452-AJ452,0)","v":0},{"$f":"IF($K452=\"ON\",$N452-AL452,0)","v":0},{"$f":"IF($O452=\"ON\",$R452-AM452,0)","v":0},{"$f":"IF($S452=\"ON\",$V452-AN452,0)","v":151.80256554022071},{"$f":"IF($W452=\"ON\",$Z452-AO452,0)","v":0},{"$f":"IF($AA452=\"ON\",$AD452-AP452,0)","v":0},{"$f":"SUM(AR452:AV452)+BN452","v":224.49189082846806},{"$f":"SUM(AW452:BA452)+BN452","v":119.61370363496735},null,null,{"$f":"N452+R452+V452+Z452+AD452","v":2018.8246220000001},null,62221.807200000039,{"$f":"19.5285952781395+42*-0.3035722016559+BH452*0.0000340867411548605+J452*0.0608468772796604","v":12.063539063348077},{"$f":"BH452*1000/(500*BI452)","v":10315.680477057482},{"$f":"0.00000128*BJ452^2+0*BJ452+24.024","v":160.23297754207346},{"$f":"0.094*BH452 + 3165.9","v":9014.7498768000041},{"$f":"0.00000128*BL452^2+0*BL452+24.024","v":128.0441156368201},{"$f":"BM452-BK452","v":-32.188861905253361},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF452:AJ452)","v":1787.8042472662785},{"$f":"A452-AF452","v":0},{"$f":"B452-AG452","v":0},{"$f":"C452-AH452","v":24.012787278893256},{"$f":"D452-AI452","v":0},{"$f":"E452-AJ452","v":0}]
[0,0,1823.8431237501288,0,0,1823.8431237501288,1999.05762,"2013-01-19T18:00:00",59,51,"OFF",-30.459236601419985,-71.667395019270003,-8.8484060000000007,"OFF",-10.199789650600016,-105.76159420724001,-8.8484060000000007,"ON",44631.075986880001,64641.561518638009,2023.317,"OFF",-1.964579186710002,-160.79935399013999,-2.3411409999999999,"OFF",0.91634433555001349,-119.67758078056001,-4.2214270000000003,null,0,0,1799.4361600092338,0,0,1799.4361600092338,0,0,1920.3681037690633,0,0,1920.3681037690633,0,0,223.88083999076616,0,0,0,0,102.94889623093673,0,0,200.58631936769351,79.654375607864068,null,null,1999.05762,null,{"$f":" -0.6251*I453^3 + 145.21*I453^2 - 8340.3*I453 + 170112","v":55127.89710000006},11.760883908713865,9374.788073395528,136.51891381898116,8347.9223274000051,113.2243931959085,-23.294520623072657,null,null,null,null,null,null,null,null,null,1799.4361600092338,0,0,24.40696374089498,0,0]
[0,0,1734.7266893400345,0,0,1734.7266893400345,1893.6636220000003,"2013-01-19T19:00:00",56,50,"OFF",-29.838771754110013,-72.363194347936002,-8.8484060000000007,"OFF",-10.459081291320009,-107.1042016105,-8.8484060000000007,"ON",41914.907228740005,76599.052929174009,1919.3240000000001,"OFF",-2.7944470315300021,-160.79935399013999,-3.9817830000000001,"OFF",1.4618207482200105,-119.67758078056001,-3.9817830000000001,null,0,0,1713.2114602085467,0,0,1713.2114602085467,0,0,1772.5269243257903,0,0,1772.5269243257903,0,0,206.1125397914534,0,0,0,0,146.79707567420974,0,0,190.80352976559561,131.48806564835195,null,null,1893.6636220000003,null,48656.198400000052,11.479437913015058,8477.1046751052236,116.00646870104427,7739.5826496000045,100.69745867518647,-15.309010025857802,null,null,null,null,null,null,null,null,null,1713.2114602085467,0,0,21.515229131487786,0,0]
[0,0,1724.6730880142236,0,0,1724.6730880142236,1854.4666220000001,"2013-01-19T20:00:00",52,47,"OFF",-29.49472163028998,-70.869522557120007,-8.8484060000000007,"OFF",-10.430102219150001,-107.1531286979,-8.8484060000000007,"ON",41600.857284540005,76119.543410151993,1880.127,"OFF",-3.5387329834999934,-166.99199929652002,-3.9817830000000001,"OFF",1.6215823368849993,-118.98177343106001,-3.9817830000000001,null,0,0,1703.4796952991201,0,0,1703.4796952991201,0,0,1763.4862857360713,0,0,1763.4862857360713,0,0,176.64730470087989,0,0,0,0,116.64071426392866,0,0,168.83160701086447,108.82501657391325,null,null,1854.4666220000001,null,41170.179200000071,11.041723282425362,7457.2017694971364,95.204618535668772,7035.8968448000069,87.388920845653359,-7.815697690015412,null,null,null,null,null,null,null,null,null,1703.4796952991201,0,0,21.193392715103528,0,0]
[0,0,1749.2076629785993,0,0,1749.2076629785993,1822.2772640000001,"2013-01-19T21:00:00",51,47,"OFF",-29.721753488769998,-72.46526748142,-8.8484060000000007,"OFF",-9.3614789119500124,-105.76159420724001,-8.8484060000000007,"ON",42364.442894349988,74301.934196578004,1846.297,"OFF",-2.9080947109199964,-166.99199929652002,-2.3411409999999999,"OFF",4.4401839425299956,-121.06919547956002,-3.9817830000000001,null,0,0,1727.2272547099528,0,0,1727.2272547099528,0,0,1795.8719356117831,0,0,1795.8719356117831,0,0,119.06974529004719,0,0,0,0,50.425064388216924,0,0,113.39926301046539,44.75458210863512,null,null,1822.2772640000001,null,39527.769900000014,10.985738901745924,7196.1968609536143,90.309119054846278,6881.5103706000009,84.638636775264473,-5.6704822795818046,null,null,null,null,null,null,null,null,null,1727.2272547099528,0,0,21.980408268646443,0,0]
[0,0,1674.6218365490838,0,0,1674.6218365490838,1745.9746220000002,"2013-01-19T22:00:00",50,47,"OFF",-29.430629361450006,-73.058993676602014,-8.8484060000000007,"OFF",-9.3074646135000165,-107.1531286979,-8.8484060000000007,"ON",40012.653161240007,77394.454974452005,1771.635,"OFF",-2.8694128668800003,-160.79935399013999,-3.9817830000000001,"OFF",5.1080518640899903,-118.28596608156001,-3.9817830000000001,null,0,0,1655.0165803149873,0,0,1655.0165803149873,0,0,1706.6769735393868,0,0,1706.6769735393868,0,0,116.61841968501267,0,0,0,0,64.958026460613155,0,0,112.90368087981345,61.243287655413937,null,null,1745.9746220000002,null,37984.500000000058,10.933133860132539,6948.5109184494313,85.824709099278039,6736.4430000000057,82.109970294078821,-3.7147388051992181,null,null,null,null,null,null,null,null,null,1655.0165803149873,0,0,19.605256234096487,0,0]
[0,0,1618.5821407763024,0,0,1618.5821407763024,1691.4600820000001,"2013-01-19T23:00:00",49,46,"OFF",-29.718038134539981,-72.363194347936002,-8.8484060000000007,"OFF",-10.677116145885002,-107.1531286979,-8.8484060000000007,"ON",38182.575993484999,77107.573804774001,1716.549,"OFF",-2.696161419629997,-164.83503661724001,-3.410323,"OFF",3.6151131914799963,-119.67758078056001,-3.9817830000000001,null,0,0,1600.7256714945481,0,0,1600.7256714945481,0,0,1648.5498750837196,0,0,1648.5498750837196,0,0,115.82332850545185,0,0,0,0,67.99912491628038,0,0,113.22718087875376,65.402977289582282,null,null,1691.4600820000001,null,36544.120100000058,10.823189126036914,6752.9301529227332,82.394644032323896,6601.047289400005,79.798496405625798,-2.5961476266980981,null,null,null,null,null,null,null,null,null,1600.7256714945481,0,0,17.856469281754244,0,0]
[0,0,1595.1986865074164,0,0,1595.1986865074164,1778.2611629999999,"2013-01-20",48,45,"OFF",-30.046860158909993,-73.652719871784015,-8.8484060000000007,"OFF",-10.345093949105006,-109.80048516794001,-8.8484060000000007,"ON",37401.611834999996,78151.485349873998,1804.4929999999999,"OFF",-3.3520400163600028,-164.83503661724001,-2.3411409999999999,"OFF",3.7794056435799903,-119.67758078056001,-6.1938839999999997,null,0,0,1578.0621888587682,0,0,1578.0621888587682,0,0,1621.2687775229128,0,0,1621.2687775229128,0,0,226.43081114123174,0,0,0,0,183.2242224770871,0,0,224.83869062161148,181.63210195746683,null,null,1778.2611629999999,null,35210.380800000043,10.71687942247009,6571.0137087433131,79.292123085430461,6475.6757952000044,77.700002565810195,-1.5921205196202664,null,null,null,null,null,null,null,null,null,1578.0621888587682,0,0,17.136497648648174,0,0]
[0,0,1625.4802309410734,0,0,1625.4802309410734,1733.8877240000002,"2013-01-20T01:00:00",47,45,"OFF",-30.155712132839998,-72.46526748142,-8.8484060000000007,"OFF",-10.235549677919987,-107.28908183420002,-8.8484060000000007,"ON",38410.957852800013,75901.825892056018,1757.336,"OFF",-3.1204232526599904,-166.99199929652002,-1.7696810000000001,"OFF",3.7203113042199951,-120.37338813006001,-3.9817830000000001,null,0,0,1607.4102500231172,0,0,1607.4102500231172,0,0,1659.1788750816163,0,0,1659.1788750816163,0,0,149.9257499768828,0,0,0,0,98.157124918383715,0,0,149.81486915220253,98.04624409370345,null,null,1733.8877240000002,null,33987.03270000004,10.675179472443098,6367.4868956974724,75.921458389605164,6360.681073800004,75.810577564924898,-0.11088082468026528,null,null,null,null,null,null,null,null,null,1607.4102500231172,0,0,18.069980917956173,0,0]
[0,0,1577.1086806355511,0,0,1577.1086806355511,1727.5346220000001,"2013-01-20T02:00:00",46,44,"OFF",-30.043171154710002,-74.450592333934011,-8.8484060000000007,"OFF",-10.563846208060006,-108.405581927,-8.8484060000000007,"ON",36790.054082154988,75487.028461746013,1753.1949999999999,"OFF",-3.2666395691300063,-166.99199929652002,-3.9817830000000001,"OFF",3.7178490400799977,-118.28596608156001,-3.9817830000000001,null,0,0,1560.525047694995,0,0,1560.525047694995,0,0,1609.1175308241468,0,0,1609.1175308241468,0,0,192.66995230500493,0,0,0,0,144.07746917585314,0,0,193.29714466472373,144.70466153557194,null,null,1727.5346220000001,null,32877.826400000049,10.576523367127997,6217.1330329935945,73.499511231923378,6256.415681600005,74.126703591642183,0.62719235971880494,null,null,null,null,null,null,null,null,null,1560.525047694995,0,0,16.583632940556072,0,0]
[0,0,1659.6413561494992,0,0,1659.6413561494992,1614.4526220000002,"2013-01-20T03:00:00",44,42,"OFF",-29.910380242299993,-73.754793005267999,-8.8484060000000007,"OFF",-9.5816641654800083,-109.10467781844001,-8.8484060000000007,"ON",39528.984302000012,77592.826240940005,1640.1130000000001,"OFF",-3.069673094880002,-166.99199929652002,-3.9817830000000001,"OFF",2.6345801769699997,-118.28596608156001,-3.9817830000000001,null,0,0,1640.5067120811777,0,0,1640.5067120811777,0,0,1690.3531659903472,0,0,1690.3531659903472,0,0,-0.39371208117768219,0,0,0,0,-50.240165990347123,0,0,1.3303436628255412,-48.516110246343899,null,null,1614.4526220000002,null,31016.841600000043,10.391394705397946,5969.7167664871658,69.64002338825982,6081.4831104000041,71.364079132263043,1.7240557440032234,null,null,null,null,null,null,null,null,null,1640.5067120811777,0,0,19.13464406832145,0,0]
[0,0,1600.6363007401433,0,0,1600.6363007401433,1768.846082,"2013-01-20T04:00:00",43,42,"OFF",-31.138660368900016,-73.058993676602014,-8.8484060000000007,"OFF",-9.294541537420022,-107.1531286979,-8.8484060000000007,"ON",37584.166035620008,76937.379728127999,1793.9349999999999,"OFF",-4.0178216517000012,-166.99199929652002,-3.410323,"OFF",1.8548490483600024,-117.59015873206,-3.9817830000000001,null,0,0,1583.3329100956066,0,0,1583.3329100956066,0,0,1630.123537901196,0,0,1630.123537901196,0,0,210.60208990439332,0,0,0,0,163.81146209880399,0,0,213.19317367243767,166.40254586684833,null,null,1768.846082,null,30272.564300000085,10.366024717725409,5840.7277860789663,67.690049370975885,6011.521044200008,70.281133139020227,2.5910837680443422,null,null,null,null,null,null,null,null,null,1583.3329100956066,0,0,17.303390644536648,0,0]
[0,0,1631.5173889981079,0,0,1631.5173889981079,1642.4432680000002,"2013-01-20T05:00:00",41,40,"OFF",-30.807875375340025,-72.956920543118002,-8.8484060000000007,"OFF",-10.090175716160024,-107.28908183420002,-8.8484060000000007,"ON",38610.10241739,76270.976756072007,1667.864,"OFF",-3.6530627590799902,-166.99199929652002,-1.7696810000000001,"OFF",0.90373584503999316,-118.98177343106001,-5.9542390000000003,null,0,0,1613.2601325042831,0,0,1613.2601325042831,0,0,1664.5113137208627,0,0,1664.5113137208627,0,0,54.603867495716941,0,0,0,0,3.3526862791372878,0,0,57.45525105219069,6.2040698356110369,null,null,1642.4432680000002,null,29175.192900000024,10.20692514830354,5716.7447543884728,65.855898351139999,5908.3681326000024,68.707281907613748,2.8513835564737491,null,null,null,null,null,null,null,null,null,1613.2601325042831,0,0,18.257256493824798,0,0]
[0,0,1606.0805361408829,0,0,1606.0805361408829,1765.8286220000002,"2013-01-20T06:00:00",42,41,"OFF",-31.169942610944993,-72.46526748142,-8.8484060000000007,"OFF",-11.331282458670012,-109.10467781844001,-8.8484060000000007,"ON",37766.363041694982,76535.768548913999,1791.489,"OFF",-3.8212813505999881,-160.79935399013999,-3.9817830000000001,"OFF",1.3777641448199953,-115.50281689190001,-3.9817830000000001,null,0,0,1588.6097255421807,0,0,1588.6097255421807,0,0,1636.932659962197,0,0,1636.932659962197,0,0,202.87927445781929,0,0,0,0,154.55634003780301,0,0,205.67185764395884,157.34892322394256,null,null,1765.8286220000002,null,29657.431200000021,10.28420995769026,5767.5662636239704,66.602970374775509,5953.6985328000019,69.395553560915062,2.7925831861395523,null,null,null,null,null,null,null,null,null,1588.6097255421807,0,0,17.470810598702201,0,0]
[0,0,1620.6289648763338,0,0,1620.6289648763338,1657.5089780000003,"2013-01-20T07:00:00",39,38,"OFF",-30.727649944349977,-73.058993676602014,-8.8484060000000007,"OFF",-11.693231649090013,-106.5932744847,-8.8484060000000007,"ON",38250.436041000001,75295.819800020006,1683.4090000000001,"OFF",-3.3862160052700103,-164.83503661724001,-3.9817830000000001,"OFF",1.8082693428499981,-116.89443159090001,-4.2214270000000003,null,0,0,1602.7091943458931,0,0,1602.7091943458931,0,0,1655.76858660996,0,0,1655.76858660996,0,0,80.699805654106967,0,0,0,0,27.640413390040067,0,0,83.204437794103868,30.145045530036967,null,null,1657.5089780000003,null,28624.403100000054,10.066456764400883,5687.086085985623,65.422973631246435,5856.5938914000053,67.927605771243336,2.5046321399969003,null,null,null,null,null,null,null,null,null,1602.7091943458931,0,0,17.919770530440701,0,0]
[0,0,1601.8087425851154,0,0,1601.8087425851154,1618.368264,"2013-01-20T08:00:00",42,41,"OFF",-30.788455403229982,-73.058993676602014,-8.8484060000000007,"OFF",-10.189539832874985,-108.5447433969,-8.8484060000000007,"ON",37623.451832070001,77732.156148354014,1642.3879999999999,"OFF",-3.7398334078699915,-166.99199929652002,-2.3411409999999999,"OFF",2.7541697990799818,-118.28596608156001,-3.9817830000000001,null,0,0,1584.4693245413821,0,0,1584.4693245413821,0,0,1629.2713745573167,0,0,1629.2713745573167,0,0,57.918675458617827,0,0,0,0,13.116625442683244,0,0,60.711258644757379,15.909208628822796,null,null,1618.368264,null,29657.431200000021,10.28420995769026,5767.5662636239704,66.602970374775509,5953.6985328000019,69.395553560915062,2.7925831861395523,null,null,null,null,null,null,null,null,null,1584.4693245413821,0,0,17.339418043733303,0,0]
[0,0,1648.8845548062709,0,0,1648.8845548062709,1791.992082,"2013-01-20T09:00:00",46,44,"OFF",-31.118990179550011,-72.436272166510008,-8.8484060000000007,"OFF",-10.407255826499982,-109.93635809590002,-8.8484060000000007,"ON",39179.227512750018,75374.961369098019,1817.0809999999999,"OFF",-4.7056452657499959,-166.99199929652002,-3.410323,"OFF",8.1509433600021178E-2,-116.89443159090001,-3.9817830000000001,null,0,0,1630.0864478030635,0,0,1630.0864478030635,0,0,1685.5127798122019,0,0,1685.5127798122019,0,0,186.99455219693641,0,0,0,0,131.56822018779803,0,0,187.62174455665522,132.19541254751684,null,null,1791.992082,null,32877.826400000049,10.576523367127997,6217.1330329935945,73.499511231923378,6256.415681600005,74.126703591642183,0.62719235971880494,null,null,null,null,null,null,null,null,null,1630.0864478030635,0,0,18.798107003207406,0,0]
[0,0,1675.5236145365432,0,0,1675.5236145365432,1674.363724,"2013-01-20T10:00:00",50,47,"OFF",-31.741546575600019,-73.681715186694007,-8.8484060000000007,"OFF",-9.9163627113199819,-106.53857239682002,-8.8484060000000007,"ON",40041.643194924996,75674.723998180008,1697.8119999999999,"OFF",-3.9796186808700127,-164.83503661724001,-1.7696810000000001,"OFF",1.9365567411400129,-116.19862424140001,-3.9817830000000001,null,0,0,1655.889957981823,0,0,1655.889957981823,0,0,1712.8483407166855,0,0,1712.8483407166855,0,0,41.922042018176853,0,0,0,0,-15.036340716685572,0,0,38.207303212977635,-18.75107952188479,null,null,1674.363724,null,37984.500000000058,10.933133860132539,6948.5109184494313,85.824709099278039,6736.4430000000057,82.109970294078821,-3.7147388051992181,null,null,null,null,null,null,null,null,null,1655.889957981823,0,0,19.633656554720119,0,0]
[0,0,1715.2488634810222,0,0,1715.2488634810222,1836.3203360000002,"2013-01-20T11:00:00",56,50,"OFF",-31.551558968159991,-70.275796361938006,-8.8484060000000007,"OFF",-10.590042494069994,-109.2405507464,-8.8484060000000007,"ON",41304.989143600003,71979.605982720008,1863.8610000000001,"OFF",-3.9033880440800064,-165.80916690654001,-3.6684019999999999,"OFF",1.3569198052899851,-120.37338813006001,-6.1754499999999997,null,0,0,1694.3563138601749,0,0,1694.3563138601749,0,0,1767.8327216028274,0,0,1767.8327216028274,0,0,169.50468613982525,0,0,0,0,96.028278397172699,0,0,154.19567611396747,80.719268371314897,null,null,1836.3203360000002,null,48656.198400000052,11.479437913015058,8477.1046751052236,116.00646870104427,7739.5826496000045,100.69745867518647,-15.309010025857802,null,null,null,null,null,null,null,null,null,1694.3563138601749,0,0,20.892549620847376,0,0]
[0,0,1679.4809818676974,0,0,1679.4809818676974,1967.6323360000001,"2013-01-20T12:00:00",59,51,"OFF",-30.736245134050012,-73.754793005267999,-8.8484060000000007,"OFF",-10.593622113900025,-107.1531286979,-8.8484060000000007,"ON",40168.696675399995,76623.861368736005,1995.173,"OFF",-3.6677133757599973,-165.80916690654001,-3.6684019999999999,"OFF",-0.46507075264999448,-118.28596608156001,-6.1754499999999997,null,0,0,1659.7225987970412,0,0,1659.7225987970412,0,0,1714.1126248858152,0,0,1714.1126248858152,0,0,335.4504012029588,0,0,0,0,281.06037511418481,0,0,312.15588057988612,257.76585449111212,null,null,1967.6323360000001,null,55127.89710000006,11.760883908713865,9374.788073395528,136.51891381898116,8347.9223274000051,113.2243931959085,-23.294520623072657,null,null,null,null,null,null,null,null,null,1659.7225987970412,0,0,19.758383070656237,0,0]
[0,0,1736.9036302154632,0,0,1736.9036302154632,1779.7886220000003,"2013-01-20T13:00:00",63,53,"OFF",-31.314797252480023,-71.667395019270003,-8.8484060000000007,"OFF",-10.698369145800008,-105.57021710800001,-8.8484060000000007,"ON",41982.697363160012,76055.456946492006,1805.4490000000001,"OFF",-3.346348409880012,-166.99199929652002,-3.9817830000000001,"OFF",-0.98617924090000908,-118.98177343106001,-3.9817830000000001,null,0,0,1715.3185911994644,0,0,1715.3185911994644,0,0,1776.6522961525447,0,0,1776.6522961525447,0,0,90.130408800535633,0,0,0,0,28.796703847455319,0,0,55.795853741682095,-5.5378512113982197,null,null,1779.7886220000003,null,64707.210300000093,12.209105232762928,10599.828417623821,167.84014397832385,9248.3777682000091,133.50558891947031,-34.334555058853539,null,null,null,null,null,null,null,null,null,1715.3185911994644,0,0,21.585039015998746,0,0]
[0,0,1779.5117263421776,0,0,1779.5117263421776,2355.8806219999997,"2013-01-20T14:00:00",66,53,"OFF",-31.151769616870009,-73.058993676602014,-8.8484060000000007,"OFF",-10.113377893275027,-108.73612049614002,-8.8484060000000007,"ON",43294.704237719998,64861.524870254005,2381.5410000000002,"OFF",-4.2223815072599873,-166.99199929652002,-3.9817830000000001,"OFF",0.34297641357000153,-117.59015873206,-3.9817830000000001,null,0,0,1756.5518218722655,0,0,1756.5518218722655,0,0,1869.191635359676,0,0,1869.191635359676,0,0,624.9891781277347,0,0,0,0,512.34936464032421,0,0,579.60368918225504,466.9638756948446,null,null,2355.8806219999997,null,72473.210400000098,12.473822867980248,11620.048026501261,196.85666065689068,9978.3817776000087,151.47117171141107,-45.385488945479608,null,null,null,null,null,null,null,null,null,1756.5518218722655,0,0,22.95990446991209,0,0]
[0,0,2066.6392527826865,0,0,2066.6392527826865,2427.0556219999994,"2013-01-20T15:00:00",69,54,"OFF",-31.446178502059993,-72.363194347936002,-8.8484060000000007,"OFF",-9.4686968379799961,-107.8489360474,-8.8484060000000007,"ON",51499.358131000008,63363.545891580005,2452.7159999999999,"OFF",-6.2268821811400157,-166.99199929652002,-3.9817830000000001,"OFF",0.71151458445001081,-118.98177343106001,-3.9817830000000001,null,0,0,2034.0412692153452,0,0,2034.0412692153452,0,0,2205.041169965049,0,0,2205.041169965049,0,0,418.67473078465468,0,0,0,0,247.6748300349509,0,0,363.70750999399013,192.70760924428637,null,null,2427.0556219999994,null,80625.134100000141,12.812542258335982,12585.345277209843,226.76437215563274,10744.662605400013,171.79715136496822,-54.967220790664527,null,null,null,null,null,null,null,null,null,2034.0412692153452,0,0,32.597983567341316,0,0]
[0,0,2153.5176045977778,0,0,2153.5176045977778,2393.2126219999996,"2013-01-20T16:00:00",69,54,"OFF",-31.256484636090011,-74.450592333934011,-8.8484060000000007,"OFF",-9.2141614842000177,-108.35336629766002,-8.8484060000000007,"ON",53797.496663879981,64703.337982106001,2418.873,"OFF",-4.2145291983200037,-166.99199929652002,-3.9817830000000001,"OFF",0.41650743032499249,-118.28596608156001,-3.9817830000000001,null,0,0,2117.8925186298266,0,0,2117.8925186298266,0,0,2294.1715772085686,0,0,2294.1715772085686,0,0,300.98048137017349,0,0,0,0,124.70142279143147,0,0,246.01326057950897,69.734202000766942,null,null,2393.2126219999996,null,80625.134100000141,12.812542258335982,12585.345277209843,226.76437215563274,10744.662605400013,171.79715136496822,-54.967220790664527,null,null,null,null,null,null,null,null,null,2117.8925186298266,0,0,35.625085967951236,0,0]
[0,0,2251.2192896863025,0,0,2251.2192896863025,2517.6427239999994,"2013-01-20T17:00:00",68,54,"OFF",-31.24958398461002,-73.754793005267999,-8.8484060000000007,"OFF",-8.8068010248000199,-110.82354254464001,-8.8484060000000007,"ON",56296.264526999999,64930.455917650012,2541.0909999999999,"OFF",-4.2349504715700075,-159.82522370084001,-1.7696810000000001,"OFF",0.2536751884999936,-119.67758078056001,-3.9817830000000001,null,0,0,2212.1369587551144,0,0,2212.1369587551144,0,0,2403.6600379419338,0,0,2403.6600379419338,0,0,328.9540412448855,0,0,0,0,137.43096205806614,0,0,277.76353710905528,86.240457922235947,null,null,2517.6427239999994,null,77871.196800000151,12.718669510434168,12245.179692123616,215.95286488626766,10485.792499200013,164.76236075043747,-51.190504135830196,null,null,null,null,null,null,null,null,null,2212.1369587551144,0,0,39.082330931188153,0,0]
[0,0,2215.6717954801734,0,0,2215.6717954801734,2505.9589549999996,"2013-01-20T18:00:00",62,50,"OFF",-31.185199886399996,-72.363194347936002,-8.8484060000000007,"OFF",-9.9221877534399958,-104.36997950824001,-8.8484060000000007,"ON",55397.091448375017,66558.965948840007,2533.8130000000001,"OFF",-5.5545599739700027,-158.64239131086001,-3.9817830000000001,"OFF",0.39714622465000193,-116.89443159090001,-6.1754499999999997,null,0,0,2177.8535654226803,0,0,2177.8535654226803,0,0,2350.107668408762,0,0,2350.107668408762,0,0,355.95943457731983,0,0,0,0,183.70533159123806,0,0,320.98034394822935,148.72624096214761,null,null,2505.9589549999996,null,62221.807200000039,11.941845308788757,10420.802747161209,163.02320626591055,9014.7498768000041,128.0441156368201,-34.97909062909045,null,null,null,null,null,null,null,null,null,2177.8535654226803,0,0,37.818230057493111,0,0]
[0,0,2151.9549249677016,0,0,2151.9549249677016,2414.1530029999999,"2013-01-20T19:00:00",61,49,"OFF",-30.52790233523999,-73.754793005267999,-8.8484060000000007,"OFF",-10.385600328950018,-107.65755894816002,-8.8484060000000007,"ON",53756.815133169992,66879.037329610015,2439.5,"OFF",-3.9728203731299896,-159.82522370084001,-3.6684019999999999,"OFF",-0.65018512540000828,-116.89443159090001,-3.9817830000000001,null,0,0,2116.3846905661862,0,0,2116.3846905661862,0,0,2276.0243516716446,0,0,2276.0243516716446,0,0,323.11530943381376,0,0,0,0,163.47564832835542,0,0,290.42747975796249,130.78781865250414,null,null,2414.1530029999999,null,59794.286900000065,11.798252175394826,10136.126268719809,155.53255134135264,8786.5629686000066,122.84472166550138,-32.687829675851262,null,null,null,null,null,null,null,null,null,2116.3846905661862,0,0,35.570234401515336,0,0]
[0,0,2128.3747169837261,0,0,2128.3747169837261,2337.0299549999995,"2013-01-20T20:00:00",54,46,"OFF",-30.087834455560007,-73.754793005267999,-8.8484060000000007,"OFF",-9.97464496559998,-105.28034416724,-8.8484060000000007,"ON",53140.097349210002,76089.449240984017,2364.884,"OFF",-4.9110658913399963,-165.80916690654001,-3.9817830000000001,"OFF",0.78342452482002323,-118.62813486,-6.1754499999999997,null,0,0,2093.630410346138,0,0,2093.630410346138,0,0,2192.2482428332592,0,0,2192.2482428332592,0,0,271.25358965386204,0,0,0,0,172.63575716674086,0,0,257.66939402866325,159.05156154154207,null,null,2337.0299549999995,null,44737.413600000087,11.102471800777217,8059.0006266655482,107.1567886087625,7371.2168784000078,93.572592983563723,-13.584195625198774,null,null,null,null,null,null,null,null,null,2093.630410346138,0,0,34.744306637588124,0,0]
[0,0,2126.740093299346,0,0,2126.740093299346,2273.9775209999998,"2013-01-20T21:00:00",55,46,"OFF",-30.404456416040002,-73.754793005267999,-8.8484060000000007,"OFF",-10.354997991689999,-107.82575583714001,-8.8484060000000007,"ON",53097.14535518999,75448.793146068012,2301.85,"OFF",-3.6053165047200006,-159.82522370084001,-3.9817830000000001,"OFF",1.6828726340299824,-116.55226281246001,-6.1938839999999997,null,0,0,2092.0529181746238,0,0,2092.0529181746238,0,0,2194.024896713539,0,0,2194.024896713539,0,0,209.79708182537615,0,0,0,0,107.82510328646094,0,0,193.43214218894485,91.460163650029628,null,null,2273.9775209999998,null,46654.737500000047,11.167827124266543,8355.2041020807137,113.38007755190577,7551.4453250000042,97.015137915474455,-16.364939636431316,null,null,null,null,null,null,null,null,null,2092.0529181746238,0,0,34.687175124722216,0,0]
[0,0,2125.6135397626808,0,0,2125.6135397626808,2352.71029,"2013-01-20T22:00:00",51,44,"OFF",-30.255393514769999,-73.754793005267999,-8.8484060000000007,"OFF",-10.911383261194993,-110.63216544540002,-8.8484060000000007,"ON",53067.52837429499,73762.517068410001,2376.1770000000001,"OFF",-5.10877016643001,-166.99199929652002,-1.7696810000000001,"OFF",-1.7033348980900223,-118.28596608156001,-4.0002170000000001,null,0,0,2090.9657292803645,0,0,2090.9657292803645,0,0,2202.3659754104178,0,0,2202.3659754104178,0,0,285.21127071963565,0,0,0,0,173.8110245895823,0,0,277.2818367497099,165.88159061965652,null,null,2352.71029,null,39527.769900000014,10.803198269906943,7317.7903269825847,92.568070745190255,6881.5103706000009,84.638636775264473,-7.9294339699257819,null,null,null,null,null,null,null,null,null,2090.9657292803645,0,0,34.647810482316345,0,0]
[0,0,2058.9237360689599,0,0,2058.9237360689599,2199.1789089999997,"2013-01-20T23:00:00",50,44,"OFF",-30.145400689410007,-71.667395019270003,-8.8484060000000007,"OFF",-9.9929309938400053,-109.93635809590002,-8.8484060000000007,"ON",51291.557554905005,76802.958571122013,2222.9589999999998,"OFF",-5.0851605395500057,-158.64239131086001,-2.083062,"OFF",-0.82830647240001298,-118.28604628990001,-4.0002170000000001,null,0,0,2026.5923156676877,0,0,2026.5923156676877,0,0,2114.7659145639254,0,0,2114.7659145639254,0,0,196.36668433231216,0,0,0,0,108.1930854360744,0,0,190.53542696891907,102.36182807268129,null,null,2199.1789089999997,null,37984.500000000058,10.750593228293559,7066.4937633454365,87.941227657471927,6736.4430000000057,82.109970294078821,-5.8312573633931066,null,null,null,null,null,null,null,null,null,2026.5923156676877,0,0,32.331420401272226,0,0]
[0,0,1973.3777567176796,0,0,1973.3777567176796,2036.3707240000001,"2013-01-21",50,45,"OFF",-30.351530860919997,-69.579997033272008,-8.8484060000000007,"OFF",-10.838199382275002,-107.1531286979,-8.8484060000000007,"ON",48944.265937874996,76045.471008162014,2059.819,"OFF",-4.8256390940799907,-158.64239131086001,-1.7696810000000001,"OFF",-2.1552877262700156,-118.98177343106001,-3.9817830000000001,null,0,0,1943.9756483937954,0,0,1943.9756483937954,0,0,2027.6083599985591,0,0,2027.6083599985591,0,0,115.84335160620458,0,0,0,0,32.210640001440879,0,0,110.72952310449391,27.096811499730208,null,null,2036.3707240000001,null,37984.500000000058,10.811440105573219,7026.7234760740748,87.223798795789492,6736.4430000000057,82.109970294078821,-5.113828501710671,null,null,null,null,null,null,null,null,null,1943.9756483937954,0,0,29.402108323884249,0,0]
[0,0,1798.8154325414962,0,0,1798.8154325414962,1873.4660030000002,"2013-01-21T01:00:00",47,44,"OFF",-30.198794431889986,-71.667395019270003,-8.8484060000000007,"OFF",-9.7379068944149854,-105.76159420724001,-8.8484060000000007,"ON",43880.110544639996,74548.037446200004,1898.8130000000001,"OFF",-4.5585815400300005,-165.80916690654001,-3.6684019999999999,"OFF",-2.0342971607700111,-115.50281689190001,-3.9817830000000001,null,0,0,1775.2274472105087,0,0,1775.2274472105087,0,0,1847.9504240628203,0,0,1847.9504240628203,0,0,123.58555278949143,0,0,0,0,50.862575937179827,0,0,122.87796005197566,50.154983199664059,null,null,1873.4660030000002,null,33987.03270000004,10.614332595163438,6403.9886437111809,76.518170302440666,6360.681073800004,75.810577564924898,-0.70759273751576757,null,null,null,null,null,null,null,null,null,1775.2274472105087,0,0,23.587985330987522,0,0]
[0,0,1940.4113847278359,0,0,1940.4113847278359,2066.9696219999996,"2013-01-21T02:00:00",44,42,"OFF",-30.56047494367002,-70.971595690604005,-8.8484060000000007,"OFF",-10.350207129925005,-107.1531286979,-8.8484060000000007,"ON",48017.447964709994,74767.150589412006,2092.63,"OFF",-3.7204924858499937,-166.99199929652002,-3.9817830000000001,"OFF",-0.49754716760001677,-120.37338813006001,-3.9817830000000001,null,0,0,1912.1247576262401,0,0,1912.1247576262401,0,0,1998.3526358449676,0,0,1998.3526358449676,0,0,180.50524237375998,0,0,0,0,94.277364155032501,0,0,182.22929811776322,96.001419899035724,null,null,2066.9696219999996,null,31016.841600000043,10.391394705397946,5969.7167664871658,69.64002338825982,6081.4831104000041,71.364079132263043,1.7240557440032234,null,null,null,null,null,null,null,null,null,1912.1247576262401,0,0,28.286627101595741,0,0]
[0,0,1906.6697561514184,0,0,1906.6697561514184,2000.9806230000002,"2013-01-21T03:00:00",44,42,"OFF",-30.341532544399985,-72.363194347936002,-8.8484060000000007,"OFF",-10.849086725235003,-105.57021710800001,-8.8484060000000007,"ON",47055.222158880024,74429.890561380002,2026.6410000000001,"OFF",-4.7337301894400072,-166.99199929652002,-1.7696810000000001,"OFF",-2.8849810927349822,-120.37338813006001,-6.1938839999999997,null,0,0,1879.516738789066,0,0,1879.516738789066,0,0,1963.7770145095037,0,0,1963.7770145095037,0,0,147.12426121093404,0,0,0,0,62.863985490496361,0,0,148.84831695493727,64.588041234499585,null,null,2000.9806230000002,null,31016.841600000043,10.391394705397946,5969.7167664871658,69.64002338825982,6081.4831104000041,71.364079132263043,1.7240557440032234,null,null,null,null,null,null,null,null,null,1879.516738789066,0,0,27.15301736235233,0,0]
[0,0,1885.1508727513835,0,0,1885.1508727513835,2047.9326219999996,"2013-01-21T04:00:00",45,43,"OFF",-30.689906291029988,-73.058993676602014,-8.8484060000000007,"OFF",-11.83583160303999,-109.43192784564,-8.8484060000000007,"ON",46434.102800850014,73881.770828322013,2073.5929999999998,"OFF",-4.8586293316399969,-166.99199929652002,-3.9817830000000001,"OFF",-2.2631179144700053,-116.89443159090001,-3.9817830000000001,null,0,0,1858.7164057969133,0,0,1858.7164057969133,0,0,1943.1357063417652,0,0,1943.1357063417652,0,0,214.8765942030866,0,0,0,0,130.45729365823468,0,0,216.11684392979924,131.69754338494732,null,null,2047.9326219999996,null,31886.51250000007,10.481885829535823,6084.1174991909102,71.405101752270156,6163.2321750000065,72.645351478982803,1.2402497267126478,null,null,null,null,null,null,null,null,null,1858.7164057969133,0,0,26.434466954470281,0,0]
[0,0,1854.2991346088841,0,0,1854.2991346088841,1942.4276220000002,"2013-01-21T05:00:00",44,41,"OFF",-31.378880525439996,-73.058993676602014,-8.8484060000000007,"OFF",-10.303339671449992,-109.04917364716,-8.8484060000000007,"ON",45533.098931759996,74728.217461175998,1968.088,"OFF",-7.2642418685549934,-166.99199929652002,-3.9817830000000001,"OFF",-1.9218396141000003,-120.37338813006001,-3.9817830000000001,null,0,0,1828.8886714717537,0,0,1828.8886714717537,0,0,1906.4946516823029,0,0,1906.4946516823029,0,0,139.19932852824627,0,0,0,0,61.593348317697064,0,0,140.38444544017437,62.778465229625183,null,null,1942.4276220000002,null,31016.841600000043,10.330547828118286,6004.8783696788278,70.178962220334924,6081.4831104000041,71.364079132263043,1.1851169119281195,null,null,null,null,null,null,null,null,null,1828.8886714717537,0,0,25.410463137130364,0,0]
[0,0,1889.1065970528603,0,0,1889.1065970528603,2137.5847239999994,"2013-01-21T06:00:00",41,37,"OFF",-31.354559447749988,-72.363194347936002,-8.8484060000000007,"OFF",-10.128420828760023,-105.28034416724,-8.8484060000000007,"ON",46548.725442659997,77332.141115106002,2161.0329999999999,"OFF",-3.9179596106700068,-165.80916690654001,-1.7696810000000001,"OFF",-3.5116131919399933,-118.98177343106001,-3.9817830000000001,null,0,0,1862.540304687893,0,0,1862.540304687893,0,0,1932.8223794753851,0,0,1932.8223794753851,0,0,298.49269531210689,0,0,0,0,228.2106205246148,0,0,299.80671848158471,229.52464369409262,null,null,2137.5847239999994,null,29175.192900000024,10.024384516464558,5820.8447315805197,67.393258738135927,5908.3681326000024,68.707281907613748,1.3140231694778208,null,null,null,null,null,null,null,null,null,1862.540304687893,0,0,26.566292364967239,0,0]
[0,0,1937.8793685916494,0,0,1937.8793685916494,1907.3843360000001,"2013-01-21T07:00:00",41,35,"OFF",-31.686654528679984,-72.212410689570007,-8.8484060000000007,"OFF",-11.085865940205013,-109.91317788564001,-8.8484060000000007,"ON",47945.726044160008,75768.335151794017,1934.925,"OFF",-4.4799530505099998,-159.82522370084001,-3.6684019999999999,"OFF",-3.2320188535599899,-118.98177343106001,-6.1754499999999997,null,0,0,1909.6780970355537,0,0,1909.6780970355537,0,0,1991.1204585262096,0,0,1991.1204585262096,0,0,25.246902964446235,0,0,0,0,-56.195458526209677,0,0,25.488450542963619,-55.953910947692293,null,null,1907.3843360000001,null,29175.192900000024,9.9026907619052373,5892.3768501858849,68.465734329096364,5908.3681326000024,68.707281907613748,0.24154757851738395,null,null,null,null,null,null,null,null,null,1909.6780970355537,0,0,28.201271556095662,0,0]
[0,0,1816.7554321264254,0,0,1816.7554321264254,1970.416569,"2013-01-21T08:00:00",40,34,"OFF",-32.024008125829994,-71.122379348970014,-8.8484060000000007,"OFF",-10.41315870546001,-105.57021710800001,-8.8484060000000007,"ON",44419.311552224994,73561.154030840014,1995.7819999999999,"OFF",-4.3569247604400054,-166.99199929652002,-3.6684019999999999,"OFF",-3.0705282882399807,-116.19862424140001,-4.0002170000000001,null,0,0,1792.5809241463292,0,0,1792.5809241463292,0,0,1871.0649165819339,0,0,1871.0649165819339,0,0,203.20107585367077,0,0,0,0,124.71708341806607,0,0,203.35564453791537,124.87165210231066,null,null,1970.416569,null,28829.600000000006,9.8300637488983202,5865.5977695426463,68.062703608401506,5875.8824000000004,68.217272292646101,0.15456868424459458,null,null,null,null,null,null,null,null,null,1792.5809241463292,0,0,24.174507980096223,0,0]
[0,0,1569.2493109114801,0,0,1569.2493109114801,1660.0719550000001,"2013-01-21T09:00:00",41,35,"OFF",-32.113304241390011,-70.971595690604005,-8.8484060000000007,"OFF",-11.607576719689998,-113.66933444784001,-8.8484060000000007,"ON",36522.29322729,76524.916360512012,1687.9259999999999,"OFF",-4.4124179236200014,-158.64239131086001,-3.9817830000000001,"OFF",-2.8695990438500005,-117.59015873206,-6.1754499999999997,null,0,0,1552.9047265296401,0,0,1552.9047265296401,0,0,1598.1362949922438,0,0,1598.1362949922438,0,0,135.0212734703598,0,0,0,0,89.789705007756083,0,0,135.26282104887719,90.031252586273467,null,null,1660.0719550000001,null,29175.192900000024,9.9026907619052373,5892.3768501858849,68.465734329096364,5908.3681326000024,68.707281907613748,0.24154757851738395,null,null,null,null,null,null,null,null,null,1552.9047265296401,0,0,16.344584381839923,0,0]
[0,0,1497.0230820070037,0,0,1497.0230820070037,1435.9307240000001,"2013-01-21T10:00:00",43,35,"OFF",-32.106841896959985,-73.604009346902004,-8.8484060000000007,"OFF",-11.191858032530002,-123.23313628442,-8.8484060000000007,"ON",33999.599589480014,72271.107152782017,1459.3789999999999,"OFF",-4.2345288710900046,-165.80916690654001,-1.7696810000000001,"OFF",-3.2045943253800027,-119.67758078056001,-3.9817830000000001,null,0,0,1482.8410189120898,0,0,1482.8410189120898,0,0,1531.9625182259476,0,0,1531.9625182259476,0,0,-23.462018912089889,0,0,0,0,-72.583518225947728,0,0,-24.693246003535933,-73.814745317393772,null,null,1435.9307240000001,null,30272.564300000085,9.9400965767677878,6091.0000353022297,71.512360230466271,6011.521044200008,70.281133139020227,-1.2312270914460441,null,null,null,null,null,null,null,null,null,1482.8410189120898,0,0,14.182063094913929,0,0]
[0,0,1523.1732270321761,0,0,1523.1732270321761,1789.5582900000002,"2013-01-21T11:00:00",45,36,"OFF",-32.356453274819998,-71.818178677635998,-8.8484060000000007,"OFF",-11.358076878719984,-107.1531286979,-8.8484060000000007,"ON",34926.301777110013,74796.891841884004,1813.0250000000001,"OFF",-4.1071791760999856,-166.99199929652002,-1.7696810000000001,"OFF",-4.644594318979995,-116.19862424140001,-4.0002170000000001,null,0,0,1508.215554201945,0,0,1508.215554201945,0,0,1553.6937047734073,0,0,1553.6937047734073,0,0,304.80944579805509,0,0,0,0,259.33129522659283,0,0,301.95096415402202,256.47281358255975,null,null,1789.5582900000002,null,31886.51250000007,10.0559576885782,6341.8151681798627,75.503833123015909,6163.2321750000065,72.645351478982803,-2.8584816440331053,null,null,null,null,null,null,null,null,null,1508.215554201945,0,0,14.957672830231104,0,0]
[0,0,1581.569986657747,0,0,1581.569986657747,1537.6317240000001,"2013-01-21T12:00:00",48,38,"OFF",-32.138077589800012,-72.363194347936002,-8.8484060000000007,"OFF",-10.216100959420011,-123.57402172942001,-8.8484060000000007,"ON",36941.485731019995,76712.531688606003,1561.08,"OFF",-4.1989826806199932,-158.64239131086001,-1.7696810000000001,"OFF",-3.4932399192249814,-116.19862424140001,-3.9817830000000001,null,0,0,1564.850348089589,0,0,1564.850348089589,0,0,1610.6372769104582,0,0,1610.6372769104582,0,0,-3.7703480895891062,0,0,0,0,-49.557276910458313,0,0,-10.032085114318249,-55.819013935187456,null,null,1537.6317240000001,null,35210.380800000043,10.290951281512466,6842.9788144571121,83.961739590539338,6475.6757952000044,77.700002565810195,-6.2617370247291433,null,null,null,null,null,null,null,null,null,1564.850348089589,0,0,16.719638568157961,0,0]
[0,0,1595.2385189195595,0,0,1595.2385189195595,1840.3026760000002,"2013-01-21T13:00:00",50,40,"OFF",-32.103012359520015,-73.058993676602014,-8.8484060000000007,"OFF",-9.370203159925012,-102.28255745974,-8.8484060000000007,"ON",37402.951223709999,74127.537202916006,1866.258,"OFF",-3.8926212573749974,-159.82522370084001,-2.083062,"OFF",-3.6256839461500032,-120.37338813006001,-6.1754499999999997,null,0,0,1578.1007999029912,0,0,1578.1007999029912,0,0,1632.0924302709336,0,0,1632.0924302709336,0,0,288.15720009700885,0,0,0,0,234.16556972906642,0,0,279.330506765829,225.33887639788654,null,null,1840.3026760000002,null,37984.500000000058,10.507205719174916,7230.1810805285759,90.936663625258703,6736.4430000000057,82.109970294078821,-8.8266933311798823,null,null,null,null,null,null,null,null,null,1578.1007999029912,0,0,17.137719016568326,0,0]
[0,0,1623.0176882171966,0,0,1623.0176882171966,1733.0526760000002,"2013-01-21T14:00:00",53,42,"OFF",-32.777619167930006,-71.667395019270003,-8.8484060000000007,"OFF",-10.569941172840018,-107.8489360474,-8.8484060000000007,"ON",38329.531104760004,79076.062926722007,1759.008,"OFF",-7.1425543664899971,-159.82522370084001,-2.083062,"OFF",-5.5867075223399834,-116.89443159090001,-6.1754499999999997,null,0,0,1605.023986443796,0,0,1605.023986443796,0,0,1647.9581547151415,0,0,1647.9581547151415,0,0,153.98401355620399,0,0,0,0,111.04984528485852,0,0,139.46012834118216,96.525960069836671,null,null,1733.0526760000002,null,42907.977300000086,10.79672477004117,7948.3321495906712,104.88925946907732,7199.249866200008,90.365374254055467,-14.523885215021849,null,null,null,null,null,null,null,null,null,1605.023986443796,0,0,17.993701773400517,0,0]
[0,0,1702.9304756460367,0,0,1702.9304756460367,1696.724003,"2013-01-21T15:00:00",55,44,"OFF",-32.810319555160007,-73.058993676602014,-8.8484060000000007,"OFF",-11.132832077095015,-103.48279505950001,-8.8484060000000007,"ON",40916.069306055011,77482.579877610013,1722.0709999999999,"OFF",-3.6188340701100037,-165.80916690654001,-3.6684019999999999,"OFF",-5.5464549030300159,-120.37338813006001,-3.9817830000000001,null,0,0,1682.429906661393,0,0,1682.429906661393,0,0,1736.1796157027568,0,0,1736.1796157027568,0,0,39.641093338606879,0,0,0,0,-14.108615702756879,0,0,21.296460841680897,-32.453248199682861,null,null,1696.724003,null,46654.737500000047,11.046133369707222,8447.2522535252756,115.35977041240044,7551.4453250000042,97.015137915474455,-18.344632496925982,null,null,null,null,null,null,null,null,null,1682.429906661393,0,0,20.500568984643678,0,0]
[0,0,1672.6804301455293,0,0,1672.6804301455293,1960.1296220000002,"2013-01-21T16:00:00",55,44,"OFF",-32.849212199440018,-73.754793005267999,-8.8484060000000007,"OFF",-11.697154699770023,-105.95289109814,-8.8484060000000007,"ON",39950.193556199985,76343.517178768001,1985.79,"OFF",-4.7384995448700042,-159.82522370084001,-3.9817830000000001,"OFF",-4.2259669623500224,-118.98177343106001,-3.9817830000000001,null,0,0,1653.136288792241,0,0,1653.136288792241,0,0,1707.7843708228777,0,0,1707.7843708228777,0,0,332.65371120775899,0,0,0,0,278.00562917712227,0,0,314.30907871083298,259.66099668019626,null,null,1960.1296220000002,null,46654.737500000047,11.046133369707222,8447.2522535252756,115.35977041240044,7551.4453250000042,97.015137915474455,-18.344632496925982,null,null,null,null,null,null,null,null,null,1653.136288792241,0,0,19.544141353288296,0,0]
[0,0,1651.3115829858166,0,0,1651.3115829858166,1625.3656760000001,"2013-01-21T17:00:00",55,44,"OFF",-32.813444742659975,-73.058993676602014,-8.8484060000000007,"OFF",-12.21996612276002,-104.87440975850001,-8.8484060000000007,"ON",39258.323751359996,78058.074717110008,1651.3209999999999,"OFF",-5.2302965047899965,-165.80916690654001,-2.083062,"OFF",-4.9808631854100085,-119.67758078056001,-6.1754499999999997,null,0,0,1632.4376464835557,0,0,1632.4376464835557,0,0,1680.2915548027545,0,0,1680.2915548027545,0,0,18.883353516444231,0,0,0,0,-28.970554802754577,0,0,0.53872101951824902,-47.315187299680559,null,null,1625.3656760000001,null,46654.737500000047,11.046133369707222,8447.2522535252756,115.35977041240044,7551.4453250000042,97.015137915474455,-18.344632496925982,null,null,null,null,null,null,null,null,null,1632.4376464835557,0,0,18.873936502260904,0,0]
[0,0,1294.8620242331026,1595.5834654876535,0,2890.4454897207561,3204.2974050000003,"2013-01-22T05:00:00",36,32,"OFF",-32.920225530290011,-72.513978006302011,-8.8484060000000007,"OFF",-13.418516591460019,-116.91761180116001,-8.8484060000000007,"ON",26220.928042289997,78396.12880770801,1452.086,"ON",20741.675702400018,73673.838727705996,1773.89,"OFF",-3.8390518697300093,-120.019749559,-3.9817830000000001,null,0,0,1286.3437154255328,1589.8416247639786,0,2876.1853401895114,0,0,1307.5002070101095,1608.3381033648614,0,2915.8383103749711,0,0,165.74228457446725,184.04837523602146,0,0,0,144.58579298989048,165.55189663513875,0,348.75138506792842,309.09841488246894,null,null,3204.2974050000003,null,28888.694400000008,9.7103843298555006,5950.0619993338405,69.340144378773275,5881.4372736000005,68.300869636213008,-1.0392747425602664,null,null,null,null,null,null,null,null,null,2876.1853401895114,0,0,8.5183088075698379,5.7418407236748408,0]
[0,0,1546.1695843395278,0,0,{"$f":"SUM(A516:E516)","v":1546.1695843395278},{"$f":"N516+R516+V516+Z516+AD516","v":1759.0266220000001},"2013-01-22T09:00:00",42,36,"OFF",-34.593195673889987,-70.971595690604005,-8.8484060000000007,"OFF",-14.268609440800018,-109.40874763538001,-8.8484060000000007,"ON",35728.556810729991,72470.481023520013,1784.6869999999999,"OFF",0.20257903063998847,-166.99199929652002,-3.9817830000000001,"OFF",-6.6802908495599977,-118.98177343106001,-3.9817830000000001,null,0,0,1530.5228633198074,0,0,{"$f":"SUM(AF516:AJ516)","v":1530.5228633198074},0,0,1584.1858695385838,0,0,{"$f":"SUM(AL516:AP516)","v":1584.1858695385838},{"$f":"IF($K516=\"ON\",$N516-AF516,0)","v":0},{"$f":"IF($O516=\"ON\",$R516-AG516,0)","v":0},{"$f":"IF($S516=\"ON\",$V516-AH516,0)","v":254.16413668019254},{"$f":"IF($W516=\"ON\",$Z516-AI516,0)","v":0},{"$f":"IF($AA516=\"ON\",$AD516-AJ516,0)","v":0},{"$f":"IF($K516=\"ON\",$N516-AL516,0)","v":0},{"$f":"IF($O516=\"ON\",$R516-AM516,0)","v":0},{"$f":"IF($S516=\"ON\",$V516-AN516,0)","v":200.5011304614161},{"$f":"IF($W516=\"ON\",$Z516-AO516,0)","v":0},{"$f":"IF($AA516=\"ON\",$AD516-AP516,0)","v":0},{"$f":"SUM(AR516:AV516)+BN516","v":254.32115535565782},{"$f":"SUM(AW516:BA516)+BN516","v":200.65814913688138},null,null,{"$f":"N516+R516+V516+Z516+AD516","v":1759.0266220000001},null,29657.431200000021,{"$f":"19.5285952781395+42*-0.3035722016559+BH516*0.0000340867411548605+J516*0.0608468772796604","v":9.9799755712919591},{"$f":"BH516*1000/(500*BI516)","v":5943.3875339958804},{"$f":"0.00000128*BJ516^2+0*BJ516+24.024","v":69.238534885449781},{"$f":"0.094*BH516 + 3165.9","v":5953.6985328000019},{"$f":"0.00000128*BL516^2+0*BL516+24.024","v":69.395553560915062},{"$f":"BM516-BK516","v":0.15701867546528092},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF516:AJ516)","v":1530.5228633198074},{"$f":"A516-AF516","v":0},{"$f":"B516-AG516","v":0},{"$f":"C516-AH516","v":15.646721019720417},{"$f":"D516-AI516","v":0},{"$f":"E516-AJ516","v":0}]
[0,0,1670.8584775451113,0,0,1670.8584775451113,1709.1199550000001,"2013-01-23",53,49,"OFF",-32.005589638959989,-71.818178677635998,-8.8484060000000007,"OFF",-15.214485441919987,-108.5447433969,-8.8484060000000007,"ON",39891.517326785004,78153.570766714009,1736.9739999999999,"OFF",-3.0678022427500071,-166.99199929652002,-3.9817830000000001,"OFF",-7.2885141185500029,-120.37338813006001,-6.1754499999999997,null,0,0,1651.3716568694772,0,0,1651.3716568694772,0,0,1700.5051477712605,0,0,1700.5051477712605,0,0,85.60234313052274,0,0,0,0,36.468852228739479,0,0,77.100063375696607,27.966572473913345,null,null,1709.1199550000001,null,42907.977300000086,11.222652910998791,7646.6727858879085,98.867654008881601,7199.249866200008,90.365374254055467,-8.5022797548261337,null,null,null,null,null,null,null,null,null,1651.3716568694772,0,0,19.486820675634135,0,0]
[0,0,2232.3981897146314,2745.9409116373149,0,4978.3391013519467,5372.5313040000001,"2013-01-23T16:00:00",73,61,"OFF",-33.507693003415014,-73.058993676602014,-8.8484060000000007,"OFF",19.079110075399996,-107.8489360474,-8.8484060000000007,"ON",51431.511340594981,75314.363968228005,2492.9960000000001,"ON",51834.342232919989,63187.432439442004,2903.4259999999999,"OFF",7.8984236188350181,-120.37338813006001,-6.1938839999999997,null,0,0,2199.568137042359,2711.5309769105488,0,4911.0991139529078,0,0,2296.7741445466977,2893.4374830690717,0,5190.2116276157694,0,0,293.42786295764108,191.89502308945112,0,0,0,196.2218554533024,9.9885169309281991,0,430.65831358527112,151.54579992240954,null,null,5372.5313040000001,null,91919.663300000131,13.623464092600019,13494.315788585514,257.1075950106474,11806.348350200013,202.44302254882635,-54.664572461821052,null,null,null,null,null,null,null,null,null,4911.0991139529078,0,0,32.830052672272359,34.409934726766096,0]
[0,0,1569.6359248814679,2053.5935839306194,0,3623.2295088120873,3527.077738,"2013-01-24T07:00:00",51,50,"OFF",-33.887008130990012,-74.450592333934011,-8.8484060000000007,"OFF",5.3162680319099831,-106.45732134840001,-8.8484060000000007,"ON",36535.494444680007,78505.372566788006,1670.3579999999999,"ON",37685.77136128,73463.708918574019,1880.5920000000001,"OFF",-3.1330715799599966,-116.89443159090001,-6.1754499999999997,null,0,0,1553.279597831819,2035.5386991517325,0,3588.8182969835516,0,0,1593.663467661886,2094.4171029253921,0,3688.0805705872781,0,0,117.0784021681809,-154.94669915173245,0,0,0,76.694532338113959,-213.825102925392,0,-41.38968456911519,-140.65195817284169,null,null,3527.077738,null,39527.769900000014,11.168279533584904,7078.5781786949956,88.160024360828118,6881.5103706000009,84.638636775264473,-3.5213875855636445,null,null,null,null,null,null,null,null,null,3588.8182969835516,0,0,16.356327049648826,18.054884778886844,0]
[0,0,1774.1090995667505,0,0,1774.1090995667505,1899.9860030000002,"2013-01-24T22:00:00",58,51,"OFF",-32.54078509828998,-71.667395019270003,-8.8484060000000007,"OFF",-1.2206931628850104,-109.26381116500001,-8.8484060000000007,"ON",43129.875689264984,80490.753565139996,1925.3330000000001,"OFF",-1.6213173458999941,-159.82522370084001,-3.6684019999999999,"OFF",-4.6837979086849915,-117.94387751146,-3.9817830000000001,null,0,0,1751.3244078684438,0,0,1751.3244078684438,0,0,1801.1202648411054,0,0,1801.1202648411054,0,0,174.00859213155627,0,0,0,0,124.2127351588947,0,0,153.85758778141525,104.06173080875368,null,null,1899.9860030000002,null,52896.528800000029,11.684823835050604,9053.8855436276153,128.94923959949966,8138.1737072000033,108.79823524935864,-20.151004350141022,null,null,null,null,null,null,null,null,null,1751.3244078684438,0,0,22.784691698306688,0,0]
[0,0,0,2020.9138298102087,0,2020.9138298102087,2130.174724,"2013-01-25T14:00:00",48,44,"OFF",-35.626186804319985,-74.450592333934011,-8.8484060000000007,"OFF",-3.7756131466249832,-106.96175159866002,-8.8484060000000007,"OFF",-7.1754062875000441E-2,-75.14639166260001,-1.7696810000000001,"ON",36645.908996985003,71173.720707404005,2153.623,"OFF",-6.3407971416300164,-116.19862424140001,-3.9817830000000001,null,0,0,0,2003.8241144893498,0,2003.8241144893498,0,0,0,2066.3398678436142,0,2066.3398678436142,0,0,0,149.79888551065028,0,0,0,0,87.283132156385818,0,147.57379134080952,85.05803798654506,null,null,2130.174724,null,35210.380800000043,10.656032545190428,6608.5347713942847,79.925096735650953,6475.6757952000044,77.700002565810195,-2.2250941698407587,null,null,null,null,null,null,null,null,null,2003.8241144893498,0,0,0,17.089715320858886,0]
[0,0,0,1857.703449084416,0,1857.703449084416,2127.1897239999998,"2013-01-26T04:00:00",46,43,"OFF",-37.520744076719993,-71.667395019270003,-8.8484060000000007,"OFF",-7.8322746617699828,-108.71294028588001,-8.8484060000000007,"OFF",-0.2907521003749976,-33.398399859304,-1.7696810000000001,"ON",31131.888454624997,71092.461638150009,2150.6379999999999,"OFF",-6.4092311035899892,-118.98177343106001,-3.9817830000000001,null,0,0,0,1845.2660769104343,0,1845.2660769104343,0,0,0,1890.9191769272002,0,1890.9191769272002,0,0,0,305.3719230895656,0,0,0,0,259.71882307279975,0,305.42489847096192,259.77179845419607,null,null,2127.1897239999998,null,32877.826400000049,10.515676489848337,6253.1072407447627,74.073728210245861,6256.415681600005,74.126703591642183,5.2975381396322518E-2,null,null,null,null,null,null,null,null,null,1845.2660769104343,0,0,0,12.437372173981657,0]
[0,0,0,2067.3626759209387,0,2067.3626759209387,2123.6597240000001,"2013-01-26T20:00:00",50,49,"OFF",-37.658830475280013,-71.667395019270003,-8.8484060000000007,"OFF",-9.4175643137899954,-102.30581787834001,-8.8484060000000007,"OFF",-8.3137276375002206E-2,-33.398399859304,-1.7696810000000001,"ON",38118.216390770009,70305.786260264009,2147.1080000000002,"OFF",-6.8136792149999854,-120.37338813006001,-3.9817830000000001,null,0,0,0,2048.8981110171167,0,2048.8981110171167,0,0,0,2119.3617017480369,0,2119.3617017480369,0,0,0,98.209888982883513,0,0,0,0,27.746298251963253,0,95.848290284087071,25.384699553166811,null,null,2123.6597240000001,null,37984.500000000058,11.05482761469186,6872.0203197956125,84.471568992875262,6736.4430000000057,82.109970294078821,-2.3615986987964419,null,null,null,null,null,null,null,null,null,2048.8981110171167,0,0,0,18.464564903822065,0]
[0,0,0,0,2228.470806513089,2228.470806513089,2818.6364450000001,"2013-01-27T11:00:00",64,60,"OFF",-37.670266388300007,-72.363194347936002,-8.8484060000000007,"OFF",-10.387999429205019,-108.5447433969,-8.8484060000000007,"OFF",-0.86431615837500231,-41.400104170214007,-1.7696810000000001,"OFF",0.86920843960999916,-166.99199929652002,-2.083062,"ON",51889.107899699993,65887.269226343997,2840.1860000000001,null,0,0,0,0,2195.5315824541963,2195.5315824541963,0,0,0,0,2350.0888882062723,2350.0888882062723,0,0,0,0,644.65441754580388,0,0,0,0,490.09711179372789,616.79714939565076,462.23984364357477,null,null,2818.6364450000001,null,67246.745600000082,12.72159785614528,10572.059635970329,167.08760953153674,9487.0940864000077,139.23034138138365,-27.857268150153089,null,null,null,null,null,null,null,null,null,2195.5315824541963,0,0,0,0,32.939224058892705]
[0,0,0,0,2166.9954778555475,2166.9954778555475,2634.7651049999999,"2013-01-28T02:00:00",67,64,"OFF",-34.882698066749988,-71.667395019270003,-8.8484060000000007,"OFF",-9.2126700847999796,-107.1531286979,-8.8484060000000007,"OFF",-0.23403512199999377,-33.398399859304,-1.7696810000000001,"OFF",-1.9642102862900159,-159.82522370084001,-3.6684019999999999,"ON",46163.097135679986,65651.240144226002,2657.9,null,0,0,0,0,2140.6915226316301,2140.6915226316301,0,0,0,0,2265.3276259315553,2265.3276259315553,0,0,0,0,517.20847736837004,0,0,0,0,392.57237406844479,486.07138877107622,361.43528547115096,null,null,2634.7651049999999,null,75152.638700000127,13.234471496961621,11357.104621405353,189.12329648837994,10230.248037800013,157.98620789108611,-31.137088597293825,null,null,null,null,null,null,null,null,null,2140.6915226316301,0,0,0,0,26.303955223917455]
[0,2965.1424753435645,0,2939.5626926251603,0,5904.7051679687247,6291.033144,"2013-01-28T18:00:00",77,66,"OFF",-33.682769048460003,-72.363194347936002,-8.8484060000000007,"ON",53965.941843350018,69527.94984144601,3149.7240000000002,"OFF",-1.6167210400001485E-2,-33.398399859304,-2.193667,"ON",52642.893305919999,64613.23193295001,3156.3330000000001,"OFF",-1.719806596130002,-116.89443159090001,-3.9817830000000001,null,0,2927.1143596450497,0,2903.7528967222911,0,5830.8672563673408,0,3078.0152318194901,0,3081.6257868668658,0,6159.6410186863559,0,222.60964035495044,0,252.58010327770899,0,0,71.708768180510106,0,74.707213133134246,0,420.66916086364029,91.895398544625237,null,null,6291.033144,null,103480.2117000001,14.321759899917355,14450.767562525223,291.31959442704795,12893.039899800009,236.79901165802883,-54.520582769019114,null,null,null,null,null,null,null,null,null,5830.8672563673408,0,38.028115698514739,0,35.809795902869155,0]
[0,2351.2187792165087,0,2534.9764712342758,0,4886.1952504507844,5094.3051299999997,"2013-01-29T09:00:00",72,67,"OFF",-36.394360907619983,-72.363194347936002,-8.8484060000000007,"ON",41523.59226559502,69252.137422688,2563.0949999999998,"OFF",-0.10247234374999833,-33.398399859304,-1.7696810000000001,"ON",42965.979107204999,64269.37075853601,2545.81,"OFF",-5.7454811065400051,-119.67758078056001,-3.9817830000000001,null,0,2328.8932837639395,0,2511.0992257800376,0,4839.9925095439776,0,2418.5191826881264,0,2631.331430432042,0,5049.8506131201684,0,234.20171623606029,0,34.710774219962332,0,0,144.57581731187338,0,-85.521430432042052,0,228.84058638539398,18.982482809202679,null,null,5094.3051299999997,null,89061.715200000035,13.891127219159252,12822.820465881588,234.48764761629661,11537.701228800002,194.41574354566797,-40.071904070628648,null,null,null,null,null,null,null,null,null,4839.9925095439776,0,22.325495452569157,0,23.877245454238164,0]
[0,1529.2337598444033,0,1915.6284585480105,0,3444.8622183924135,3642.3831299999997,"2013-01-30",55,43,"OFF",-36.876893335030005,-75.14639166260001,-8.8484060000000007,"ON",27531.795329199995,75895.746099883996,1862.76,"OFF",0.91153541437499541,-33.398399859304,-1.7696810000000001,"ON",33155.157966599996,69958.829043926002,1794.223,"OFF",-8.2062593974900082,-118.28604628990001,-3.9817830000000001,null,0,1519.5917451037867,0,1901.5743164161445,0,3421.1660615199312,0,1547.2038100791731,0,1956.078355933467,0,3503.2821660126401,0,343.16825489621328,0,-107.35131641614453,0,0,315.55618992082691,0,-161.85535593346708,0,216.45769653336805,134.34159204065912,null,null,3642.3831299999997,null,46654.737500000047,10.985286492427562,8494.041103463318,116.37437986217516,7551.4453250000042,97.015137915474455,-19.359241946700706,null,null,null,null,null,null,null,null,null,3421.1660615199312,0,9.6420147406165597,0,14.054142131866001,0]
[0,0,0,1930.5617834118716,0,1930.5617834118716,2328.3913119999997,"2013-01-30T16:00:00",53,40,"OFF",-41.887035339170012,-73.058993676602014,-8.8484060000000007,"OFF",-11.372718930199996,-109.93635809590002,-8.8484060000000007,"OFF",-0.48761611162500068,-33.398399859304,-1.388093,"ON",33664.28704000001,62117.188496319999,2351.4580000000001,"OFF",-7.3124150618399879,-117.59015873206,-3.9817830000000001,null,0,0,0,1916.0843943955304,0,1916.0843943955304,0,0,0,1995.9877654471932,0,1995.9877654471932,0,0,0,435.37360560446973,0,0,0,0,355.47023455280691,0,418.99550772628243,339.09213667461961,null,null,2328.3913119999997,null,42907.977300000086,10.675031015481849,8038.9419455121479,106.74347213224274,7199.249866200008,90.365374254055467,-16.378097878187276,null,null,null,null,null,null,null,null,null,1916.0843943955304,0,0,0,14.477389016341249,0]
[0,0,0,1894.6980902688181,0,1894.6980902688181,1961.3877240000002,"2013-01-31T10:00:00",47,38,"OFF",-42.521242371029999,-72.363194347936002,-8.8484060000000007,"OFF",-10.6596908432,-110.63216544540002,-8.8484060000000007,"OFF",-0.80955493787500332,-41.226148322422006,-1.7696810000000001,"ON",32433.162210569993,73150.367017530007,1984.836,"OFF",-8.6157169428399971,-117.59023894040001,-3.9817830000000001,null,0,0,0,1881.2328184208893,0,1881.2328184208893,0,0,0,1925.8358165997543,0,1925.8358165997543,0,0,0,103.6031815791107,0,0,0,0,59.00018340024576,0,99.089269269034702,54.486271090169765,null,null,1961.3877240000002,null,33987.03270000004,10.249251331485475,6632.1005507187874,80.324489875000893,6360.681073800004,75.810577564924898,-4.5139123100759946,null,null,null,null,null,null,null,null,null,1881.2328184208893,0,0,0,13.465271847928761,0]
[0,0,0,1825.7148813783776,0,1825.7148813783776,1773.9667240000001,"2013-02-01T06:00:00",30,26,"OFF",-42.24405081180501,-71.667395019270003,-8.8484060000000007,"OFF",-13.429652394125004,-103.67417215874002,-8.8484060000000007,"OFF",0.12249617735999817,-67.318643199481997,-1.7696810000000001,"ON",29979.237338344989,72557.603322428011,1797.415,"OFF",-8.258476378389993,-119.33829950236,-3.9817830000000001,null,0,0,0,1814.1522719775608,0,1814.1522719775608,0,0,0,1853.614148608757,0,1853.614148608757,0,0,0,-16.737271977560795,0,0,0,0,-56.199148608757014,0,-29.718440096381755,-69.180316727577974,null,null,1773.9667240000001,null,33714.300000000047,9.5097922351801838,7090.4388163767808,88.375132939241695,6335.0442000000039,75.393964820420734,-12.98116811882096,null,null,null,null,null,null,null,null,null,1814.1522719775608,0,0,0,11.562609400816882,0]
[0,0,0,1971.025608689592,0,1971.025608689592,1838.4462740000001,"2013-02-01T21:00:00",48,41,"OFF",-38.303984609800018,-74.450592333934011,-8.8484060000000007,"OFF",-11.97698419937498,-103.67417215874002,-8.8484060000000007,"OFF",-1.7871176749997459E-2,-33.398399859304,-1.7696810000000001,"ON",35019.879465479993,71451.58645966601,1864.079,"OFF",-7.4129858161100266,-118.64257236120001,-6.1662330000000001,null,0,0,0,1955.3889199469199,0,1955.3889199469199,0,0,0,2011.8049512150906,0,2011.8049512150906,0,0,0,-91.30991994691999,0,0,0,0,-147.72595121509062,0,-95.500575437995806,-151.91660670616642,null,null,1838.4462740000001,null,35210.380800000043,10.473491913351447,6723.713751115688,81.890658056886011,6475.6757952000044,77.700002565810195,-4.190655491075816,null,null,null,null,null,null,null,null,null,1955.3889199469199,0,0,0,15.63668874267205,0]
[0,2306.3287492166219,0,0,0,2306.3287492166219,2473.8519989999995,"2013-02-02T12:00:00",62,51,"OFF",-39.014263678320006,-71.667395019270003,-8.8484060000000007,"ON",48369.491707079993,75016.245610116021,2492.4059999999999,"OFF",9.8443716750001062E-2,-41.226148322422006,-1.7696810000000001,"OFF",0.76646480984999299,-165.84389711776001,-1.7696810000000001,"OFF",-9.671567053599988,-116.19862424140001,-6.1662330000000001,null,0,2276.5945820809079,0,0,0,2276.5945820809079,0,2366.0426991019199,0,0,0,2366.0426991019199,0,215.81141791909204,0,0,0,0,126.36330089808007,0,0,0,182.23805022504698,92.789933204035009,null,null,2473.8519989999995,null,62221.807200000039,12.002692186068415,10367.975156810437,161.61748333086516,9014.7498768000041,128.0441156368201,-33.573367694045061,null,null,null,null,null,null,null,null,null,2276.5945820809079,0,29.73416713571396,0,0,0]
[0,1931.9411263158852,0,0,0,1931.9411263158852,1980.2396959999999,"2013-02-03T04:00:00",41,37,"OFF",-37.99782361122999,-73.058993676602014,-8.8484060000000007,"ON",39361.352553359982,73307.631509768005,1998.8489999999999,"OFF",-1.8105585750004642E-3,-33.398399859304,-1.7696810000000001,"OFF",-1.3351823701299954,-166.99199929652002,-3.9817830000000001,"OFF",-8.4730045490000183,-119.67758078056001,-4.0094339999999997,null,0,1912.3575200375237,0,0,0,1912.3575200375237,0,1976.747090068164,0,0,0,1976.747090068164,0,86.491479962476205,0,0,0,0,22.101909931835962,0,0,0,87.805503131954026,23.415933101313783,null,null,1980.2396959999999,null,29175.192900000024,10.024384516464558,5820.8447315805197,67.393258738135927,5908.3681326000024,68.707281907613748,1.3140231694778208,null,null,null,null,null,null,null,null,null,1912.3575200375237,0,19.583606278361458,0,0,0]
[0,2271.4281135203173,0,0,0,2271.4281135203173,2386.1173469999994,"2013-02-03T19:00:00",61,46,"OFF",-37.593640501059994,-73.019362735808002,-8.8484060000000007,"ON",47586.87024769999,72689.297395874004,2404.6990000000001,"OFF",-0.3982234661399997,-33.398399859304,-1.7696810000000001,"OFF",-2.3723722509899918,-159.79049348962002,-3.9817830000000001,"OFF",-6.812044092649991,-117.94676501170001,-3.9817830000000001,null,0,2242.6680179659893,0,0,0,2242.6680179659893,0,2340.3324540721555,0,0,0,2340.3324540721555,0,162.03098203401078,0,0,0,0,64.366545927844527,0,0,0,125.17736740286814,27.512931296701893,null,null,2386.1173469999994,null,59794.286900000065,11.615711543555845,10295.415253002335,159.69833629664402,8786.5629686000066,122.84472166550138,-36.853614631142634,null,null,null,null,null,null,null,null,null,2242.6680179659893,0,28.760095554328018,0,0,0]
[0,2086.88739182158,0,0,0,2086.88739182158,2247.7722849999996,"2013-02-04T11:00:00",63,57,"OFF",-38.468066246609972,-73.058993676602014,-8.8484060000000007,"ON",41879.898967030014,63400.65829049801,2264.4459999999999,"OFF",-0.67063757312500338,-67.318643199481997,-1.7696810000000001,"OFF",-4.1901554205699991,-166.99199929652002,-2.0738449999999999,"OFF",-7.0285329876299807,-118.28596608156001,-3.9817830000000001,null,0,2064.6098972546101,0,0,0,2064.6098972546101,0,2181.1105733344966,0,0,0,2181.1105733344966,0,199.83610274538978,0,0,0,0,83.335426665503292,0,0,0,171.06846211294402,54.56778603305753,null,null,2247.7722849999996,null,64707.210300000093,12.452492741881569,10392.651759172653,162.27322955191607,9248.3777682000091,133.50558891947031,-28.767640632445762,null,null,null,null,null,null,null,null,null,2064.6098972546101,0,22.277494566969835,0,0,0]
[0,0,1729.854570076204,2131.965505381349,0,3861.8200754575528,4089.167825,"2013-02-05T06:00:00",59,58,"OFF",-6.7509426265199952,-74.450592333934011,3.0151150000000002,"OFF",-7.6672667227799742,-166.99199929652002,-8.8484060000000007,"ON",39785.028922710007,81835.205760220008,1955.2629999999999,"ON",38034.928404899983,77836.114177828014,2145.9319999999998,"OFF",-9.6870990135500232,-118.62524735976001,-6.1938839999999997,null,0,0,1710.3809480179846,2113.4866242539415,0,3823.8675722719263,0,0,1749.3402426849766,2160.9468418560236,0,3910.2870845410002,0,0,244.88205198201535,32.445375746058289,0,0,0,205.92275731502332,-15.01484185602385,0,261.75887201178409,175.33935974270995,null,null,4089.167825,null,55127.89710000006,12.186812049671488,9047.1399534689808,128.79294891219803,8347.9223274000051,113.2243931959085,-15.568555716289524,null,null,null,null,null,null,null,null,null,3823.8675722719263,0,0,19.473622058219462,18.478881127407476,0]
[1873.1881222316254,0,0,0,0,1873.1881222316254,1854.6257189999999,"2013-03-05T22:00:00",44,35,"ON",40452.986240224993,70629.747745524,1871.2809999999999,"OFF",-22.193877885690014,-166.99199929652002,-8.8484060000000007,"OFF",5.3535170260000778E-2,-33.398399859304,-1.7696810000000001,"OFF",-3.7244976904100104,-165.91351795688001,-2.0554109999999999,"OFF",-10.917339574119978,-118.98177343106001,-3.9817830000000001,null,1826.4159876896788,0,0,0,0,1826.4159876896788,1903.0975190031827,0,0,0,0,1903.0975190031827,44.865012310321163,0,0,0,0,-31.816519003182748,0,0,0,0,42.606444099550473,-34.075087213953438,null,null,1854.6257189999999,null,31016.841600000043,9.9654665644403231,6224.8649171484121,73.622647343033734,6081.4831104000041,71.364079132263043,-2.2585682107706901,null,null,null,null,null,null,null,null,null,1826.4159876896788,46.772134541946571,0,0,0,0]
[2075.817201895426,0,0,0,0,2075.817201895426,2108.9043469999992,"2013-03-06T14:00:00",58,41,"ON",46220.221541020001,76303.798008800019,2127.4859999999999,"OFF",-19.135873678945011,-166.99199929652002,-8.8484060000000007,"OFF",2.7531388633500482E-2,-66.970747545565999,-1.7696810000000001,"OFF",-4.088892255279986,-166.99199929652002,-3.9817830000000001,"OFF",-13.440311261019994,-116.54937531222001,-3.9817830000000001,null,2018.7560957767907,0,0,0,0,2018.7560957767907,2093.445011745659,0,0,0,0,2093.445011745659,108.72990422320913,0,0,0,0,34.040988254340846,0,0,0,0,76.734330426821998,2.0454144579537115,null,null,2108.9043469999992,null,52896.528800000029,11.076355062253999,9551.2519240667552,140.79380904574577,8138.1737072000033,108.79823524935864,-31.995573796387134,null,null,null,null,null,null,null,null,null,2018.7560957767907,57.06110611863528,0,0,0,0]
[1801.4460434699224,0,0,0,0,1801.4460434699224,1771.929449,"2013-03-07T05:00:00",41,34,"ON",38287.77512713999,76049.176633470008,1788.299,"OFF",-25.419446082849973,-166.99199929652002,-8.8484060000000007,"OFF",-0.48818995674999976,-33.398399859304,-1.7696810000000001,"OFF",-5.2764090572899924,-166.99199929652002,-1.7696810000000001,"OFF",-13.093004658789976,-118.28596608156001,-3.9817830000000001,null,1758.2921670661347,0,0,0,0,1758.2921670661347,1810.271534122892,0,0,0,0,1810.271534122892,30.006832933865326,0,0,0,0,-21.972534122892057,0,0,0,0,29.697162688280997,-22.282204368476386,null,null,1771.929449,null,29175.192900000024,9.8418438846255771,5928.8062769571079,69.016952153198076,5908.3681326000024,68.707281907613748,-0.30967024558432854,null,null,null,null,null,null,null,null,null,1758.2921670661347,43.153876403787763,0,0,0,0]
[0,0,2074.2800619786399,0,0,2074.2800619786399,2166.9978879999999,"2013-03-07T20:00:00",60,46,"OFF",-3.7819598038249871,-71.667395019270003,3.0657580000000002,"OFF",-24.048724024500004,-166.99199929652002,-8.8484060000000007,"ON",48756.999608944985,74328.170344592014,2178.5320000000002,"OFF",-8.0160447539199815,-166.99199929652002,-1.7696810000000001,"OFF",-12.974646168749992,-120.37338813006001,-3.9817830000000001,null,0,0,2071.7376011226875,0,0,2071.7376011226875,0,0,2164.4887358466076,0,0,2164.4887358466076,0,0,106.79439887731269,0,0,0,0,14.043264153392556,0,0,73.769690793532178,-18.981443930387954,null,null,2166.9978879999999,null,57428.400000000081,11.535066169193872,9957.1860547053057,150.93030928386281,8564.1696000000084,117.9056012000823,-33.02470808378051,null,null,null,null,null,null,null,null,null,2071.7376011226875,0,0,2.5424608559524131,0,0]
[0,0,2017.7795648988681,0,1998.204250754183,4015.9838156530514,4141.2855249999993,"2013-03-08T12:00:00",60,55,"OFF",-7.3942433544300119,-71.667395019270003,3.5683419999999999,"OFF",-20.368410929999971,-166.99199929652002,-8.8484060000000007,"ON",47275.976121665,80388.969181680004,2084.9969999999998,"OFF",-6.9157234736799884,-165.91351795688001,-2.0554109999999999,"ON",45275.350245120004,72504.425193008006,2063.6239999999998,null,0,0,2015.9784827480958,0,2000.8148934085007,4016.7933761565964,0,0,2077.4174238170958,0,2087.8086655434954,4165.2260893605908,0,0,69.018517251904086,0,62.80910659149913,0,0,7.5795761829040202,0,-24.184665543495612,110.04574177914476,-38.386971424850046,null,null,4141.2855249999993,null,57428.400000000081,12.082688064710815,9505.8979744296757,139.68748326434076,8564.1696000000084,117.9056012000823,-21.781882064258454,null,null,null,null,null,null,null,null,null,4016.7933761565964,0,0,1.8010821507723449,0,-2.610642654317644]
[0,0,2103.3182614593075,0,0,2103.3182614593075,2168.8451890000001,"2013-03-09T03:00:00",61,58,"OFF",-9.9986356750350129,-72.363194347936002,3.314673,"OFF",-5.3199877812899938,-166.99199929652002,-8.8484060000000007,"ON",47493.761740800015,72030.666611963999,2182.6190000000001,"OFF",-7.501669090790001,20411.121592342002,-2.0554109999999999,"OFF",-18.60032538902998,-119.67758078056001,-6.1846670000000001,null,0,0,2101.4254047650443,0,0,2101.4254047650443,0,0,2200.8396285923582,0,0,2200.8396285923582,0,0,81.193595234955865,0,0,0,0,-18.220628592358025,0,0,59.913584130323429,-39.500639696990461,null,null,2168.8451890000001,null,59794.286900000065,12.345874070911769,9686.5214332425367,144.12473277013382,8786.5629686000066,122.84472166550138,-21.280011104632436,null,null,null,null,null,null,null,null,null,2101.4254047650443,0,0,1.8928566942631733,0,0]
[0,0,2668.7653861761178,0,0,2668.7653861761178,2621.4330869999994,"2013-03-09T19:00:00",69,65,"OFF",-12.046376186875007,-74.450592333934011,3.211957,"OFF",-5.2025758120500232,-166.99199929652002,-8.8484060000000007,"ON",55776.551746800018,71674.10845732801,2632.8209999999999,"OFF",-7.7161583349900074,13618.197069402002,-1.7696810000000001,"OFF",-14.056011347349992,-116.89443159090001,-3.9817830000000001,null,0,0,2661.9138055767894,0,0,2661.9138055767894,0,0,2804.0011233152445,0,0,2804.0011233152445,0,0,-29.092805576789488,0,0,0,0,-171.1801233152446,0,0,-64.42936207793133,-206.51667981638644,null,null,2621.4330869999994,null,80625.134100000141,13.481857908412247,11960.53758283458,207.13370786611006,10744.662605400013,171.79715136496822,-35.336556501141843,null,null,null,null,null,null,null,null,null,2661.9138055767894,0,0,6.851580599328372,0,0]
[0,0,2128.4167048254385,2789.0323478271603,0,4917.4490526525988,5316.8333739999998,"2013-03-10T04:00:00",59,51,"OFF",-14.37291886257,-74.450592333934011,2.36178,"OFF",-2.3666436504199755,-166.99199929652002,-8.8484060000000007,"ON",50147.651561444996,77329.101219020013,2320.1779999999999,"ON",54233.823810524998,70463.612210882013,3007.1329999999998,"OFF",-15.15706125338999,-120.37338813006001,-3.9910000000000001,null,0,0,2125.1275317013592,2784.4841229335707,0,4909.6116546349294,0,0,2208.4158005558206,2928.8054796167357,0,5137.2212801725564,0,0,195.05046829864068,222.64887706642912,0,0,0,111.76219944417926,78.327520383264073,0,394.40482474199712,166.79519920437068,null,null,5316.8333739999998,null,55127.89710000006,11.760883908713865,9374.788073395528,136.51891381898116,8347.9223274000051,113.2243931959085,-23.294520623072657,null,null,null,null,null,null,null,null,null,4909.6116546349294,0,0,3.2891731240792978,4.5482248935895768,0]
[0,0,0,2172.2821507352805,0,2172.2821507352805,2503.7016159999998,"2013-03-11T01:00:00",40,36,"OFF",-21.458015180350007,-73.754793005267999,2.35737,"OFF",-12.62539667116002,-158.97982779724001,-8.8484060000000007,"OFF",-5.800977150500003E-2,-33.398399859304,-1.7696810000000001,"ON",38642.836702159992,70080.104054006006,2518.1469999999999,"OFF",-16.132245211320008,-118.28596608156001,-6.1846670000000001,null,0,0,0,2175.2069520239879,0,2175.2069520239879,0,0,0,2249.7570406594218,0,2249.7570406594218,0,0,0,342.94004797601201,0,0,0,0,268.38995934057812,0,344.16507438307025,269.61498574763635,null,null,2503.7016159999998,null,28829.600000000006,9.9517575034576407,5793.8710805570663,66.992245885587849,5875.8824000000004,68.217272292646101,1.2250264070582517,null,null,null,null,null,null,null,null,null,2175.2069520239879,0,0,0,-2.9248012887073855,0]
[0,0,0,2249.067447632191,0,2249.067447632191,2599.2183233999995,"2013-03-11T17:00:00",60,44,"OFF",-24.051174332710016,-73.058993676602014,2.6891850000000002,"OFF",-9.0315087558300355,-110.63216544540002,-8.8484060000000007,"OFF",-0.37641897974999561,-75.14639166260001,-0.16867260000000001,"ON",40796.565830500025,70999.115172058009,2609.5279999999998,"OFF",-17.253721621429982,-118.98177343106001,-3.9817830000000001,null,0,0,0,2251.3234379722212,0,2251.3234379722212,0,0,0,2330.7168387404131,0,2330.7168387404131,0,0,0,358.20456202777859,0,0,0,0,278.8111612595867,0,322.45917892445289,243.06577815626099,null,null,2599.2183233999995,null,57428.400000000081,11.413372414634551,10063.353391739631,153.65098430340802,8564.1696000000084,117.9056012000823,-35.745383103325722,null,null,null,null,null,null,null,null,null,2251.3234379722212,0,0,0,-2.2559903400301664,0]
[0,0,0,1977.7324382234531,0,1977.7324382234531,2487.3245729999994,"2013-03-12T08:00:00",46,39,"OFF",-25.787588609650015,-71.667395019270003,2.3964430000000001,"OFF",-11.855631623809948,-107.17711099156001,-8.8484060000000007,"OFF",0.32944565737499731,-66.970747545565999,-1.7696810000000001,"ON",32813.622559750009,70451.115751510006,2499.5279999999998,"OFF",-16.25551452085001,-118.28596608156001,-3.9817830000000001,null,0,0,0,1981.9037815532204,0,1981.9037815532204,0,0,0,2035.0247823784116,0,2035.0247823784116,0,0,0,517.62421844677942,0,0,0,0,464.50321762158819,0,515.27738006755169,462.15637924236046,null,null,2487.3245729999994,null,32877.826400000049,10.272288980729696,6401.2658642445167,76.473541970869888,6256.415681600005,74.126703591642183,-2.3468383792277052,null,null,null,null,null,null,null,null,null,1981.9037815532204,0,0,0,-4.1713433297672964,0]
[0,0,0,2344.2924722009893,0,2344.2924722009893,2494.9496049999998,"2013-03-12T23:00:00",51,42,"OFF",-24.772190203600012,-72.214319648062002,2.5706920000000002,"OFF",-8.2262400952500592,-166.99199929652002,-8.8484060000000007,"OFF",-0.42455170350000404,-75.14639166260001,-1.7696810000000001,"ON",43369.307990060006,69884.933100284004,2506.9879999999998,"OFF",-14.705193330869996,-119.32682970974001,-3.9910000000000001,null,0,0,0,2345.5995976781483,0,2345.5995976781483,0,0,0,2440.2250255969134,0,2440.2250255969134,0,0,0,161.38840232185157,0,0,0,0,66.762974403086446,0,151.88823423546938,57.262806316704243,null,null,2494.9496049999998,null,39527.769900000014,10.681504515347623,7401.1614830485532,94.138804861646676,6881.5103706000009,84.638636775264473,-9.5001680863822031,null,null,null,null,null,null,null,null,null,2345.5995976781483,0,0,0,-1.3071254771589338,0]
[0,0,0,2382.9870089233345,0,2382.9870089233345,2428.2891120000004,"2013-03-13T15:00:00",68,50,"OFF",-26.470502337159989,-73.754793005267999,2.4411999999999998,"OFF",-11.756949594650004,-107.17711099156001,-8.8484060000000007,"OFF",-0.20043502001999969,-41.574051997172006,-1.3797980000000001,"ON",44386.200773900004,70330.899491518008,2442.27,"OFF",-16.576768794249997,-118.28596608156001,-6.1938839999999997,null,0,0,0,2383.8736417857358,0,2383.8736417857358,0,0,0,2480.8807130227965,0,2480.8807130227965,0,0,0,58.396358214264183,0,0,0,0,-38.610713022796517,0,-0.35610158861618402,-97.363172825676884,null,null,2428.2891120000004,null,77871.196800000151,12.475282001315527,12484.07800189023,223.51482055331783,10485.792499200013,164.76236075043747,-58.752459802880367,null,null,null,null,null,null,null,null,null,2383.8736417857358,0,0,0,-0.88663286240125672,0]
[0,0,0,2449.4710641768324,1994.0566852876736,4443.5277494645061,4357.2795340000002,"2013-03-14T06:00:00",48,42,"OFF",-27.641260520089997,-71.7014434596,2.131621,"OFF",-12.479844270874983,-109.02735697868,-8.8484060000000007,"OFF",-9.0942623121000057E-2,-66.970747545565999,-1.7696810000000001,"ON",46097.726667665003,69712.549335956006,2361.002,"ON",45131.830839779999,74264.613255976001,2004.7639999999999,null,0,0,0,2449.5913042931002,1996.7287755172697,4446.3200798103699,0,0,0,2557.3784581580317,2075.6861705844681,4633.0646287424997,0,0,0,-88.589304293100213,8.0352244827302002,0,0,0,-196.37645815803171,-70.922170584468176,-84.078184365922169,-270.82273329805207,null,null,4357.2795340000002,null,35210.380800000043,10.534338790631107,6684.877238107244,81.224107121362351,6475.6757952000044,77.700002565810195,-3.5241045555521566,null,null,null,null,null,null,null,null,null,4446.3200798103699,0,0,0,-0.12024011626772335,-2.6720902295960514]
[0,0,0,0,2385.8947798789,2385.8947798789,2505.399085,"2013-03-14T17:00:00",77,58,"OFF",-29.223492738750007,-72.404806434728002,1.540583,"OFF",2.3288331169599772,-166.99199929652002,-8.8484060000000007,"OFF",4.3755687045002557E-3,-66.970747545565999,-1.7696810000000001,"OFF",-2.1628895124900023,-158.64239131086001,-2.0554109999999999,"ON",54621.747941279995,59464.482130002005,2516.5320000000002,null,0,0,0,0,2383.4261876665714,2383.4261876665714,0,0,0,0,2613.2888942934678,2613.2888942934678,0,0,0,0,133.10581233342873,0,0,0,0,-96.756894293467667,59.44508784903266,-170.41761877786374,null,null,2505.399085,null,103480.2117000001,13.834984881680072,14959.208497152162,310.4597361424249,12893.039899800009,236.79901165802883,-73.66072448439607,null,null,null,null,null,null,null,null,null,2383.4261876665714,0,0,0,0,2.4685922123285309]
[0,0,0,0,2422.8148962846954,2422.8148962846954,2672.2408930000001,"2013-03-14T21:00:00",67,54,"OFF",-27.678748869365009,-74.492204420725997,2.1616610000000001,"OFF",-11.659523490960023,-166.99199929652002,-8.8484060000000007,"OFF",3.6322801126500562E-2,-75.14639166260001,-1.7696810000000001,"OFF",-2.6031721637599881,-158.64239131086001,-1.7696810000000001,"ON",58825.625060139981,69203.924189514015,2682.4670000000001,null,0,0,0,0,2417.3743262477165,2417.3743262477165,0,0,0,0,2589.8417133854473,2589.8417133854473,0,0,0,0,265.09267375228364,0,0,0,0,92.625286614552806,217.65931391472961,45.19192677699877,null,null,2672.2408930000001,null,75152.638700000127,12.626002724165017,11904.423013653375,205.41956772864015,10230.248037800013,157.98620789108611,-47.433359837554036,null,null,null,null,null,null,null,null,null,2417.3743262477165,0,0,0,0,5.4405700369788974]
[0,0,0,0,2481.09991909874,2481.09991909874,2591.023189,"2013-03-15T12:00:00",75,61,"OFF",-30.491358814980025,-71.667395019270003,1.9886870000000001,"OFF",-40.756485666330008,-166.99199929652002,-8.8484060000000007,"OFF",-0.93407933000000321,-41.574051997172006,-1.7696810000000001,"OFF",-2.7752378596600082,-159.72087265050001,-2.0554109999999999,"ON",54437.250679454992,59226.664401902002,2601.7080000000001,null,0,0,0,0,2478.7464049382229,2478.7464049382229,0,0,0,0,2710.6173705741503,2710.6173705741503,0,0,0,0,122.96159506177719,0,0,0,0,-108.90937057415022,62.333771468476272,-169.53719416745113,null,null,2591.023189,null,97681.6875,13.819872720033457,14136.409137603623,279.81672103132576,12347.978625,219.18889743802484,-60.627823593300917,null,null,null,null,null,null,null,null,null,2478.7464049382229,0,0,0,0,2.3535141605170793]
[2255.150894305662,0,0,0,2342.3469913063409,4597.4978856120033,5086.6925019999999,"2013-03-16T04:00:00",60,54,"ON",50963.09234095001,78631.371848094001,2467.259,"OFF",-51.41466209367502,-106.59656302664001,-8.8484060000000007,"OFF",-0.57617563887500145,-41.574051997172006,-1.7696810000000001,"OFF",-4.7679852284400024,-158.64239131086001,-2.0554109999999999,"ON",56411.350201439986,67451.997585566001,2632.107,null,2188.9055089047738,0,0,0,2338.6707643004133,4527.5762732051871,2268.4593500015631,0,0,0,2510.6794651181672,4779.1388151197298,278.35349109522622,0,0,0,293.43623569958663,198.79964999843696,0,0,0,121.4275348818328,548.83405246560085,297.27151055105776,null,null,5086.6925019999999,null,57428.400000000081,12.021841187431155,9554.0107550316879,140.86127552929429,8564.1696000000084,117.9056012000823,-22.955674329211988,null,null,null,null,null,null,null,null,null,4527.5762732051871,66.245385400888154,0,0,0,3.6762270059275579]
[2768.3934329630238,0,0,0,0,2768.3934329630238,3055.2268599999998,"2013-03-16T19:00:00",77,62,"ON",57230.779308780009,61281.738426880001,3073.5320000000002,"OFF",-56.150196996660014,-166.99199929652002,-8.8484060000000007,"OFF",-1.4717314552500003E-2,-75.14639166260001,-1.7696810000000001,"OFF",-7.6181044956799884,-165.91351795688001,-3.696053,"OFF",-3.9702311144299904,-166.99199929652002,-3.9910000000000001,null,2687.9195812301255,0,0,0,0,2687.9195812301255,2926.8469230633596,0,0,0,0,2926.8469230633596,385.61241876987469,0,0,0,0,146.6850769366406,0,0,0,0,321.76991211558732,82.842570282353194,null,null,3055.2268599999998,null,103480.2117000001,14.078372390798714,14700.593055434772,300.64151831231624,12893.039899800009,236.79901165802883,-63.842506654287405,null,null,null,null,null,null,null,null,null,2687.9195812301255,80.473851732898311,0,0,0,0]
[2656.6678436340576,0,2654.4042406154322,0,0,5311.0720842494902,5749.303758,"2013-03-17T11:00:00",67,57,"ON",58886.851917450003,80550.990028479995,2976.165,"OFF",-49.872609791259976,-111.51718426896001,-8.8484060000000007,"ON",60962.189737239998,69093.421159496007,2789.665,"OFF",-7.4532640856800088,-158.64239131086001,-3.696053,"OFF",-7.7817735503199854,-117.59015873206,-3.9817830000000001,null,2573.2653974800455,0,2643.5802506388159,0,0,5216.8456481188614,2668.4140253425985,0,2834.3606450427856,0,0,5502.7746703853845,402.89960251995444,0,146.08474936118409,0,0,307.75097465740146,0,-44.6956450427856,0,0,506.68445847738315,220.75543621086047,null,null,5749.303758,null,75152.638700000127,12.808543356003998,11734.767430017304,200.2861012948415,10230.248037800013,157.98620789108611,-42.299893403755391,null,null,null,null,null,null,null,null,null,5216.8456481188614,83.402446154012068,0,10.823989976616303,0,0]
[0,0,2164.343718937856,0,0,2164.343718937856,2429.2754879999998,"2013-03-18T02:00:00",59,53,"OFF",-6.2391049919400041,-73.754793005267999,2.722575,"OFF",-49.199577750940016,-107.1531286979,-8.8484060000000007,"ON",51055.936063580004,66830.431075569999,2441.1619999999998,"OFF",-8.1790229619699897,-166.99199929652002,-1.7696810000000001,"OFF",-10.662335389649984,-119.67758078056001,-3.9910000000000001,null,0,0,2160.5402408307586,0,0,2160.5402408307586,0,0,2307.2999516373484,0,0,2307.2999516373484,0,0,280.62175916924116,0,0,0,0,133.86204836265142,0,0,259.61964126808323,112.85993046149346,null,null,2429.2754879999998,null,55127.89710000006,11.882577663273187,9278.7774946155041,134.22651109706646,8347.9223274000051,113.2243931959085,-21.002117901157959,null,null,null,null,null,null,null,null,null,2160.5402408307586,0,0,3.8034781070973622,0,0]
[0,0,2480.8416575493002,0,0,2480.8416575493002,2879.7000149999999,"2013-03-18T17:00:00",68,55,"OFF",-7.3772969491900104,-72.363194347936002,2.301615,"OFF",-48.065723716375004,-166.99199929652002,-8.8484060000000007,"ON",58613.519033500001,54559.357138970001,2892.2840000000001,"OFF",-8.390376552599994,-165.91351795688001,-2.0554109999999999,"OFF",-12.174240511930009,-166.99199929652002,-3.9817830000000001,null,0,0,2471.9309453729752,0,0,2471.9309453729752,0,0,2800.945904724751,0,0,2800.945904724751,0,0,420.3530546270249,0,0,0,0,91.338095275249088,0,0,370.98585427878953,41.970894927013717,null,null,2879.7000149999999,null,{"$f":" -0.6251*I1157^3 + 145.21*I1157^2 - 8340.3*I1157 + 170112","v":77871.196800000151},12.779516387713828,12186.876942364608,214.12956109867284,10485.792499200013,164.76236075043747,-49.367200348235372,null,null,null,null,null,null,null,null,null,2471.9309453729752,0,0,8.9107121763249779,0,0]
[0,0,2174.3146263257445,0,0,2174.3146263257445,2265.8234089999996,"2013-03-19T08:00:00",51,45,"OFF",-9.824013513225001,-73.754793005267999,2.6992790000000002,"OFF",-41.722135853474967,-105.76159420724001,-8.8484060000000007,"ON",51306.016496670003,69459.411814916006,2277.7240000000002,"OFF",-8.9404861289099955,-159.72087265050001,-1.7696810000000001,"OFF",-13.980990503900008,-119.67758078056001,-3.9817830000000001,null,0,0,2170.3658380691209,0,0,2170.3658380691209,0,0,2301.5525610505715,0,0,2301.5525610505715,0,0,107.35816193087931,0,0,0,0,-23.828561050571352,0,0,100.1943752104642,-30.992347770986456,null,null,2265.8234089999996,null,39527.769900000014,10.864045147186603,7276.8051613327989,91.802423495679577,6881.5103706000009,84.638636775264473,-7.1637867204151036,null,null,null,null,null,null,null,null,null,2170.3658380691209,0,0,3.9487882566236294,0,0]
[0,0,2261.5875984677596,0,0,2261.5875984677596,2464.3987569999999,"2013-03-19T23:00:00",58,45,"OFF",-8.8074374176499912,-73.754793005267999,2.5048439999999998,"OFF",-35.901536833349958,-104.36997950824001,-8.8484060000000007,"ON",53459.402857930007,71316.844469300006,2476.5030000000002,"OFF",-8.1203150951300032,-158.64239131086001,-1.7696810000000001,"OFF",-13.566937402399986,-117.59015873206,-3.9910000000000001,null,0,0,2256.3210334510277,0,0,2256.3210334510277,0,0,2386.7423307221929,0,0,2386.7423307221929,0,0,220.18196654897247,0,0,0,0,89.76066927780721,0,0,193.15378102096537,62.73248374980011,null,null,2464.3987569999999,null,52896.528800000029,11.319742571372641,9345.8890017117683,135.82642077736574,8138.1737072000033,108.79823524935864,-27.0281855280071,null,null,null,null,null,null,null,null,null,2256.3210334510277,0,0,5.2665650167318745,0,0]
[0,0,0,2756.0260208952359,0,2756.0260208952359,2901.3689400000003,"2013-03-20T14:00:00",66,48,"OFF",-12.546882984860002,-75.14639166260001,2.3249110000000002,"OFF",-47.356161061999991,-166.99199929652002,-8.8484060000000007,"OFF",4.1024070874998833E-2,-166.99199929652002,-1.7696810000000001,"ON",53482.312523009998,56888.28649921,2915.8560000000002,"OFF",-14.620372576530007,-166.99199929652002,-6.1938839999999997,null,0,0,0,2751.9811252418858,0,2751.9811252418858,0,0,0,3007.1857516600298,0,3007.1857516600298,0,0,0,163.8748747581144,0,0,0,0,-91.329751660029615,0,109.73988741824635,-145.46473899989766,null,null,2901.3689400000003,null,72473.210400000098,12.169588481581945,11910.544142011808,205.60615905127912,9978.3817776000087,151.47117171141107,-54.134987339868047,null,null,null,null,null,null,null,null,null,2751.9811252418858,0,0,0,4.0448956533500677,0]
[0,0,0,2465.4461108146465,0,2465.4461108146465,2442.4347183999998,"2013-03-21T06:00:00",54,43,"OFF",-16.777864146360013,-72.363194347936002,2.9415800000000001,"OFF",-42.511999090079975,-119.51443701700001,-8.8484060000000007,"OFF",-0.41708673156000181,-33.398399859304,-0.16867260000000001,"ON",46502.549443169999,69099.220222478005,2452.4920000000002,"OFF",-14.318550394350011,-118.28596608156001,-3.9817830000000001,null,0,0,0,2465.3742579203063,0,2465.3742579203063,0,0,0,2578.3051853659053,0,2578.3051853659053,0,0,0,-12.882257920306074,0,0,0,0,-125.81318536590516,0,-29.26902569260173,-142.19995313820081,null,null,2442.4347183999998,null,44737.413600000087,10.919931168938236,8193.7171412317584,109.95936075585938,7371.2168784000078,93.572592983563723,-16.386767772295656,null,null,null,null,null,null,null,null,null,2465.3742579203063,0,0,0,7.1852894340281637E-2,0]
[0,0,0,3050.0302689909586,0,3050.0302689909586,3292.1244419999998,"2013-03-21T21:00:00",66,60,"OFF",-19.166642921579999,-73.754793005267999,2.295979,"OFF",-34.772958796369998,-148.67008839866,-8.8484060000000007,"OFF",0.27038645399999894,-75.14639166260001,-1.7696810000000001,"ON",56245.014553799985,69368.471599024007,3306.6219999999998,"OFF",-14.201715754470005,-118.28596608156001,-6.1754499999999997,null,0,0,0,3044.0347254478088,0,3044.0347254478088,0,0,0,3209.2762196035287,0,3209.2762196035287,0,0,0,262.58727455219105,0,0,0,0,97.345780396471127,0,228.42665088466453,63.185156728944605,null,null,3292.1244419999998,null,72473.210400000098,12.899751008937869,11236.373531517853,185.6317953789376,9978.3817776000087,151.47117171141107,-34.160623667526522,null,null,null,null,null,null,null,null,null,3044.0347254478088,0,0,0,5.995543543149779,0]
[0,2335.6895788777733,0,0,0,2335.6895788777733,2413.8462520000003,"2013-03-22T13:00:00",48,46,"OFF",-21.944957654100005,-74.450592333934011,2.5460690000000001,"ON",46144.145845455001,71482.169899708009,2426.1950000000002,"OFF",6.9001948500000604E-2,-166.99199929652002,-8.8484060000000007,"OFF",6.9669479319983671E-2,-159.68606223094,-2.0461939999999998,"OFF",-14.18896691806999,-119.67758078056001,-4.0002170000000001,null,0,2340.3048538353314,0,0,0,2340.3048538353314,0,2439.7555056445217,0,0,0,2439.7555056445217,0,85.890146164668749,0,0,0,0,-13.560505644521527,0,0,0,84.920309012308309,-14.530342796881968,null,null,2413.8462520000003,null,35210.380800000043,10.777726299749748,6533.9163049292883,78.669839718170635,6475.6757952000044,77.700002565810195,-0.96983715236044077,null,null,null,null,null,null,null,null,null,2340.3048538353314,0,-4.6152749575580856,0,0,0]
[0,2109.7935202693229,0,0,0,2109.7935202693229,2449.5409339999997,"2013-03-23T04:00:00",47,45,"OFF",-25.120353149989999,-72.363194347936002,2.689238,"ON",41045.521524830016,70497.965442904009,2461.4699999999998,"OFF",-0.48434870775000372,-166.99199929652002,-8.8484060000000007,"OFF",-1.5632945798400002,-159.68606223094,-1.7696810000000001,"OFF",-13.507598996569996,-118.98177343106001,-4.0002170000000001,null,0,2116.4353433784663,0,0,0,2116.4353433784663,0,2198.6909704297764,0,0,0,2198.6909704297764,0,345.03465662153349,0,0,0,0,262.77902957022343,0,0,0,344.92377579685319,262.66814874554314,null,null,2449.5409339999997,null,33987.03270000004,10.675179472443098,6367.4868956974724,75.921458389605164,6360.681073800004,75.810577564924898,-0.11088082468026528,null,null,null,null,null,null,null,null,null,2116.4353433784663,0,-6.6418231091433881,0,0,0]
[0,2250.1819747437503,0,0,0,2250.1819747437503,2366.6258929999995,"2013-03-23T19:00:00",51,48,"OFF",-27.43688968740998,-72.513978006302011,2.9067630000000002,"ON",44265.192326090008,69379.428058268008,2378.319,"OFF",0.17465180189499666,-166.99199929652002,-8.8484060000000007,"OFF",-2.8738984116800061,-166.99199929652002,-1.7696810000000001,"OFF",-13.914042390990023,-118.28596608156001,-3.9817830000000001,null,0,2255.622232005046,0,0,0,2255.622232005046,0,2356.7690945818417,0,0,0,2356.7690945818417,0,122.69676799495392,0,0,0,0,21.549905418158232,0,0,0,117.75449886981779,16.607636293022111,null,null,2366.6258929999995,null,39527.769900000014,11.046585779025584,7156.5587215286623,89.580905900400595,6881.5103706000009,84.638636775264473,-4.9422691251361215,null,null,null,null,null,null,null,null,null,2255.622232005046,0,-5.4402572612957556,0,0,0]
[0,2032.0850785808384,0,0,0,2032.0850785808384,2215.628467,"2013-03-24T13:00:00",50,40,"OFF",-31.067976521469998,-72.363194347936002,2.8858730000000001,"ON",39182.869890304988,68503.897881330005,2229.5729999999999,"OFF",-0.42627323887500129,-166.99199929652002,-8.8484060000000007,"OFF",-4.2880984820800085,-166.99199929652002,-3.9817830000000001,"OFF",-11.21077353508,-117.59015873206,-4.0002170000000001,null,0,2039.3015426083139,0,0,0,2039.3015426083139,0,2121.6312382814608,0,0,0,2121.6312382814608,0,190.271457391686,0,0,0,0,107.94176171853906,0,0,0,181.44476406050612,99.115068387359173,null,null,2215.628467,null,37984.500000000058,10.507205719174916,7230.1810805285759,90.936663625258703,6736.4430000000057,82.109970294078821,-8.8266933311798823,null,null,null,null,null,null,null,null,null,2039.3015426083139,0,-7.2164640274754674,0,0,0]
[0,1954.1069858986889,0,0,0,1954.1069858986889,1854.266601,"2013-03-25T01:00:00",37,31,"OFF",-32.112043760160006,-74.450592333934011,2.7571379999999999,"ON",37249.017979679986,67993.484088906014,1868.3030000000001,"OFF",-1.1748785284995789E-2,-166.99199929652002,-8.8484060000000007,"OFF",-4.1691280966299908,-166.99199929652002,-1.7696810000000001,"OFF",-12.695349000179993,-118.98177343106001,-6.1754499999999997,null,0,1961.8280014001152,0,0,0,1961.8280014001152,0,2037.9721490213385,0,0,0,2037.9721490213385,0,-93.525001400115116,0,0,0,0,-169.6691490213384,0,0,0,-94.79605680703429,-170.94020442825757,null,null,1854.266601,null,28650.199700000056,9.6414079454701351,5943.1568215015532,69.235024646349373,5859.0187718000052,67.963969239430199,-1.2710554069191744,null,null,null,null,null,null,null,null,null,1961.8280014001152,0,-7.7210155014263364,0,0,0]
[0,0,0,0,2113.9608506186905,2113.9608506186905,2490.3571849999998,"2013-03-25T17:00:00",53,38,"OFF",-3.6968067360900019,-74.450592333934011,2.4621909999999998,"OFF",-5.3802950551200084,-111.13659569566001,-8.8484060000000007,"OFF",-0.17197787062500069,-166.99199929652002,-8.8484060000000007,"OFF",-4.6052474431599837,-166.99199929652002,-2.0461939999999998,"ON",49183.897391749997,67605.548431662013,2507.6379999999999,null,0,0,0,0,2114.7079822303176,2114.7079822303176,0,0,0,0,2244.502794625043,2244.502794625043,0,0,0,0,392.93001776968231,0,0,0,0,263.13520537495697,374.6331936149632,244.83838122023786,null,null,2490.3571849999998,null,42907.977300000086,10.553337260922527,8131.6414398850084,108.66219840877457,7199.249866200008,90.365374254055467,-18.296824154719104,null,null,null,null,null,null,null,null,null,2114.7079822303176,0,0,0,0,-0.74713161162708275]
[0,0,0,0,0,0,-23.847991,"2013-03-26T08:00:00",38,31,"OFF",-10.566757280450009,-112.96197709738001,1.812387,"OFF",-8.1022693793699982,-166.99199929652002,-8.8484060000000007,"OFF",-0.34222126332499708,-166.99199929652002,-8.8484060000000007,"OFF",-6.1781861339799935,-166.99199929652002,-3.9817830000000001,"OFF",-0.2892735836199985,-166.99199929652002,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-1.1473453976915522,-1.1473453976915522,null,null,-23.847991,null,28563.352800000052,9.6384476176697333,5926.9612562164348,68.988953257844088,5850.8551632000053,67.841607860152536,-1.1473453976915522,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2037.9249862165052,0,0,0,0,2037.9249862165052,2046.3699549999999,"2013-03-26T23:00:00",43,35,"ON",45177.287467119997,67527.521758510004,2074.2240000000002,"OFF",-5.2545716374499962,-107.34450579714002,-8.8484060000000007,"OFF",2.2236797591999757E-2,-166.99199929652002,-8.8484060000000007,"OFF",-6.8430500909400065,13581.670191366002,-3.9817830000000001,"OFF",-5.3998301646799991,-120.37338813006001,-6.1754499999999997,null,1982.7953680265641,0,0,0,0,1982.7953680265641,2093.5457564297185,0,0,0,0,2093.5457564297185,91.42863197343604,0,0,0,0,-19.321756429718334,0,0,0,0,90.197404881989996,-20.552983521164379,null,null,2046.3699549999999,null,30272.564300000085,9.9400965767677878,6091.0000353022297,71.512360230466271,6011.521044200008,70.281133139020227,-1.2312270914460441,null,null,null,null,null,null,null,null,null,1982.7953680265641,55.129618189941084,0,0,0,0]
[2055.6837299115869,0,0,0,0,2055.6837299115869,2188.7216219999996,"2013-03-27T15:00:00",71,53,"ON",45667.972458420001,54088.429912328007,2214.3820000000001,"OFF",-10.627911419720002,-107.1531286979,-8.8484060000000007,"OFF",-7.8537754000005486E-3,-166.99199929652002,-8.8484060000000007,"OFF",-9.2383732180599996,-166.99199929652002,-3.9817830000000001,"OFF",-8.315532981910005,-119.3239422095,-3.9817830000000001,null,1999.6493012595545,0,0,0,0,1999.6493012595545,2200.5691173957994,0,0,0,0,2200.5691173957994,214.73269874044558,0,0,0,0,13.812882604200695,0,0,0,0,150.09538634876475,-50.824429787480142,null,null,2188.7216219999996,null,86224.143900000025,12.942547378832446,13324.138034992977,251.26579760069956,11270.969526600002,186.62848520901872,-64.637312391680837,null,null,null,null,null,null,null,null,null,1999.6493012595545,56.034428652032375,0,0,0,0]
[1933.0691211677329,0,0,0,0,1933.0691211677329,1959.9786219999999,"2013-03-28T06:00:00",51,48,"ON",42208.018311209999,54535.695678670003,1985.6389999999999,"OFF",-11.46706580777998,-108.01713293638001,-8.8484060000000007,"OFF",-0.64052827074999918,-166.99199929652002,-8.8484060000000007,"OFF",-12.06604816132001,13444.947055002001,-3.9817830000000001,"OFF",-12.126183908369988,-120.37338813006001,-3.9817830000000001,null,1883.2667699697881,0,0,0,0,1883.2667699697881,2051.610329225161,0,0,0,0,2051.610329225161,102.37223003021177,0,0,0,0,-65.971329225161071,0,0,0,0,97.429960905075646,-70.913598350297192,null,null,1959.9786219999999,null,39527.769900000014,11.046585779025584,7156.5587215286623,89.580905900400595,6881.5103706000009,84.638636775264473,-4.9422691251361215,null,null,null,null,null,null,null,null,null,1883.2667699697881,49.802351197944745,0,0,0,0]
[2548.7118311665536,0,0,0,2429.5772835607963,4978.2891147273494,5391.9394049999992,"2013-03-28T22:00:00",67,60,"ON",53964.275258500013,66932.29566737001,2770.5439999999999,"OFF",-12.527866932659977,-105.06578685774001,-8.8484060000000007,"OFF",-0.20154846125000042,-166.99199929652002,-8.8484060000000007,"OFF",-7.8507806382600132,-166.99199929652002,-3.9817830000000001,"ON",53934.941998025017,65201.969169384007,2643.0740000000001,null,2475.6167769241856,0,0,0,2427.5533313628725,4903.1701082870586,2640.2630201672123,0,0,0,2603.1745667822292,5243.4375869494415,294.92722307581425,0,0,0,215.52066863712753,130.28097983278758,0,0,0,39.89943321777082,473.06659422239449,132.7991155600111,null,null,5391.9394049999992,null,75152.638700000127,12.99108398784298,11569.879583617156,195.36750538163341,10230.248037800013,157.98620789108611,-37.381297490547297,null,null,null,null,null,null,null,null,null,4903.1701082870586,73.095054242367951,0,0,0,2.0239521979237907]
[0,0,0,0,2727.8983240314346,2727.8983240314346,2912.9657120000002,"2013-03-29T13:00:00",73,62,"OFF",-4.846838104529982,-77.512112588398011,-1.5107950000000001,"OFF",-12.604528652159997,-106.45732134840001,-8.8484060000000007,"OFF",-0.37562262325000079,-166.99199929652002,-8.8484060000000007,"OFF",-9.8255309365499848,13534.700187462002,-1.7696810000000001,"ON",60102.373144770012,59045.128865980005,2933.9430000000002,null,0,0,0,0,2721.3980177985977,2721.3980177985977,0,0,0,0,3007.2052010754574,3007.2052010754574,0,0,0,0,212.54498220140249,0,0,0,0,-73.262201075457142,159.948599815835,-125.85858346102464,null,null,2912.9657120000002,null,91919.663300000131,13.684310969879679,13434.31371916687,255.03940493439384,11806.348350200013,202.44302254882635,-52.596382385567495,null,null,null,null,null,null,null,null,null,2721.3980177985977,0,0,0,0,6.5003062328369197]
[0,0,0,0,2183.1856752188996,2183.1856752188996,2361.8121510000001,"2013-03-30T04:00:00",56,55,"OFF",-8.0640050810199906,-75.14639166260001,2.5706440000000002,"OFF",-14.138794633300009,-103.697352369,-8.8484060000000007,"OFF",6.9552371375000574E-2,-166.99199929652002,-8.8484060000000007,"OFF",-9.8132254725400099,13497.130601006002,-1.7696810000000001,"ON",51437.973631704997,71938.731812656013,2378.7080000000001,null,0,0,0,0,2182.6902920132115,2182.6902920132115,0,0,0,0,2298.0641312722732,2298.0641312722732,0,0,0,0,196.01770798678854,0,0,0,0,80.64386872772684,185.39704580381169,70.023206544749982,null,null,2361.8121510000001,null,48656.198400000052,11.783672299413361,8258.2402435652166,111.31812085816333,7739.5826496000045,100.69745867518647,-10.620662182976858,null,null,null,null,null,null,null,null,null,2182.6902920132115,0,0,0,0,0.49538320568808558]
[0,0,0,0,2915.4384262303843,2915.4384262303843,6374.0619129999995,"2013-03-30T20:00:00",68,63,"check",12738.514903045007,30829.118187420005,1516.9749999999999,"check",-2662.4584770000019,33622.445815426006,1623.6210000000001,"OFF",5.8229172418500189E-2,-166.99199929652002,-8.8484060000000007,"OFF",-9.6166015486799843,-166.99199929652002,-1.7696810000000001,"ON",63861.025571159989,63093.620764978004,3244.0839999999998,null,0,0,0,0,2905.7238854903685,2905.7238854903685,0,0,0,0,3178.1571521529468,3178.1571521529468,0,0,0,0,338.36011450963133,0,0,0,0,65.926847847053068,302.68790887411365,30.254642211535355,null,null,6374.0619129999995,null,77871.196800000151,13.266291405951112,11739.708471211177,200.43456638595518,10485.792499200013,164.76236075043747,-35.672205635517713,null,null,null,null,null,null,null,null,null,2905.7238854903685,0,0,0,0,9.7145407400157637]
[0,3295.3537999762339,0,0,0,3295.3537999762339,3483.3691320000003,"2013-03-31T11:00:00",68,61,"OFF",-5.7558213663299984,-75.14639166260001,3.283436,"ON",60066.018269400003,61935.829418746005,3494.7040000000002,"OFF",-5.8885273043000272E-2,-166.99199929652002,-8.8484060000000007,"OFF",-9.5753374016999935,13618.197069402002,-1.7696810000000001,"OFF",-0.13610377298000553,-166.99199929652002,-4.0002170000000001,null,0,3290.8361427662749,0,0,0,3290.8361427662749,0,3559.2222496881673,0,0,0,3559.2222496881673,0,203.86785723372532,0,0,0,0,-64.518249688167089,0,0,0,164.91408432900198,-103.47202259289043,null,null,3483.3691320000003,null,77871.196800000151,13.144597651391791,11848.395647432371,203.7161336551608,10485.792499200013,164.76236075043747,-38.953772904723337,null,null,null,null,null,null,null,null,null,3290.8361427662749,0,4.5176572099589976,0,0,0]
[0,0,0,2594.1866940587311,0,2594.1866940587311,2679.0961729999995,"2013-04-01T02:00:00",57,53,"OFF",-10.323124903070003,-74.995608004234015,3.4207679999999998,"OFF",-5.3962941944749909,-103.67417215874002,-8.8484060000000007,"OFF",-0.12048405399999879,-166.99199929652002,-8.8484060000000007,"ON",49680.459753540017,53535.01642883,2697.3539999999998,"OFF",-6.0810282748600013,-166.99199929652002,-3.9817830000000001,null,0,0,0,2592.4617997387113,0,2592.4617997387113,0,0,0,2844.6000767837108,0,2844.6000767837108,0,0,0,104.89220026128851,0,0,0,0,-147.24607678371103,0,89.745370695089633,-162.39290634990991,null,null,2679.0961729999995,null,{"$f":" -0.6251*I1477^3 + 145.21*I1477^2 - 8340.3*I1477 + 170112","v":50738.045700000075},11.732941934893086,8648.8190228075855,119.7706502262763,7935.2762958000076,104.62382066007743,-15.146829566198875,null,null,null,null,null,null,null,null,null,2592.4617997387113,0,0,0,1.7248943200197573,0]
[0,0,0,3255.0411565253817,0,3255.0411565253817,4066.9964459999997,"2013-04-01T18:00:00",76,59,"OFF",-16.000736269760001,-75.285553132500013,3.3940410000000001,"OFF",-9.190669434019993,-109.21737053614001,-8.8484060000000007,"OFF",-0.41531162587500026,-166.99199929652002,-8.8484060000000007,"ON",61086.601567575017,52632.736770502001,4085.2809999999999,"OFF",3637.0117793749914,30101.829064470003,-3.9817830000000001,null,0,0,0,3245.1598114362428,0,3245.1598114362428,0,0,0,3647.055555582655,0,3647.055555582655,0,0,0,840.12118856375719,0,0,0,0,438.22544441734499,0,771.89682417456243,370.00108002815028,null,null,4066.9964459999997,null,100578.26240000024,13.79691376432611,14579.820403032409,296.11508862039057,12620.256665600022,227.89072423119586,-68.224364389194704,null,null,null,null,null,null,null,null,null,3245.1598114362428,0,0,0,9.8813450891389039,0]
[0,0,0,0,0,0,3048.4335470000001,"2013-04-02T09:00:00",67,63,"OFF",-18.853156614670006,-162.15736139468004,3.3261419999999999,"OFF",-10.555137786014999,-110.63216544540002,-8.8484060000000007,"OFF",-4.7961272879999992,-166.99199929652002,-8.8484060000000007,"OFF",3.7979088739900022,-166.99199929652002,-3.9817830000000001,"check",57843.146426304993,38743.692178587997,3066.7860000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-32.66574556839771,-32.66574556839771,null,null,3048.4335470000001,null,75152.638700000127,13.173624619681961,11409.561281671689,190.65195345948382,10230.248037800013,157.98620789108611,-32.66574556839771,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2831.3895900409093,0,0,0,0,2831.3895900409093,3011.4606219999996,"2013-04-02T14:00:00",63,61,"ON",59369.487401935003,61912.833687668011,3037.1210000000001,"OFF",-10.791603578159982,-108.52156318664002,-8.8484060000000007,"OFF",5.9175664430005027E-2,-166.99199929652002,-8.8484060000000007,"OFF",-0.79069967380501038,-158.64239131086001,-3.9817830000000001,"OFF",0.61076205950000118,-143.78066820059999,-3.9817830000000001,null,2746.2498276630572,0,0,0,0,2746.2498276630572,2996.5082174227091,0,0,0,0,2996.5082174227091,290.87117233694289,0,0,0,0,40.612782577291,0,0,0,0,267.35336198975915,17.094972230107231,null,null,3011.4606219999996,null,64707.210300000093,12.695880251000212,10193.418498083629,157.02339926665408,9248.3777682000091,133.50558891947031,-23.517810347183769,null,null,null,null,null,null,null,null,null,2746.2498276630572,85.139762377852094,0,0,0,0]
[2116.1557190791209,0,0,0,0,2116.1557190791209,2161.1752109999998,"2013-04-03T15:00:00",49,46,"ON",47314.089290040014,65650.205456640004,2184.9,"OFF",-12.792366381080019,-109.2405507464,-8.8484060000000007,"OFF",-4.2901778782999819E-2,-166.99199929652002,-8.8484060000000007,"OFF",-6.5008686013600032,-165.94832837644,-2.0461939999999998,"OFF",-6.6026459877999857,-117.94387751146,-3.9817830000000001,null,2057.0348535196035,0,0,0,0,2057.0348535196035,2189.3878601264501,0,0,0,0,2189.3878601264501,127.86514648039656,0,0,0,0,-4.4878601264499594,0,0,0,0,125.26899885369846,-7.0840077531480574,null,null,2161.1752109999998,null,36544.120100000058,10.823189126036914,6752.9301529227332,82.394644032323896,6601.047289400005,79.798496405625798,-2.5961476266980981,null,null,null,null,null,null,null,null,null,2057.0348535196035,59.12086555951737,0,0,0,0]
[0,0,0,0,0,0,173.86989,"2013-04-04T06:00:00",42,41,"OFF",480.15209333999888,8349.2951731340017,197.3366,"OFF",-13.367646476200008,128.07940439556,-8.8484060000000007,"OFF",-0.15048795625000291,-166.99199929652002,-8.8484060000000007,"OFF",-6.85214085128999,-159.68606223094,-1.7696810000000001,"OFF",-6.9392971389700113,-160.49263729798002,-4.0002170000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,2.7925831861395523,2.7925831861395523,null,null,173.86989,null,29657.431200000021,10.28420995769026,5767.5662636239704,66.602970374775509,5953.6985328000019,69.395553560915062,2.7925831861395523,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,2308.4844775165943,0,0,0,2308.4844775165943,2324.1665359999993,"2013-04-04T22:00:00",49,44,"OFF",-5.292640479965006,-74.450592333934011,3.197406,"ON",45552.620788979999,75087.133741008016,2335.569,"OFF",-0.20086921600000116,-166.99199929652002,-8.8484060000000007,"OFF",-8.1817370150600084,14151.526384564002,-1.7696810000000001,"OFF",-6.3584150660799965,-118.28596608156001,-3.9817830000000001,null,0,2313.369403903836,0,0,0,2313.369403903836,0,2393.8445259675022,0,0,0,2393.8445259675022,0,22.199596096163987,0,0,0,0,-58.27552596750229,0,0,0,18.268358189830437,-62.20676387383584,null,null,2324.1665359999993,null,36544.120100000058,10.701495371477593,6829.7221708659745,83.729734311959348,6601.047289400005,79.798496405625798,-3.9312379063335499,null,null,null,null,null,null,null,null,null,2313.369403903836,0,-4.8849263872416486,0,0,0]
[0,2711.8193519989013,0,0,0,2711.8193519989013,2878.9404070000001,"2013-04-05T13:00:00",63,52,"OFF",-9.3657454717500119,-73.754793005267999,3.6499670000000002,"ON",53801.285636000015,73941.846874982002,2894.038,"OFF",-0.64696938949999661,-166.99199929652002,-8.8484060000000007,"OFF",-8.5702682074099883,14120.221069462001,-3.7052700000000001,"OFF",-9.4337758806199972,-116.19862424140001,-6.1938839999999997,null,0,2712.1031379950223,0,0,0,2712.1031379950223,0,2832.437921826358,0,0,0,2832.437921826358,0,181.93486200497773,0,0,0,0,61.600078173642032,0,0,0,146.15603766189039,25.821253830554696,null,null,2878.9404070000001,null,64707.210300000093,12.148258355483268,10652.919687173708,169.28441326255765,9248.3777682000091,133.50558891947031,-35.778824343087337,null,null,null,null,null,null,null,null,null,2712.1031379950223,0,-0.28378599612096878,0,0,0]
[0,0,0,2549.4739237280719,0,2549.4739237280719,2538.2026359999995,"2013-04-06T04:00:00",58,53,"OFF",-10.433574755279995,-72.363194347936002,3.5762309999999999,"OFF",-4.4832014208799826,-102.78698771000001,-8.8484060000000007,"OFF",-0.33503186399999807,-166.99199929652002,-8.8484060000000007,"ON",48593.211348650002,72227.161003296002,2556.3049999999998,"OFF",-10.493150896760019,-117.59015873206,-3.9817830000000001,null,0,0,0,2548.3436674397826,0,2548.3436674397826,0,0,0,2654.3114751793646,0,2654.3114751793646,0,0,0,7.9613325602172154,0,0,0,0,-98.00647517936477,0,-10.037819582332432,-116.00562732191442,null,null,2538.2026359999995,null,52896.528800000029,11.806517589609925,8960.5640949623448,126.79738739190829,8138.1737072000033,108.79823524935864,-17.999152142549647,null,null,null,null,null,null,null,null,null,2548.3436674397826,0,0,0,1.1302562882892744,0]
[0,0,0,3271.7072483346542,0,3271.7072483346542,3972.1758679999998,"2013-04-06T20:00:00",69,61,"OFF",-13.027860560869991,-74.450592333934011,3.471463,"OFF",-10.443480363679978,-106.64869844764,-8.8484060000000007,"OFF",-7.1490582560000029E-2,-166.99199929652002,-8.8484060000000007,"ON",59967.150950524985,58469.634026480009,3990.3829999999998,"OFF",-10.034320710119983,-166.99199929652002,-3.9817830000000001,null,0,0,0,3262.7613123403949,0,3262.7613123403949,0,0,0,3567.9692812816784,0,3567.9692812816784,0,0,0,727.62168765960496,0,0,0,0,422.41371871832143,0,685.49034445376662,380.2823755124831,null,null,3972.1758679999998,null,80625.134100000141,13.238470399293606,12180.43046790394,213.92849457080652,10744.662605400013,171.79715136496822,-42.131343205838306,null,null,null,null,null,null,null,null,null,3262.7613123403949,0,0,0,8.9459359942593437,0]
[0,0,0,2569.0695380361349,2213.8446972734632,4782.9142353095976,4934.0908140000001,"2013-04-07T03:00:00",62,59,"OFF",-14.613217054200009,-74.450592333934011,3.4656259999999999,"OFF",-11.026429516744983,-104.87440975850001,-8.8484060000000007,"OFF",0.19698276126000303,-166.99199929652002,-8.8484060000000007,"ON",46309.04099134502,68559.602573460012,2687.6480000000001,"ON",48499.791752500023,69005.721360540003,2260.674,null,0,0,0,2569.1099496964357,2214.9615023811357,4784.0714520775709,0,0,0,2684.7706351880947,2334.0936645821926,5018.8642997702873,0,0,0,118.53805030356443,45.71249761886429,0,0,0,2.8773648119054087,-73.419664582192581,141.19353915651016,-93.59930853620574,null,null,4934.0908140000001,null,62221.807200000039,12.489467204305701,9963.8849571660339,151.10112440273866,9014.7498768000041,128.0441156368201,-23.057008765918567,null,null,null,null,null,null,null,null,null,4784.0714520775709,0,0,0,-4.0411660300833319E-2,-1.1168051076724623]
[0,0,0,3038.450858772203,2309.5292549848732,5347.9801137570757,5798.5495510000001,"2013-04-07T11:00:00",66,62,"OFF",-17.301052333619982,-74.450592333934011,3.4843630000000001,"OFF",-11.927337374759983,-105.76159420724001,-8.8484060000000007,"OFF",-0.31129341362499391,-166.99199929652002,-8.8484060000000007,"ON",54625.678493450017,67472.587066444001,3408.2959999999998,"ON",48653.184544160002,68329.853804364015,2404.4659999999999,null,0,0,0,3033.610836101635,2310.5796552771831,5344.1904913788185,0,0,0,3204.3153615480974,2434.9992926140676,5639.3146541621645,0,0,0,374.68516389836486,93.88634472281683,0,0,0,203.98063845190245,-30.533292614067705,437.41742700289683,142.29326421954991,null,null,5798.5495510000001,null,72473.210400000098,13.021444763497191,11131.362412742877,182.62525332969591,9978.3817776000087,151.47117171141107,-31.154081618284835,null,null,null,null,null,null,null,null,null,5344.1904913788185,0,0,0,4.8400226705680325,-1.0504002923098597]
[0,0,0,0,2593.3526411084854,2593.3526411084854,2779.4130679999998,"2013-04-08T02:00:00",66,61,"OFF",-18.221790147840004,-73.754793005267999,3.0600740000000002,"OFF",-13.063574014979984,-100.89094276074,-8.8484060000000007,"OFF",-0.40644630424999884,-166.99199929652002,-8.8484060000000007,"OFF",-1.0923668436800043,-159.68606223094,-2.0461939999999998,"ON",57513.188532800013,60599.013057634009,2796.096,null,0,0,0,0,2588.8528912971692,2588.8528912971692,0,0,0,0,2833.3015686544068,2833.3015686544068,0,0,0,0,207.2431087028308,0,0,0,0,-37.205568654406761,174.59634222381263,-69.85233513342493,null,null,2779.4130679999998,null,72473.210400000098,12.960597886217531,11183.621471208369,184.11793819042924,9978.3817776000087,151.47117171141107,-32.646766479018169,null,null,null,null,null,null,null,null,null,2588.8528912971692,0,0,0,0,4.4997498113161782]
[0,0,0,0,2871.227984125142,2871.227984125142,5206.40787,"2013-04-08T18:00:00",73,67,"OFF",-19.778177989080003,-72.363194347936002,3.6579570000000001,"check",-5969.2753153550048,44531.999222194005,1974.0730000000001,"OFF",-0.21121013937500496,-166.99199929652002,-8.8484060000000007,"OFF",-2.3832284633499925,-158.64239131086001,-1.7696810000000001,"ON",59054.14836040001,65004.600507146009,3239.2950000000001,null,0,0,0,0,2865.5146369003032,2865.5146369003032,0,0,0,0,3080.8901308435479,3080.8901308435479,0,0,0,0,373.78036309969684,0,0,0,0,158.40486915645215,331.12333377912728,115.74783983588259,null,null,5206.40787,null,91919.663300000131,13.988545356277982,13142.133218125799,245.10005186939591,11806.348350200013,202.44302254882635,-42.657029320569563,null,null,null,null,null,null,null,null,null,2865.5146369003032,0,0,0,0,5.7133472248387989]
[0,3479.8785419738256,0,0,2992.0916219034584,6471.970163877284,6714.59566,"2013-04-09T10:00:00",75,67,"OFF",-23.262977625720023,-73.754793005267999,3.436747,"ON",59174.727384780002,67792.048863830016,3715.884,"OFF",-0.39822778708000134,-166.99199929652002,-8.8484060000000007,"OFF",-5.3455851820249913,-159.68606223094,-1.7696810000000001,"ON",61937.448710960009,64570.055783528005,3005.893,null,0,3476.0608902445661,0,0,2984.0122187527982,6460.0731089973642,0,3678.8953386002058,0,0,3225.7856709645662,6904.6810095647725,0,239.82310975543396,0,0,21.880781247201867,0,36.988661399794182,0,0,-219.89267096456615,214.07341561112648,-230.53448495628132,null,null,6714.59566,null,97681.6875,14.18495398371142,13772.57728324926,266.81937282953419,12347.978625,219.18889743802484,-47.63047539150935,null,null,null,null,null,null,null,null,null,6460.0731089973642,0,3.8176517292595236,0,0,8.0794031506602551]
[0,3351.2095483269995,0,0,0,3351.2095483269995,3612.5837699999997,"2013-04-10T01:00:00",73,68,"OFF",-24.300032028514991,-72.363194347936002,3.2327409999999999,"ON",56539.954348400017,75025.333215038016,3626.163,"OFF",-5.2053549765999865E-2,-166.99199929652002,-8.8484060000000007,"OFF",-5.7870989887200084,-158.64239131086001,-1.7696810000000001,"OFF",-4.5140518667300045,-118.28596608156001,-6.1938839999999997,null,0,3349.498072464185,0,0,0,3349.498072464185,0,3478.6366124497672,0,0,0,3478.6366124497672,0,276.66492753581497,0,0,0,0,147.52638755023281,0,0,0,235.91867952548759,106.78013953990543,null,null,3612.5837699999997,null,91919.663300000131,14.04939223355764,13085.215612451284,243.18927055915373,11806.348350200013,202.44302254882635,-40.746248010327378,null,null,null,null,null,null,null,null,null,3349.498072464185,0,1.7114758628144955,0,0,0]
[0,2409.9540572001911,0,0,0,2409.9540572001911,2515.1576769999997,"2013-04-10T16:00:00",44,40,"OFF",-31.137702984539978,-74.450592333934011,3.3977270000000002,"ON",47730.576156799987,73953.453021780006,2528.83,"OFF",-0.22872009758499923,-166.99199929652002,-8.8484060000000007,"OFF",-7.3841479569899757,-166.99199929652002,-2.0461939999999998,"OFF",-8.3350188308799744,-118.98177343106001,-6.1754499999999997,null,0,2413.8007403820279,0,0,0,2413.8007403820279,0,2507.8085165006896,0,0,0,2507.8085165006896,0,115.029259617972,0,0,0,0,21.021483499310307,0,0,0,115.66582988252513,21.658053763863435,null,null,2515.1576769999997,null,31016.841600000043,10.269700950838626,6040.4566303300589,70.727508867709915,6081.4831104000041,71.364079132263043,0.6365702645531286,null,null,null,null,null,null,null,null,null,2413.8007403820279,0,-3.8466831818368519,0,0,0]
[0,2304.635029766906,0,0,0,2304.635029766906,2272.2157560000001,"2013-04-11T08:00:00",42,37,"OFF",-34.947470921179992,-72.363194347936002,3.3977270000000002,"ON",45468.456742800015,75387.409703466008,2285.63,"OFF",-9.0175662500006179E-2,-166.99199929652002,-8.8484060000000007,"OFF",-6.1562365589900097,-159.68606223094,-1.7696810000000001,"OFF",-11.525391458210018,-118.98177343106001,-6.1938839999999997,null,0,2309.5575793015178,0,0,0,2309.5575793015178,0,2388.4416681483094,0,0,0,2388.4416681483094,0,-23.927579301517653,0,0,0,0,-102.81166814830931,0,0,0,-23.224225440017193,-102.10831428680885,null,null,2272.2157560000001,null,29657.431200000021,10.040822448571618,5907.3709055016725,68.692199699414601,5953.6985328000019,69.395553560915062,0.7033538615004602,null,null,null,null,null,null,null,null,null,2309.5575793015178,0,-4.9225495346117896,0,0,0]
[0,2457.5183792614698,0,0,0,2457.5183792614698,2512.0524189999996,"2013-04-12T09:00:00",58,50,"OFF",-36.491761296550017,-74.450592333934011,3.7952889999999999,"ON",48725.879075574994,74394.975870978014,2522.857,"OFF",1.2453540613999857E-2,-166.99199929652002,-8.8484060000000007,"OFF",-5.1892168080200074,-158.64239131086001,-1.7696810000000001,"OFF",-10.30308957685002,-115.50281689190001,-3.9817830000000001,null,0,2460.8488617013049,0,0,0,2460.8488617013049,0,2556.6687581336037,0,0,0,2556.6687581336037,0,62.00813829869503,0,0,0,0,-33.811758133603689,0,0,0,40.755775433704798,-55.064120998593921,null,null,2512.0524189999996,null,52896.528800000029,11.623976957770942,9101.279018733303,130.05059811434887,8138.1737072000033,108.79823524935864,-21.252362864990232,null,null,null,null,null,null,null,null,null,2460.8488617013049,0,-3.3304824398351229,0,0,0]
[0,3067.9720458241873,0,0,0,3067.9720458241873,3313.1782589999998,"2013-04-12T14:00:00",74,56,"OFF",-35.684396377350005,-73.058993676602014,3.5762309999999999,"ON",59620.755218605002,61403.655103680008,3326.4140000000002,"OFF",3.7754110649974018E-3,-166.99199929652002,-8.8484060000000007,"OFF",-4.614364553540014,-165.94832837644,-3.9817830000000001,"OFF",-9.4055105890900048,-115.50281689190001,-3.9817830000000001,null,0,3063.8784804294705,0,0,0,3063.8784804294705,0,3331.6003794889848,0,0,0,3331.6003794889848,0,262.53551957052969,0,0,0,0,-5.1863794889845849,0,0,0,193.64534503328753,-74.076554026226745,null,null,3313.1782589999998,null,94794.23760000011,13.41721457629623,14130.240976762809,279.59354887857506,12076.55833440001,210.7033743413329,-68.89017453724216,null,null,null,null,null,null,null,null,null,3063.8784804294705,0,4.0935653947167339,0,0,0]
[0,2425.0844509179515,0,0,0,2425.0844509179515,2544.678355,"2013-04-13T05:00:00",56,50,"OFF",-34.849363926649993,-75.842190991265994,3.252405,"ON",48048.895001099998,74452.806084117998,2558.4960000000001,"OFF",-6.8638903625001871E-2,-166.99199929652002,-8.8484060000000007,"OFF",-3.4753581567599778,-166.99199929652002,-2.0461939999999998,"OFF",-10.712462216540013,-118.98177343106001,-6.1754499999999997,null,0,2428.7689050263816,0,0,0,2428.7689050263816,0,2521.596992664694,0,0,0,2521.596992664694,0,129.72709497361848,0,0,0,0,36.899007335306123,0,0,0,114.41808494776068,21.589997309448322,null,null,2544.678355,null,48656.198400000052,11.479437913015058,8477.1046751052236,116.00646870104427,7739.5826496000045,100.69745867518647,-15.309010025857802,null,null,null,null,null,null,null,null,null,2428.7689050263816,0,-3.6844541084301454,0,0,0]
[0,3069.701880215549,0,0,0,3069.701880215549,3414.5026050000001,"2013-04-13T20:00:00",67,56,"OFF",-35.539594546575003,-71.667395019270003,3.4309090000000002,"ON",59650.955590200007,62664.770833500006,3425.69,"OFF",-1.7090452062999646E-2,-166.99199929652002,-8.8484060000000007,"OFF",-3.7770133001999784,-159.68606223094,-1.7696810000000001,"OFF",-10.37211787843,-118.98177343106001,-4.0002170000000001,null,0,3065.5831019734173,0,0,0,3065.5831019734173,0,3319.4420485507449,0,0,0,3319.4420485507449,0,360.10689802658271,0,0,0,0,106.2479514492552,0,0,0,316.12033212228243,62.261385544954919,null,null,3414.5026050000001,null,75152.638700000127,12.747696478724338,11790.779428334907,201.97277379538639,10230.248037800013,157.98620789108611,-43.986565904300278,null,null,null,null,null,null,null,null,null,3065.5831019734173,0,4.1187782421316115,0,0,0]
[0,0,0,3057.9501677642761,0,3057.9501677642761,3375.453301,"2013-04-14T12:00:00",74,64,"OFF",-38.838416598284994,-74.450592333934011,3.5103300000000002,"OFF",-0.83243925444998068,-107.84749229728,-8.8484060000000007,"OFF",-0.56817640049499984,-166.99199929652002,-8.8484060000000007,"ON",53687.829447559998,60255.408549908003,3393.64,"OFF",-12.345539909950025,-118.98177343106001,-4.0002170000000001,null,0,0,0,3053.748960769728,0,3053.748960769728,0,0,0,3280.7514169967699,0,3280.7514169967699,0,0,0,339.89103923027187,0,0,0,0,112.88858300323,0,288.58246313519584,61.580006908153962,null,null,3375.453301,null,94794.23760000011,13.903989594533513,13635.544957149476,262.01195043640894,12076.55833440001,210.7033743413329,-51.308576095076035,null,null,null,null,null,null,null,null,null,3053.748960769728,0,0,0,4.2012069945481016,0]
[0,0,0,3037.6853147748279,0,3037.6853147748279,3340.5765699999997,"2013-04-15T03:00:00",70,67,"OFF",-38.632971746560017,-74.450592333934011,3.068165,"OFF",-7.2242114275200002,-104.87224413332001,-8.8484060000000007,"OFF",-0.19917110287500303,-166.99199929652002,-8.8484060000000007,"ON",51369.362334600002,60626.965664124,3359.1869999999999,"OFF",5257.3346683699901,32767.007827658002,-3.9817830000000001,null,0,0,0,3034.9800688910905,0,3034.9800688910905,0,0,0,3240.3311896667446,0,3240.3311896667446,0,0,0,324.20693110890943,0,0,0,0,118.85581033325525,0,289.43911478882114,84.087994013166963,null,null,3340.5765699999997,null,83410.700000000012,13.698502526774668,12178.075645417162,213.85507382464337,11006.505800000001,179.08725750455508,-34.767816320088286,null,null,null,null,null,null,null,null,null,3034.9800688910905,0,0,0,2.7052458837374616,0]
[0,0,0,3533.3644648973368,3205.3558462109013,6738.7203111082381,7682.3738599999997,"2013-04-15T18:00:00",81,70,"OFF",-38.856494467259999,-74.450592333934011,3.7626719999999998,"OFF",-12.763758477330002,-108.5447433969,-8.8484060000000007,"OFF",-0.50039294899999542,-166.99199929652002,-8.8484060000000007,"ON",58775.306817255005,68377.353183312007,3934.4850000000001,"ON",64119.524856675023,65391.68595598601,3761.8229999999999,null,0,0,0,3525.3234087732835,3195.2953556155576,6720.6187643888406,0,0,0,3718.065395875059,3446.7102765705035,7164.775672445563,0,0,0,409.16159122671661,566.52764438444228,0,0,0,216.41960412494109,315.11272342949633,923.02959995393644,478.87269189721491,null,null,7682.3738599999997,null,115066.74090000021,14.960094430759636,15383.157029197631,326.9251458367392,13982.17364460002,274.2655101795167,-52.659635657222509,null,null,null,null,null,null,null,null,null,6720.6187643888406,0,0,0,8.0410561240532843,10.060490595343708]
[0,0,0,3314.5015451425775,2915.9167830907486,6230.4183282333261,6901.5735910000003,"2013-04-16T08:00:00",72,66,"OFF",-39.22236399892499,-75.14639166260001,3.4944030000000001,"OFF",-14.455058735699993,-108.04247877182002,-8.8484060000000007,"OFF",-0.5483617170000018,-166.99199929652002,-8.8484060000000007,"ON",57366.976970100004,67982.591796334003,3907.9270000000001,"ON",61033.920396539987,65629.182850726007,3007.8490000000002,null,0,0,0,3307.6182973363948,2908.612892565262,6216.2311899016568,0,0,0,3493.1413695264418,3132.0899230486093,6625.2312925750512,0,0,0,600.30870266360535,99.236107434738187,0,0,0,414.78563047355829,-124.24092304860915,657.61694565656501,248.61684298317061,null,null,6901.5735910000003,null,89061.715200000035,13.830280341879591,12879.23498272287,236.34360798744649,11537.701228800002,194.41574354566797,-41.927864441778524,null,null,null,null,null,null,null,null,null,6216.2311899016568,0,0,0,6.8832478061826805,7.3038905254866222]
[0,0,0,3515.414797215024,3285.5413916245407,6800.9561888395647,7569.5023719999999,"2013-04-17",74,69,"OFF",-37.407548894859993,-73.754793005267999,3.2791839999999999,"OFF",-18.200207989600006,-109.43409347082,-8.8484060000000007,"OFF",-4.9420947500001318E-2,-166.99199929652002,-8.8484060000000007,"ON",59094.401616800002,67895.172726568009,4005.1019999999999,"ON",66786.715758279999,65592.543681014009,3578.8180000000002,null,0,0,0,3507.119236194093,3272.957011419458,6780.0762476135515,0,0,0,3706.0851302190003,3543.1344895435964,7249.2196197625963,0,0,0,497.98276380590687,305.8609885805422,0,0,0,299.01686978099951,35.683510456403837,762.61791985795981,293.47454770891409,null,null,7569.5023719999999,null,94794.23760000011,14.208223980931816,13343.57309220617,251.92920686982214,12076.55833440001,210.7033743413329,-41.225832528489235,null,null,null,null,null,null,null,null,null,6780.0762476135515,0,0,0,8.295561020931018,12.584380205082653]
[0,0,0,0,2830.4666281108202,2830.4666281108202,5863.3092109999998,"2013-04-17T16:00:00",82,71,"check",33523.002411599999,44232.581488974007,2123.5430000000001,"OFF",-18.409780449320003,-109.93635809590002,-8.8484060000000007,"OFF",-0.8825386688750031,-166.99199929652002,-8.8484060000000007,"OFF",-1.7409728321299858,-158.64239131086001,-2.0369769999999998,"ON",54698.878576519986,52837.556787526002,3759.5,null,0,0,0,0,2827.9155107335901,2827.9155107335901,0,0,0,0,3138.1991568406729,3138.1991568406729,0,0,0,0,931.58448926640995,0,0,0,0,621.30084315932709,880.01922190511345,569.7355757980306,null,null,5863.3092109999998,null,117939.30320000008,15.118857595610601,15601.615724489782,335.58932891474797,14252.194500800008,284.02406155345153,-51.565267361296435,null,null,null,null,null,null,null,null,null,2827.9155107335901,0,0,0,0,2.5511173772301845]
[2793.4915958991924,0,0,0,2244.2298526431196,5037.7214485423119,5556.5415069999999,"2013-04-18T07:00:00",47,45,"ON",63678.30558031,76754.32023374601,3262.761,"OFF",-17.752631710839989,-111.32797279490001,-8.8484060000000007,"OFF",-0.59991408924999734,-166.99199929652002,-8.8484060000000007,"OFF",-3.9889202414600073,-166.99199929652002,-1.7696810000000001,"ON",53378.387931680001,70863.779639976012,2313.2469999999998,null,2699.2958367149186,0,0,0,2242.5656849335878,4941.8615216485068,2839.0505759526368,0,0,0,2373.5739508127526,5212.6245267653894,563.46516328508142,0,0,0,70.681315066412026,423.71042404736318,0,0,0,-60.326950812752784,634.03559752681315,363.2725924099301,null,null,5556.5415069999999,null,33987.03270000004,10.675179472443098,6367.4868956974724,75.921458389605164,6360.681073800004,75.810577564924898,-0.11088082468026528,null,null,null,null,null,null,null,null,null,4941.8615216485068,94.195759184273811,0,0,0,1.6641677095317391]
[2053.7808368305928,0,0,0,0,2053.7808368305928,2087.1387239999995,"2013-04-18T22:00:00",47,41,"ON",45615.555860105014,72613.757181262001,2110.587,"OFF",-17.841355294000049,-109.2405507464,-8.8484060000000007,"OFF",-2.2754262824999923E-2,-166.99199929652002,-8.8484060000000007,"OFF",-4.6509383951799954,-159.65133201972,-1.7696810000000001,"OFF",-5.7739245026400141,-166.99199929652002,-3.9817830000000001,null,1997.8433955673627,0,0,0,0,1997.8433955673627,2086.2683392746922,0,0,0,0,2086.2683392746922,112.74360443263731,0,0,0,0,24.318660725307836,0,0,0,0,110.18280045071981,21.757856743390334,null,null,2087.1387239999995,null,33987.03270000004,10.431791963324457,6516.0487899854324,78.3713815468424,6360.681073800004,75.810577564924898,-2.5608039819175019,null,null,null,null,null,null,null,null,null,1997.8433955673627,55.937441263230085,0,0,0,0]
[2039.590432982267,0,0,0,0,2039.590432982267,2150.3657239999993,"2013-04-19T14:00:00",61,45,"ON",45223.44900276501,79535.263694056019,2173.8139999999999,"OFF",-17.667707875650013,-109.2405507464,-8.8484060000000007,"OFF",0.43157837849999603,-166.99199929652002,-8.8484060000000007,"OFF",-4.2484283632000004,-165.98305858766,-1.7696810000000001,"OFF",-5.3366603536400081,-155.11907955968002,-3.9817830000000001,null,1984.3759909761243,0,0,0,0,1984.3759909761243,2043.5568744445302,0,0,0,0,2043.5568744445302,189.43800902387557,0,0,0,0,130.25712555546966,0,0,0,0,151.15173448364169,91.970851015235795,null,null,2150.3657239999993,null,59794.286900000065,11.554864666276185,10349.629983034691,161.13099620573524,8786.5629686000066,122.84472166550138,-38.286274540233862,null,null,null,null,null,null,null,null,null,1984.3759909761243,55.21444200614269,0,0,0,0]
[2058.0471954388199,0,0,0,0,2058.0471954388199,2174.6209179999996,"2013-04-20T05:00:00",44,39,"ON",45733.022287289998,78700.046228802006,2200.0140000000001,"OFF",-19.427851867690048,-109.74281537148001,-8.8484060000000007,"OFF",2.8617595384499924E-2,-166.99199929652002,-8.8484060000000007,"OFF",-4.2948704397900048,-159.65133201972,-3.7144870000000001,"OFF",-8.6463678861000126,-118.28596608156001,-3.9817830000000001,null,2001.8922932045805,0,0,0,0,2001.8922932045805,2065.5725676303509,0,0,0,0,2065.5725676303509,198.12170679541964,0,0,0,0,134.44143236964919,0,0,0,0,198.19989285777231,134.51961843200186,null,null,2174.6209179999996,null,31016.841600000043,10.208854073558966,6076.4589985342182,71.285893069910372,6081.4831104000041,71.364079132263043,7.8186062352671115E-2,null,null,null,null,null,null,null,null,null,2001.8922932045805,56.154902234239444,0,0,0,0]
[2473.3878296893126,0,0,0,0,2473.3878296893126,2636.9707769999995,"2013-04-20T21:00:00",61,47,"ON",56361.524122935014,78104.042116764016,2660.7139999999999,"OFF",-21.953333744639991,-113.22185211898001,-8.8484060000000007,"OFF",-1.469746187499695E-2,-166.99199929652002,-8.8484060000000007,"OFF",-3.9420698881199834,-166.99199929652002,-2.0369769999999998,"OFF",-7.859547134879997,-118.98177343106001,-4.0094339999999997,null,2395.8765451437107,0,0,0,0,2395.8765451437107,2496.5871885736224,0,0,0,0,2496.5871885736224,264.83745485628924,0,0,0,0,164.12681142637757,0,0,0,0,229.39416164642131,128.68351821650964,null,null,2636.9707769999995,null,59794.286900000065,11.676558420835505,10241.765551963306,158.2880148753693,8786.5629686000066,122.84472166550138,-35.443293209867917,null,null,null,null,null,null,null,null,null,2395.8765451437107,77.511284545601939,0,0,0,0]
[2399.9209533371918,2635.8080959893559,0,0,0,5035.7290493265482,5519.1020280000002,"2013-04-21T13:00:00",67,57,"ON",52898.310244080014,80173.537601274002,2612.4690000000001,"ON",50964.02041644002,53271.620261104006,2923.4450000000002,"OFF",-0.2658425374999962,-166.99199929652002,-8.8484060000000007,"OFF",-4.0265217342700161,-166.99199929652002,-3.9817830000000001,"OFF",-8.2074905295600082,-118.98177343106001,-3.9817830000000001,null,2329.4680967260342,2637.8867488107276,0,0,0,4967.3548455367618,2407.8069933001361,2909.2645243513502,0,0,0,5317.0715176514859,283.00090327396583,285.5582511892726,0,0,0,204.66200669986392,14.180475648649917,0,0,0,526.25926105948304,176.54258894475845,null,null,5519.1020280000002,null,75152.638700000127,12.808543356003998,11734.767430017304,200.2861012948415,10230.248037800013,157.98620789108611,-42.299893403755391,null,null,null,null,null,null,null,null,null,4967.3548455367618,70.452856611157586,-2.0786528213716338,0,0,0]
[0,2380.7146243938423,0,0,0,2380.7146243938423,2433.6641929999996,"2013-04-22T02:00:00",55,50,"OFF",-4.7857280348999982,-75.14639166260001,4.1211650000000004,"ON",47110.798207829997,76601.178450184001,2446.355,"OFF",6.5711122374996225E-2,-166.99199929652002,-8.8484060000000007,"OFF",-3.2380497865799933,-158.64239131086001,-3.9817830000000001,"OFF",-9.2821839210099988,-117.94676501170001,-3.9817830000000001,null,0,2384.8694760690978,0,0,0,2384.8694760690978,0,2464.191579575795,0,0,0,2464.191579575795,0,61.485523930902218,0,0,0,0,-17.836579575794985,0,0,0,48.891650360999563,-30.430453145697641,null,null,2433.6641929999996,null,46654.737500000047,11.411214633385185,8176.997628894781,109.60901148537711,7551.4453250000042,97.015137915474455,-12.593873569902655,null,null,null,null,null,null,null,null,null,2384.8694760690978,0,-4.154851675255486,0,0,0]
[0,3206.4859830835985,0,0,0,3206.4859830835985,3374.2066899999995,"2013-04-22T18:00:00",76,64,"OFF",-6.8836525723699928,-74.450592333934011,3.897856,"ON",56660.361474714999,62631.227705712008,3385.1759999999999,"OFF",-0.37501055141999867,-166.99199929652002,-8.8484060000000007,"OFF",-4.1831990126500198,-166.99199929652002,-2.0369769999999998,"OFF",-10.259108444969996,-166.99199929652002,-3.9817830000000001,null,0,3204.7007844844852,0,0,0,3204.7007844844852,0,3436.6092653531437,0,0,0,3436.6092653531437,0,180.47521551551472,0,0,0,0,-51.433265353143724,0,0,0,123.86500833176279,-108.04347253689565,null,null,3374.2066899999995,null,100578.26240000024,14.101148150724411,14265.258590993993,284.50093141494779,12620.256665600022,227.89072423119586,-56.610207183751925,null,null,null,null,null,null,null,null,null,3204.7007844844852,0,1.7851985991133006,0,0,0]
[0,2832.2995401413477,0,3001.9990263341838,0,5834.2985664755315,6692.2096030000002,"2013-04-23T09:00:00",52,50,"OFF",-9.1568490591000025,-74.450592333934011,3.9757920000000002,"ON",56077.283097300009,76800.119195886,3317.3589999999999,"OFF",-0.27477812587499495,-166.99199929652002,-8.8484060000000007,"ON",58909.889572100008,73862.665201734009,3383.7049999999999,"OFF",-11.937820701659984,-118.28596608156001,-3.9817830000000001,null,0,2830.9879780493175,0,2993.9819593638495,0,5824.9699374131669,0,2943.2722781496018,0,3137.9984459248121,0,6081.2707240744139,0,486.37102195068246,0,389.72304063615047,0,0,374.08672185039813,0,245.7065540751878,0,870.57476481509593,614.27397815384893,null,null,6692.2096030000002,null,41170.179200000071,11.224263914264345,7335.9250128962103,92.908218617390418,7035.8968448000069,87.388920845653359,-5.5192977717370582,null,null,null,null,null,null,null,null,null,5824.9699374131669,0,1.3115620920302717,0,8.0170669703343265,0]
[0,0,0,2328.2272347337157,0,2328.2272347337157,2207.538528,"2013-04-24",41,39,"OFF",-16.256283493404997,-73.754793005267999,3.7605729999999999,"OFF",-4.6557526071599993,-109.2405507464,-8.8484060000000007,"OFF",1.8810992925000367E-2,-166.99199929652002,-8.8484060000000007,"ON",42942.417761100005,70647.417642825996,2227.6410000000001,"OFF",-13.009499942180016,-119.67758078056001,-6.1662330000000001,null,0,0,0,2329.7031808965849,0,2329.7031808965849,0,0,0,2419.1355795989457,0,2419.1355795989457,0,0,0,-102.06218089658478,0,0,0,0,-191.49457959894562,0,-99.714040588664943,-189.14643929102579,null,null,2207.538528,null,29175.192900000024,10.14607827102388,5751.0285492910634,66.359141599693913,5908.3681326000024,68.707281907613748,2.3481403079198344,null,null,null,null,null,null,null,null,null,2329.7031808965849,0,0,0,-1.4759461628691497,0]
[0,0,0,0,0,0,-19.579411,"2013-04-24T16:00:00",60,47,"OFF",-21.353686923509983,-166.99199929652002,3.868865,"OFF",-8.0302783126650006,-166.99199929652002,-8.8484060000000007,"OFF",-8.0032608871499503E-2,-166.99199929652002,-8.8484060000000007,"OFF",-0.44950516176999245,-166.99199929652002,-1.7696810000000001,"OFF",-10.790776920200027,-166.99199929652002,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-31.696379167127347,-31.696379167127347,null,null,-19.579411,null,57428.400000000081,11.595913046473532,9904.9380190833363,149.60198036720965,8564.1696000000084,117.9056012000823,-31.696379167127347,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2103.1577400214046,0,0,0,1980.9044606041994,4084.062200625604,4173.6145689999994,"2013-04-25T07:00:00",52,45,"ON",46963.424257650004,77619.583743163996,2198.982,"OFF",-11.579807567964988,-107.82342979528002,-8.8484060000000007,"OFF",-0.41218475550000633,-166.99199929652002,-8.8484060000000007,"OFF",-5.4313181415000118,-165.84389711776001,-3.677619,"ON",44675.045119380018,74635.969849342015,1996.0070000000001,null,2044.7009731660371,0,0,0,1983.7688474872327,4028.4698206532698,2116.2851039580078,0,0,0,2059.6474080409489,4175.9325119989571,154.28102683396287,0,0,0,12.238152512767329,82.696896041992204,0,0,0,-63.640408040948842,157.10815573616659,9.6454643904797592,null,null,4173.6145689999994,null,41170.179200000071,10.920029527866042,7540.3054716914157,96.799944456216963,7035.8968448000069,87.388920845653359,-9.4110236105636034,null,null,null,null,null,null,null,null,null,4028.4698206532698,58.456766855367505,0,0,0,-2.8643868830333759]
[2002.6042978734938,0,0,0,0,2002.6042978734938,2073.2244049999995,"2013-04-25T23:00:00",64,52,"ON",44191.127326829985,73889.013641424011,2098.8939999999998,"OFF",-11.680649582490002,-108.72970382894002,-8.8484060000000007,"OFF",1.6942250315000005,-166.99199929652002,-8.8484060000000007,"OFF",-4.7142048172100068,-165.84389711776001,-3.9817830000000001,"OFF",-2.8684103646100159,-118.98177343106001,-3.9910000000000001,null,1949.272094621185,0,0,0,0,1949.272094621185,2026.9800808088419,0,0,0,0,2026.9800808088419,149.62190537881474,0,0,0,0,71.913919191157902,0,0,0,0,110.15431193660569,32.446325748948851,null,null,2073.2244049999995,null,67246.745600000082,12.234822837907998,10992.679908963592,178.6979348235927,9487.0940864000077,139.23034138138365,-39.467593442209051,null,null,null,null,null,null,null,null,null,1949.272094621185,53.332203252308773,0,0,0,0]
[0,2107.4108619214321,0,0,0,2107.4108619214321,2298.8625709999997,"2013-04-26T04:00:00",62,52,"OFF",-2.3013650252399867,-73.798434363062015,3.5785429999999998,"ON",40989.308871600013,77937.184707062013,2312.096,"OFF",3.1128170250003175E-2,-166.99199929652002,-8.8484060000000007,"OFF",-5.1030258598900025,-166.99199929652002,-3.9817830000000001,"OFF",-5.7320462477000147,-119.33260471022001,-3.9817830000000001,null,0,2114.0713104452602,0,0,0,2114.0713104452602,0,2169.4557508213352,0,0,0,2169.4557508213352,0,198.02468955473978,0,0,0,0,142.64024917866482,0,0,0,165.83582764948642,110.45138727341146,null,null,2298.8625709999997,null,62221.807200000039,12.063539063348077,10315.680477057482,160.23297754207346,9014.7498768000041,128.0441156368201,-32.188861905253361,null,null,null,null,null,null,null,null,null,2114.0713104452602,0,-6.6604485238281086,0,0,0]
[0,3320.1820924697954,0,3387.0405780766687,0,6707.2226705464636,7420.2918929999996,"2013-04-27T04:00:00",68,66,"OFF",-8.8607519152150136,-74.450592333934011,3.7390819999999998,"ON",57267.216061769999,77378.525598128006,3588.1239999999998,"OFF",3.9904191139500139E-2,-166.99199929652002,-8.8484060000000007,"ON",58720.821838880001,76503.829587925997,3841.259,"OFF",-9.475277184800003,-116.89443159090001,-3.9817830000000001,null,0,3317.9180642034689,0,3379.079171192689,0,6696.9972353961584,0,3433.8463537772855,0,3505.557970693867,0,6939.404324471152,0,270.20593579653087,0,462.17982880731097,0,0,154.27764622271434,0,335.70102930613302,0,701.46989127622373,459.06280220122926,null,null,7420.2918929999996,null,77871.196800000151,13.448832037790092,11580.365727103826,195.6782340780556,10485.792499200013,164.76236075043747,-30.915873327618129,null,null,null,null,null,null,null,null,null,6696.9972353961584,0,2.264028266326477,0,7.9614068839796346,0]
[0,0,0,3187.6989539692554,0,3187.6989539692554,3764.0390269999998,"2013-04-27T20:00:00",66,59,"OFF",-12.640820841809996,-75.842190991265994,3.8366220000000002,"OFF",-12.02750934546,-107.8489360474,-8.8484060000000007,"OFF",0.42113205500000045,-166.99199929652002,-8.8484060000000007,"ON",59752.438778165,58696.591545344003,3781.8809999999999,"OFF",-11.967622588320003,-118.63102236024001,-3.9817830000000001,null,0,0,0,3178.9536041987803,0,3178.9536041987803,0,0,0,3478.0040472784358,0,3478.0040472784358,0,0,0,602.92739580121952,0,0,0,0,303.87695272156407,0,567.2313403033304,268.18089722367495,null,null,3764.0390269999998,null,72473.210400000098,12.838904131658211,11289.625603059909,187.16722720930022,9978.3817776000087,151.47117171141107,-35.696055497889148,null,null,null,null,null,null,null,null,null,3178.9536041987803,0,0,0,8.7453497704750589,0]
[0,0,0,3078.8890383400249,0,3078.8890383400249,3284.7344719999996,"2013-04-28T11:00:00",67,62,"OFF",-18.589918502714998,-75.14639166260001,3.4110670000000001,"OFF",-14.795058830360002,-110.14682478006002,-8.8484060000000007,"OFF",-0.56384382424999824,-166.99199929652002,-8.8484060000000007,"ON",55448.416910694992,72836.327303928003,3303.002,"OFF",-12.207990511780013,-117.59015873206,-3.9817830000000001,null,0,0,0,3073.4652838930351,0,3073.4652838930351,0,0,0,3209.3236896167678,0,3209.3236896167678,0,0,0,229.53671610696483,0,0,0,0,93.678310383232201,0,195.3209840724262,59.462578348693569,null,null,3284.7344719999996,null,75152.638700000127,13.112777742402301,11462.504768456776,192.20193992562474,10230.248037800013,157.98620789108611,-34.215732034538632,null,null,null,null,null,null,null,null,null,3073.4652838930351,0,0,0,5.423754446989733,0]
[0,0,0,3105.8244049936739,2829.993598556513,5935.8180035501864,6729.6492090000002,"2013-04-29T03:00:00",63,60,"OFF",-18.588335387669993,-73.711151647474011,3.3550209999999998,"OFF",-14.992934695529986,-110.63216544540002,-8.8484060000000007,"OFF",0.24965776275000146,-166.99199929652002,-8.8484060000000007,"ON",57385.238516630008,68868.484890800013,3438.8249999999998,"ON",64729.911822449998,70823.418803288005,3305.1660000000002,null,0,0,0,3098.9682100962236,2819.5378720985282,5918.5060821947518,0,0,0,3275.2324626239806,3014.9157725728001,6290.1482351967807,0,0,0,339.85678990377619,485.628127901472,0,0,0,163.59253737601921,290.25022742720012,800.68304531765716,429.04089231562835,null,null,6729.6492090000002,null,64707.210300000093,12.63503337372055,10242.50722353988,158.30746140706128,9248.3777682000091,133.50558891947031,-24.80187248759097,null,null,null,null,null,null,null,null,null,5918.5060821947518,0,0,0,6.8561948974502229,10.455726457984838]
[0,0,0,3506.9931646808604,0,3506.9931646808604,4810.2833019999998,"2013-04-29T18:00:00",81,66,"OFF",-1.5338720272600084,-74.450592333934011,3.478691,"OFF",16888.698971099999,23918.945113068003,915.26980000000003,"OFF",-0.23524136787500219,-166.99199929652002,-8.8484060000000007,"ON",60914.783030699989,66936.546709389993,3904.3649999999998,"OFF",-4.7471027329500082,-166.99199929652002,-3.9817830000000001,null,0,0,0,3497.1771577057434,0,3497.1771577057434,0,0,0,3717.3126176194851,0,3717.3126176194851,0,0,0,407.18784229425637,0,0,0,0,187.0523823805147,0,344.42649400738719,124.29103409364552,null,null,4810.2833019999998,null,115066.74090000021,14.716706921640993,15637.566408391811,337.02685846638587,13982.17364460002,274.2655101795167,-62.761348286869179,null,null,null,null,null,null,null,null,null,3497.1771577057434,0,0,0,9.816006975117034,0]
[0,0,0,3265.3629378960914,0,3265.3629378960914,3681.4122070000003,"2013-04-30T09:00:00",68,64,"OFF",-9.1253745459150082,-74.450592333934011,3.8396859999999999,"OFF",-7.6976733652500045,-111.32797279490001,-8.8484060000000007,"OFF",-0.52812055394999924,-166.99199929652002,-8.8484060000000007,"ON",57765.545545279994,62068.726617292006,3701.4540000000002,"OFF",-6.9621367615099921,-166.99199929652002,-6.1846670000000001,null,0,0,0,3258.1822951295553,0,3258.1822951295553,0,0,0,3502.1717720390538,0,3502.1717720390538,0,0,0,443.27170487044486,0,0,0,0,199.28222796094633,0,409.20667521051087,165.2171983010123,null,null,3681.4122070000003,null,77871.196800000151,13.327138283230772,11686.109222410285,198.82739041037149,10485.792499200013,164.76236075043747,-34.065029659934027,null,null,null,null,null,null,null,null,null,3258.1822951295553,0,0,0,7.1806427665360388,0]
[3274.8390788580987,0,0,3476.1237615006721,0,6750.9628403587703,7605.9584050000003,"2013-04-30T17:00:00",81,68,"ON",62695.62863911999,66854.774306759995,3699.578,"OFF",-10.762551693540003,-107.17871515836001,-8.8484060000000007,"OFF",-0.14075601137500107,-166.99199929652002,-8.8484060000000007,"ON",59036.0718633,62542.781969194009,3928.0590000000002,"OFF",-1.0222216935699868,-166.99199929652002,-3.9817830000000001,null,3180.689115613673,0,0,3467.885716256932,0,6648.5748318706046,3408.7215653854205,0,0,3719.5843195139723,0,7128.3058848993933,518.88888438632694,0,0,460.17328374306817,0,290.85643461457948,0,0,208.47468048602786,0,921.41380993119424,441.68275690240648,null,null,7605.9584050000003,null,115066.74090000021,14.838400676200315,15509.318478582218,331.91386837771756,13982.17364460002,274.2655101795167,-57.648358198200867,null,null,null,null,null,null,null,null,null,6648.5748318706046,94.149963244425635,0,0,8.2380452437400891,0]
[3289.1851039375292,0,0,0,0,3289.1851039375292,3657.9687379999996,"2013-05-01T16:00:00",80,69,"ON",62213.224369799995,70154.080205988008,3685.8319999999999,"OFF",-14.079673665119991,-108.70419757682001,-8.8484060000000007,"OFF",-6.56760493365003E-2,-166.99199929652002,-8.8484060000000007,"OFF",1.198900014970006,-166.99199929652002,-3.9817830000000001,"OFF",-9.2679622229600085,-149.45781450580003,-6.1846670000000001,null,3196.0257032668355,0,0,0,0,3196.0257032668355,3388.6894649554438,0,0,0,0,3388.6894649554438,489.80629673316434,0,0,0,0,297.1425350445561,0,0,0,0,436.30656802897323,243.64280634036498,null,null,3657.9687379999996,null,112180.80000000005,14.800875233033445,15158.671123668211,318.14919710148155,13710.895200000004,264.64946839729043,-53.499728704191114,null,null,null,null,null,null,null,null,null,3196.0257032668355,93.159400670693685,0,0,0,0]
[2292.6390047521104,0,0,0,0,2292.6390047521104,2404.6126219999996,"2013-05-02T07:00:00",49,47,"ON",51917.592546710002,74556.683905252008,2430.2730000000001,"OFF",-15.26270400928,-109.93635809590002,-8.8484060000000007,"OFF",2.253220450000407E-2,-166.99199929652002,-8.8484060000000007,"OFF",-2.7182427447700039,-166.99199929652002,-3.9817830000000001,"OFF",-11.35141976087,-166.99199929652002,-3.9817830000000001,null,2224.465128672779,0,0,0,0,2224.465128672779,2328.3184518895955,0,0,0,0,2328.3184518895955,205.80787132722116,0,0,0,0,101.95454811040463,0,0,0,0,203.86253809635184,100.00921487953531,null,null,2404.6126219999996,null,36544.120100000058,10.884036003316574,6715.1780991654878,81.743829636495121,6601.047289400005,79.798496405625798,-1.9453332308693234,null,null,null,null,null,null,null,null,null,2224.465128672779,68.173876079331421,0,0,0,0]
[2292.6568777342454,0,0,0,0,2292.6568777342454,2371.7046219999993,"2013-05-02T08:00:00",50,46,"ON",51918.044780249991,74433.900978379999,2397.3649999999998,"OFF",-15.142654196649996,-107.1531286979,-8.8484060000000007,"OFF",-0.30037864512500767,-166.99199929652002,-8.8484060000000007,"OFF",-2.1659988160300157,-165.84389711776001,-3.9817830000000001,"OFF",-10.437707500779975,-166.99199929652002,-3.9817830000000001,null,2224.4820815356375,0,0,0,0,2224.4820815356375,2329.0145954094673,0,0,0,0,2329.0145954094673,172.88291846436232,0,0,0,0,68.350404590532435,0,0,0,0,168.47450726559987,63.941993391769969,null,null,2371.7046219999993,null,37984.500000000058,10.872286982852879,6987.3983385293168,86.518381492841286,6736.4430000000057,82.109970294078821,-4.4084111987624652,null,null,null,null,null,null,null,null,null,2224.4820815356375,68.174796198607964,0,0,0,0]
[0,2280.3068619168394,0,0,0,2280.3068619168394,2362.7598149999999,"2013-05-02T23:00:00",46,40,"OFF",-1.3751886071999881,-73.899897913162008,3.481004,"ON",44933.831854960015,76719.309293336017,2376.1,"OFF",-0.17109953625000479,-166.99199929652002,-8.8484060000000007,"OFF",-4.312946560369995,-166.99199929652002,-3.9817830000000001,"OFF",-12.069721644469984,-166.99199929652002,-3.9910000000000001,null,0,2285.4640851884592,0,0,0,2285.4640851884592,0,2357.01353378658,0,0,0,2357.01353378658,0,90.635914811540715,0,0,0,0,19.086466213419953,0,0,0,88.904958116823337,17.355509518702576,null,null,2362.7598149999999,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,2285.4640851884592,0,-5.1572232716198414,0,0,0]
[0,3145.4855747183155,0,0,0,3145.4855747183155,3374.2910429999997,"2013-05-03T15:00:00",66,47,"OFF",-5.5350644893199945,-73.754793005267999,3.9349129999999999,"ON",61669.016923750023,66090.452993232,3384.9560000000001,"OFF",0.18974364725000628,-166.99199929652002,-8.8484060000000007,"OFF",-4.4495187658600006,-165.84389711776001,-1.7696810000000001,"OFF",-14.18845748411001,-166.99199929652002,-3.9817830000000001,null,0,3139.6351915468199,0,0,0,3139.6351915468199,0,3373.1690698431025,0,0,0,3373.1690698431025,0,245.32080845318023,0,0,0,0,11.786930156897597,0,0,0,189.35632176601823,-44.177556530264411,null,null,3374.2910429999997,null,72473.210400000098,12.108741604302285,11970.395069666047,207.43565839857308,9978.3817776000087,151.47117171141107,-55.964486687162008,null,null,null,null,null,null,null,null,null,3139.6351915468199,0,5.8503831714956505,0,0,0]
[0,2270.5238440221751,0,0,0,2270.5238440221751,2414.8891119999998,"2013-05-04T06:00:00",44,40,"OFF",-10.981269602379996,-72.363194347936002,3.58392,"ON",44717.505578200005,76221.62456447001,2427.8130000000001,"OFF",-0.3394703803750006,-166.99199929652002,-8.8484060000000007,"OFF",-5.2641826433700052,-166.99199929652002,-3.677619,"OFF",-13.042041019455022,-166.99199929652002,-3.9817830000000001,null,0,2275.773908586274,0,0,0,2275.773908586274,0,2348.6205856303327,0,0,0,2348.6205856303327,0,152.03909141372606,0,0,0,0,79.192414369667404,0,0,0,152.6756616782792,79.828984634220532,null,null,2414.8891119999998,null,31016.841600000043,10.269700950838626,6040.4566303300589,70.727508867709915,6081.4831104000041,71.364079132263043,0.6365702645531286,null,null,null,null,null,null,null,null,null,2275.773908586274,0,-5.2500645640989205,0,0,0]
[0,2718.8584179470226,0,2713.7746228539027,0,5432.6330408009253,5742.3348019999994,"2013-05-04T21:00:00",56,46,"OFF",-13.365351605699999,-74.450592333934011,4.0632080000000004,"ON",53936.376963089991,76856.738263092018,2914.0360000000001,"OFF",2.0558936536500042E-2,-166.99199929652002,-8.8484060000000007,"ON",52508.928830680001,75278.21406939,2837.0749999999998,"OFF",-11.338216930739971,-166.99199929652002,-3.9910000000000001,null,0,2719.051516757751,0,2710.3596021032063,0,5429.4111188609568,0,2822.3087315716034,0,2816.0837020254703,0,5638.3924335970732,0,194.9844832422491,0,126.71539789679355,0,0,91.727268428396656,0,20.991297974529516,0,302.36279129929147,93.381476563174985,null,null,5742.3348019999994,null,48656.198400000052,11.236050403896417,8660.7298207076656,120.03454851493765,7739.5826496000045,100.69745867518647,-19.337089839751187,null,null,null,null,null,null,null,null,null,5429.4111188609568,0,-0.19309881072831558,0,3.4150207506963852,0]
[0,0,0,2620.1438669326285,0,2620.1438669326285,2610.5458749999998,"2013-05-05T23:00:00",57,51,"OFF",-20.040831516859988,-75.14639166260001,3.9794700000000001,"OFF",-11.144795884250003,-107.1531286979,-8.8484060000000007,"OFF",0.25700063812500223,-166.99199929652002,-8.8484060000000007,"ON",50304.002818020002,61424.396980404003,2628.2449999999999,"OFF",-13.243499941139994,-166.99199929652002,-3.9817830000000001,null,0,0,0,2618.0642052372737,0,2618.0642052372737,0,0,0,2804.406217687249,0,2804.406217687249,0,0,0,10.180794762726237,0,0,0,0,-176.16121768724906,0,-6.9835316983047875,-193.32554414828007,null,null,2610.5458749999998,null,50738.045700000075,11.611248180333764,8739.4645109620978,121.78814712110845,7935.2762958000076,104.62382066007743,-17.164326461031024,null,null,null,null,null,null,null,null,null,2618.0642052372737,0,0,0,2.0796616953548437,0]
[0,0,0,2414.4843787483792,0,2414.4843787483792,2388.1300279999996,"2013-05-06T03:00:00",55,51,"OFF",-21.580809584619999,-74.450592333934011,3.8466230000000001,"OFF",-12.405940006600003,-107.66397561536002,-8.8484060000000007,"OFF",-0.26088873162499654,-166.99199929652002,-8.8484060000000007,"ON",45202.528011795017,72693.748958744007,2405.962,"OFF",-12.904089621999978,-166.99199929652002,-3.9817830000000001,null,0,0,0,2415.0146828021088,0,2415.0146828021088,0,0,0,2504.5371899274724,0,2504.5371899274724,0,0,0,-9.0526828021088477,0,0,0,0,-98.575189927472366,0,-20.741092189367208,-110.26359931473073,null,null,2388.1300279999996,null,46654.737500000047,11.472061510664844,8133.6275013219047,108.70354730273282,7551.4453250000042,97.015137915474455,-11.688409387258361,null,null,null,null,null,null,null,null,null,2415.0146828021088,0,0,0,-0.53030405372965106,0]
[0,0,0,3217.6547290705339,0,3217.6547290705339,3320.7399429999996,"2013-05-06T18:00:00",74,60,"OFF",-24.238025746654987,-73.204098584496009,3.9395380000000002,"OFF",-13.354162784174987,-107.12762244578002,-8.8484060000000007,"OFF",-0.65131421687499436,-166.99199929652002,-8.8484060000000007,"ON",59623.668514440011,61819.022013204005,3338.4789999999998,"OFF",-13.241165035489978,-166.99199929652002,-3.9817830000000001,null,0,0,0,3209.006418331338,0,3209.006418331338,0,0,0,3470.3254853382109,0,3470.3254853382109,0,0,0,129.47258166866186,0,0,0,0,-131.8464853382111,0,69.608116679248553,-191.7109503276244,null,null,3320.7399429999996,null,94794.23760000011,13.660602085414872,13878.486029720441,270.56783933074621,12076.55833440001,210.7033743413329,-59.864464989413307,null,null,null,null,null,null,null,null,null,3209.006418331338,0,0,0,8.6483107391959493,0]
[0,0,0,3206.9555694178962,2605.9253032356796,5812.8808726535754,6026.8401009999998,"2013-05-07T10:00:00",75,62,"OFF",-27.554978870760021,-73.899897913162008,3.9349129999999999,"OFF",-15.149952588150031,-110.44720501336,-8.8484060000000007,"OFF",-9.1935303975003366E-2,-166.99199929652002,-8.8484060000000007,"ON",58000.79026217998,65583.544305266012,3266.442,"ON",56896.05823852498,63612.721120624003,2774.16,null,0,0,0,3199.6047055188915,2601.8699322616285,5801.4746377805204,0,0,0,3409.7747640307675,2812.3709663879672,6222.1457304187352,0,0,0,66.837294481108529,172.29006773837136,0,0,0,-143.33276403076752,-38.210966387967346,180.73718559693069,-239.93390704128407,null,null,6026.8401009999998,null,97681.6875,13.880719597313117,14074.441431539068,277.57907406057404,12347.978625,219.18889743802484,-58.390176622549205,null,null,null,null,null,null,null,null,null,5801.4746377805204,0,0,0,7.3508638990047075,4.0553709740511295]
[0,0,0,0,2422.4586955763152,2422.4586955763152,2732.3896009999999,"2013-05-08T01:00:00",66,58,"OFF",-27.356194326599997,-75.842190991265994,3.974094,"OFF",-17.735647733504983,-109.08109656648,-8.8484060000000007,"OFF",0.14116590074999802,-166.99199929652002,-8.8484060000000007,"OFF",1.0304801561600048,-159.79049348962002,-1.7696810000000001,"ON",55687.152917494997,66612.472932454009,2747.8820000000001,null,0,0,0,0,2419.272558159862,2419.272558159862,0,0,0,0,2594.3922217657628,2594.3922217657628,0,0,0,0,328.60944184013806,0,0,0,0,153.48977823423729,291.35596795445269,116.2363043485519,null,null,2732.3896009999999,null,72473.210400000098,12.778057254378549,11343.384828733071,188.72464559709647,9978.3817776000087,151.47117171141107,-37.253473885685395,null,null,null,null,null,null,null,null,null,2419.272558159862,0,0,0,0,3.1861374164532208]
[3167.7121300086783,0,0,0,3186.8320387007525,6354.5441687094308,7181.8065069999993,"2013-05-08T18:00:00",84,67,"ON",61428.69279995501,71009.590381262009,3546.0450000000001,"OFF",-19.447098090375,-111.32797279490001,-8.8484060000000007,"OFF",-0.59610797362500412,-166.99199929652002,-8.8484060000000007,"OFF",0.46289097701000997,-166.99199929652002,-1.7696810000000001,"ON",66435.84799437999,67409.703727884,3655.2280000000001,null,3076.7755506129511,0,0,0,3174.6325037459164,6251.408054358868,3256.1660316433527,0,0,0,3419.867162266275,6676.0331939096277,469.26944938704901,0,0,0,480.59549625408363,289.87896835664742,0,0,0,235.36083773372502,885.1425180040676,460.5173784533074,null,null,7181.8065069999993,null,123629.28960000002,15.069423180083433,16407.965735993825,368.62731467974061,14787.053222400002,303.90488704267557,-64.722427637065039,null,null,null,null,null,null,null,null,null,6251.408054358868,90.936579395727222,0,0,0,12.199534954836054]
[0,3235.459584665206,0,0,2773.6546720978363,6009.1142567630422,6546.3155970000007,"2013-05-09T09:00:00",69,65,"OFF",-4.3379493606399908,-74.450592333934011,3.9948480000000002,"ON",56510.91750096,71888.810141840004,3615.3870000000002,"OFF",-0.61749248787500166,-166.99199929652002,-8.8484060000000007,"OFF",-3.4598379890899942,-158.64239131086001,-2.0738449999999999,"ON",58451.276986079996,67660.186352870005,2937.8560000000002,null,0,3233.7835455771224,0,0,2768.4238100521929,6002.2073556293153,0,3384.6243437142184,0,0,2954.8234070021222,6339.447750716341,0,381.6034544228778,0,0,169.43218994780727,0,230.76265628578176,0,0,-16.967407002121945,515.69908786954329,178.45869278251797,null,null,6546.3155970000007,null,80625.134100000141,13.481857908412247,11960.53758283458,207.13370786611006,10744.662605400013,171.79715136496822,-35.336556501141843,null,null,null,null,null,null,null,null,null,6002.2073556293153,0,1.6760390880835985,0,0,5.2308620456433346]
[0,3087.8903959575023,0,0,0,3087.8903959575023,3562.764944,"2013-05-10T09:00:00",66,65,"OFF",-8.1393521763749881,-74.450592333934011,3.789752,"ON",54045.870725604982,61600.069286672006,3575.4830000000002,"OFF",-5.3007703506000335E-2,-166.99199929652002,-8.8484060000000007,"OFF",-4.0946638969599922,-165.84389711776001,-3.677619,"OFF",-7.2497920759999888,-118.98177343106001,-3.9817830000000001,null,0,3087.9997558839323,0,0,0,3087.9997558839323,0,3308.1751072361235,0,0,0,3308.1751072361235,0,487.48324411606791,0,0,0,0,267.30789276387668,0,0,0,460.68406778516203,240.50871643297083,null,null,3562.764944,null,72473.210400000098,13.203985395336172,10977.475092572977,178.27034804231693,9978.3817776000087,151.47117171141107,-26.799176330905851,null,null,null,null,null,null,null,null,null,3087.9997558839323,0,-0.10935992642998826,0,0,0]
[0,3238.1414939195438,0,3455.2766088060234,0,6693.4181027255672,7313.6388889999998,"2013-05-10T15:00:00",80,67,"OFF",-9.363165173099997,-72.508299255829996,3.5792950000000001,"ON",55323.533754250006,66887.090246945998,3564.558,"OFF",7.9682494499995704E-2,-166.99199929652002,-8.8484060000000007,"ON",59312.214852025005,64429.161813484003,3758.3409999999999,"OFF",-7.1675235530499988,-118.98177343106001,-3.9910000000000001,null,0,3237.3415171417332,0,3446.8188344676505,0,6684.1603516093837,0,3421.1388813561134,0,3680.4470917034105,0,7101.5859730595239,0,327.21648285826677,0,311.52216553234939,0,0,143.41911864388658,0,77.893908296589416,0,580.34197546882046,162.91635401868024,null,null,7313.6388889999998,null,112180.80000000005,14.679181478474124,15284.339956489324,323.04614131908619,13710.895200000004,264.64946839729043,-58.396672921795755,null,null,null,null,null,null,null,null,null,6684.1603516093837,0,0.79997677781057064,0,8.4577743383729285,0]
[0,2712.6582188083066,0,2916.8361196320898,0,5629.4943384403959,6259.469126,"2013-05-11T06:00:00",60,57,"OFF",-18.165860513644997,-73.754793005267999,3.4733149999999999,"ON",52448.643687334988,67164.867770034005,3015.6210000000001,"OFF",-8.4060046794000781E-2,-166.99199929652002,-8.8484060000000007,"ON",55586.394302049994,65054.233427938008,3253.2049999999999,"OFF",-11.879023532110024,-119.67758078056001,-3.9817830000000001,null,0,2713.8245166599581,0,2911.3353569793949,0,5625.1598736393535,0,2873.2129575489284,0,3106.9088092267707,0,5980.1217667756991,0,301.79648334004196,0,341.86964302060505,0,0,142.40804245107165,0,146.29619077322923,0,624.17937861793519,269.21748548158905,null,null,6259.469126,null,57428.400000000081,12.204381819270136,9411.1116565237862,137.39234894279411,8564.1696000000084,117.9056012000823,-19.486747742711813,null,null,null,null,null,null,null,null,null,5625.1598736393535,0,-1.1662978516515068,0,5.5007626526949025,0]
[0,0,0,3022.1699077326771,0,3022.1699077326771,3353.8047409999995,"2013-05-11T22:00:00",70,57,"OFF",-21.600404153714994,-73.754793005267999,4.1583360000000003,"OFF",-10.802632533409996,-109.05350489752001,-8.8484060000000007,"OFF",0.15501170917499993,-166.99199929652002,-8.8484060000000007,"ON",57831.244456410008,60283.064385540005,3371.3249999999998,"OFF",-12.28419334163001,-118.28596608156001,-3.9817830000000001,null,0,0,0,3014.9899519767232,0,3014.9899519767232,0,0,0,3275.6757409322804,0,3275.6757409322804,0,0,0,356.33504802327661,0,0,0,0,95.649259067719413,0,303.50909024159398,42.823301286036781,null,null,3353.8047409999995,null,83410.700000000012,13.090033753978064,12744.153539657831,231.91321528623772,11006.505800000001,179.08725750455508,-52.825957781682632,null,null,null,null,null,null,null,null,null,3014.9899519767232,0,0,0,7.1799557559538698,0]
[0,0,0,2953.2323470573442,0,2953.2323470573442,3179.7418659999998,"2013-05-12T13:00:00",73,53,"OFF",-26.650710192329992,-75.14639166260001,4.0634610000000002,"OFF",-12.087153561679973,-108.56952777396,-8.8484060000000007,"OFF",3.664557088649973E-2,-166.99199929652002,-8.8484060000000007,"ON",57864.168263440006,60091.783536308008,3197.357,"OFF",-12.146136738469986,-118.28596608156001,-3.9817830000000001,null,0,0,0,2946.0418133741264,0,2946.0418133741264,0,0,0,3208.2223721393243,0,3208.2223721393243,0,0,0,251.31518662587359,0,0,0,0,-10.865372139324336,0,179.05693197623603,-83.1236267889619,null,null,3179.7418659999998,null,91919.663300000131,13.136689074362735,13994.342528725669,274.70127719846391,11806.348350200013,202.44302254882635,-72.258254649637564,null,null,null,null,null,null,null,null,null,2946.0418133741264,0,0,0,7.1905336832178364,0]
[0,0,0,2607.8722127278243,0,2607.8722127278243,3441.3624529999997,"2013-05-13T04:00:00",56,49,"OFF",-28.345198964489999,-75.285553132500013,3.5684420000000001,"OFF",799.15749886000003,20222.503659998001,704.21119999999996,"OFF",-4.8421988537499606E-2,-166.99199929652002,-8.8484060000000007,"ON",50009.8994819,70679.91004136001,2746.413,"OFF",-11.662768816090008,-117.65977957118,-3.9817830000000001,null,0,0,0,2605.9611331967567,0,2605.9611331967567,0,0,0,2727.1575506456556,0,2727.1575506456556,0,0,0,140.45186680324332,0,0,0,0,19.255449354344364,0,124.15994074533413,2.9635232964351701,null,null,3441.3624529999997,null,48656.198400000052,11.418591035735398,8522.2770914076118,116.98938473309566,7739.5826496000045,100.69745867518647,-16.291926057909194,null,null,null,null,null,null,null,null,null,2605.9611331967567,0,0,0,1.9110795310675712,0]
[0,3047.7683035069481,0,0,2759.6059311725558,{"$f":"SUM(A2500:E2500)","v":5807.3742346795043},{"$f":"N2500+R2500+V2500+Z2500+AD2500","v":6690.4216219999998},"2013-05-13T20:00:00",76,59,"OFF",-2.6645868319500017,-73.754793005267999,3.9426559999999999,"ON",57214.130124124982,62498.073840478006,3551.5619999999999,"OFF",-0.3287781232499935,-166.99199929652002,-8.8484060000000007,"OFF",-3.6937280197850026,-166.99199929652002,-2.0646279999999999,"ON",63944.180515875007,62187.049960460005,3145.83,null,0,3045.5839576065382,0,0,2749.8793695626086,{"$f":"SUM(AF2500:AJ2500)","v":5795.4633271691473},0,3281.3180548898745,0,0,3031.8758296168326,{"$f":"SUM(AL2500:AP2500)","v":6313.193884506707},{"$f":"IF($K2500=\"ON\",$N2500-AF2500,0)","v":0},{"$f":"IF($O2500=\"ON\",$R2500-AG2500,0)","v":505.97804239346169},{"$f":"IF($S2500=\"ON\",$V2500-AH2500,0)","v":0},{"$f":"IF($W2500=\"ON\",$Z2500-AI2500,0)","v":0},{"$f":"IF($AA2500=\"ON\",$AD2500-AJ2500,0)","v":395.95063043739128},{"$f":"IF($K2500=\"ON\",$N2500-AL2500,0)","v":0},{"$f":"IF($O2500=\"ON\",$R2500-AM2500,0)","v":270.24394511012542},{"$f":"IF($S2500=\"ON\",$V2500-AN2500,0)","v":0},{"$f":"IF($W2500=\"ON\",$Z2500-AO2500,0)","v":0},{"$f":"IF($AA2500=\"ON\",$AD2500-AP2500,0)","v":113.95417038316737},{"$f":"SUM(AR2500:AV2500)+BN2500","v":833.70430844165821},{"$f":"SUM(AW2500:BA2500)+BN2500","v":315.97375110409808},null,null,{"$f":"N2500+R2500+V2500+Z2500+AD2500","v":6690.4216219999998},null,100578.26240000024,{"$f":"19.5285952781395+42*-0.3035722016559+BH2500*0.0000340867411548605+J2500*0.0608468772796604","v":13.79691376432611},{"$f":"BH2500*1000/(500*BI2500)","v":14579.820403032409},{"$f":"0.00000128*BJ2500^2+0*BJ2500+24.024","v":296.11508862039057},{"$f":"0.094*BH2500 + 3165.9","v":12620.256665600022},{"$f":"0.00000128*BL2500^2+0*BL2500+24.024","v":227.89072423119586},{"$f":"BM2500-BK2500","v":-68.224364389194704},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF2500:AJ2500)","v":5795.4633271691473},{"$f":"A2500-AF2500","v":0},{"$f":"B2500-AG2500","v":2.1843459004098804},{"$f":"C2500-AH2500","v":0},{"$f":"D2500-AI2500","v":0},{"$f":"E2500-AJ2500","v":9.7265616099471117}]
[0,0,0,0,3062.8751870361334,3062.8751870361334,3320.8276900000001,"2013-05-14T11:00:00",82,67,"OFF",-8.2357710843999996,-74.450592333934011,3.929338,"OFF",-19.488895955545004,-106.27027549952001,-8.8484060000000007,"OFF",-0.58288611350000119,-166.99199929652002,-8.8484060000000007,"OFF",-4.4535766704799968,-166.99199929652002,-3.686836,"ON",63592.775560000016,63707.543420172005,3338.2820000000002,null,0,0,0,0,3053.3407036558442,3053.3407036558442,0,0,0,0,3318.2510873313586,3318.2510873313586,0,0,0,0,284.94129634415594,0,0,0,0,20.030912668641577,223.09716443322066,-41.813219242293712,null,null,3320.8276900000001,null,117939.30320000008,14.875470086491958,15856.884187760601,345.86819346438682,14252.194500800008,284.02406155345153,-61.844131910935289,null,null,null,null,null,null,null,null,null,3053.3407036558442,0,0,0,0,9.5344833802892026]
[0,3084.8628501710223,0,3331.451166728144,0,6416.3140168991667,7368.0297469999996,"2013-05-15",74,65,"OFF",-10.619167381200004,-73.754793005267999,4.3449359999999997,"ON",53994.443504820003,66835.780971848013,3539.1529999999998,"OFF",0.60270133699999995,-166.99199929652002,-8.8484060000000007,"ON",58349.243631959973,62310.282054036004,3837.3620000000001,"OFF",-5.1857829958200181,-118.28596608156001,-3.9817830000000001,null,0,3085.0076288922437,0,3323.7988878795745,0,6408.8065167718178,0,3259.5072582995872,0,3570.7181229346033,0,6830.2253812341905,0,454.14537110775609,0,513.56311212042556,0,0,279.6457417004126,0,266.64387706539674,0,918.46928704861875,497.05042258624638,null,null,7368.0297469999996,null,94794.23760000011,13.964836471813173,13576.132852158227,259.94257052089586,12076.55833440001,210.7033743413329,-49.239196179562953,null,null,null,null,null,null,null,null,null,6408.8065167718178,0,-0.14477872122142799,0,7.6522788485694946,0]
[0,0,0,0,0,0,-21.812565000000003,"2013-05-15T17:00:00",73,70,"OFF",-15.170154094349993,-75.14639166260001,3.5528659999999999,"OFF",-1.3480235625599863,-104.18285345102001,-8.8484060000000007,"OFF",3.8096289624993174E-2,-166.99199929652002,-8.8484060000000007,"OFF",2.062018737330003,-165.87870753732003,-3.686836,"OFF",-6.4447853465450073,-118.98177343106001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-36.998260553652756,-36.998260553652756,null,null,-21.812565000000003,null,91919.663300000131,14.17108598811696,12972.846735540037,239.4412831024791,11806.348350200013,202.44302254882635,-36.998260553652756,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,2515.6184409518592,0,2379.6445791853257,0,4895.2630201371849,5699.9581619999999,"2013-05-16T08:00:00",67,64,"OFF",-22.34064482586999,-76.537990319932007,3.9203510000000001,"ON",44192.849731240021,67655.133227450002,2663.7179999999998,"OFF",-0.63323216512500147,-166.99199929652002,-8.8484060000000007,"ON",38658.796281614981,69088.207617395994,3045.15,"OFF",-1.5674858420899771,-118.28596608156001,-3.9817830000000001,null,0,2521.1745444191729,0,2382.6520293991562,0,4903.8265738183291,0,2632.3677447899886,0,2462.0619751136755,0,5094.4297199036646,0,142.54345558082696,0,662.49797060084393,0,0,31.350255210011255,0,583.08802488632455,0,773.90433758437712,583.30119149904203,null,null,5699.9581619999999,null,75152.638700000127,13.234471496961621,11357.104621405353,189.12329648837994,10230.248037800013,157.98620789108611,-31.137088597293825,null,null,null,null,null,null,null,null,null,4903.8265738183291,0,-5.5561034673137328,0,-3.0074502138304524,0]
[0,0,0,3461.8448738045417,3184.4476234382446,6646.2924972427863,9945.1475119999996,"2013-05-17",74,71,"OFF",-25.24033342896001,-78.068750447164007,4.0979179999999999,"check",160.65598661999414,51981.982445580004,2473.7759999999998,"OFF",-1.0377813418750006,-166.99199929652002,-8.8484060000000007,"ON",56881.662568970001,64372.903683808006,3866.857,"ON",62783.975527199997,69851.494243338006,3609.2649999999999,null,0,0,0,3455.3048620750437,3175.5775642113249,6630.8824262863691,0,0,0,3671.7739480754326,3371.9959421907756,7043.7698902662087,0,0,0,411.55213792495624,433.68743578867497,0,0,0,195.08305192456737,237.26905780922425,807.86817713845483,394.98071315861523,null,null,9945.1475119999996,null,94794.23760000011,14.329917735491136,13230.255658093794,248.07477091650927,12076.55833440001,210.7033743413329,-37.371396575176362,null,null,null,null,null,null,null,null,null,6630.8824262863691,0,0,0,6.5400117294980191,8.8700592269196932]
[0,0,0,0,0,0,-19.466493,"2013-05-17T15:00:00",89,76,"OFF",-26.901314581600001,-73.754793005267999,3.9817830000000001,"OFF",-16.125910116600014,-112.53246143668001,-8.8484060000000007,"OFF",-0.24254910987500014,-166.99199929652002,-8.8484060000000007,"OFF",-20.27711223587,-166.99199929652002,-1.7696810000000001,"OFF",-25.100125785249993,-116.19862424140001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-42.50206058694522,-42.50206058694522,null,null,-19.466493,null,137357.58810000028,16.084998033066547,17078.968591432716,397.38869522834585,16077.513281400026,354.88663464140063,-42.50206058694522,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,3307.8924107650919,0,3431.8782489944419,3181.9255242728691,9921.696184032402,11305.368063,"2013-05-18T06:00:00",73,69,"OFF",-3.5182464405399894,-75.14639166260001,3.8924690000000002,"ON",55249.760696774989,68032.056279612007,3653.8719999999998,"OFF",-0.2099216951250012,-166.99199929652002,-8.8484060000000007,"ON",57595.096599089993,67823.795324802006,3892.1190000000001,"ON",64489.134535630001,69358.766389883996,3764.3330000000001,null,0,3307.1408439056881,0,3424.7953742938212,3171.5401926730769,9903.4764108725867,0,3481.6954982366265,0,3614.1911031011732,3383.0786056966335,10478.965207034433,0,346.7311560943117,0,467.32362570617897,592.79280732692314,0,172.17650176337338,0,277.92789689882693,381.25439430336655,1367.9874564642059,792.49866030235887,null,null,11305.368063,null,91919.663300000131,14.110239110837302,13028.78889265621,241.30315521203434,11806.348350200013,202.44302254882635,-38.860132663207992,null,null,null,null,null,null,null,null,null,9903.4764108725867,0,0.75156685940373791,0,7.0828747006207777,10.385331599792153]
[0,3457.8065435749895,0,0,3258.1979923616077,6716.0045359365977,7444.4077539999998,"2013-05-18T22:00:00",82,71,"OFF",-1.4982310708749838,-75.14639166260001,3.6108410000000002,"ON",56426.025153989998,73695.863937870003,3697.9209999999998,"OFF",-0.54859593950000118,-166.99199929652002,-8.8484060000000007,"OFF",-19.880845685884999,-165.87870753732003,-1.7696810000000001,"ON",64401.521145780011,73699.200604814003,3753.4940000000001,null,0,3456.1691039594675,0,0,3247.8607683433088,6704.0298723027763,0,3594.9108072980544,0,0,3418.5757950285843,7013.4866023266386,0,241.7518960405323,0,0,505.63323165669135,0,103.01019270194547,0,0,334.91820497141589,695.81986033592716,386.36313031206492,null,null,7444.4077539999998,null,117939.30320000008,15.118857595610601,15601.615724489782,335.58932891474797,14252.194500800008,284.02406155345153,-51.565267361296435,null,null,null,null,null,null,null,null,null,6704.0298723027763,0,1.6374396155219983,0,0,10.337224018298912]
[0,0,0,0,0,0,-21.309911,"2013-05-19T13:00:00",87,74,"OFF",-9.5116524047999906,-73.058993676602014,4.3504659999999999,"OFF",-44.126907922000008,-112.02378014440001,-8.8484060000000007,"OFF",-2.1048756296250026,-166.99199929652002,-8.8484060000000007,"OFF",-19.28877531062999,-165.87870753732003,-1.7696810000000001,"OFF",-25.514490452640008,-119.67758078056001,-6.1938839999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-47.770291266393201,-47.770291266393201,null,null,-21.309911,null,131970.16469999996,15.779664571579776,16726.612166102313,382.14182983065848,15571.095481799995,334.37153856426528,-47.770291266393201,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,3304.7205017546589,0,3528.6988272762769,3321.0968177467021,10154.516146777638,11104.951644000001,"2013-05-20T04:00:00",75,70,"OFF",-13.018874103974992,-75.14639166260001,4.0610499999999998,"ON",54609.172285599976,75287.269590976008,3573.7,"OFF",-0.48002730262500498,-166.99199929652002,-8.8484060000000007,"ON",58692.887960869986,70583.066491644015,3913.723,"ON",66655.680956149998,74725.19360675801,3622.3159999999998,null,0,3304.4283231360555,0,3520.7254383692548,3308.6211407536275,10133.774902258938,0,3423.3599246711592,0,3693.7634240171915,3481.7263971689395,10598.849745857289,0,269.27167686394432,0,392.99756163074517,313.69485924637229,0,150.34007532884061,0,219.95957598280847,140.58960283106035,934.46391528132915,469.38907168297681,null,null,11104.951644000001,null,97681.6875,14.367494615550399,13597.59514289652,260.68907989775749,12347.978625,219.18889743802484,-41.500182459732656,null,null,null,null,null,null,null,null,null,10133.774902258938,0,0.29217861860342964,0,7.9733889070221267,12.475676993074558]
[3318.8280812406729,0,0,3602.5580773575484,0,6921.3861585982213,7656.9824049999997,"2013-05-20T19:00:00",84,73,"ON",59873.374543289996,70241.812088279999,3624.5279999999998,"OFF",-2.3295019094400038,-109.93635809590002,-8.8484060000000007,"OFF",-4.8117499287500323E-2,-166.99199929652002,-8.8484060000000007,"ON",58118.569109955002,62636.746039504011,4054.1329999999998,"OFF",-5.2720895992099939,-116.19862424140001,-3.9817830000000001,null,3230.5682399940033,0,0,3595.0273441334857,0,6825.595584127489,3409.2190625826561,0,0,3839.8862423990718,0,7249.1053049817274,393.95976000599649,0,0,459.1056558665141,0,215.30893741734371,0,0,214.24675760092805,0,804.4523886779275,380.94266782368862,null,null,7656.9824049999997,null,123629.28960000002,15.434504443761396,16019.858629147086,352.51791423725871,14787.053222400002,303.90488704267557,-48.61302719458314,null,null,null,null,null,null,null,null,null,6825.595584127489,88.259841246669566,0,0,7.5307332240627147,0]
[0,3368.6633589526327,0,3088.7982605072593,3294.0996818223784,9751.5613012822705,11150.175561,"2013-05-21T10:00:00",80,72,"OFF",-4.9136994752800058,-166.99199929652002,3.6499670000000002,"ON",54461.056119599998,71599.827513654003,3607.2260000000001,"OFF",-0.21790890287499265,-166.99199929652002,-8.8484060000000007,"ON",49395.230506654996,66984.382963366006,3873.4050000000002,"ON",64311.426260509987,72375.161432264009,3674.7429999999999,null,0,3368.4732565576696,0,3087.2711961733912,3283.8296177026587,9739.5740704337186,0,3512.1115709677265,0,3232.0846633349088,3466.3297774066837,10210.526011709318,0,238.75274344233048,0,786.13380382660898,390.91338229734129,0,95.11442903227362,0,641.32033666509142,208.41322259331628,1369.4231096234166,898.47116834781718,null,null,11150.175561,null,112180.80000000005,14.983415864872425,14973.995384190077,311.02628834015457,13710.895200000004,264.64946839729043,-46.376819942864131,null,null,null,null,null,null,null,null,null,9739.5740704337186,0,0.19010239496310533,0,1.5270643338681111,10.270064119719791]
[0,2000.715032265271,0,2191.9567531792491,0,4192.6717854445196,5333.7203329999993,"2013-05-22T02:00:00",58,56,"OFF",-9.9513455719499877,-114.71653453488001,3.9236230000000001,"ON",37774.068146590005,72547.047904884006,2302.3739999999998,"OFF",3.7830681309999985,-166.99199929652002,-8.8484060000000007,"ON",38550.417629760021,64878.344559152007,3042.4650000000001,"OFF",5.7588962008199793,-118.28596608156001,-6.1938839999999997,null,0,2008.3220515672606,0,2194.917449529215,0,4203.2395010964756,0,2071.3289236618457,0,2289.2980728565585,0,4360.6269965184038,0,294.05194843273921,0,847.54755047078515,0,0,231.0450763381541,0,753.16692714344163,0,1126.7060953775442,969.3185999556157,null,null,5333.7203329999993,null,52896.528800000029,11.989058221448905,8824.1341101115049,123.69163877533872,8138.1737072000033,108.79823524935864,-14.893403525980077,null,null,null,null,null,null,null,null,null,4203.2395010964756,0,-7.6070193019895669,0,-2.9606963499659287,0]
[0,0,0,0,0,0,-19.493315000000003,"2013-05-22T17:00:00",84,66,"OFF",-20.57092657050001,-75.842190991265994,3.9549609999999999,"OFF",0.16785762977499433,-109.93635809590002,-8.8484060000000007,"OFF",-1.3414039686249981,-166.99199929652002,-8.8484060000000007,"OFF",1.3246423581300011,-166.99199929652002,-1.7696810000000001,"OFF",-4.8474339407200073,-116.19862424140001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-67.522232076329487,-67.522232076329487,null,null,-19.493315000000003,null,123629.28960000002,15.008576302803773,16474.485934672521,371.42711911900506,14787.053222400002,303.90488704267557,-67.522232076329487,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,3072.4111387278786,3322.8153442721286,6395.2264830000076,7555.6784669999997,"2013-05-23T08:00:00",76,72,"OFF",-21.29163551912001,-166.99199929652002,3.3572790000000001,"OFF",-4.1485542399999895,-112.02378014440001,-8.8484060000000007,"OFF",-0.64194531687499967,-166.99199929652002,-8.8484060000000007,"ON",49080.498477829999,59667.906521910001,3899.4780000000001,"ON",64927.489208070008,66911.040457270006,3670.54,null,0,0,0,3071.0620550304452,3311.9689116024124,6383.0309666328576,0,0,0,3267.7107465168601,3553.6258047226233,6821.336551239483,0,0,0,828.41594496955486,358.57108839758757,0,0,0,631.76725348313994,116.91419527737662,1147.4701729925655,709.16458838593962,null,null,7555.6784669999997,null,100578.26240000024,14.587923168961694,13789.250359365442,267.40758460577274,12620.256665600022,227.89072423119586,-39.516860374576879,null,null,null,null,null,null,null,null,null,6383.0309666328576,0,0,0,1.3490836974333433,10.846432669716251]
[3197.1059803192325,3088.7235780327674,0,3403.8791441734975,0,9689.7087025254968,10902.576811000001,"2013-05-24",78,71,"ON",59046.968585099989,65029.801967574007,3567.8870000000002,"ON",50513.580988264999,65403.147727772011,3468.5410000000002,"OFF",9.1670287000500048E-2,-166.99199929652002,-8.8484060000000007,"ON",55842.648230429993,59715.221421676004,3878.9789999999998,"OFF",-15.826584835319998,-118.28596608156001,-3.9817830000000001,null,3111.10093221856,3091.1143101351554,0,3398.1255198083627,0,9600.340762162079,3331.1859628652301,3255.1867579231575,0,3652.8227695768505,0,10239.195490365239,456.78606778144012,377.42668986484478,0,480.85348019163712,0,236.7010371347701,213.35424207684264,0,226.15623042314928,0,1269.6986043186575,630.84387611549755,null,null,10902.576811000001,null,106383.78480000014,14.724967630999576,14449.44226241107,291.27056856928147,13165.975771200012,245.90293505001699,-45.367633519264473,null,null,null,null,null,null,null,null,null,9600.340762162079,86.005048100672411,-2.3907321023880286,0,5.7536243651347831,0]
[3240.7626604280122,3254.5543709581702,0,3351.3730571692331,0,9846.6900885554169,11007.304811,"2013-05-24T04:00:00",74,71,"ON",59858.417107499998,65180.70593845001,3593.4079999999999,"ON",53225.351514859998,64565.700470666001,3558.3209999999999,"OFF",-4.1925827499993823E-3,-166.99199929652002,-8.8484060000000007,"ON",54891.015191750004,59831.836327202007,3868.4059999999999,"OFF",-15.783304632900016,-118.98177343106001,-3.9817830000000001,null,3152.8652686337809,3255.2204780379407,0,3346.313718525058,0,9754.3994651967805,3377.6862763557292,3444.9141702498,0,3591.021653272167,0,10413.622099877695,440.54273136621896,303.10052196205925,0,522.09228147494196,0,215.7217236442707,113.4068297501999,0,277.38434672783296,0,1228.3641382280439,569.14150354712717,null,null,11007.304811,null,94794.23760000011,14.329917735491136,13230.255658093794,248.07477091650927,12076.55833440001,210.7033743413329,-37.371396575176362,null,null,null,null,null,null,null,null,null,9754.3994651967805,87.897391794231226,-0.66610707977042694,0,5.0593386441751136,0]
[1938.8604526609302,0,0,2156.5360153537094,2081.7063187579788,6177.1027867726189,7283.0651880000005,"2013-05-25T06:00:00",68,66,"ON",34754.386960240001,67495.48654751401,2152.509,"OFF",-15.991192661750015,-107.17791307496,-8.8484060000000007,"OFF",0.10287052199999989,-166.99199929652002,-8.8484060000000007,"ON",31932.550010019986,64691.868189486006,3064.8960000000002,"ON",38734.913873900005,70187.984271306006,2083.357,null,1900.5375376725003,0,0,2160.9525323447456,2086.7429831645222,6148.2330531817679,1967.6505716530698,0,0,2227.7950482706883,2159.8443899748013,6355.2900098985592,251.97146232749969,0,0,903.94346765525461,-3.3859831645222584,184.85842834693017,0,0,837.10095172931187,-76.487389974801317,1121.6130734906139,914.55611677382262,null,null,7283.0651880000005,null,77871.196800000151,13.448832037790092,11580.365727103826,195.6782340780556,10485.792499200013,164.76236075043747,-30.915873327618129,null,null,null,null,null,null,null,null,null,6148.2330531817679,38.322914988429829,0,0,-4.4165169910361328,-5.036664406543423]
[3120.8840883492203,3334.024700616284,0,0,0,6454.9087889655038,7021.2401300000001,"2013-05-25T21:00:00",70,68,"ON",59781.16417846,66365.583641100005,3516.2689999999998,"ON",56266.138172639992,71311.767281377994,3519.5709999999999,"OFF",0.26268053374999945,-166.99199929652002,-8.8484060000000007,"OFF",-9.6274050609800064,-166.99199929652002,-1.7696810000000001,"OFF",-8.4622499623900005,-121.06919547956002,-3.9817830000000001,null,3033.6576038496441,3332.5214870393434,0,0,0,6366.179090888987,3245.0827171141696,3487.2300855373678,0,0,0,6732.3128026515369,482.61139615035563,187.04951296065656,0,0,0,271.18628288583022,32.340914462632099,0,0,0,636.56833018801774,270.43461842546787,null,null,7021.2401300000001,null,83410.700000000012,13.75934940405433,12124.22150940105,212.17983642754953,11006.505800000001,179.08725750455508,-33.092578922994448,null,null,null,null,null,null,null,null,null,6366.179090888987,87.226484499576145,1.5032135769406523,0,0,0]
[0,3335.3785473425933,0,3415.0009388745539,0,6750.3794862171471,7477.956709,"2013-05-26T12:00:00",82,73,"OFF",-8.9963911419450096,-73.754793005267999,3.897999,"ON",53370.778531719996,71137.362266882003,3593.9740000000002,"OFF",-4.9139880499995313E-2,-166.99199929652002,-8.8484060000000007,"ON",54837.19872647999,65773.686196070004,3895.127,"OFF",-8.1204622280599832,-118.98177343106001,-6.1938839999999997,null,0,3335.9461125578423,0,3409.9729122783488,0,6745.9190248361911,0,3477.143288143564,0,3599.3802909569185,0,7076.5235791004825,0,258.02788744215786,0,485.15408772165119,0,0,116.83071185643621,0,295.74670904308141,0,696.57245756430825,365.96790330001681,null,null,7477.956709,null,117939.30320000008,15.240551350169921,15477.038919420083,330.63357915295234,14252.194500800008,284.02406155345153,-46.609517599500805,null,null,null,null,null,null,null,null,null,6745.9190248361911,0,-0.56756521524903292,0,5.0280265962051089,0]
[0,3405.4768820739755,0,3510.9309927154363,0,6916.4078747894118,7502.9504619999998,"2013-05-26T13:00:00",82,73,"OFF",-10.999358402280006,-75.14639166260001,3.5047519999999999,"ON",54464.243880970011,70622.697432437999,3607.3420000000001,"OFF",1.1055301999997534E-2,-166.99199929652002,-8.8484060000000007,"ON",56530.124458099999,65134.674372124005,3907.1460000000002,"OFF",-8.5969103391499999,-116.89443159090001,-6.1938839999999997,null,0,3405.2829685743814,0,3504.6488829211544,0,6909.9318514955357,0,3556.2772386163047,0,3712.0139414607575,0,7268.2911800770617,0,202.05903142561874,0,402.4971170788458,0,0,51.064761383695441,0,195.13205853924273,0,557.94663090496374,199.58730232343737,null,null,7502.9504619999998,null,117939.30320000008,15.240551350169921,15477.038919420083,330.63357915295234,14252.194500800008,284.02406155345153,-46.609517599500805,null,null,null,null,null,null,null,null,null,6909.9318514955357,0,0.19391349959414583,0,6.2821097942819506,0]
[3143.2908985011604,0,0,3344.3565558754899,3152.3529091266164,{"$f":"SUM(A2820:E2820)","v":9640.0003635032663},{"$f":"N2820+R2820+V2820+Z2820+AD2820","v":10992.185187999999},"2013-05-27T04:00:00",72,68,"ON",60210.802754549986,71608.522097710011,3553.1529999999998,"OFF",-15.281430500284998,-112.71958749390001,-8.8484060000000007,"OFF",1.7145086999999982E-2,-166.99199929652002,-8.8484060000000007,"ON",56629.380575349991,68887.25364236001,3816.9369999999999,"ON",64729.038355199998,73885.949682836013,3639.7919999999999,null,3055.0607088025627,0,0,3338.0278310191238,3141.7614802583585,{"$f":"SUM(AF2820:AJ2820)","v":9534.8500200800445},3222.5332616267196,0,0,3511.8369998696689,3311.6411054013706,{"$f":"SUM(AL2820:AP2820)","v":10046.011366897759},{"$f":"IF($K2820=\"ON\",$N2820-AF2820,0)","v":498.09229119743713},{"$f":"IF($O2820=\"ON\",$R2820-AG2820,0)","v":0},{"$f":"IF($S2820=\"ON\",$V2820-AH2820,0)","v":0},{"$f":"IF($W2820=\"ON\",$Z2820-AI2820,0)","v":478.90916898087607},{"$f":"IF($AA2820=\"ON\",$AD2820-AJ2820,0)","v":498.03051974164146},{"$f":"IF($K2820=\"ON\",$N2820-AL2820,0)","v":330.61973837328014},{"$f":"IF($O2820=\"ON\",$R2820-AM2820,0)","v":0},{"$f":"IF($S2820=\"ON\",$V2820-AN2820,0)","v":0},{"$f":"IF($W2820=\"ON\",$Z2820-AO2820,0)","v":305.10000013033095},{"$f":"IF($AA2820=\"ON\",$AD2820-AP2820,0)","v":328.15089459862929},{"$f":"SUM(AR2820:AV2820)+BN2820","v":1436.7918067544374},{"$f":"SUM(AW2820:BA2820)+BN2820","v":925.63045993672324},null,null,{"$f":"N2820+R2820+V2820+Z2820+AD2820","v":10992.185187999999},null,89061.715200000035,{"$f":"19.5285952781395+42*-0.3035722016559+BH2820*0.0000340867411548605+J2820*0.0608468772796604","v":13.951974096438914},{"$f":"BH2820*1000/(500*BI2820)","v":12766.898015203747},{"$f":"0.00000128*BJ2820^2+0*BJ2820+24.024","v":232.65591671118514},{"$f":"0.094*BH2820 + 3165.9","v":11537.701228800002},{"$f":"0.00000128*BL2820^2+0*BL2820+24.024","v":194.41574354566797},{"$f":"BM2820-BK2820","v":-38.240173165517177},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF2820:AJ2820)","v":9534.8500200800445},{"$f":"A2820-AF2820","v":88.230189698597769},{"$f":"B2820-AG2820","v":0},{"$f":"C2820-AH2820","v":0},{"$f":"D2820-AI2820","v":6.3287248563660796},{"$f":"E2820-AJ2820","v":10.591428868257935}]
[0,0,0,0,0,0,1138.3587769999999,"2013-05-27T19:00:00",83,72,"check",7596.6258554500018,25672.981196358,1162.1020000000001,"OFF",-18.461476416855014,-109.02872052046001,-8.8484060000000007,"OFF",-2.0954715962500134E-2,-166.99199929652002,-8.8484060000000007,"OFF",0.61661705203001305,-165.87870753732003,-2.0646279999999999,"OFF",2957.0515655399927,43822.556454894009,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-50.216104071689017,-50.216104071689017,null,null,1138.3587769999999,null,120794.73630000022,15.277036881854986,15813.896010616025,344.12551300425912,14520.60521220002,293.9094089325701,-50.216104071689017,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,3648.8182142703581,3337.2712500558641,6986.0894643262218,7744.0219969999998,"2013-05-28T11:00:00",81,71,"OFF",-4.7570572366499837,-74.450592333934011,3.3628089999999999,"OFF",-20.135505903190008,-107.8489360474,-8.8484060000000007,"OFF",-1.0301492636250011,-166.99199929652002,-8.8484060000000007,"ON",60154.643347040001,67272.723924831997,4026.7620000000002,"ON",66112.339736519993,72374.295182192014,3731.5940000000001,null,0,0,0,3639.6058345345109,3325.3077330822548,6964.9135676167662,0,0,0,3852.7032622265833,3517.9780500031329,7370.6813122297162,0,0,0,387.15616546548927,406.28626691774525,0,0,0,174.05873777341685,213.61594999686713,743.23181228730846,337.46406767435786,null,null,7744.0219969999998,null,115066.74090000021,15.020941308039296,15320.842887311706,324.47613027544281,13982.17364460002,274.2655101795167,-50.210620095926117,null,null,null,null,null,null,null,null,null,6964.9135676167662,0,0,0,9.2123797358472075,11.96351697360933]
[3219.1606587740521,3314.8192836218168,0,0,0,6533.9799423958684,7218.1000290000002,"2013-05-29T09:00:00",76,71,"ON",59457.728684399997,60475.941380738004,3619.4560000000001,"ON",54187.904854479995,63312.148387308007,3615.4560000000001,"OFF",-0.73718018537500563,-166.99199929652002,-8.8484060000000007,"OFF",-3.6059489054399956,-165.87870753732003,-1.7696810000000001,"OFF",-2.1251058761799739,-120.37338813006001,-6.1938839999999997,null,3132.2003028569447,3314.8233832026831,0,0,0,6447.0236860596278,3404.1423728097684,3522.8097834689825,0,0,0,6926.9521562787504,487.25569714305539,300.63261679731704,0,0,0,215.31362719023173,92.646216531017672,0,0,0,746.32835212673467,266.3998819076117,null,null,7218.1000290000002,null,100578.26240000024,14.527076291682034,13847.006841643655,269.45068604483356,12620.256665600022,227.89072423119586,-41.559961813637699,null,null,null,null,null,null,null,null,null,6447.0236860596278,86.960355917107336,-4.0995808662955824E-3,0,0,0]
[0,0,0,0,0,0,-19.972604000000004,"2013-05-29T17:00:00",82,73,"OFF",-13.213549935879994,-86.696713455960008,3.4756719999999999,"OFF",-23.19203618061001,-111.32797279490001,-8.8484060000000007,"OFF",-0.8895653438750033,-166.99199929652002,-8.8484060000000007,"OFF",-4.9790940242799913,-165.87870753732003,-1.7696810000000001,"OFF",-6.5184197823499881,-116.89443159090001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-46.609517599500805,-46.609517599500805,null,null,-19.972604000000004,null,117939.30320000008,15.240551350169921,15477.038919420083,330.63357915295234,14252.194500800008,284.02406155345153,-46.609517599500805,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3338.8774318246524,3331.1546559661974,0,3465.5929653170238,0,10135.625053107873,11014.45371,"2013-05-30T08:00:00",77,72,"ON",60940.893121850007,68237.381609178003,3585.1019999999999,"ON",53871.672659804994,70434.424395955997,3563.0990000000002,"OFF",-0.3085881437500006,-166.99199929652002,-8.8484060000000007,"ON",56336.226615549996,65831.861305072001,3881.2950000000001,"OFF",-11.458971209700021,-117.59015873206,-6.1938839999999997,null,3248.2547074466975,3331.3783927787463,0,3459.4639806233199,0,10039.097080848764,3451.5871663994089,3480.0640105603516,0,3658.7197822956218,0,10590.370959255382,336.8472925533024,231.72060722125389,0,421.83101937668016,0,133.51483360059092,83.034989439648598,0,222.57521770437825,0,949.00188653458622,397.72800812796754,null,null,11014.45371,null,103480.2117000001,14.686841163595318,14091.554548366656,278.19604427467902,12893.039899800009,236.79901165802883,-41.397032616650193,null,null,null,null,null,null,null,null,null,10039.097080848764,90.62272437795491,-0.22373681254885014,0,6.1289846937038419,0]
[3190.402189252904,3251.0281546015431,0,0,3284.3872277860255,9725.817571640473,10645.051912999999,"2013-05-30T23:00:00",81,74,"ON",56844.124441649983,70984.268608324011,3470.6819999999998,"ON",51479.691222494992,73199.622959123997,3558.248,"OFF",-3.0484058374998436E-2,-166.99199929652002,-8.8484060000000007,"OFF",4.4102572211600082,-159.75568307006003,-1.7696810000000001,"ON",62417.325221720013,73414.829956178,3626.74,null,3108.9773156987376,3252.834816044282,0,0,3275.8004682061351,9637.6125999491542,3264.2144247529332,3371.2494491679863,0,0,3439.3013379921326,10074.765211913053,361.7046843012622,305.41318395571807,0,0,350.93953179386472,206.46757524706663,186.99855083201373,0,0,187.43866200786715,975.01822598170781,537.86561401781034,null,null,10645.051912999999,null,115066.74090000021,15.203481939878277,15136.89316105722,317.30468424865387,13982.17364460002,274.2655101795167,-43.039174069137175,null,null,null,null,null,null,null,null,null,9637.6125999491542,81.424873554166425,-1.806661442738914,0,0,8.5867595798904404]
[0,0,0,0,0,0,-23.923878000000002,"2013-05-31T15:00:00",89,76,"OFF",-9.9782860270150024,-75.14639166260001,1.4415530000000001,"OFF",-22.268540628090005,-112.02378014440001,-8.8484060000000007,"OFF",-8.266883137500329E-2,-166.99199929652002,-8.8484060000000007,"OFF",-3.2801834845499989,-158.64239131086001,-3.686836,"OFF",-16.648301812799989,-116.89443159090001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-42.50206058694522,-42.50206058694522,null,null,-23.923878000000002,null,137357.58810000028,16.084998033066547,17078.968591432716,397.38869522834585,16077.513281400026,354.88663464140063,-42.50206058694522,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3324.3955970770435,3392.2234728202798,0,0,3154.2401602720797,9870.8592301694025,10639.810758,"2013-06-01T06:00:00",78,72,"ON",60678.473673060005,73782.521028406016,3578.9920000000002,"ON",54829.049470875005,72534.358945496017,3575.8,"OFF",-0.3002745194999954,-166.99199929652002,-8.8484060000000007,"OFF",-3.7113490254400117,-165.87870753732003,-3.686836,"ON",61265.915982809995,73690.257374904002,3497.5540000000001,null,3234.3973277195369,3391.7699510498874,0,0,3146.6735836535395,9772.8408624229633,3387.9003898927331,3530.7707089014089,0,0,3301.3487702191114,10220.019869013253,344.59467228046333,184.03004895011281,0,0,350.88041634646061,191.09161010726712,45.02929109859133,0,0,196.20522978088866,836.33253499258171,389.15352840229207,null,null,10639.810758,null,106383.78480000014,14.785814508279236,14389.979630872702,289.07553763447203,13165.975771200012,245.90293505001699,-43.172602584455035,null,null,null,null,null,null,null,null,null,9772.8408624229633,89.998269357506615,0.45352177039239905,0,0,7.566576618540239]
[3121.6012052961055,3461.7873530506226,0,0,3130.7255481682664,9714.114106514995,10280.667913000001,"2013-06-01T22:00:00",78,70,"ON",58337.663806224991,70684.874937606,3356.8249999999998,"ON",57076.866000000009,71593.683554810006,3528.4879999999998,"OFF",7.0477550250003004E-2,-166.99199929652002,-8.8484060000000007,"OFF",-6.6823676080000043,-159.75568307006003,-1.7696810000000001,"ON",62455.470254729989,73142.867537740007,3405.973,null,3037.3902776891268,3459.6507479263364,0,0,3122.158438923484,9619.1994645389459,3202.2623499275242,3617.4227192117282,0,0,3286.9732151070325,10106.658284246285,319.43472231087298,68.837252073663421,0,0,283.81456107651593,154.56265007247566,-88.934719211728407,0,0,118.99978489296745,624.49649036418464,137.03767065684707,null,null,10280.667913000001,null,106383.78480000014,14.664120753719914,14509.398358986275,293.49298014688463,13165.975771200012,245.90293505001699,-47.590045096867641,null,null,null,null,null,null,null,null,null,9619.1994645389459,84.210927606978657,2.1366051242862341,0,0,8.5671092447823867]
[0,2992.6334041870923,0,0,2711.5100872461544,5704.1434914332467,6406.7855609999997,"2013-06-02T22:00:00",69,60,"OFF",-2.6239254167549899,-74.450592333934011,2.693648,"ON",55584.129787030011,71293.078738158001,3415.5430000000001,"OFF",-2.4581651375005537E-2,-166.99199929652002,-8.8484060000000007,"OFF",-7.5852777359799912,-158.64239131086001,-1.7696810000000001,"ON",61652.69564292,72743.413962872015,2999.1669999999999,null,0,2991.664287675344,0,0,2703.7582705482282,5695.4225582235722,0,3140.3406469973511,0,0,2864.657979958858,6004.9986269562087,0,423.87871232465614,0,0,295.40872945177171,0,275.20235300264903,0,0,134.50902004114187,675.39830469631761,365.82223596368061,null,null,6406.7855609999997,null,80625.134100000141,13.177623522013945,12236.672866744359,215.6862884450785,10744.662605400013,171.79715136496822,-43.889137080110288,null,null,null,null,null,null,null,null,null,5695.4225582235722,0,0.96911651174832514,0,0,7.7518166979261878]
[0,2973.4158748070136,0,0,2460.5816965883214,5433.9975713953354,6231.2484559999994,"2013-06-03T03:00:00",64,59,"OFF",-3.9851521871699904,-73.797407696310017,2.540645,"ON",55906.707537709997,73512.435485124006,3478.402,"OFF",0.41563953737499615,-166.99199929652002,-8.8484060000000007,"OFF",-10.333662918690029,-165.87870753732003,-3.9817830000000001,"ON",55786.986543924992,74833.210178235997,2763.136,null,0,2972.2146875668477,0,0,2457.3230976919413,5429.537785258789,0,3106.4921753861563,0,0,2575.1023301379032,5681.5945055240591,0,506.18731243315233,0,0,305.81290230805871,0,371.90982461384374,0,0,188.03366986209676,782.76453045740027,530.70781019212973,null,null,6231.2484559999994,null,67246.745600000082,12.660750978865622,10622.868376805443,168.46602566519439,9487.0940864000077,139.23034138138365,-29.235684283810741,null,null,null,null,null,null,null,null,null,5429.537785258789,0,1.2011872401658366,0,0,3.2585988963801356]
[3226.1955784755041,0,0,3475.2965757857928,0,6701.4921542612974,7542.2794049999993,"2013-06-03T19:00:00",84,68,"ON",61784.131704165004,60803.127241266011,3563.4609999999998,"OFF",-4.725212768220012,-112.85874896380001,-8.8484060000000007,"OFF",-1.9029524123749997,-166.99199929652002,-8.8484060000000007,"ON",59021.164689655001,55178.60562794,4000.4969999999998,"OFF",2659.8646839999997,38533.257577764001,-3.9817830000000001,null,3134.2399401915095,0,0,3467.0708488376781,0,6601.3107890291876,3422.8461758953999,0,0,3809.75250466734,0,7232.5986805627399,429.22105980849028,0,0,533.42615116232173,0,140.61482410459985,0,0,190.74449533265988,0,900.69087722337508,269.40298568982286,null,null,7542.2794049999993,null,123629.28960000002,15.130270057363095,16341.980563636567,365.86122079011244,14787.053222400002,303.90488704267557,-61.956333747436872,null,null,null,null,null,null,null,null,null,6601.3107890291876,91.955638283994631,0,0,8.2257269481146977,0]
[0,0,0,3443.2764805652728,3195.4169085067801,6638.6933890720529,7653.8420260000003,"2013-06-04T10:00:00",79,70,"OFF",-3.8952560542400154,-75.378426369386005,2.285838,"OFF",-9.408969155494983,-108.96070384814,-8.8484060000000007,"OFF",-0.90290431524999348,-166.99199929652002,-8.8484060000000007,"ON",57170.516270174994,61964.319421114007,3986.5459999999998,"ON",63899.24154897,68335.869429864004,3682.7069999999999,null,0,0,0,3436.5191579763236,3185.5582503810642,6622.0774083573879,0,0,0,3678.9740909734824,3403.8336230674486,7082.8077140409314,0,0,0,550.02684202367618,497.14874961893565,0,0,0,307.57190902651746,278.87337693255131,997.77152205627044,537.04121637272738,null,null,7653.8420260000003,null,109285.23110000021,14.763021602722745,14805.266027632815,304.59475475069229,13438.71172340002,255.1906851643509,-49.404069586341393,null,null,null,null,null,null,null,null,null,6622.0774083573879,0,0,0,6.7573225889491368,9.8586581257159196]
[0,3204.958842773352,0,2818.0532110683594,3175.1158053820895,9198.1278592238014,11063.215169999999,"2013-06-05T01:00:00",81,70,"OFF",-8.3051939060600084,-74.450592333934011,2.5555759999999998,"ON",53000.721660749987,67267.029132692012,3485.3989999999999,"OFF",-1.6611784552999841E-2,-166.99199929652002,-8.8484060000000007,"ON",45137.585916719989,62672.936042512003,3932.8879999999999,"ON",63448.036211430008,69703.124856006005,3651.221,null,0,3205.7752934685132,0,2818.7007145007983,3165.666609402514,9190.1426173718246,0,3372.0002599583786,0,2964.3973091232747,3367.3776136876745,9703.7751827693282,0,279.62370653148673,0,1114.1872854992016,485.55439059748596,0,113.39874004162129,0,968.49069087672524,283.84338631232549,1826.7057469709519,1313.0731815734496,null,null,11063.215169999999,null,115066.74090000021,14.960094430759636,15383.157029197631,326.9251458367392,13982.17364460002,274.2655101795167,-52.659635657222509,null,null,null,null,null,null,null,null,null,9190.1426173718246,0,-0.81645069516116564,0,-0.64750343243895259,9.4491959795755065]
[0,0,0,0,0,0,-21.285338000000003,"2013-06-05T17:00:00",89,73,"OFF",-17.611748949900004,-75.14639166260001,2.236675,"OFF",-33.752660339399974,-109.93635809590002,-8.8484060000000007,"OFF",-1.8095561904999948,-166.99199929652002,-8.8484060000000007,"OFF",-15.527572028429994,-166.99199929652002,-1.843418,"OFF",-22.366952730779982,-116.18891903226,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-51.122789943830014,-51.122789943830014,null,null,-21.285338000000003,null,137357.58810000028,15.902457401227565,17275.014123213081,406.00942458523065,16077.513281400026,354.88663464140063,-51.122789943830014,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,3035.0076325945106,0,3454.9552582938395,0,6489.9628908883496,7388.5241109999997,"2013-06-06T08:00:00",71,67,"OFF",0.35794053101999546,-154.745950362,2.1783000000000001,"ON",51931.811306350006,65073.298950356002,3515.596,"OFF",4.5395228899999781E-3,-166.99199929652002,-8.8484060000000007,"ON",59306.373310599993,60520.68159279001,3883.58,"OFF",366.13372755000552,24097.160023714001,-3.9817830000000001,null,0,3036.5153432008256,0,3446.5023480136852,0,6483.0176912145107,0,3211.4577328120968,0,3723.054483982623,0,6934.5122167947193,0,479.08065679917445,0,437.07765198631478,0,0,304.13826718790324,0,160.52551601737696,0,878.7204742108031,427.22594863059408,null,null,7388.5241109999997,null,86224.143900000025,13.79440366074769,12501.322423288642,224.06631978370484,11270.969526600002,186.62848520901872,-37.437834574686121,null,null,null,null,null,null,null,null,null,6483.0176912145107,0,-1.5077106063149586,0,8.4529102801543559,0]
[0,3116.128930583041,0,3277.2619117413251,2777.75928657443,9171.1501288987965,10332.648679,"2013-06-07",69,65,"OFF",-7.3058926748899999,-75.14639166260001,2.0160849999999999,"ON",54523.848531119998,73511.970276752007,3492.2440000000001,"OFF",-0.31622379725000277,-166.99199929652002,-8.8484060000000007,"ON",57322.975043505023,68348.566410086016,3800.915,"ON",58554.083944980011,74609.613388818019,3046.3220000000001,null,0,3115.9055376860329,0,3270.4196551600462,2772.4495928623455,9158.774785708425,0,3244.8782374551379,0,3452.2101796781035,2905.2750557100303,9602.3634728432717,0,376.33846231396728,0,530.49534483995376,273.87240713765459,0,247.36576254486226,0,348.70482032189648,141.04694428996982,1145.3696577904338,701.78097065558677,null,null,10332.648679,null,80625.134100000141,13.481857908412247,11960.53758283458,207.13370786611006,10744.662605400013,171.79715136496822,-35.336556501141843,null,null,null,null,null,null,null,null,null,9158.774785708425,0,0.22339289700812515,0,6.8422565812788889,5.3096937120844814]
[0,2844.3963647064752,0,2889.1408871929943,0,5733.53725189947,6048.3990899999999,"2013-06-07T13:00:00",81,64,"OFF",-15.838946194799986,-116.12667736042002,2.1512790000000002,"ON",50398.481412605026,66036.248197060006,3036.1680000000001,"OFF",8.0988982304999652E-2,-166.99199929652002,-8.8484060000000007,"ON",50212.67493488,65695.900147938009,3022.91,"OFF",-3.0612735712999988,-119.67758078056001,-3.9817830000000001,null,0,2846.8312687095017,0,2887.1272805221793,0,5733.958549231681,0,3003.4583837251544,0,3043.6404645684111,0,6047.0988482935654,0,189.33673129049839,0,135.78271947782059,0,0,32.709616274845757,0,-20.730464568411207,0,257.11668302399625,-56.023616037888189,null,null,6048.3990899999999,null,115066.74090000021,14.595013167081673,15767.953010077103,342.26827792383943,13982.17364460002,274.2655101795167,-68.002767744322739,null,null,null,null,null,null,null,null,null,5733.958549231681,0,-2.4349040030265314,0,2.0136066708150793,0]
[0,2274.8373160439328,0,2487.2495346247624,0,4762.0868506686948,5027.1905389999993,"2013-06-08T05:00:00",66,60,"OFF",-20.755923541725004,-73.754793005267999,1.9417279999999999,"ON",41612.13951088499,70256.241568646001,2537.66,"OFF",-0.49856601349999802,-166.99199929652002,-8.8484060000000007,"ON",43691.225622870021,65438.591793218009,2500.4189999999999,"OFF",2.8656509306600144,-118.98177343106001,-3.9817830000000001,null,0,2281.3443732013784,0,2488.4608667023235,0,4769.8052399037024,0,2367.7472705708847,0,2607.3453077657196,0,4975.0925783366038,0,256.31562679862145,0,11.958133297676341,0,0,169.91272942911519,0,-106.92630776571968,0,234.11313642877127,28.825797995868982,null,null,5027.1905389999993,null,72473.210400000098,12.899751008937869,11236.373531517853,185.6317953789376,9978.3817776000087,151.47117171141107,-34.160623667526522,null,null,null,null,null,null,null,null,null,4769.8052399037024,0,-6.5070571574456153,0,-1.2113320775611101,0]
[3112.2332531107381,0,0,0,3082.2103878082507,6194.4436409189893,6868.5665069999995,"2013-06-08T21:00:00",80,67,"ON",60361.583744799987,66176.725083736004,3518.1909999999998,"OFF",-11.573062823400022,-109.37971221630001,-8.8484060000000007,"OFF",0.23062718462499382,-166.99199929652002,-8.8484060000000007,"OFF",-6.4021768692550118,-166.71367635672001,-1.7696810000000001,"ON",64040.840803610001,68332.460575413992,3369.8420000000001,null,3023.8152577603714,0,0,0,3072.2698468882581,6096.0851046486296,3240.9182124992153,0,0,0,3290.3678965856507,6531.2861090848655,494.37574223962838,0,0,0,297.57215311174195,277.27278750078449,0,0,0,79.474103414349429,733.55122242957464,298.35021799333816,null,null,6868.5665069999995,null,112180.80000000005,14.679181478474124,15284.339956489324,323.04614131908619,13710.895200000004,264.64946839729043,-58.396672921795755,null,null,null,null,null,null,null,null,null,6096.0851046486296,88.417995350366709,0,0,0,9.9405409199925998]
[3283.4324233319016,0,0,3541.7626471423014,0,{"$f":"SUM(A3140:E3140)","v":6825.195070474203},{"$f":"N3140+R3140+V3140+Z3140+AD3140","v":7299.6594049999994},"2013-06-09T12:00:00",81,71,"ON",60645.183370519997,69017.407715678011,3498.7460000000001,"OFF",-10.119677967359982,-107.1531286979,-8.8484060000000007,"OFF",-0.3946180680000056,-166.99199929652002,-8.8484060000000007,"ON",58294.926825850009,65252.267819398003,3822.5920000000001,"OFF",-2.7908065913699973,-116.65284407082001,-3.9817830000000001,null,3193.6802903126932,0,0,3534.1052139980361,0,{"$f":"SUM(AF3140:AJ3140)","v":6727.7855043107293},3387.4024308707553,0,0,3753.022304571648,0,{"$f":"SUM(AL3140:AP3140)","v":7140.4247354424033},{"$f":"IF($K3140=\"ON\",$N3140-AF3140,0)","v":305.06570968730693},{"$f":"IF($O3140=\"ON\",$R3140-AG3140,0)","v":0},{"$f":"IF($S3140=\"ON\",$V3140-AH3140,0)","v":0},{"$f":"IF($W3140=\"ON\",$Z3140-AI3140,0)","v":288.48678600196399},{"$f":"IF($AA3140=\"ON\",$AD3140-AJ3140,0)","v":0},{"$f":"IF($K3140=\"ON\",$N3140-AL3140,0)","v":111.34356912924477},{"$f":"IF($O3140=\"ON\",$R3140-AM3140,0)","v":0},{"$f":"IF($S3140=\"ON\",$V3140-AN3140,0)","v":0},{"$f":"IF($W3140=\"ON\",$Z3140-AO3140,0)","v":69.569695428352134},{"$f":"IF($AA3140=\"ON\",$AD3140-AP3140,0)","v":0},{"$f":"SUM(AR3140:AV3140)+BN3140","v":543.34187559334487},{"$f":"SUM(AW3140:BA3140)+BN3140","v":130.70264446167079},null,null,{"$f":"N3140+R3140+V3140+Z3140+AD3140","v":7299.6594049999994},null,115066.74090000021,{"$f":"19.5285952781395+42*-0.3035722016559+BH3140*0.0000340867411548605+J3140*0.0608468772796604","v":15.020941308039296},{"$f":"BH3140*1000/(500*BI3140)","v":15320.842887311706},{"$f":"0.00000128*BJ3140^2+0*BJ3140+24.024","v":324.47613027544281},{"$f":"0.094*BH3140 + 3165.9","v":13982.17364460002},{"$f":"0.00000128*BL3140^2+0*BL3140+24.024","v":274.2655101795167},{"$f":"BM3140-BK3140","v":-50.210620095926117},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF3140:AJ3140)","v":6727.7855043107293},{"$f":"A3140-AF3140","v":89.752133019208486},{"$f":"B3140-AG3140","v":0},{"$f":"C3140-AH3140","v":0},{"$f":"D3140-AI3140","v":7.6574331442652692},{"$f":"E3140-AJ3140","v":0}]
[2949.7919098704551,0,0,3129.4048658911115,3050.4710397488175,9129.6678155103837,10589.245188000001,"2013-06-10T03:00:00",71,68,"ON",56435.404572439998,70675.474520157994,3416.5140000000001,"OFF",-12.132964144954983,-110.21468103570001,-8.8484060000000007,"OFF",6.6115127959994451E-3,-166.99199929652002,-8.8484060000000007,"ON",52555.243747355009,63809.592491154006,3651.2130000000002,"ON",62397.07991611,72414.856539729997,3539.2150000000001,null,2870.1831839370775,0,0,3125.9480232832811,3041.9814791350641,9038.1126863554218,3023.7498344520322,0,0,3313.8366270689107,3212.0727471212067,9549.6592086421497,546.33081606292262,0,0,525.26497671671905,497.23352086493605,392.76416554796788,0,0,337.37637293108946,327.14225287879344,1533.1446372983287,1021.5981150116016,null,null,10589.245188000001,null,86224.143900000025,13.855250538027352,12446.421472256716,222.31316155526787,11270.969526600002,186.62848520901872,-35.684676346249148,null,null,null,null,null,null,null,null,null,9038.1126863554218,79.608725933377627,0,0,3.4568426078303673,8.4895606137533832]
[0,3219.232604508888,0,3542.3811255618957,0,6761.6137300707833,7472.4261910000005,"2013-06-10T19:00:00",91,70,"OFF",-9.7496799856050007,-74.450592333934011,1.8427979999999999,"ON",53232.902644689988,63497.036631842006,3552.2220000000002,"OFF",-0.37944045000000604,-166.99199929652002,-8.8484060000000007,"ON",58934.376144249996,53966.248548006006,3933.0349999999999,"check",1369.7757601500059,50359.407831550001,-5.8252009999999999,null,0,3219.8935469860194,0,3534.2089375040136,0,6754.102484490033,0,3418.3730131333532,0,3894.5205526695522,0,7312.8935658029059,0,332.32845301398083,0,398.82606249598621,0,0,133.84898686664701,0,38.514447330447638,0,670.71220295718786,111.92112164431552,null,null,7472.4261910000005,null,142571.47790000017,15.897641281411147,17936.18001265467,435.80838841133163,16567.618922600017,375.36607585855251,-60.442312552779129,null,null,null,null,null,null,null,null,null,6754.102484490033,0,-0.66094247713135701,0,8.1721880578820674,0]
[0,3104.9462943846329,0,3533.9760311181622,3071.1170573993199,9710.0393829021159,10203.166423999999,"2013-06-11T10:00:00",87,76,"OFF",-13.984968071989989,-76.537990319932007,1.92883,"ON",48049.889955840015,70471.368357360014,3372.6860000000001,"OFF",-0.20762653512499915,-166.99199929652002,-8.8484060000000007,"ON",55165.547276490004,67679.340104461997,3715.3130000000001,"ON",56245.558694744992,72308.516322558004,3122.087,null,0,3108.7566072657332,0,3528.6988971176338,3067.4649492939925,9704.9204536773595,0,3226.9334652962339,0,3705.4122201716555,3208.2040087989903,10140.54969426688,0,263.92939273426691,0,186.6141028823663,54.622050706007485,0,145.75253470376629,0,9.9007798283446391,-86.117008798990355,462.85566163683285,27.226421047312726,null,null,10203.166423999999,null,131970.16469999996,15.901358326139096,16598.602709689741,376.68142325007312,15571.095481799995,334.37153856426528,-42.309884685807845,null,null,null,null,null,null,null,null,null,9704.9204536773595,0,-3.8103128811003444,0,5.2771340005283491,3.6521081053274429]
[0,3179.1800900228091,0,3564.0914174910504,3233.6683021011145,9976.9398096149744,10971.565516999999,"2013-06-12T02:00:00",78,73,"OFF",-16.223541139504995,-74.438897957961998,2.0769229999999999,"ON",50878.701777915012,68600.244139338,3498.0129999999999,"OFF",0.1102368196249998,-166.99199929652002,-8.8484060000000007,"ON",57455.021403079983,63244.877652550007,3775.7550000000001,"ON",62161.126154214995,70242.309379988001,3704.569,null,0,3181.3564971024293,0,3557.090784806242,3225.3192908558472,9963.7665727645181,0,3325.8166323832793,0,3790.0327429546501,3414.915089555368,10530.764464893298,0,316.65650289757059,0,218.66421519375808,479.2497091441528,0,172.19636761672064,0,-14.277742954649966,289.65391044463195,973.56592288426828,406.56803075548936,null,null,10971.565516999999,null,106383.78480000014,14.846661385558896,14331.004397187628,286.90743940123025,13165.975771200012,245.90293505001699,-41.004504351213257,null,null,null,null,null,null,null,null,null,9963.7665727645181,0,-2.1764070796202759,0,7.0006326848083518,8.3490112452673202]
[0,0,0,0,0,0,-23.255307999999999,"2013-06-12T16:00:00",93,75,"OFF",-19.209603360799985,-75.14639166260001,2.0271680000000001,"OFF",-5.9175018976000064,-112.02378014440001,-8.8484060000000007,"OFF",1.4045843189993729E-3,-166.99199929652002,-8.8484060000000007,"OFF",-2.4208826562200181,-166.99199929652002,-1.7696810000000001,"OFF",-17.208140046264997,-118.52755360164001,-5.8159830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-44.402216122917082,-44.402216122917082,null,null,-23.255307999999999,null,147581.8293000001,16.37266221907614,18027.835342263315,440.02764432353058,17038.591954200008,395.6254282006135,-44.402216122917082,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,3350.5812201875578,0,3497.7820213973641,3290.3273449925259,10138.690586577448,10976.452794000001,"2013-06-13T07:00:00",79,72,"OFF",-25.208460667615022,-75.853364013027999,1.8502000000000001,"ON",54177.471238400001,87325.065591520019,3524.127,"OFF",-0.60886138874999973,-166.99199929652002,-8.8484060000000007,"ON",56904.963254945003,83661.389245340004,3834.8139999999999,"ON",64230.266311364991,85016.829983000003,3624.51,null,0,3350.5914751947162,0,3491.2177988059343,3280.1324693718157,10121.941743372467,0,3402.3455511478205,0,3567.2687720068006,3363.8121616067192,10333.426484761341,0,173.53552480528379,0,343.59620119406554,344.37753062818456,0,121.78144885217944,0,267.54522799319921,260.69783839328102,816.67418718489694,605.18944579602271,null,null,10976.452794000001,null,109285.23110000021,14.884715357282065,14684.221831159772,300.02575460698785,13438.71172340002,255.1906851643509,-44.83506944263695,null,null,null,null,null,null,null,null,null,10121.941743372467,0,-1.025500715832095E-2,0,6.5642225914298251,10.194875620710263]
[3341.137476801066,3302.3094727578186,0,0,3366.1856765066618,10009.632626065546,10745.421958999999,"2013-06-13T23:00:00",83,72,"ON",60981.785267829997,86663.025953160002,3555.4490000000001,"ON",53415.430009930016,86520.736358000009,3515.518,"OFF",0.36084318349999445,-166.99199929652002,-8.8484060000000007,"OFF",-7.2578259131700023,-158.95552467022003,-1.852635,"ON",65852.190747734989,84707.386207280011,3685.1559999999999,null,3250.4172471114539,3302.8467718326219,0,0,3354.4554058300641,9907.719424774139,3317.3041963811002,3356.8071294960673,0,0,3444.6183756693367,10118.729701546505,305.03175288854618,212.6712281673781,0,0,330.70059416993581,238.14480361889991,158.71087050393271,0,0,240.53762433066322,798.18747115417113,587.17719438180688,null,null,10745.421958999999,null,120794.73630000022,15.277036881854986,15813.896010616025,344.12551300425912,14520.60521220002,293.9094089325701,-50.216104071689017,null,null,null,null,null,null,null,null,null,9907.719424774139,90.720229689612097,-0.5372990748032862,0,0,11.730270676597684]
[2477.9736423456429,2641.8796005318613,0,0,2804.8699531306552,7924.723196008159,9096.7179130000004,"2013-06-14T14:00:00",93,75,"ON",42165.045793320001,66643.657935046009,2707.5859999999998,"ON",40607.224809030013,67072.836720717998,2712.386,"OFF",-0.54932981379000023,-166.99199929652002,-8.8484060000000007,"OFF",-6.8098227031099992,-166.67886593716003,-1.7696810000000001,"ON",51034.884189119985,66616.387099446001,3687.364,null,2426.3391430280076,2648.9077411191556,0,0,2804.6404069031614,7879.8872910503251,2530.5689169358925,2747.1427646971429,0,0,2956.2415146358057,8233.9531962688416,281.2468569719922,63.478258880844351,0,0,882.72359309683861,177.01708306410728,-34.756764697142899,0,0,731.12248536419429,1183.0464928267581,828.98058760824165,null,null,9096.7179130000004,null,147581.8293000001,16.37266221907614,18027.835342263315,440.02764432353058,17038.591954200008,395.6254282006135,-44.402216122917082,null,null,null,null,null,null,null,null,null,7879.8872910503251,51.634499317635346,-7.0281405872942742,0,0,0.22954622749375631]
[3062.3778016259107,0,0,3440.8603521413797,3356.9177438875772,9860.1558976548677,10570.665187999999,"2013-06-15T06:00:00",76,71,"ON",56499.78550940998,85949.492560520011,3113.1489999999999,"OFF",-30.560683195799992,-108.54795173050002,-8.8484060000000007,"OFF",-2.5050096375004445E-2,-166.99199929652002,-8.8484060000000007,"ON",56506.901990250015,84098.925740040009,3820.529,"ON",66533.747320265,84311.397632699998,3654.6840000000002,null,2982.1779467577148,0,0,3434.6074028737416,3344.5418330484281,9761.3271826798846,3042.871375916081,0,0,3507.0584098611444,3439.2717144739477,9989.2015002511725,130.97105324228505,0,0,385.92159712625835,310.14216695157211,70.277624083918909,0,0,313.47059013885564,215.41228552605253,785.47485550647775,557.60053793518932,null,null,10570.665187999999,null,100578.26240000024,14.527076291682034,13847.006841643655,269.45068604483356,12620.256665600022,227.89072423119586,-41.559961813637699,null,null,null,null,null,null,null,null,null,9761.3271826798846,80.199854868195871,0,0,6.2529492676380869,12.375910839149128]
[0,0,0,3637.0041107819779,3431.3295086432177,7068.3336194251951,9296.3341880000007,"2013-06-15T21:00:00",82,73,"check",16517.651429324997,42985.109197787999,1671.5060000000001,"OFF",-28.959415865625015,-112.02378014440001,-8.8484060000000007,"OFF",-0.12421990287500298,-166.99199929652002,-8.8484060000000007,"ON",58708.783198019992,57937.716378102006,3929.9670000000001,"ON",66357.044765405008,74039.548653936014,3712.558,null,0,0,0,3628.991566179599,3419.0872943593859,7048.0788605389844,0,0,0,3934.0341794657711,3597.9259298558181,7531.9601093215897,0,0,0,300.97543382040112,293.47070564061414,0,0,0,-4.0671794657710052,114.63207014418185,547.83662186151446,63.955373078910043,null,null,9296.3341880000007,null,117939.30320000008,15.240551350169921,15477.038919420083,330.63357915295234,14252.194500800008,284.02406155345153,-46.609517599500805,null,null,null,null,null,null,null,null,null,7048.0788605389844,0,0,0,8.0125446023789664,12.2422142838318]
[3563.5480570737923,0,0,3698.1748754025984,3491.0610023922336,10752.783934868625,11252.590188,"2013-06-16T12:00:00",91,76,"ON",62099.379846570002,85640.36961816001,3666.2260000000001,"OFF",-30.733226651099997,-107.8489360474,-8.8484060000000007,"OFF",-0.68545595717999763,-166.99199929652002,-8.8484060000000007,"ON",57941.502691650006,83291.388172920007,3899.308,"ON",65060.342818790014,83825.736134000006,3704.7530000000002,null,3469.4480225754046,0,0,3690.7638905311192,3480.0184524388528,10640.230365545376,3545.6693267912665,0,0,3772.3767689719734,3574.7582113157664,10892.804307079006,196.77797742459552,0,0,208.54410946888083,224.73454756114734,120.55667320873363,0,0,126.93123102802656,129.99478868423375,587.8950660579851,335.32112452435541,null,null,11252.590188,null,142571.47790000017,16.262722545089108,17533.531363486592,417.52764425519103,16567.618922600017,375.36607585855251,-42.161568396638529,null,null,null,null,null,null,null,null,null,10640.230365545376,94.100034498387686,0,0,7.4109848714792861,11.042549953380785]
[0,0,0,0,0,0,-25.628931000000001,"2013-06-16T17:00:00",94,74,"OFF",-4.7902927228200047,-73.520392152452004,1.7826930000000001,"OFF",-31.505778535239987,-109.93635809590002,-8.8484060000000007,"OFF",-0.61950680137500036,-166.99199929652002,-8.8484060000000007,"OFF",-4.5589607053199872,-166.99199929652002,-3.8988290000000001,"OFF",-7.3082935420999942,-120.36328187922001,-5.8159830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-47.034594422340092,-47.034594422340092,null,null,-25.628931000000001,null,150001.30160000012,16.394287267817937,18299.215958531284,452.64647001211648,17266.022350400013,405.61187558977639,-47.034594422340092,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,0,0,0,1638.693266,"2013-06-17T18:00:00",86,76,"OFF",152.99627326099989,1390.4596989040001,14.01909,"check",5518.6716190499992,33630.402482754005,1639.357,"OFF",-1.1320207647499987,-166.99199929652002,-8.8484060000000007,"OFF",-0.24958748416000623,-166.67886593716003,-1.852635,"check",5124.0754050200076,54506.620155420009,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-42.006395148153331,-42.006395148153331,null,null,1638.693266,null,129220.75440000021,15.807639888914498,16349.152094566563,366.16131099042593,15312.650913600019,324.1549158422726,-42.006395148153331,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3121.402796123552,2759.4869476820618,0,0,2741.5301617750129,8622.4199055806275,8797.3819590000003,"2013-06-18T09:00:00",75,70,"ON",58333.888216380001,68505.173193936003,3183.136,"ON",45371.023884180002,62617.80885043001,2955.9989999999998,"OFF",0.20047103774999961,-166.99199929652002,-8.8484060000000007,"OFF",-4.1260721476100111,-158.95552467022003,-1.852635,"ON",53372.125276470004,71964.687231479998,2668.9479999999999,null,3037.2005239217888,2764.5810442241136,0,0,2739.8571954789036,8541.6387636248055,3220.1058245803788,2913.0439379222539,0,0,2867.3607147868638,9000.5104772894974,145.9354760782112,191.41795577588618,0,0,-70.909195478903712,-36.969824580378827,42.955062077745879,0,0,-198.41271478686394,224.94405391546101,-233.92765974922955,null,null,8797.3819590000003,null,97681.6875,14.367494615550399,13597.59514289652,260.68907989775749,12347.978625,219.18889743802484,-41.500182459732656,null,null,null,null,null,null,null,null,null,8541.6387636248055,84.202272201763208,-5.0940965420518296,0,0,1.6729662961092799]
[3032.3004740701035,3184.5765083666079,0,0,3210.4469004154589,9427.3238828521717,10228.894913,"2013-06-19T01:00:00",73,70,"ON",56623.300051859987,69813.363198502004,3123.72,"ON",52667.965169319992,70392.467413302002,3525.248,"OFF",5.7189290894995894E-2,-166.99199929652002,-8.8484060000000007,"OFF",-7.7425610650500181,-158.95552467022003,-1.7696810000000001,"ON",64232.205384399989,72289.121945946012,3590.5450000000001,null,2951.9736205010727,3185.6131799487684,0,0,3200.2826777744312,9337.869478224271,3113.7529994077195,3327.2634486384304,0,0,3382.457375909129,9823.4738239552789,171.74637949892713,339.6348200512316,0,0,390.26232222556882,9.9670005922803284,197.98455136156963,0,0,208.08762409087103,864.64526122207485,379.04091549106823,null,null,10228.894913,null,91919.663300000131,14.17108598811696,12972.846735540037,239.4412831024791,11806.348350200013,202.44302254882635,-36.998260553652756,null,null,null,null,null,null,null,null,null,9337.869478224271,80.326853569030845,-1.0366715821605794,0,0,10.164222641027663]
[0,0,0,0,0,0,-22.320745000000002,"2013-06-19T16:00:00",90,77,"OFF",-2.2900694961599877,-75.831025990338006,1.5054320000000001,"OFF",-10.42504901514002,-107.1531286979,-8.8484060000000007,"OFF",6.8738262111000162E-2,-166.99199929652002,-8.8484060000000007,"OFF",2.0912081795700064,-158.95552467022003,-1.7696810000000001,"OFF",-0.38384776650500702,-117.59015873206,-4.3596839999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-39.527086888747249,-39.527086888747249,null,null,-22.320745000000002,null,139988.10000000021,16.235510488586286,17244.681046329049,404.66915121871409,16324.78140000002,365.14206432996684,-39.527086888747249,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,0,0,0,-23.915735000000002,"2013-06-19T17:00:00",89,76,"OFF",-2.7357127865999975,-75.14639166260001,1.744642,"OFF",-12.182342791850017,-110.34774667176001,-8.8484060000000007,"OFF",-2.8197461218750002,-166.99199929652002,-8.8484060000000007,"OFF",2.0084519866599981,-166.99199929652002,-1.7696810000000001,"OFF",-1.5107841019599921,-116.89443159090001,-6.1938839999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-42.50206058694522,-42.50206058694522,null,null,-23.915735000000002,null,137357.58810000028,16.084998033066547,17078.968591432716,397.38869522834585,16077.513281400026,354.88663464140063,-42.50206058694522,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2812.2982311747764,3017.3548009945794,0,0,2560.1671415258043,8389.8201736951596,8967.7629130000005,"2013-06-20T08:00:00",82,73,"ON",50266.958932850008,65770.670362485995,2959.09,"ON",48209.908277714989,67673.741562330018,3315.6619999999998,"OFF",-0.29216489787000566,-166.99199929652002,-8.8484060000000007,"OFF",-4.3582686119700007,-158.64239131086001,-1.7696810000000001,"ON",46652.602552604985,69338.858679896002,2703.6289999999999,null,2745.2029147580047,3021.0615598274189,0,0,2562.2687659680309,8328.5332405534537,2899.1207542956386,3156.067824647826,0,0,2673.6055156734928,8728.7940946169583,213.88708524199546,294.60044017258087,0,0,141.36023403196896,59.969245704361583,159.59417535217381,0,0,30.023484326507059,603.23824184704449,202.97738778354164,null,null,8967.7629130000005,null,117939.30320000008,15.240551350169921,15477.038919420083,330.63357915295234,14252.194500800008,284.02406155345153,-46.609517599500805,null,null,null,null,null,null,null,null,null,8328.5332405534537,67.095316416771766,-3.7067588328395686,0,0,-2.1016244422266936]
[0,3297.6844452122277,0,3223.1689957022813,3236.7706272183514,9757.62406813286,10076.782040999999,"2013-06-21T02:00:00",81,71,"OFF",-2.8118790653849985,-74.861980909794013,2.9124469999999998,"ON",53915.422203764996,89221.431374139996,3419.5059999999999,"OFF",-0.13309693562499975,-166.99199929652002,-8.8484060000000007,"ON",52523.626767499991,85395.573764479996,3304.5909999999999,"ON",63933.775181674995,85316.728966260009,3358.6210000000001,null,0,3297.8786173667804,0,3219.7299281418959,3226.8646863653589,9744.4732318740353,0,3340.4252197277506,0,3276.2079697586582,3307.6672498952944,9924.3004393817027,0,121.62738263321944,0,84.861071858103969,131.75631363464117,0,79.080780272249285,0,28.383030241341658,50.953750104705705,288.03414803003847,108.20694052237053,null,null,10076.782040999999,null,115066.74090000021,15.020941308039296,15320.842887311706,324.47613027544281,13982.17364460002,274.2655101795167,-50.210620095926117,null,null,null,null,null,null,null,null,null,9744.4732318740353,0,-0.19417215455268888,0,3.4390675603854106,9.905940852992444]
[0,3267.4925148730076,0,3740.7490231107827,3333.712613678751,10341.954151662541,10705.811342999999,"2013-06-21T14:00:00",94,75,"OFF",-13.061032322689995,-72.363194347936002,2.8757489999999999,"ON",51193.037092174993,86982.17493802002,3340.2849999999999,"OFF",-0.10604423687500041,-166.99199929652002,-8.8484060000000007,"ON",59244.325442900008,85978.52797960001,3889.3939999999998,"ON",62637.068960130011,83510.196524440005,3482.105,null,0,3269.4807844466027,0,3732.271938081501,3324.9179830143489,10326.670705542452,0,3317.2406044636014,0,3801.53093027042,3414.559216214323,10533.330750948346,0,70.804215553397171,0,157.12206191849873,157.1870169856511,0,23.044395536398497,0,87.86306972957982,67.545783785677031,341.24271187387274,134.58266646798108,null,null,10705.811342999999,null,150001.30160000012,16.455134145097595,18231.550138372993,449.48245817345065,17266.022350400013,405.61187558977639,-43.870582583674263,null,null,null,null,null,null,null,null,null,10326.670705542452,0,-1.988269573595062,0,8.4770850292816249,8.7946306644021206]
[0,3246.1336331707316,0,3474.9763559332418,3214.0711845426213,9935.1811736465952,10681.280208,"2013-06-22T05:00:00",75,69,"OFF",-19.336204988940011,-73.754793005267999,3.0966140000000002,"ON",54255.44460018001,88338.41775908001,3402.6779999999999,"OFF",0.21674950149999911,-166.99199929652002,-8.8484060000000007,"ON",58371.734972180013,85927.194642000002,3629.605,"ON",65206.648815360015,84991.163314200006,3654.7489999999998,null,0,3246.0928242664577,0,3467.2730729039372,3203.0139420850451,9916.3798392554399,0,3293.0232801206116,0,3534.0590573701656,3288.9910836573463,10116.073421148125,0,156.5851757335422,0,162.33192709606283,451.73505791495472,0,109.65471987938827,0,95.545942629834371,365.75791634265352,727.13460090957051,527.44101901688691,null,null,10681.280208,null,97681.6875,14.30664773827074,13655.426384574825,262.70645727301411,12347.978625,219.18889743802484,-43.517559834989271,null,null,null,null,null,null,null,null,null,9916.3798392554399,0,4.080890427394479E-2,0,7.7032830293046572,11.057242457576194]
[0,3198.7471732758122,0,3498.8313551971901,3305.7936765917725,10003.372205064776,10880.950094,"2013-06-22T21:00:00",88,72,"OFF",-24.922298916899983,-75.14639166260001,2.7515000000000001,"ON",51755.282435634988,89112.82928178001,3446.02,"OFF",-7.6192579250002987E-2,-166.99199929652002,-8.8484060000000007,"ON",56923.444121499997,83128.645451060002,3772.61,"ON",64562.678430600005,85022.364358460007,3668.4169999999999,null,0,3200.3757144552046,0,3492.2528400533192,3295.2897515922514,9987.9183061007752,0,3240.0041403509799,0,3571.35084242823,3379.8102771602139,10191.165259939424,0,245.64428554479537,0,280.35715994668089,373.12724840774854,0,206.01585964902006,0,201.25915757177017,288.60672283978602,845.34672225052486,642.09976841187631,null,null,10880.950094,null,{"$f":" -0.6251*I3461^3 + 145.21*I3461^2 - 8340.3*I3461 + 170112","v":134683.69280000008},15.7504661469816,17102.184982101076,398.40445588736458,15826.167123200006,344.6224842386647,-53.78197164869988,null,null,null,null,null,null,null,null,null,9987.9183061007752,0,-1.6285411793924141,0,6.5785151438708453,10.503924999521132]
[0,3430.5133372374185,0,3606.1709932511221,2852.6134923529685,9889.2978228415086,10108.435990999998,"2013-06-23T12:00:00",91,75,"OFF",-29.147295554789991,-75.14639166260001,3.1713969999999998,"ON",53729.514560100011,88117.523990720001,3478.2069999999999,"OFF",-1.0809368375002685E-2,-166.99199929652002,-8.8484060000000007,"ON",56981.5709584,82639.133952040007,3837.8130000000001,"ON",52129.374470349983,84062.27052866001,2798.0929999999998,null,0,3430.8336999613748,0,3599.5284530655122,2851.7232866368181,9882.0854396637042,0,3478.358397321284,0,3682.0079371618535,2911.2442609916311,10071.610595474769,0,47.373300038625075,0,238.28454693448793,-53.630286636818255,0,-0.15139732128409378,0,155.80506283814657,-113.15126099163126,186.90480042928351,-2.6203553817800298,null,null,10108.435990999998,null,142571.47790000017,16.201875667809446,17599.379333994897,420.48883576556375,16567.618922600017,375.36607585855251,-45.122759907011243,null,null,null,null,null,null,null,null,null,9882.0854396637042,0,-0.32036272395635024,0,6.6425401856099597,0.89020571615037625]
[0,3212.9370431385873,0,3539.7047802506427,3245.6794244888652,9998.3212478780952,10992.74294,"2013-06-24T03:00:00",79,70,"OFF",-6.2023777023950064,-74.450592333934011,3.0733459999999999,"ON",53130.582984760003,88752.934460200006,3452.8290000000002,"OFF",-0.26153284350000128,-166.99199929652002,-8.8484060000000007,"ON",58887.189755679996,86305.617590120004,3850.8820000000001,"ON",65009.138531209988,84964.453936980004,3694.8069999999998,null,0,3213.6667039035374,0,3531.5715645592177,3234.7909387114187,9980.0292071741751,0,3256.8901838563693,0,3597.5555087861326,3320.5775690074302,10175.023261649932,0,239.1622960964628,0,319.31043544078238,460.01606128858111,0,195.9388161436309,0,253.32649121386748,374.22943099256963,969.0847232394849,774.09066876372663,null,null,10992.74294,null,109285.23110000021,14.763021602722745,14805.266027632815,304.59475475069229,13438.71172340002,255.1906851643509,-49.404069586341393,null,null,null,null,null,null,null,null,null,9980.0292071741751,0,-0.72966076495004017,0,8.1332156914249936,10.888485777446476]
[0,0,0,3624.6100650442977,3090.1146591926931,6714.7247242369904,11041.058831999999,"2013-06-24T19:00:00",92,73,"OFF",-13.717731222345009,-73.754793005267999,3.2452380000000001,"check",9284.2260727499943,58726.044047792006,3034.3539999999998,"OFF",-0.60598045200000072,-166.99199929652002,-8.8484060000000007,"ON",58496.846445319992,67951.655439596012,4130.933,"ON",59021.874997020008,68658.339040000006,3881.375,null,0,0,0,3616.7716489263044,3084.3777385245103,6701.1493874508142,0,0,0,3812.4739730785632,3268.4937862778997,7080.9677593564629,0,0,0,514.16135107369564,796.99726147548972,0,0,0,318.45902692143682,612.88121372210026,1260.1962072210601,880.37783531541186,null,null,11041.058831999999,null,145103.97120000015,16.166506356843648,17951.184751623761,436.49764350326967,16805.673292800013,385.53523817514451,-50.962405328125158,null,null,null,null,null,null,null,null,null,6701.1493874508142,0,0,0,7.8384161179933471,5.7369206681828473]
[3306.2979779391148,0,0,3213.8157769309987,2414.3103376897011,8934.4240925598151,9829.1491940000014,"2013-06-25T10:00:00",85,74,"ON",58955.253497139987,71362.972285633994,3480.3119999999999,"OFF",13029.497135820004,19306.821188056001,702.12159999999994,"OFF",-0.63329079549999856,-166.99199929652002,-8.8484060000000007,"ON",50611.256578750006,66404.669165182,3211.64,"ON",42323.63672857498,67463.908524056009,2443.924,null,3220.0264043713937,0,0,3211.5784746922013,2418.2588604948442,8849.8637395584392,3384.2006086174051,0,0,3368.2775389751878,2518.6025331983788,9271.0806807909721,260.28559562860619,0,0,6.1525307798547146E-2,25.665139505155821,96.111391382594775,0,0,-156.63753897518791,-74.678533198378773,239.2539513851699,-181.96298984736256,null,null,9829.1491940000014,null,126439.21250000014,15.591132435598475,16219.375086739386,360.75120410155813,15051.185975000013,313.99289504516747,-46.758309056390658,null,null,null,null,null,null,null,null,null,8849.8637395584392,86.271573567721134,0,0,2.2373022387973833,-3.9485228051430568]
[3446.8171161553619,0,0,3642.9423482956759,3129.8381902918472,10219.597654742884,10714.841187999999,"2013-06-26T07:00:00",78,73,"ON",62161.026034560011,87965.769811440012,3617.1889999999999,"OFF",-10.574846054524995,-107.29597975144002,-8.8484060000000007,"OFF",-9.5753170191001047E-2,-33.398399859304,-8.8484060000000007,"ON",58810.156855799993,85358.597719740006,3957.9059999999999,"ON",59898.6830844,85075.221654520006,3157.4430000000002,null,3353.0881792096352,0,0,3634.8460712709857,3123.3974274549059,10111.331677935526,3415.019847636036,0,0,3706.3723167610706,3195.8817734689019,10317.273937866008,264.10082079036465,0,0,323.05992872901425,34.045572545094274,202.1691523639638,0,0,251.53368323892937,-38.438773468901672,580.20181771325997,374.25955778277824,null,null,10714.841187999999,null,106383.78480000014,14.846661385558896,14331.004397187628,286.90743940123025,13165.975771200012,245.90293505001699,-41.004504351213257,null,null,null,null,null,null,null,null,null,10111.331677935526,93.728936945726673,0,0,8.0962770246901528,6.4407628369413032]
[0,0,0,0,0,0,-18.165303000000002,"2013-06-26T16:00:00",97,77,"OFF",-10.545197267840001,-75.14639166260001,2.794359,"OFF",-12.448504342424989,-112.72103124402001,-8.8484060000000007,"OFF",-0.42407154737499314,-33.398399859304,-2.737476,"OFF",-0.75350234580001108,-158.64239131086001,-3.9817830000000001,"OFF",-12.473728187399985,-118.98137238936,-5.3919969999999999,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-35.164320872136102,-35.164320872136102,null,null,-18.165303000000002,null,156871.89770000021,16.811024130497213,18662.979302422842,469.85669944660913,17911.85838380002,434.69237857447303,-35.164320872136102,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3494.2008054787188,0,3417.7321633123247,0,3418.8903671709554,10330.823335961999,11033.572164000001,"2013-06-27T07:00:00",80,73,"ON",62995.227762360002,86366.255095159999,3648.0450000000001,"OFF",-14.559738865290015,-110.63040086192001,-8.8484060000000007,"ON",64639.674954900009,94263.969293260001,3647.5160000000001,"OFF",-4.2489686875300015,-162.60845309884002,-2.82043,"ON",66097.08911772001,83616.793408300015,3749.68,null,3398.4357225478389,0,3403.386545092163,0,3406.9028139318925,10208.725081571894,3471.9118298529265,0,3433.2203529318617,0,3505.705753489889,10410.837936274676,249.60927745216122,0,244.12945490783704,0,342.77718606810731,176.13317014707354,0,214.29564706813835,0,243.97424651011079,792.45597876940781,590.34312406662491,null,null,11033.572164000001,null,112180.80000000005,15.044262742152085,14913.432704905359,308.70940805598821,13710.895200000004,264.64946839729043,-44.059939658697772,null,null,null,null,null,null,null,null,null,10208.725081571894,95.765082930879998,0,14.345618220161668,0,11.98755323906289]
[3383.7841261157423,0,3353.8684953608199,0,3356.2284881188993,10093.881109595461,10930.326467000001,"2013-06-27T23:00:00",85,72,"ON",61750.344608340005,86762.724919780012,3605.7049999999999,"OFF",-16.093583823240007,-110.63216544540002,-8.8484060000000007,"ON",64174.620145920002,92586.732695520011,3605.6260000000002,"OFF",-2.4693667114200175,-166.99199929652002,-2.7651270000000001,"ON",65640.499930275008,84330.40700928001,3730.6089999999999,null,3291.2213530616073,0,3339.9838131822739,0,3344.7025390915792,9975.9077053354595,3359.2531854652284,0,3378.6104855445424,0,3436.909018684722,10174.772689694493,314.48364693839267,0,265.64218681772627,0,385.90646090842074,246.45181453477153,0,227.01551445545783,0,293.69998131527791,913.95526936547503,715.09028500644263,null,null,10930.326467000001,null,126439.21250000014,15.469438681039154,16346.968381596977,366.06992034423206,15051.185975000013,313.99289504516747,-52.077025299064587,null,null,null,null,null,null,null,null,null,9975.9077053354595,92.56277305413505,0,13.884682178545972,0,11.525949027320166]
[3012.6564435856039,0,3153.3707510519953,0,2890.3044758074411,9056.3316704450408,9242.188811,"2013-06-28T14:00:00",100,75,"ON",52865.561020635017,82389.686014639999,3172.6860000000001,"OFF",-15.619322435199972,-109.82631225342,-8.8484060000000007,"ON",58880.925726250003,93248.611917200004,3088.8330000000001,"OFF",-1.8031325529000011,-166.99199929652002,-3.9817830000000001,"ON",52986.305212575011,80883.453597780011,2993.5,null,2939.8502788470309,0,3144.1097123792729,0,2888.8758019755742,8972.8357932018771,3009.7552874468092,0,3173.4965002523945,0,2965.5943748533946,9148.8461625525997,232.8357211529692,0,-55.276712379272794,0,104.62419802442582,162.93071255319092,0,-84.663500252394442,0,27.905625146605416,243.34269154445155,67.332322193731216,null,null,9242.188811,null,163082.00000000012,16.901012525583191,19298.488744759125,500.73653482444109,18495.608000000011,461.89601957077042,-38.840515253670674,null,null,null,null,null,null,null,null,null,8972.8357932018771,72.806164738572988,0,9.2610386727224068,0,1.428673831866945]
[3408.8228902570049,0,3450.4888619244748,0,3392.1450676969357,10251.456819878416,10867.045958999999,"2013-06-29T05:00:00",78,74,"ON",60787.025431729991,86161.082161440005,3585.0659999999998,"OFF",-16.896708642345043,-109.00136947652,-8.8484060000000007,"ON",64572.497204559993,93105.279613620005,3601.0619999999999,"OFF",-2.0008368279899962,-158.64239131086001,-1.852635,"ON",64687.231558850006,84138.949701699996,3691.6190000000001,null,3318.2311721708311,0,3436.1926830887955,0,3381.4906131256562,10135.914468385283,3387.850990231902,0,3472.4913352236586,0,3472.6420030102131,10332.984328465773,266.83482782916872,0,164.86931691120435,0,310.12838687434396,197.21500976809784,0,128.57066477634135,0,218.97699698978704,702.96963161345548,505.89977153296473,null,null,10867.045958999999,null,106383.78480000014,14.907508262838556,14272.510593228204,284.76583505127849,13165.975771200012,245.90293505001699,-38.862900001261494,null,null,null,null,null,null,null,null,null,10135.914468385283,90.591718086173842,0,14.296178835679257,0,10.65445457127953]
[3180.2957831243116,0,3177.6483015353783,0,3272.3743059034477,9630.3183905631377,10674.166811000001,"2013-06-29T21:00:00",86,69,"ON",60175.980865000012,86389.996763800009,3536.2530000000002,"OFF",-14.904925172280002,-108.54041214654002,-8.8484060000000007,"ON",62977.732163535009,91361.630510360017,3493.1120000000001,"OFF",-1.9004264243199975,-158.78155278076002,-3.9817830000000001,"ON",66497.168456789994,84091.305947740009,3657.6320000000001,null,3091.9821494170801,0,3164.9207884900475,0,3260.07467276122,9516.9776106683476,3158.2495241752058,0,3208.5915916271251,0,3355.9354656001742,9722.7765814025042,444.27085058292005,0,328.19121150995261,0,397.55732723878009,378.00347582479435,0,284.52040837287495,0,301.69653439982585,1108.8027103194675,903.00373958530986,null,null,10674.166811000001,null,129220.75440000021,15.381711747956874,16801.869196016414,385.37159485445795,15312.650913600019,324.1549158422726,-61.216679012185352,null,null,null,null,null,null,null,null,null,9516.9776106683476,88.313633707231475,0,12.727513045330852,0,12.299633142227776]
[2433.1023635806446,0,2343.7446710378122,0,2287.1083424670182,7063.9553770854745,7299.2348109999994,"2013-06-30T12:00:00",89,67,"ON",46190.856452130021,62459.990920646007,2535.248,"OFF",-14.516206798000002,-106.45732134840001,-8.8484060000000007,"ON",47680.810884174978,65260.088132548008,2438.1469999999999,"OFF",-2.7101796355899905,-166.92245866574001,-3.9817830000000001,"ON",43925.730955999999,66258.489465532009,2338.67,null,2374.7839744985022,0,2341.799841750566,0,2290.3734530113138,7006.9572692603815,2523.1275323732775,0,2481.4947393379825,0,2403.0393784146572,7407.6616501259168,160.46402550149787,0,96.34715824943396,0,48.296546988686259,12.12046762672253,0,-43.347739337982603,0,-64.369378414657149,235.82304348062678,-164.88133738490853,null,null,7299.2348109999994,null,137357.58810000028,15.537376137549604,17680.924614812462,424.17132190039194,16077.513281400026,354.88663464140063,-69.284687258991312,null,null,null,null,null,null,null,null,null,7006.9572692603815,58.318389082142403,0,1.9448292872461934,0,-3.2651105442955668]
[3007.0191895289045,0,3158.9470070612829,0,2946.4970389341788,9112.4632355243666,10399.683611,"2013-06-30T22:00:00",80,64,"ON",60594.832843605,65325.337617138008,3522.6570000000002,"OFF",-16.548010056959974,-105.76568483258001,-8.8484060000000007,"ON",65985.385094475001,68111.687119563998,3520.7530000000002,"OFF",-3.3837918025100082,-158.85109341154001,-1.824983,"ON",63650.232264019993,67988.342734312013,3366.9470000000001,null,2918.5543180554932,0,3143.4351708225117,0,2936.956543913479,8998.946032791484,3144.631204755377,0,3381.5936490299914,0,3154.647077232918,9680.871931018286,604.10268194450691,0,377.31782917748842,0,429.99045608652114,378.02579524462317,0,139.15935097000875,0,212.29992276708208,1345.4363528734577,663.51045464665526,null,null,10399.683611,null,112180.80000000005,14.496640846635142,15476.79923739556,330.62408273234917,13710.895200000004,264.64946839729043,-65.974614335058732,null,null,null,null,null,null,null,null,null,8998.946032791484,88.464871473411222,0,15.511836238771139,0,9.5404950206998365]
[0,0,0,0,0,0,133.72879299999997,"2013-07-01T18:00:00",86,65,"OFF",309.6607622800002,4001.2251242360003,154.2276,"OFF",-15.427883899979983,-110.63216544540002,-8.8484060000000007,"OFF",0.22226722625599943,-33.746303534054,-3.9817830000000001,"OFF",-6.1848526915699944,-166.99199929652002,-1.89872,"check",-1348.5013988999845,62034.710260298009,-5.7698980000000004,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-72.929267635758436,-72.929267635758436,null,null,133.72879299999997,null,129220.75440000021,15.138324238838234,17072.002470191121,397.08418347803104,15312.650913600019,324.1549158422726,-72.929267635758436,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2633.9901047607091,0,2466.0641617063311,0,0,5100.0542664670402,5239.5410279999996,"2013-07-02T09:00:00",78,64,"ON",52791.46609438501,58685.169877728003,2708.6559999999999,"OFF",-13.594209824725043,-105.06578685774001,-8.8484060000000007,"ON",52135.440023700015,69085.312096322014,2547.6970000000001,"OFF",-7.108210442830031,-159.30338824080002,-3.9817830000000001,"OFF",-0.26121599399000106,-120.37338813006001,-3.9817830000000001,null,2562.8189324436566,0,2461.6272628017387,0,0,5024.4461952453948,2789.7257336834296,0,2601.6396143583656,0,0,5391.3653480417952,145.8370675563433,0,86.069737198261464,0,0,-81.069733683429604,0,-53.942614358365518,0,0,170.38100346324802,-196.53814933315186,null,null,5239.5410279999996,null,106383.78480000014,14.299039490041952,14879.85047864051,307.42873634137374,13165.975771200012,245.90293505001699,-61.525801291356743,null,null,null,null,null,null,null,null,null,5024.4461952453948,71.171172317052424,0,4.4368989045924536,0,0]
[2583.3744677864975,0,2721.8825545821355,0,2492.1575606330025,7797.414583001635,8338.1862380000002,"2013-07-03T01:00:00",73,60,"ON",54752.144427219995,66735.376171836018,2814.4029999999998,"OFF",-15.981455101119973,-107.8489360474,-8.8484060000000007,"ON",60223.810459679997,74308.302738774,2825.1489999999999,"OFF",-8.0636361805999872,-166.99199929652002,-3.7513559999999999,"ON",55700.357421300003,69039.817925873998,2711.2339999999999,null,2508.602937240295,0,2711.6450099984704,0,2488.9550128144738,7709.2029600532396,2679.7119421196462,0,2855.8636682370766,0,2646.1327182631694,8181.7083286198922,305.80006275970482,0,113.50399000152947,0,222.27898718552615,134.69105788035358,0,-30.714668237076694,0,65.101281736830515,584.82237903520286,112.31701046854985,null,null,8338.1862380000002,null,91919.663300000131,13.562617215320358,13554.8562406034,259.2036834603839,11806.348350200013,202.44302254882635,-56.760660911557551,null,null,null,null,null,null,null,null,null,7709.2029600532396,74.771530546202484,0,10.237544583665112,0,3.2025478185287284]
[0,0,0,0,0,0,-17.493777999999999,"2013-07-03T16:00:00",90,63,"OFF",-10.435031430155,-166.99199929652002,1.235349,"OFF",-15.656828167844957,-105.40931917796001,-8.8484060000000007,"OFF",0.68177485300000207,-166.99199929652002,-3.8527439999999999,"OFF",-8.6501614983699788,-165.94832837644,-2.0461939999999998,"OFF",-5.1065235622099872,-116.17319819762001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-82.850035396711462,-82.850035396711462,null,null,-17.493777999999999,null,139988.10000000021,15.383654206671039,18199.590047895788,447.9920997266783,16324.78140000002,365.14206432996684,-82.850035396711462,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2008.1960531756308,0,1799.5002480370899,0,1727.8036718685482,5535.4999730812688,6254.8699130000005,"2013-07-04T07:00:00",74,66,"ON",36572.210833439996,60131.935831312003,2160.2220000000002,"OFF",-15.597497250620021,-108.5447433969,-8.8484060000000007,"ON",35193.339776929999,65264.291049564003,2041.42,"OFF",-8.3172552193500184,-166.99199929652002,-1.7696810000000001,"ON",27457.483035359997,64233.036380516009,2063.846,null,1966.9637903856303,0,1801.8332155229259,0,1734.4998947247825,5503.2969006333387,2069.4052987456889,0,1877.474200577487,0,1783.6415716589142,5730.5210709820904,193.25820961436989,0,239.58678447707416,0,329.3461052752175,90.816701254311283,0,163.94579942251312,0,280.20442834108576,714.99440912192495,487.7702387731735,null,null,6254.8699130000005,null,94794.23760000011,14.025683349092834,13517.23623592733,257.90006458606956,12076.55833440001,210.7033743413329,-47.196690244736658,null,null,null,null,null,null,null,null,null,5503.2969006333387,41.232262790000505,0,-2.3329674858359795,0,-6.6962228562342716]
[3016.5969385051444,0,3024.9979674380593,0,2879.065500236426,8920.6604061796297,9692.0939130000006,"2013-07-04T23:00:00",79,67,"ON",58493.66487624999,62271.966530018006,3237.89,"OFF",-15.253289070044955,-109.56010077296001,-8.8484060000000007,"ON",61465.822483500022,68038.585238488013,3198.2959999999998,"OFF",-8.4275827949600259,-160.10354664064002,-1.7696810000000001,"ON",59243.370930119985,65802.529115133992,3266.5259999999998,null,2932.5011341232957,0,3013.6406777757343,0,2873.2034077306298,8819.3452196296603,3174.2373811163716,0,3220.9412674195232,0,3082.3852681080225,9477.5639166439178,305.38886587670413,0,184.65532222426555,0,393.32259226937003,63.652618883628293,0,-22.645267419523407,0,184.14073189197734,826.89351188752255,168.67481487326506,null,null,9692.0939130000006,null,109285.23110000021,14.580480970883762,14990.620860619818,311.66395364716806,13438.71172340002,255.1906851643509,-56.473268482817161,null,null,null,null,null,null,null,null,null,8819.3452196296603,84.095804381848666,0,11.357289662325002,0,5.8620925057962268]
[2453.7569509470682,0,2327.3665055743386,0,2330.8245572498704,7111.9480137712781,7023.8569130000014,"2013-07-05T11:00:00",90,70,"ON",44682.279428170019,61504.035841190002,2381.201,"OFF",-14.742615252419958,-111.32797279490001,-8.8484060000000007,"ON",45675.729794570012,64576.247867376005,2350.5120000000002,"OFF",-7.0125861839600097,-166.99199929652002,-1.7696810000000001,"ON",42908.14043330001,65280.821988438009,2302.7620000000002,null,2397.973051056953,0,2326.3926372201959,0,2334.5166544432159,7058.8823427203642,2543.3263941361288,0,2458.971458347607,0,2447.4891307904113,7449.7869832741471,-16.772051056952932,0,24.119362779804305,0,-31.754654443215713,-162.12539413612876,0,-108.45945834760687,0,-144.72713079041114,-84.720738500055859,-475.62537905383829,null,null,7023.8569130000014,null,139988.10000000021,15.809582347628663,17709.272379481619,425.45546010965836,16324.78140000002,365.14206432996684,-60.313395779691518,null,null,null,null,null,null,null,null,null,7058.8823427203642,55.783899890115208,0,0.97386835414272355,0,-3.6920971933454894]
[2407.4732782205083,0,2499.8891386190962,0,2504.1027791710449,7411.4651960106494,7604.197913,"2013-07-06T05:00:00",75,66,"ON",46288.014815354996,84618.114324860013,2456.0100000000002,"OFF",-13.674524518249974,-105.76159420724001,-8.8484060000000007,"ON",51636.000082099992,90789.183587780004,2622.4780000000001,"OFF",-8.6702665712599938,-160.52103105034001,-1.7696810000000001,"ON",50627.415917429993,82789.604797880005,2536.328,null,2349.0789408642099,0,2495.757944456383,0,2504.0920836271225,7348.9289689477155,2393.7605895335309,0,2526.7960012189374,0,2564.6854069387837,7485.2419976912524,106.93105913579029,0,126.72005554361704,0,32.235916372877455,62.249410466469271,0,95.681998781062703,0,-28.357406938783697,216.16011699246874,79.847088248932238,null,null,7604.197913,null,{"$f":" -0.6251*I3781^3 + 145.21*I3781^2 - 8340.3*I3781 + 170112","v":97681.6875},14.124107106431758,13831.909764478953,268.91581149784088,12347.978625,219.18889743802484,-49.726914059816039,null,null,null,null,null,null,null,null,null,7348.9289689477155,58.394337356298365,0,4.1311941627132001,0,1.0695543922338402E-2]
[3228.5862349314343,0,3185.2747795666514,0,0,6413.8610144980858,7034.5048369999995,"2013-07-06T20:00:00",88,67,"ON",62586.194134019999,88802.021964280008,3522.3449999999998,"OFF",-13.799036642294995,-107.85334750610001,-8.8484060000000007,"ON",64424.374545619983,99529.165564220006,3528.4279999999999,"OFF",-12.957053812559963,-164.93938766758004,-3.4379740000000001,"OFF",593.95063655549961,6607.6793512929999,-3.9817830000000001,null,3134.876880287391,0,3171.2273960525877,0,0,6306.1042763399782,3192.1096025554798,0,3173.5052574280703,0,0,6365.6148599835506,387.46811971260877,0,357.20060394741222,0,0,330.23539744452,0,354.92274257192958,0,0,675.99365557688293,616.48307193331152,null,null,7034.5048369999995,null,134683.69280000008,15.446231760583299,17439.035602676209,413.29755232180275,15826.167123200006,344.6224842386647,-68.675068083138058,null,null,null,null,null,null,null,null,null,6306.1042763399782,93.709354644043287,0,14.047383514063768,0,0]
[2987.3802484145986,0,2912.5510918234436,0,2745.6627264925246,8645.5940667305658,8817.702913000001,"2013-07-07T11:00:00",91,73,"ON",53695.432569609999,67572.831449776015,3033.5430000000001,"OFF",-13.484732480910001,-107.8489360474,-8.8484060000000007,"ON",55692.098546134999,71151.952163927999,2917.01,"OFF",-6.9278181374500267,-160.86897482926003,-1.7696810000000001,"ON",51134.722792124994,69014.736777956001,2877.768,null,2913.0613602605927,0,2905.7340200059357,0,2745.3709245192549,8564.1663047857837,3075.2298941483527,0,3052.9761027759405,0,2881.1150801581475,9009.3210770824408,120.48163973940746,0,11.275979994064528,0,132.39707548074512,-41.686894148352621,0,-135.96610277594027,0,-3.3470801581474916,213.00838895120955,-232.14638334544793,null,null,8817.702913000001,null,142571.47790000017,16.080181913250129,17732.570274285361,426.51238212156005,16567.618922600017,375.36607585855251,-51.146306263007546,null,null,null,null,null,null,null,null,null,8564.1663047857837,74.31888815400589,0,6.8170718175078946,0,0.29180197326968482]
[3352.8075101658533,0,3298.6058469114314,0,3355.6250890463998,10007.038446123684,10701.889912999999,"2013-07-08T03:00:00",80,73,"ON",60485.719231619994,83631.150701160004,3568.078,"OFF",-12.693272328224998,-105.52385668748001,-8.8484060000000007,"ON",62601.913517055007,89279.662628980004,3523.5680000000002,"OFF",-10.114797517379969,-166.99199929652002,-1.7696810000000001,"ON",64766.598304275023,82165.102662639998,3620.8620000000001,null,3263.1001478113672,0,3286.1702147042861,0,3344.9130146979237,9894.1833772135778,3346.9849158128941,0,3341.3402951849521,0,3450.0060916634184,10138.331302661263,304.97785218863282,0,237.39778529571413,0,275.94898530207638,221.09308418710589,0,182.22770481504813,0,170.85590833658171,774.26468312772556,530.11675768003795,null,null,10701.889912999999,null,112180.80000000005,15.044262742152085,14913.432704905359,308.70940805598821,13710.895200000004,264.64946839729043,-44.059939658697772,null,null,null,null,null,null,null,null,null,9894.1833772135778,89.707362354486122,0,12.435632207145318,0,10.712074348476108]
[3190.1244171885028,0,0,0,0,3190.1244171885028,3385.3373469999992,"2013-07-08T18:00:00",93,76,"ON",55511.652368050003,81126.003617940005,3403.9189999999999,"OFF",-10.453031048139962,-102.99007522688001,-8.8484060000000007,"OFF",-0.7490903995,-33.398399859304,-3.9817830000000001,"OFF",-9.1344486997400196,-164.34793136842001,-1.7696810000000001,"check",1553.6381818599934,56267.610301788001,-3.9817830000000001,null,3111.3958603172655,0,0,0,0,3111.3958603172655,3195.6078942930467,0,0,0,0,3195.6078942930467,292.52313968273438,0,0,0,0,208.31110570695319,0,0,0,0,251.19581904859069,166.9837850728095,null,null,3385.3373469999992,null,147581.8293000001,16.433509096355799,17961.085296472316,436.95274883475719,17038.591954200008,395.6254282006135,-41.327320634143689,null,null,null,null,null,null,null,null,null,3111.3958603172655,78.728556871237288,0,0,0,0]
[3075.0719674520174,0,2871.5683049032064,0,3013.0179784422526,8959.6582507974763,9393.1463960000001,"2013-07-09T09:00:00",86,74,"ON",54698.236328924984,61662.800229386005,3117.8040000000001,"OFF",-9.5422462319800019,-105.76159420724001,-8.8484060000000007,"ON",54362.922254375,66242.415714196002,3134.75,"OFF",-11.941218977359966,-164.17403968730002,-3.235198,"ON",56509.659710280022,65261.908861866003,3152.6759999999999,null,2998.4296712469409,0,2865.6807892127417,0,3009.1832172902027,8873.2936777498853,3217.5789923112638,0,3042.4192435927948,0,3206.4999046729413,9466.4981405769995,119.37432875305922,0,269.06921078725827,0,143.49278270979721,-99.774992311263759,0,92.330756407205172,0,-53.823904672941353,484.60063648304174,-108.6038263440729,null,null,9393.1463960000001,null,129220.75440000021,15.685946134355177,16475.991093324286,371.49060160934556,15312.650913600019,324.1549158422726,-47.33568576707296,null,null,null,null,null,null,null,null,null,8873.2936777498853,76.642296205076491,0,5.8875156904646246,0,3.8347611520498504]
[3381.6980473625258,0,3305.1842037285073,0,3374.1294840964015,10061.011735187434,10861.010913000002,"2013-07-10T01:00:00",87,72,"ON",61712.884820475017,82541.359985580013,3587.3560000000002,"OFF",-9.5937910852499719,-111.32797279490001,-8.8484060000000007,"ON",63333.601152225019,89081.62823752001,3584.34,"OFF",-8.4924038687600056,-163.96525737828,-1.7696810000000001,"ON",66020.819553000008,82328.086009520019,3699.933,null,3289.2255189356019,0,3292.0896303206614,0,3362.2356100775341,9943.550759333797,3383.5401822957792,0,3349.6804645031757,0,3470.0754780475886,10203.296124846544,298.13048106439828,0,292.25036967933875,0,337.69738992246585,203.81581770422099,0,234.65953549682445,0,229.85752195241139,874.71973386173806,614.97436834899202,null,null,10861.010913000002,null,131970.16469999996,15.657970817020455,16856.611401593156,387.73004536873009,15571.095481799995,334.37153856426528,-53.35850680446481,null,null,null,null,null,null,null,null,null,9943.550759333797,92.472528426923873,0,13.094573407845928,0,11.893874018867336]
[0,0,0,0,0,0,-19.106923999999999,"2013-07-10T16:00:00",102,73,"OFF",-1.0743474433600047,-73.754793005267999,1.391883,"OFF",-8.2887281271600308,-106.97923701678,-8.8484060000000007,"OFF",-1.654618006749994,-46.618603145626004,-3.9817830000000001,"OFF",-8.7635456774600211,-166.99199929652002,-2.6176529999999998,"OFF",-2.0738896359000041,-117.59015873206,-5.0509649999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-43.820199901260651,-43.820199901260651,null,null,-19.106923999999999,null,166805.11920000007,16.906227771482961,19732.979048272748,522.44379151305111,18845.581204800008,478.62359161179046,-43.820199901260651,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,3270.4801043419061,3540.9122394535511,3410.7542298419876,10222.146573637445,11248.395811999999,"2013-07-11T07:00:00",85,74,"OFF",-2.6451427534200129,-75.14639166260001,1.4372180000000001,"OFF",-9.0274648650799936,-112.69408124178001,-8.8484060000000007,"ON",61509.618440619997,90423.51376572001,3646.627,"ON",56453.92971524001,84528.76223410001,3947.9859999999999,"ON",65075.129516214998,85062.308111780003,3661.194,null,0,0,3259.0096682324006,3534.6826253993863,3399.7328799517563,10193.425173583542,0,0,3305.9965229809759,3605.0356536027175,3485.6549100260199,10396.687086609712,0,0,387.61733176759935,413.30337460061355,261.46112004824363,0,0,340.63047701902406,342.95034639728237,175.53908997398003,1015.6235173600659,812.3616043338958,null,null,11248.395811999999,null,126439.21250000014,15.591132435598475,16219.375086739386,360.75120410155813,15051.185975000013,313.99289504516747,-46.758309056390658,null,null,null,null,null,null,null,null,null,10193.425173583542,0,0,11.470436109505499,6.2296140541648128,11.021349890231249]
[3443.8244844253395,0,3519.3513601780501,0,3364.9410893210256,10328.116933924415,11028.39977,"2013-07-11T22:00:00",83,73,"ON",62108.113692905012,86067.077986960008,3623.2779999999998,"OFF",-7.8454219647600123,-105.58698065106,-8.8484060000000007,"ON",66346.05997147999,92522.566023520019,3641.6419999999998,"OFF",-2.5882843968099998,-162.19096868914002,-2.7098239999999998,"ON",64963.403433900021,83812.581966240017,3775.038,null,3350.2239414594778,0,3503.3161945747206,0,3354.0432859896973,10207.583422023896,3423.4193291466008,0,3545.1540264001178,0,3448.0803919802393,10416.653747526958,273.05405854052196,0,138.32580542527921,0,420.99471401030269,199.85867085339896,0,96.487973599882025,0,326.95760801976076,784.69318388852366,575.62285838546154,null,null,11028.39977,null,120794.73630000022,15.337883759134646,15751.160746417781,341.59080302015025,14520.60521220002,293.9094089325701,-47.681394087580145,null,null,null,null,null,null,null,null,null,10207.583422023896,93.600542965861678,0,16.03516560332946,0,10.897803331328305]
[3319.035305417709,0,3346.3228743150303,0,3187.2101800107703,9852.5683597435091,10372.35204,"2013-07-12T13:00:00",96,75,"ON",58503.47171097,84726.636208880009,3554.4340000000002,"OFF",-7.0476540521999871,-110.83060087856001,-8.8484060000000007,"ON",62209.552617179994,89727.626207880006,3432.8009999999999,"OFF",0.18416035967000238,-163.26945002878,-2.9955539999999998,"ON",59531.381423999992,83168.348579360012,3396.9609999999998,null,3233.6550453010163,0,3334.2181329839491,0,3181.0489334062345,9748.9221116911995,3306.0704159274842,0,3386.3043333427709,0,3263.9816582132062,9956.3564074834612,320.77895469898385,0,98.582867016050841,0,215.9120665937653,248.36358407251601,0,46.496666657229071,0,132.97934178679361,592.76883493622529,385.33453914396398,null,null,10372.35204,null,154650.08640000015,16.613596069259849,18617.292217203878,467.67656896097293,17703.008121600014,425.17151558839822,-42.505053372574707,null,null,null,null,null,null,null,null,null,9748.9221116911995,85.380260116692625,0,12.104741331081186,0,6.1612466045357905]
[3455.0738489197965,0,3419.3445132415677,0,3372.3395517167651,10246.757913878129,10978.018559,"2013-07-13T05:00:00",81,73,"ON",62306.871992285,85608.446698840009,3641.616,"OFF",-6.7035706927800094,-110.67275086544001,-8.8484060000000007,"ON",64666.974528900006,91515.229481460017,3630.7550000000001,"OFF",-2.6048849157099889,-158.64239131086001,-2.9310350000000001,"ON",65119.479942720005,83691.948622880009,3717.4270000000001,null,3360.9905442374647,0,3404.9725137869741,0,3361.2937311147502,10127.25678913919,3437.5099575907416,0,3450.4999065230263,0,3456.6334449120213,10344.643309025789,280.62545576253524,0,225.782486213026,0,356.13326888524989,204.10604240925841,0,180.2550934769738,0,260.7935550879788,817.14035178972131,599.75383190312118,null,null,10978.018559,null,115066.74090000021,15.142635062598616,15197.7169659471,319.66636925060652,13982.17364460002,274.2655101795167,-45.400859071089826,null,null,null,null,null,null,null,null,null,10127.25678913919,94.0833046823318,0,14.371999454593606,0,11.045820602014828]
[3352.0328321927173,0,3444.4842048758283,0,3353.798490286068,10150.315527354614,11030.679645,"2013-07-13T20:00:00",91,70,"ON",62627.748668835004,86118.651949580017,3653.8629999999998,"OFF",-5.5590550957250189,-112.57818019048001,-8.8484060000000007,"ON",67011.132305509978,92834.255632760003,3638.0880000000002,"OFF",-4.7020574533799895,-162.85196561908,-2.8849490000000002,"ON",67362.798700450003,84177.529913240011,3750.462,null,3257.6953050689349,0,3427.8264625856436,0,3340.6193107765516,10026.14107843113,3331.4191652996255,0,3468.4151350412772,0,3438.5670841861452,10238.401384527047,396.16769493106494,0,210.26153741435655,0,409.84268922344836,322.44383470037428,0,169.67286495872304,0,311.89491581385482,955.82960901609067,743.56930292017296,null,null,11030.679645,null,142571.47790000017,15.897641281411147,17936.18001265467,435.80838841133163,16567.618922600017,375.36607585855251,-60.442312552779129,null,null,null,null,null,null,null,null,null,10026.14107843113,94.337527123782365,0,16.657742290184615,0,13.179179509516416]
[3222.9010688167709,0,0,3449.8833700449659,2986.9819637712308,9659.7664026329676,10220.505912999999,"2013-07-14T11:00:00",71,68,"ON",61722.091356629993,89457.48451876,3525.6439999999998,"OFF",-6.2514690841349729,-107.71667249474001,-8.8484060000000007,"OFF",-0.38920752825000243,-166.99199929652002,-1.7696810000000001,"ON",58561.965265229999,86560.920736340006,3714.5309999999999,"ON",60919.887687459996,86619.312407860009,2990.9490000000001,null,3131.0938231538466,0,0,3442.0340817492338,2979.7510132130637,9552.8789181161446,3183.1675639312475,0,0,3505.6463729209854,3045.1652669531518,9733.9792038053856,394.55017684615314,0,0,272.49691825076616,11.197986786936326,342.47643606875226,0,0,208.88462707901454,-54.216266953151717,642.56040553760647,461.46011984836593,null,null,10220.505912999999,null,86224.143900000025,13.855250538027352,12446.421472256716,222.31316155526787,11270.969526600002,186.62848520901872,-35.684676346249148,null,null,null,null,null,null,null,null,null,9552.8789181161446,91.807245662924288,0,0,7.8492882957320944,7.2309505581670237]
[0,0,0,0,0,0,-15.869635000000001,"2013-07-14T15:00:00",71,68,"OFF",-7.259340315689994,-73.058993676602014,1.550665,"OFF",-6.6470360878700303,-109.80762371020002,-8.8484060000000007,"OFF",1.5568301130000013,-166.99199929652002,-1.7696810000000001,"OFF",-3.7983041244399964,-162.60845309884002,-2.82043,"OFF",-7.058886761079993,-118.98177343106001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-35.684676346249148,-35.684676346249148,null,null,-15.869635000000001,null,86224.143900000025,13.855250538027352,12446.421472256716,222.31316155526787,11270.969526600002,186.62848520901872,-35.684676346249148,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2717.5972566871328,0,2772.2928014563295,0,2559.8402219664672,8049.7302801099304,8617.1534740000006,"2013-07-15T02:00:00",69,66,"ON",53119.888061589991,73118.38795237201,2868.5,"OFF",20.513862062984987,-111.32797279490001,-8.8484060000000007,"ON",57230.414228880014,65023.457487880005,3033.5880000000002,"OFF",-2.9557777755550014,-166.99199929652002,-2.9771200000000002,"ON",52096.67929782001,74710.627772214008,2726.8910000000001,null,2645.4649507924078,0,2764.3733263096856,0,2558.9648826862372,7968.803159788331,2765.1939809966498,0,2969.167676413706,0,2663.6624736981789,8398.0241311085356,223.03504920759224,0,269.21467369031461,0,167.92611731376292,103.30601900335023,0,64.420323586294217,0,63.228526301821148,626.48099776652691,197.26002644632271,null,null,8617.1534740000006,null,80625.134100000141,13.542704785691907,11906.799324929823,205.4919938101111,10744.662605400013,171.79715136496822,-33.694842445142882,null,null,null,null,null,null,null,null,null,7968.803159788331,72.13230589472505,0,7.9194751466438902,0,0.87533928023003682]
[0,0,0,0,0,0,1245.243925,"2013-07-15T18:00:00",74,71,"check",9111.6687428000005,29323.110353912001,1262.867,"OFF",7.8443402426899587,-108.61011319400001,-8.8484060000000007,"OFF",-0.34764474562499903,-33.398399859304,-1.7696810000000001,"OFF",-5.8870973525699952,-166.99199929652002,-3.0232049999999999,"check",-102.67564343000214,53796.648013076003,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-37.371396575176362,-37.371396575176362,null,null,1245.243925,null,94794.23760000011,14.329917735491136,13230.255658093794,248.07477091650927,12076.55833440001,210.7033743413329,-37.371396575176362,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2409.244805140559,0,2218.7765774882951,0,2372.5905735936331,7000.6119562224876,7198.974913,"2013-07-16T09:00:00",77,73,"ON",41857.397320700002,67597.575722666006,2427.627,"OFF",15.535573289799993,-106.48635676748002,-8.8484060000000007,"ON",41807.011799279979,58654.570396018004,2434.0360000000001,"OFF",8.5769347650001382E-2,-166.99199929652002,-1.7696810000000001,"ON",41927.679874079993,70995.634130102015,2347.9299999999998,null,2358.3567437168858,0,2219.3837615038615,0,2376.6750780522284,6954.4155832729757,2456.3324200912471,0,2362.7810129235504,0,2459.8785491096246,7278.9919821244221,69.270256283114122,0,214.65223849613858,0,-28.745078052228564,-28.705420091247106,0,71.254987076449652,0,-111.94854910962476,215.87341330301999,-108.70298554842637,null,null,7198.974913,null,103480.2117000001,14.747688040874978,14033.414785177492,276.10301508203298,12893.039899800009,236.79901165802883,-39.304003424004151,null,null,null,null,null,null,null,null,null,6954.4155832729757,50.888061423673207,0,-0.60718401556641766,0,-4.0845044585953474]
[3133.8210961057252,0,0,0,3058.3855069666411,6192.2066030723663,7242.1282319999991,"2013-07-17",72,70,"ON",58569.918478440006,82034.363068440012,3592.8249999999998,"OFF",7.7718659337000364,-108.5447433969,-8.8484060000000007,"OFF",0.53784512675000051,-166.99199929652002,-1.7696810000000001,"OFF",-7.3036205946399981,-163.79128548881999,-1.7696810000000001,"ON",60819.983747324986,81532.258860040005,3661.6909999999998,null,3049.0768698225015,0,0,0,3051.2160806130191,6100.2929504355207,3136.5104875704715,0,0,0,3147.3040824517593,6283.8145700222303,543.7481301774983,0,0,0,610.47491938698067,456.31451242952835,0,0,0,514.38691754824049,1119.575320451243,936.05370086453286,null,null,7242.1282319999991,null,89061.715200000035,14.073667850998234,12656.503783224209,229.06347265890398,11537.701228800002,194.41574354566797,-34.647729113236011,null,null,null,null,null,null,null,null,null,6100.2929504355207,84.744226283223725,0,0,0,7.1694263536219296]
[0,0,0,0,0,0,-15.732803000000001,"2013-07-17T16:00:00",88,74,"OFF",-16.217609942610004,-75.14639166260001,1.5861080000000001,"OFF",2.5961248083750275,-110.63216544540002,-8.8484060000000007,"OFF",-1.2891606399999993,-51.315250619330001,-2.7190409999999998,"OFF",-5.869047582019995,-166.99199929652002,-1.7696810000000001,"OFF",-15.925457476390012,-117.59015873206,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-48.06313974353327,-48.06313974353327,null,null,-15.732803000000001,null,134683.69280000008,15.87215990154092,16971.060477651128,392.68562398219797,15826.167123200006,344.6224842386647,-48.06313974353327,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,2356.4981284587134,2669.5964523524099,2341.363686458023,7367.4582672691458,7134.9474849999988,"2013-07-18T07:00:00",78,74,"OFF",-5.848957782239995,-74.450592333934011,1.990891,"OFF",1.6207627657949977,-109.16202678154001,-8.8484060000000007,"ON",44244.867148999998,82040.298485600011,2386.7139999999999,"ON",39929.266231199996,89566.166819460006,2554.6210000000001,"ON",40465.631245325007,86498.117606120009,2200.4699999999998,null,0,0,2356.1715653247256,2672.3082956285948,2345.9609080308924,7374.4407689842137,0,0,2405.8388692751337,2694.6234924856831,2375.5538516343136,7476.0162133951308,0,0,30.542434675274308,-117.68729562859471,-145.49090803089257,0,0,-19.124869275133733,-140.00249248568298,-175.08385163431376,-271.49866898547447,-373.07411339639197,null,null,7134.9474849999988,null,106383.78480000014,14.907508262838556,14272.510593228204,284.76583505127849,13165.975771200012,245.90293505001699,-38.862900001261494,null,null,null,null,null,null,null,null,null,7374.4407689842137,0,0,0.32656313398774728,-2.7118432761849363,-4.59722157286933]
[3315.7606847307984,0,3252.1715828989659,0,3339.5749978629542,9907.5072654927189,10782.143309999999,"2013-07-18T23:00:00",80,73,"ON",59817.915094575008,85369.105012280008,3589.8159999999998,"OFF",0.39332289813998161,-110.63360919552001,-8.8484060000000007,"ON",61796.217928250007,92728.621248980009,3564.44,"OFF",-4.1737657019100025,-164.34793136842001,-3.2812839999999999,"ON",64426.805179840012,82965.742312520015,3640.0169999999998,null,3227.6313534653382,0,3240.4590276539061,0,3329.1811957304399,9797.2715768496837,3299.3981497401887,0,3275.5067309005676,0,3427.5108338144764,10002.415714455234,362.18464653466162,0,323.98097234609395,0,310.83580426955996,290.41785025981108,0,288.93326909943244,0,212.5061661855234,952.94148349161776,747.79734588606914,null,null,10782.143309999999,null,112180.80000000005,15.044262742152085,14913.432704905359,308.70940805598821,13710.895200000004,264.64946839729043,-44.059939658697772,null,null,null,null,null,null,null,null,null,9797.2715768496837,88.129331265460223,0,11.712555245059775,0,10.393802132514338]
[3408.2173204775995,0,0,3749.519099406858,3350.4611728549944,10508.197592739452,11120.780677000001,"2013-07-19T20:00:00",81,74,"ON",60776.301185880016,88101.16148936002,3609.87,"OFF",-1.837019710799954,-109.2405507464,-8.8484060000000007,"OFF",-6.4308709665004586E-3,-33.398399859304,-2.543917,"ON",59995.914296325005,87717.926040840015,3861.087,"ON",63814.014262660014,85119.737283220005,3661.2159999999999,null,3317.651207141585,0,0,3740.411487495136,3340.6181577389802,10398.680852375701,3376.1410462493172,0,0,3801.2950894908336,3422.8329743278809,10600.269110068031,292.21879285841487,0,0,120.67551250486395,320.59784226101965,233.72895375068265,0,0,59.791910509166428,238.38302567211895,690.45297355516129,488.86471586283085,null,null,11120.780677000001,null,115066.74090000021,15.203481939878277,15136.89316105722,317.30468424865387,13982.17364460002,274.2655101795167,-43.039174069137175,null,null,null,null,null,null,null,null,null,10398.680852375701,90.566113336014496,0,0,9.1076119117219605,9.8430151160141577]
[3120.5453764375184,0,0,3471.9159937022428,3005.5726599209138,9598.0340300606749,9782.6783959999993,"2013-07-20T04:00:00",75,71,"ON",57607.642035495002,85041.534151719999,3145.8510000000001,"OFF",-3.4618817987600012,-105.76159420724001,-8.8484060000000007,"OFF",-3.5882886999997921E-2,-75.14639166260001,-3.235198,"ON",57060.972714280004,85149.173744000014,3564.47,"ON",58767.876398400003,83014.508983240012,3084.4409999999998,null,3037.8457234337375,0,0,3465.2372640259514,3000.0514831611786,9503.1344706208674,3105.803966339819,0,0,3533.3903400102795,3081.1651471410664,9720.3594534911645,108.00527656626264,0,0,99.23273597404841,84.389516838821237,40.047033660181114,0,0,31.079659989720312,3.2758528589333764,252.11925523455531,34.89427236425783,null,null,9782.6783959999993,null,97681.6875,14.428341492830061,13540.25167044201,258.69717158260181,12347.978625,219.18889743802484,-39.508274144576973,null,null,null,null,null,null,null,null,null,9503.1344706208674,82.699653003780895,0,0,6.6787296762913684,5.5211767597352264]
[0,3422.5563092098951,0,3649.9740957855452,3373.7684741897247,10446.298879185164,11036.462874000001,"2013-07-20T20:00:00",80,73,"OFF",-6.927487959074992,-73.754793005267999,2.0185550000000001,"ON",54728.427471899995,88706.33341466001,3509.5210000000002,"OFF",0.14095510049999768,-62.100144224070007,-1.7696810000000001,"ON",58930.056772600008,85559.519611440002,3870.1860000000001,"ON",65149.601866109988,85317.851883020019,3656.5070000000001,null,0,3422.1732964101893,0,3641.7784135490465,3362.6940132238906,10426.645723183126,0,3468.6003088651041,0,3712.4469303457458,3446.9296539844258,10627.976893195275,0,87.347703589810862,0,228.40758645095366,293.81298677610948,0,40.92069113489606,0,157.73906965425431,209.57734601557422,565.50833715817623,364.17716714602682,null,null,11036.462874000001,null,112180.80000000005,15.044262742152085,14913.432704905359,308.70940805598821,13710.895200000004,264.64946839729043,-44.059939658697772,null,null,null,null,null,null,null,null,null,10426.645723183126,0,0.38301279970573887,0,8.1956822364986692,11.074460965834078]
[0,3204.7036603173656,0,3614.8747186995311,3267.6075416788603,10087.185920695758,10510.704909,"2013-07-21T11:00:00",91,77,"OFF",-11.588542291359998,-74.450592333934011,1.631569,"ON",49127.866880900001,89335.00638358001,3248.7579999999998,"OFF",-2.3044331996250036,-33.398399859304,-2.4056600000000001,"ON",55966.404922640017,85460.221686520017,3852.7080000000001,"ON",59664.030204780007,85435.918559500002,3410.0129999999999,null,0,3207.9258912920245,0,3608.9988945261989,3261.3208222249646,10078.245608043188,0,3243.052155384712,0,3673.5649334823938,3331.6969882983262,10248.314077165433,0,40.832108707975294,0,243.70910547380117,148.69217777503536,0,5.7058446152877877,0,179.14306651760626,78.316011701673688,393.99996288165971,223.93149375941562,null,null,10510.704909,null,142571.47790000017,16.32356942236877,17468.174295828878,414.59950493370462,16567.618922600017,375.36607585855251,-39.233429075152117,null,null,null,null,null,null,null,null,null,10078.245608043188,0,-3.2222309746589417,0,5.8758241733321483,6.2867194538957847]
[3427.2595172866145,0,0,3667.7530151378778,3376.3689537713449,10471.381486195838,11195.082913,"2013-07-22T02:00:00",80,75,"ON",60422.514120434978,86424.165516640001,3633.25,"OFF",-11.550264219359997,-110.63216544540002,-8.8484060000000007,"OFF",-0.22794533699999966,-44.531197138794006,-1.7696810000000001,"ON",58023.682377270001,81362.698429280004,3886.2640000000001,"ON",63527.120421660024,84055.131986400011,3686.1869999999999,null,3337.3699311765722,0,0,3660.2833390851738,3366.7731077809012,10364.426378042648,3404.7447758678627,0,0,3753.6375316205904,3455.3646114097314,10613.746918898185,295.88006882342779,0,0,225.98066091482633,319.41389221909867,228.5052241321373,0,0,132.62646837940974,230.82238859026847,801.765063315921,552.44452246038372,null,null,11195.082913,null,112180.80000000005,15.165956496711406,14793.765236544808,304.15902703872217,13710.895200000004,264.64946839729043,-39.509558641431738,null,null,null,null,null,null,null,null,null,10364.426378042648,89.889586110042274,0,0,7.4696760527040169,9.5958459904436495]
[0,0,0,0,0,0,877.67526500000019,"2013-07-22T18:00:00",95,75,"OFF",7105.3644077599974,25613.466608078004,895.86980000000005,"OFF",-13.608141324480011,-105.09795040208002,-8.8484060000000007,"OFF",-0.79575923262499315,-33.398399859304,-1.7696810000000001,"OFF",-12.58356222662,-165.53084396674001,-3.594665,"check",11324.844285455001,61164.914979670008,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-43.235217542776127,-43.235217542776127,null,null,877.67526500000019,null,152358.63750000007,16.535488043735953,18428.078699221369,458.70442821721133,17487.611925000008,415.4692106744352,-43.235217542776127,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3582.3125650811839,0,0,3682.5461182290269,3541.5539181836175,10806.412601493828,11376.647912999999,"2013-07-23T09:00:00",86,77,"ON",61738.463482559986,85825.009216840015,3642.7429999999999,"OFF",-15.99807393371999,-108.57265589922001,-8.8484060000000007,"OFF",-0.27440873028000246,-75.14639166260001,-1.7696810000000001,"ON",57098.313777705007,84864.514345340009,3987.2919999999999,"ON",65260.121709435,84643.941410340005,3757.2310000000002,null,3488.9187304567067,0,0,3675.799436957851,3530.302274404477,10695.020441819035,3563.2390621887193,0,0,3746.3103823405581,3620.0726528240216,10929.622097353298,153.82426954329321,0,0,311.49256304214896,226.92872559552325,79.503937811280593,0,0,240.98161765944178,137.15834717597863,652.85794761424233,418.25629207997792,null,null,11376.647912999999,null,129220.75440000021,15.86848676619416,16286.4621313847,363.54252640899568,15312.650913600019,324.1549158422726,-39.387610566723083,null,null,null,null,null,null,null,null,null,10695.020441819035,93.393834624477222,0,0,6.7466812711759303,11.251643779140522]
[3387.3188056157319,0,0,3452.1817304903229,3182.0676865953415,10021.568222701397,11028.751810999998,"2013-07-24T01:00:00",85,72,"ON",61813.78559771998,86018.872774620017,3578.5749999999998,"OFF",-19.615886937900004,-108.56583819032001,-8.8484060000000007,"OFF",-0.31807908169999666,-33.398399859304,-3.9817830000000001,"ON",56098.217713884995,83391.969431280013,3919.6419999999998,"ON",61877.961228895001,84673.778912820009,3543.3649999999998,null,3294.6030938151907,0,0,3446.2322426906871,3173.9772098285671,9914.8125463344441,3367.2470325150975,0,0,3521.5704471578811,3253.69173309391,10142.509212766889,283.97190618480909,0,0,473.40975730931268,369.3877901714327,211.32796748490227,0,0,398.07155284211876,289.67326690608979,1074.6924283664898,846.99576193404619,null,null,11028.751810999998,null,126439.21250000014,15.469438681039154,16346.968381596977,366.06992034423206,15051.185975000013,313.99289504516747,-52.077025299064587,null,null,null,null,null,null,null,null,null,9914.8125463344441,92.715711800541158,0,0,5.94948779963579,8.0904767667743727]
[3037.5802947709644,0,0,2951.8337604836238,2752.7442786964762,8742.1583339510653,8299.1753239999998,"2013-07-24T11:00:00",84,73,"ON",54656.335963749989,87032.786400560013,2901.7930000000001,"OFF",492.85861747499973,1904.5141478806001,-7.5139950000000004,"OFF",2.9119595201249955,-75.14639166260001,-1.7696810000000001,"ON",46177.657506899995,67680.182292032012,2832.0189999999998,"ON",51302.366493959998,86045.662360180009,2574.6469999999999,null,2961.1716395093536,0,0,2952.0079407400235,2752.3531806119113,8665.5327608612879,3013.0565667397441,0,0,3074.689460047699,2801.4671020722417,8889.2131288596847,-59.378639509353434,0,0,-119.98894074002374,-177.70618061191135,-111.26356673974396,0,0,-242.67046004769918,-226.82010207224175,-405.68678805587166,-629.36715605426798,null,null,8299.1753239999998,null,123629.28960000002,15.434504443761396,16019.858629147086,352.51791423725871,14787.053222400002,303.90488704267557,-48.61302719458314,null,null,null,null,null,null,null,null,null,8665.5327608612879,76.408655261610875,0,0,-0.17418025639972257,0.39109808456487372]
[2690.825324624876,0,0,2605.5863930323944,2451.9371969604576,7748.348914617729,8403.428018999999,"2013-07-25T06:00:00",75,71,"ON",49102.34342970002,83171.396496280009,2734.127,"OFF",8755.5240728999979,18260.824226116001,533.0557,"OFF",3.5174949493750045,-33.398399859304,-1.7696810000000001,"ON",40088.802252700007,68966.643857292001,2686.6529999999998,"ON",45367.000620580002,82339.636010479997,2451.3620000000001,null,2626.3417542872439,0,0,2608.2190033457487,2454.6190743520688,7689.1798319850623,2682.8991597873764,0,0,2695.0553093216959,2505.34947011958,7883.3039392286519,107.78524571275602,0,0,78.433996654251132,-3.2570743520686847,51.227840212623505,0,0,-8.402309321696066,-53.987470119579939,143.4538938703615,-50.670213373229473,null,null,8403.428018999999,null,97681.6875,14.428341492830061,13540.25167044201,258.69717158260181,12347.978625,219.18889743802484,-39.508274144576973,null,null,null,null,null,null,null,null,null,7689.1798319850623,64.483570337632045,0,0,-2.6326103133542347,-2.681877391611124]
[3496.4480264876479,0,0,3759.5996705256784,3434.8789907670384,10690.926687780364,11304.943912999999,"2013-07-25T22:00:00",87,75,"ON",61631.044930000004,87122.699949700007,3623.4470000000001,"OFF",-24.151884199699985,-109.2405507464,-8.8484060000000007,"OFF",-9.2131420375002882E-2,-33.398399859304,-1.7696810000000001,"ON",59557.033263750011,86372.350929000007,3944.19,"ON",64737.932701715006,85322.022716699998,3747.9250000000002,null,3403.658131637445,0,0,3750.8577794352436,3424.1597273740408,10578.67563844673,3469.6645747162584,0,0,3818.5822060008741,3507.5947735329546,10795.841554250088,219.78886836255515,0,0,193.33222056475643,323.76527262595937,153.78242528374176,0,0,125.60779399912599,240.33022646704558,691.86200446389432,474.6960886605367,null,null,11304.943912999999,null,131970.16469999996,15.840511448859436,16662.361581702869,379.3958956536419,15571.095481799995,334.37153856426528,-45.024357089376622,null,null,null,null,null,null,null,null,null,10578.67563844673,92.789894850202927,0,0,8.7418910904348195,10.719263392997618]
[3274.6631730096565,0,0,3539.3166904843497,3092.2875048559272,9906.2673683499343,10189.738810999999,"2013-07-26T13:00:00",92,75,"ON",57706.192324499993,90399.050222020014,3248.1790000000001,"OFF",-3.900862773599989,-108.78633091698001,-8.8484060000000007,"OFF",-0.62651005412500149,-70.971595690604005,-3.9817830000000001,"ON",55837.033172759991,88915.757390400016,3850.59,"ON",57476.893756339981,88245.536501360009,3103.8,null,3191.121858042251,0,0,3533.5478349162618,3087.7305099212399,9812.4002028797513,3232.5483867364755,0,0,3580.433578129298,3138.5258137660594,9951.5077786318325,57.057141957749081,0,0,317.04216508373838,16.069490078760282,15.630613263524538,0,0,270.15642187070216,-34.725813766059218,345.34678222476259,206.23920647268233,null,null,10189.738810999999,null,145103.97120000015,16.288200111402965,17817.066367991938,430.35725307062967,16805.673292800013,385.53523817514451,-44.822014895485154,null,null,null,null,null,null,null,null,null,9812.4002028797513,83.541314967405469,0,0,5.768855568087929,4.5569949346872818]
[3245.6833673194615,0,0,3552.9556915971825,3080.6032304216301,9879.2422893382736,10767.793610999999,"2013-07-27T05:00:00",74,69,"ON",61404.376388820019,86716.284290919997,3574.6129999999998,"OFF",-21.124492585275018,-104.74687849790001,-8.8484060000000007,"OFF",7.1472995875002762E-2,-33.398399859304,-1.824983,"ON",59760.163526400007,82673.062079860014,3819.9639999999999,"ON",62198.777887199991,85356.913344600005,3383.89,null,3154.4636919012505,0,0,3544.1016596516952,3072.2729890915762,9770.8383406445209,3221.6141441138875,0,0,3633.8543290784428,3148.1884035273756,10003.656876719706,420.14930809874932,0,0,275.86234034830477,311.61701090842371,352.99885588611232,0,0,186.10967092155715,235.70159647262426,966.40282682698853,733.58429075180447,null,null,10767.793610999999,null,94794.23760000011,14.208223980931816,13343.57309220617,251.92920686982214,12076.55833440001,210.7033743413329,-41.225832528489235,null,null,null,null,null,null,null,null,null,9770.8383406445209,91.219675418210954,0,0,8.8540319454873497,8.3302413300539229]
[3222.4439826155121,0,0,3499.8733642148281,3258.3797421131339,9980.6970889434742,10781.925912999999,"2013-07-27T20:00:00",84,69,"ON",60969.548253034998,88616.820907220012,3510.9630000000002,"OFF",-21.32622462283997,-109.2405507464,-8.8484060000000007,"OFF",0.17039686874999813,-73.232949524394002,-1.7696810000000001,"ON",58817.347726399988,83236.044418320002,3753.2420000000002,"ON",66188.662412249992,86063.709236680006,3528.3389999999999,null,3132.2584695220426,0,0,3491.8065799720403,3246.3810790045454,9870.4461284986282,3187.7256871252848,0,0,3575.2837768705072,3327.614107047948,10090.62357104374,378.70453047795763,0,0,261.43542002795994,281.95792099545451,323.23731287471537,0,0,177.95822312949304,200.72489295205196,862.87446011109819,642.69701756598647,null,null,10781.925912999999,null,123629.28960000002,15.191116934642753,16276.52398857759,363.12829843294941,14787.053222400002,303.90488704267557,-59.223411390273839,null,null,null,null,null,null,null,null,null,9870.4461284986282,90.185513093469581,0,0,8.0667842427878895,11.998663108588516]
[2717.4326293431936,0,0,2892.1619167192953,2597.8359294852539,8207.4304755477424,8180.0249130000002,"2013-07-28T11:00:00",85,72,"ON",48997.866879719986,70544.895342638003,2767.3670000000002,"OFF",-23.57906198116002,-106.45732134840001,-8.8484060000000007,"OFF",-0.32179829274999977,-75.14639166260001,-1.7696810000000001,"ON",45539.191028240006,65406.428248878008,2842.799,"ON",48308.837433190005,72197.660375844003,2580.4769999999999,null,2653.0394046305146,0,0,2892.6352559340949,2599.1072315532856,8144.781892117895,2769.8771433681031,0,0,3024.6494851045913,2702.7561359272859,8497.2827643999808,114.32759536948561,0,0,-49.836255934094879,-18.630231553285739,-2.5101433681029448,0,0,-181.85048510459137,-122.27913592728601,-6.2159174169595985,-358.71678969904491,null,null,8180.0249130000002,null,126439.21250000014,15.469438681039154,16346.968381596977,366.06992034423206,15051.185975000013,313.99289504516747,-52.077025299064587,null,null,null,null,null,null,null,null,null,8144.781892117895,64.393224712679057,0,0,-0.47333921479958008,-1.2713020680316731]
[3396.4404618291787,0,0,3612.8183181822033,3397.3955874626486,10406.65436747403,11080.227912999999,"2013-07-29",83,74,"ON",60567.518915749999,87038.561401040002,3566.2559999999999,"OFF",-23.05119440999999,-109.2405507464,-8.8484060000000007,"OFF",-0.54844369487500289,-33.398399859304,-1.7696810000000001,"ON",57689.947643515006,80801.400465960018,3873.47,"ON",64796.796035399988,84776.445588020011,3651.12,null,3306.3720939103791,0,0,3605.6241141194096,3386.6379026450613,10298.63411067485,3370.4286916429387,0,0,3701.1768990561213,3473.748610480045,10545.354201179105,259.88390608962072,0,0,267.84588588059023,264.48209735493856,195.82730835706116,0,0,172.29310094387847,177.37138951995485,747.03521750187861,500.31512699762357,null,null,11080.227912999999,null,120794.73630000022,15.398730636414307,15688.921269179114,339.08608075584101,14520.60521220002,293.9094089325701,-45.176671823270908,null,null,null,null,null,null,null,null,null,10298.63411067485,90.068367918799595,0,0,7.1942040627936876,10.757684817587233]
[0,0,0,0,0,0,-15.910007000000002,"2013-07-29T17:00:00",96,76,"OFF",-2.5321600834000062,-74.450592333934011,1.3996869999999999,"OFF",-21.321287945100011,-112.02378014440001,-8.8484060000000007,"OFF",-2.106550320500002,-33.398399859304,-2.0185430000000002,"OFF",-3.753401801415003,-165.49603354718002,-1.7696810000000001,"OFF",0.4764905639199995,-116.89443159090001,-4.6730640000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-39.273086958720228,-39.273086958720228,null,null,-15.910007000000002,null,154650.08640000015,16.674442946539507,18549.355669131375,464.44460254711845,17703.008121600014,425.17151558839822,-39.273086958720228,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2923.7915923762885,0,0,3251.5587333665085,2718.2814971795019,8893.6318229222979,8741.4147489999996,"2013-07-30T08:00:00",81,74,"ON",51810.61400020001,86408.765515360021,2890.3649999999998,"OFF",-0.94354604917501605,-110.63216544540002,-8.8484060000000007,"OFF",0.36016393825000353,-33.398399859304,-2.0738449999999999,"ON",51305.074432660011,83990.163231000013,3273.5810000000001,"ON",49745.388508514996,85568.262320500013,2588.3910000000001,null,2853.3583300035243,0,0,3248.8958191743832,2718.788429709316,8821.0425788872235,2902.6008423127737,0,0,3309.2548495065871,2766.9143782624124,8978.7700700817732,37.006669996475466,0,0,24.685180825616953,-130.39742970931593,-12.235842312773912,0,0,-35.673849506586976,-178.52337826241228,-111.74475295636068,-269.47224415091034,null,null,8741.4147489999996,null,115066.74090000021,15.203481939878277,15136.89316105722,317.30468424865387,13982.17364460002,274.2655101795167,-43.039174069137175,null,null,null,null,null,null,null,null,null,8821.0425788872235,70.433262372764148,0,0,2.6629141921252995,-0.50693252981409387]
[3004.102920052153,0,0,2997.7477971739754,3094.570763689544,9096.4214809156729,10305.965319000001,"2013-07-31",85,71,"ON",55377.050801484991,80770.279630040008,3001.3380000000002,"check",3931.1647233250078,28947.221989336002,1141.002,"OFF",3.1617534600499701E-2,-68.36234620289801,-1.7696810000000001,"ON",48197.759995440021,84732.170584340012,2986.8069999999998,"ON",60782.972942249988,80914.253600340002,3178.5880000000002,null,2926.3972557359307,0,0,2996.8805027479266,3087.4214388501441,9010.6991973340009,3011.369007792327,0,0,3046.9236526232453,3187.5608171796557,9245.8534775952285,74.940744264069508,0,0,-10.073502747926796,91.166561149856079,-10.031007792326818,0,0,-60.1166526232455,-8.9728171796555216,101.25003824051998,-133.90424202070665,null,null,10305.965319000001,null,126439.21250000014,15.408591803759494,16411.520807391447,368.77665947064628,15051.185975000013,313.99289504516747,-54.783764425478807,null,null,null,null,null,null,null,null,null,9010.6991973340009,77.705664316222283,0,0,0.86729442604882934,7.1493248393999238]
[0,0,0,0,0,0,-18.372731999999999,"2013-07-31T15:00:00",101,77,"OFF",-0.65286517132500144,-75.14639166260001,1.1674979999999999,"OFF",-11.061325722959994,-117.72723478512002,-8.8484060000000007,"OFF",-2.9255710633999902E-2,-67.492591026439996,-3.5762309999999999,"OFF",3.4116174341900036,-160.72981335936001,-1.7696810000000001,"OFF",2.1574952734300226,-120.37338813006001,-5.3459120000000002,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-30.92282082709221,-30.92282082709221,null,null,-18.372731999999999,null,164987.75490000029,17.087667254123428,19310.740599795688,501.34201921612487,18674.748960600027,470.41919838903266,-30.92282082709221,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2951.0636322003165,3150.3656132500641,0,3086.1160728855598,3064.0075681205535,12251.552886456495,12181.029071999999,"2013-08-01T07:00:00",83,77,"ON",50436.535473885007,68569.195490924016,3020.2809999999999,"ON",48259.76164982,68756.145089796002,3168.864,"OFF",-4.8024952418499883E-2,-75.14639166260001,-3.5209280000000001,"ON",46613.766929450001,70773.288590788012,2997.95,"ON",55339.600601200007,71440.597917086008,2997.4549999999999,null,2883.1192928855726,3154.068806302656,0,3086.0949056602453,3060.9974937861325,12184.280498634605,3020.4789574377701,3283.6980672726568,0,3194.8275010045695,3203.4946871599768,12702.499212874973,137.16170711442737,14.795193697344075,0,-88.144905660245513,-63.542493786132582,-0.19795743777012831,-114.83406727265674,0,-196.87750100456969,-206.03968715997689,-37.568264051592564,-555.78697829195937,null,null,12181.029071999999,null,120794.73630000022,15.581271268253289,15505.119475856696,331.74717434955602,14520.60521220002,293.9094089325701,-37.837765416985917,null,null,null,null,null,null,null,null,null,12184.280498634605,67.944339314743956,-3.7031930525918142,0,2.1167225314457028E-2,3.0100743344210059]
[3163.7621277930102,3202.5131927761581,0,3231.1721785966588,3105.285213315678,12702.732712481504,12874.730594000001,"2013-08-01T22:00:00",91,75,"ON",55685.737599269996,73139.635141638006,3228.174,"ON",50159.133403750006,72379.244036770018,3256.1480000000001,"OFF",8.8796802709999706E-2,-65.539116905740016,-8.8484060000000007,"ON",50369.962465509998,72589.093116712,3206.884,"ON",57760.249317390007,72117.572348354006,3192.373,null,3084.7910023234808,3205.129228382882,0,3229.0812043276915,3100.5134491730178,12619.51488420707,3218.6645517546176,3322.3790181759441,0,3344.8581744149606,3250.1411903102407,13136.042934655765,143.38299767651915,51.018771617118091,0,-22.197204327691452,91.859550826982286,9.509448245382373,-66.231018175943973,0,-137.97417441496054,-57.768190310240698,218.94135588591683,-297.58669456277408,null,null,12874.730594000001,null,142571.47790000017,16.201875667809446,17599.379333994897,420.48883576556375,16567.618922600017,375.36607585855251,-45.122759907011243,null,null,null,null,null,null,null,null,null,12619.51488420707,78.971125469529397,-2.6160356067239263,0,2.0909742689673294,4.7717641426602313]
[2845.0275036212079,2657.4004596558902,0,2902.2999493627908,2734.2972951971738,11139.025207837061,11421.748594000001,"2013-08-02T13:00:00",98,75,"ON",49639.161616399993,72785.13032050601,2889.123,"ON",40888.930754600013,71316.331135924003,2842.8690000000001,"OFF",-0.11865711850000139,-44.009345637086007,-8.8484060000000007,"ON",44139.101784399994,72615.722285592012,2965.3989999999999,"ON",49398.077346450002,72002.689942972007,2733.2060000000001,null,2778.9717733107154,2664.3335338687634,0,2903.4231167512448,2734.9992862477329,11081.727710178457,2886.9081243622945,2745.8490184058437,0,2992.0841112694425,2845.0079943195301,11469.84924835711,110.15122668928461,178.53546613123672,0,61.975883248755054,-1.7932862477327944,2.2148756377055179,97.019981594156434,0,-26.685111269442586,-111.80199431952997,308.06945751626751,-80.052080662386686,null,null,11421.748594000001,null,159020.32080000022,16.762563118038713,18973.270338218565,484.80478377871924,18113.810155200023,444.00495147344316,-40.799832305276084,null,null,null,null,null,null,null,null,null,11081.727710178457,66.055730310492436,-6.9330742128731799,0,-1.1231673884540214,-0.70199105055917244]
[3094.4664858062451,2933.217068691139,0,2977.0172272511618,3100.1255615829368,12104.826343331482,12875.031594,"2013-08-03T05:00:00",82,72,"ON",56417.226753019997,71939.766500241996,3220.4119999999998,"ON",47328.104880649989,72240.820483598014,3266.42,"OFF",0.12297796397500217,-44.879100813544007,-8.8484060000000007,"ON",47224.897010000001,71897.320246714007,3214.2759999999998,"ON",60066.761967675004,73203.095980246013,3182.7719999999999,null,3014.302441236418,2937.3795270061319,0,2976.6641931308382,3093.5572614357416,12021.90342280913,3159.5799976781859,3041.5973974817198,0,3081.3898647710403,3245.9707890661252,12528.538048997072,206.10955876358184,329.04047299386821,0,237.61180686916168,89.214738564258369,60.832002321813889,224.82260251828029,0,132.88613522895957,-63.1987890661253,812.90408323582369,306.2694570478821,null,null,12875.031594,null,117939.30320000008,15.179704472890261,15539.077642865872,333.09655550849789,14252.194500800008,284.02406155345153,-49.072493955046355,null,null,null,null,null,null,null,null,null,12021.90342280913,80.164044569827183,-4.1624583149928185,0,0.35303412032362758,6.5683001471952593]
[3424.6991925218945,0,0,3708.7573836448687,3344.0510070940063,10477.507583260769,11197.297188,"2013-08-03T19:00:00",96,73,"ON",61769.319875444991,87370.383303620009,3600.7460000000001,"OFF",-19.838707344500001,-107.8489360474,-8.8484060000000007,"OFF",-0.24438775650000127,-33.398399859304,-8.8484060000000007,"ON",59926.455599549998,85854.205052600009,3916.1990000000001,"ON",64521.658645599993,86086.327988560006,3698.049,null,3331.9186127245057,0,0,3699.7200535798929,3333.5686644173702,10365.207330721769,3396.5254259737635,0,0,3771.1082387145448,3411.1308598220421,10578.76452451035,268.8273872754944,0,0,216.47894642010715,364.48033558262978,204.22057402623659,0,0,145.0907612854553,286.91814017795787,800.71003416987605,587.15284038129448,null,null,11197.297188,null,154650.08640000015,16.491902314700525,18754.669224804758,474.24815069675356,17703.008121600014,425.17151558839822,-49.076635108355333,null,null,null,null,null,null,null,null,null,10365.207330721769,92.780579797388782,0,0,9.0373300649757766,10.482342676636108]
[2780.6349859500092,0,0,2765.4378600298874,2648.2865893674229,8194.35943534732,10084.512594,"2013-08-04T10:00:00",91,75,"ON",48370.452657325011,76757.504504844008,2796.4870000000001,"check",29550.386654250011,51843.438579898,1953.675,"OFF",-0.19555236525000275,-75.14639166260001,-8.8484060000000007,"ON",41405.713251419998,73967.914585482009,2774.761,"ON",47371.415788280021,76612.840742820001,2568.4380000000001,null,2717.1461948933311,0,0,2767.6503324690893,2650.0486641776656,8134.8451915400856,2800.0047208082979,0,0,2840.4589691053538,2729.3947525227527,8369.8584424364035,79.340805106668995,0,0,7.1106675309106322,-81.610664177665512,-3.5177208082977813,0,0,-65.697969105353877,-160.95675252275259,-40.281951447097128,-275.2952023434155,null,null,10084.512594,null,142571.47790000017,16.201875667809446,17599.379333994897,420.48883576556375,16567.618922600017,375.36607585855251,-45.122759907011243,null,null,null,null,null,null,null,null,null,8134.8451915400856,63.48879105667811,0,0,-2.2124724392019743,-1.762074810242666]
[3142.2380653626906,3213.2935357077786,0,3151.4412852888549,3116.0112340298833,12622.984120389208,12831.892594000001,"2013-08-05T02:00:00",86,74,"ON",55953.579851854985,72486.715191536001,3219.8980000000001,"ON",50876.775327280018,70215.078648558003,3231.7249999999999,"OFF",8.6837991875003573E-2,-33.398399859304,-8.8484060000000007,"ON",49452.571910529987,71618.548140210012,3202.8629999999998,"ON",58785.522012140005,71778.491591004,3186.2550000000001,null,3062.8155008443546,3215.4740678270905,0,3149.8859775374922,3110.4528350800219,12538.62838128896,3202.3137202954977,3349.5178709814704,0,3266.7978656085716,3267.8417818136431,13086.471238699185,157.08249915564556,16.250932172909415,0,52.977022462507648,75.802164919978168,17.584279704502478,-117.79287098147051,0,-63.934865608571727,-81.586781813643029,254.77693294396784,-293.06592446625575,null,null,12831.892594000001,null,129220.75440000021,15.685946134355177,16475.991093324286,371.49060160934556,15312.650913600019,324.1549158422726,-47.33568576707296,null,null,null,null,null,null,null,null,null,12538.62838128896,79.422564518336003,-2.1805321193119198,0,1.5553077513627613,5.5583989498613846]
[0,0,0,0,0,0,-23.803328200000003,"2013-08-05T17:00:00",101,74,"OFF",-3.0159465261199925,-73.058993676602014,0.89847180000000004,"OFF",-13.108562445799988,-109.2405507464,-8.8484060000000007,"OFF",-1.2278880339999974,-75.14639166260001,-8.8484060000000007,"OFF",-0.32716197248000889,-162.26058952826003,-3.0232049999999999,"OFF",-1.7004905584799943,-116.95972117966001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-41.286581702185174,-41.286581702185174,null,null,-23.803328200000003,null,164987.75490000029,16.905126622284445,19519.256919674579,511.70578009121783,18674.748960600027,470.41919838903266,-41.286581702185174,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2581.3863412217843,2553.7554215170012,0,2769.2834942338091,2547.5113727325356,10451.936629705129,10739.710594,"2013-08-06T09:00:00",89,74,"ON",44932.748412749999,70938.373396176001,2608.4090000000001,"ON",39483.290251620012,71962.232856276009,2677.66,"OFF",-5.7687313459999147E-2,-33.398399859304,-8.8484060000000007,"ON",41990.911270544988,70280.841466524013,2904.1390000000001,"ON",45636.787646504999,72133.71828719601,2558.3510000000001,null,2524.7123521984122,2561.1292754650644,0,2771.2709971065501,2550.0925222963233,10407.20514706635,2621.3272016739666,2634.5606595271352,0,2861.1718587998662,2643.284142192048,10760.343862193015,83.696647801587915,116.53072453493542,0,132.86800289345001,8.2584777036768173,-12.91820167396645,43.099340472864696,0,42.967141200133938,-84.933142192047853,293.13751935087811,-60.001195775787721,null,null,10739.710594,null,137357.58810000028,15.963304278507225,17209.167438465316,403.10296822417268,16077.513281400026,354.88663464140063,-48.216333582772052,null,null,null,null,null,null,null,null,null,10407.20514706635,56.673989023372087,-7.3738539480632426,0,-1.9875028727410609,-2.581149563787676]
[3046.8193331804418,0,0,3071.9423053786873,3011.5823692351105,9130.3440077942396,10566.526593999999,"2013-08-07",90,72,"ON",55510.726602525014,77249.694962420006,3014.41,"check",4451.882902609992,41948.175778268007,1610.84,"OFF",1.2691931400005787E-3,-50.793399117622009,-8.8484060000000007,"ON",49071.476994800003,84153.627827920005,2974.9479999999999,"ON",58078.444814189992,78101.988783260007,2975.1770000000001,null,2968.6735807475502,0,0,3070.5982845509257,3006.5874125486771,9045.8592778471539,3074.6084904072959,0,0,3124.9185691235957,3115.4880766580854,9315.0151361889766,45.73641925244965,0,0,-95.65028455092579,-31.410412548676959,-60.198490407296049,0,0,-149.97056912359585,-140.31107665808531,-135.52829227374053,-404.68415061556465,null,null,10566.526593999999,null,139988.10000000021,15.931276102187983,17573.997098797929,419.34607875655428,16324.78140000002,365.14206432996684,-54.204014426587435,null,null,null,null,null,null,null,null,null,9045.8592778471539,78.145752432891641,0,0,1.3440208277615966,4.9949566864333974]
[2391.4668775847572,0,2874.047568377513,3132.1252587575655,2483.1734985210378,10880.813203240872,11521.564593999999,"2013-08-07T14:00:00",103,76,"ON",39750.18179391,61963.020046006008,2576.732,"OFF",-6.5985939256600066,-109.41099346890002,-8.8484060000000007,"ON",53307.208138275018,74845.554241762002,3000.9369999999999,"ON",47998.683173609985,70204.226460156002,3175.26,"ON",42720.590689044991,64030.574488688006,2777.4839999999999,null,2344.0479495733312,0,2868.865784555253,3131.3821785424211,2486.9901362323121,10831.286048903317,2458.0433482341268,0,2980.833485723891,3249.7339779024983,2606.6066764056272,11295.217488266144,232.68405042666882,0,132.07121544474694,43.877821457579103,290.4938637676878,118.68865176587315,0,20.103514276108854,-74.473977902498063,170.87732359437268,667.02212987751682,203.09069051469083,null,null,11521.564593999999,null,168530.34230000025,17.147575636566035,19656.462916031207,518.58596399271687,19007.752176200025,486.48114277355108,-32.104821219165785,null,null,null,null,null,null,null,null,null,10831.286048903317,47.418928011426033,0,5.1817838222600585,0.74308021514434586,-3.8166377112743248]
[0,0,0,0,0,0,-19.093037900000002,"2013-08-07T15:00:00",104,75,"OFF",-1.2804447338399931,-166.99199929652002,0.45641009999999999,"OFF",-5.717520084375006,-166.99199929652002,-8.8484060000000007,"OFF",2.5003251874997898E-2,-166.99199929652002,-2.737476,"OFF",1.8155170670000003,-166.99199929652002,-3.9817830000000001,"OFF",0.23350888123500338,-116.93846596956001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-34.543443354034764,-34.543443354034764,null,null,-19.093037900000002,null,170159.67360000021,17.142267353564986,19852.644937848669,528.50721411620907,19160.909318400019,493.96377076217431,-34.543443354034764,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3152.0624735964743,0,3028.8161162256815,3213.279888182276,2996.0160032305344,12390.174481234966,12867.884593999999,"2013-08-08T06:00:00",81,74,"ON",56135.876776924997,72825.80396972,3220.8119999999999,"OFF",-11.939301186854992,-109.2405507464,-8.8484060000000007,"ON",57243.39553673999,73741.999775038013,3229.3809999999999,"ON",50601.366306665012,71127.801432754,3220.5940000000001,"ON",56129.80137039,72307.770384996009,3205.9459999999999,null,3072.2320604715133,0,3020.8466309341143,3211.0485594703396,2992.4559548278362,12296.583205703804,3210.2657170860816,0,3157.7685154968399,3336.5099603267663,3132.1176270211467,12836.661819930836,148.57993952848665,0,208.53436906588558,9.5454405296604818,213.49004517216372,10.546282913918276,0,71.612484503159976,-115.91596032676625,73.828372978853167,537.11062022705926,-2.9679939999720091,null,null,12867.884593999999,null,115066.74090000021,15.203481939878277,15136.89316105722,317.30468424865387,13982.17364460002,274.2655101795167,-43.039174069137175,null,null,null,null,null,null,null,null,null,12296.583205703804,79.830413124961069,0,7.9694852915672527,2.2313287119363849,3.5600484026981576]
[3003.5869894286066,2932.2189325886966,2905.3376133592237,0,2970.0354957359309,11811.179031112457,12605.362096999999,"2013-08-08T22:00:00",90,71,"ON",55367.052174719996,71151.896018090003,3137.248,"ON",47862.776170130004,70945.832771796006,3154.3760000000002,"ON",56727.339114730021,73674.873415292008,3198.8040000000001,"OFF",-3.1693056252000118,-158.64239131086001,-2.9679030000000002,"ON",57953.523408399989,71806.363989154008,3117.902,null,2925.9033607617603,2936.0978669210517,2897.7709176525154,0,2965.1426353385318,11724.91478067386,3071.0077095372853,3049.5823451264841,3031.9825830984023,0,3117.0421013747055,12269.614739136878,211.34463923823978,218.27813307894849,301.03308234748465,0,152.75936466146823,66.240290462714711,104.79365487351606,166.82141690159779,0,0.8598986252945906,826.17408156242641,281.47412309940836,null,null,12605.362096999999,null,139988.10000000021,15.870429224908323,17641.375417911404,422.38320209368163,16324.78140000002,365.14206432996684,-57.241137763714789,null,null,null,null,null,null,null,null,null,11724.91478067386,77.683628666846289,-3.8789343323551293,7.5666957067082876,0,4.8928603973990903]
[3416.9526402739898,0,3327.9569850009802,0,3189.4451272656916,9934.3547525406611,10126.510913000002,"2013-08-09T13:00:00",98,75,"ON",60241.276997639994,89054.598026940002,3560.7460000000001,"OFF",-4.7014903327500193,-111.32797279490001,-8.8484060000000007,"ON",61897.438677865,92896.016054560008,3279.2710000000002,"OFF",-3.7204924858500124,-163.33907086790003,-1.7696810000000001,"ON",59579.344725779978,87460.216644419997,3297.1120000000001,null,3327.4939549183796,0,3316.1320020656644,0,3183.2451219136069,9826.8710788976514,3379.8505310166756,0,3350.5374971698166,0,3242.0253970417225,9972.4134252282147,233.25204508162051,0,-36.861002065664252,0,113.86687808639317,180.89546898332446,0,-71.266497169816375,0,55.086602958277581,269.45808879707334,123.91574246650958,null,null,10126.510913000002,null,159020.32080000022,16.762563118038713,18973.270338218565,484.80478377871924,18113.810155200023,444.00495147344316,-40.799832305276084,null,null,null,null,null,null,null,null,null,9826.8710788976514,89.458685355610214,0,11.824982935315802,0,6.200005352084645]
[3431.4198522770421,0,3381.6105481213253,0,3375.099497013729,10188.129897412096,10972.983705000001,"2013-08-10T04:00:00",78,75,"ON",60495.580471169997,89133.362616819999,3625.9160000000002,"OFF",-13.830978304700006,-107.97422147448,-8.8484060000000007,"ON",62806.551680729994,92315.94933968001,3633.377,"OFF",-2.6489948659300038,-164.76541577812,-3.3918889999999999,"ON",63500.722298025008,87367.656220060002,3725.931,null,3341.3562492824817,0,3368.9630894250877,0,3365.527713816517,10075.847052524086,3393.7384484752761,0,3407.5614058423066,0,3432.9321108933259,10234.231965210909,284.55975071751845,0,264.41391057491228,0,360.40328618348303,232.17755152472409,0,225.81559415769334,0,292.99888910667414,872.62958785869989,714.2446751718777,null,null,10972.983705000001,null,106383.78480000014,14.968355140118216,14214.492347909372,282.65029466723087,13165.975771200012,245.90293505001699,-36.747359617213874,null,null,null,null,null,null,null,null,null,10075.847052524086,90.06360299456037,0,12.647458696237663,0,9.5717831972119711]
[3339.666672902255,0,3372.8014574619347,0,3356.31893452748,10068.787064891671,10719.287811,"2013-08-10T23:00:00",84,73,"ON",60249.343975030009,89986.1376877,3570.241,"OFF",-16.242922129859991,-107.1531286979,-8.8484060000000007,"ON",63875.943890000017,96566.510109640003,3584.8820000000001,"OFF",-5.5285707801200044,-160.62546230902001,-3.9817830000000001,"ON",64781.26678880999,88398.333389060004,3576.9949999999999,null,3250.5194957905951,0,3359.1853590061314,0,3345.5930523753764,9955.297907172102,3297.7511662124343,0,3376.1851096256969,0,3409.0469799341204,10082.983255772251,319.72150420940488,0,225.69664099386864,0,231.40194762462352,272.48983378756566,0,208.69689037430317,0,167.94802006587952,728.20706563331396,600.52171703316526,null,null,10719.287811,null,123629.28960000002,15.434504443761396,16019.858629147086,352.51791423725871,14787.053222400002,303.90488704267557,-48.61302719458314,null,null,null,null,null,null,null,null,null,9955.297907172102,89.147177111659857,0,13.61609845580324,0,10.725882152103623]
[3140.2348734403845,0,3440.9249677273165,0,3182.1921173708697,9763.3519585385693,10726.218913000001,"2013-08-11T14:00:00",98,75,"ON",55251.849561299998,85652.561285840013,3374.232,"OFF",-19.095945394439969,-109.97798622436001,-8.8484060000000007,"ON",63802.207780260018,95945.617349699998,3648.4870000000001,"OFF",-7.3134244764700131,-165.21771060738001,-1.7696810000000001,"ON",59423.623174075015,83940.915310240016,3714.1179999999999,null,3062.2284218486006,0,3427.3500907477796,0,3176.117731467009,9665.6962440633888,3122.1015527692066,0,3447.5748429384103,0,3254.2131330611865,9823.8895287688028,312.00357815139932,0,221.13690925222045,0,538.00026853299096,252.13044723079338,0,200.91215706158982,0,459.90486693881348,1030.3409236313346,872.14763892592055,null,null,10726.218913000001,null,159020.32080000022,16.762563118038713,18973.270338218565,484.80478377871924,18113.810155200023,444.00495147344316,-40.799832305276084,null,null,null,null,null,null,null,null,null,9665.6962440633888,78.006451591783843,0,13.574876979536839,0,6.0743859038607297]
[2449.848242547976,0,2218.3186271268823,2794.9952564765144,2466.2590513709938,9929.4211775223666,9752.7125940000005,"2013-08-12T08:00:00",83,74,"ON",42147.715503465006,70478.80367047801,2431.6010000000001,"OFF",-25.721618239084989,-106.61781823674001,-8.8484060000000007,"ON",41320.846039214979,71849.363680228009,2342.0160000000001,"ON",42514.299688099978,73383.324120226011,2674.2919999999999,"ON",43627.677659065004,70201.467293260008,2313.652,null,2398.3405485817748,0,2219.1036197719718,2796.7815369545237,2469.7016989783197,9883.9274042865909,2485.2346993983506,0,2296.7274780699927,2875.7537261250914,2563.4073616440128,10221.123265237447,33.26045141822533,0,122.91238022802827,-122.48953695452383,-156.04969897831961,-53.633699398350473,0,45.288521930007391,-201.46172612509145,-249.75536164401274,-167.54307610986075,-504.73893706071817,null,null,9752.7125940000005,null,120794.73630000022,15.398730636414307,15688.921269179114,339.08608075584101,14520.60521220002,293.9094089325701,-45.176671823270908,null,null,null,null,null,null,null,null,null,9883.9274042865909,51.507693966201259,0,-0.78499264508945998,-1.7862804780093029,-3.4426476073258527]
[3462.1766859812806,0,3508.2624880501721,0,3392.0226971350326,10362.461871166486,10983.885495,"2013-08-12T20:00:00",93,73,"ON",62432.171371599987,90158.826243720003,3611.4380000000001,"OFF",-20.760913819879981,-105.23622958024001,-8.8484060000000007,"ON",66161.238615499999,94314.580755800009,3654.0450000000001,"OFF",-7.6761326394199969,-160.03400600986004,-3.6130990000000001,"ON",65533.770125819989,87947.64272660001,3730.864,null,3367.7883894013144,0,3492.4143108544722,0,3380.5808670570755,10240.783567312861,3417.615854898112,0,3523.4268077430538,0,3448.411523894536,10389.454186535702,243.64961059868574,0,161.63068914552787,0,350.28313294292457,193.82214510188805,0,130.61819225694626,0,282.45247610546403,704.9074851884468,556.23686596560697,null,null,10983.885495,null,147581.8293000001,16.250968464516816,18162.834987002494,446.28137569930482,17038.591954200008,395.6254282006135,-50.655947498691319,null,null,null,null,null,null,null,null,null,10240.783567312861,94.388296579966209,0,15.848177195699918,0,11.441830077957093]
[2760.3630591110282,0,2595.4792764534986,3021.6477159549886,2614.412760090649,10991.902811610164,10989.611594,"2013-08-13T13:00:00",98,76,"ON",47355.945725519996,72073.080782156016,2738.3470000000002,"OFF",-21.549019923749992,-112.90029688392001,-8.8484060000000007,"ON",48046.017657400022,73421.52735256801,2706.2660000000001,"ON",45923.527285999997,71985.028066504005,2927.9749999999999,"ON",45878.698946399978,72007.181610012005,2625.8719999999998,null,2698.7780689101482,0,2593.3872135032061,3021.9603250240334,2616.8964630257415,10931.02207046313,2800.6935788793535,0,2690.980021039124,3121.2029763840355,2712.0063855479543,11324.882961850468,39.568931089851958,0,112.87878649679396,-93.9853250240335,8.9755369742583753,-62.346578879353274,0,15.285978960876037,-193.22797638403563,-86.13438554795448,29.965171777980515,-363.89571960935763,null,null,10989.611594,null,159020.32080000022,16.823409995318375,18904.647850138877,481.47770923233344,18113.810155200023,444.00495147344316,-37.472757758890282,null,null,null,null,null,null,null,null,null,10931.02207046313,61.584990200879929,0,2.0920629502925294,-0.31260906904481089,-2.483702935092424]
[2804.8196293399228,3169.0727491975708,3027.4518057681694,0,2949.5495997039088,11950.893784009571,12463.819023,"2013-08-14T05:00:00",76,74,"ON",49477.434442215002,68401.672352000009,2981.2220000000002,"ON",50164.288729905013,71618.106994340007,3190.1759999999999,"ON",57218.773090570001,72949.148354972014,3111.9569999999999,"OFF",-8.8608826882800038,-159.65133201972,-2.0369769999999998,"ON",55085.456178060012,71668.124915163993,3182.5010000000002,null,2739.2152685360838,3171.6819675714742,3019.5010733743397,0,2946.7257632985884,11877.124072780487,2871.6399169656961,3293.2699339358942,3162.0049450704541,0,3085.5841757177086,12412.498971689754,242.00673146391637,18.49403242852577,92.45592662566014,0,235.77523670141181,109.58208303430411,-103.09393393589426,-50.047945070454261,0,96.9168242822916,553.22546974249212,17.850570833225163,null,null,12463.819023,null,100578.26240000024,14.709616923521015,13675.170865826329,263.39718170821789,12620.256665600022,227.89072423119586,-35.506457477022025,null,null,null,null,null,null,null,null,null,11877.124072780487,65.604360803838972,-2.6092183739033317,7.9507323938296395,0,2.823836405320435]
[3414.1616758362425,0,3318.8723667442105,0,3344.6844776571766,10077.718520237629,10891.882702999999,"2013-08-14T20:00:00",77,74,"ON",60881.523711040012,90977.191936740011,3621.6930000000002,"OFF",-13.855349948279988,-110.63216544540002,-8.8484060000000007,"ON",62342.221317759999,94122.241156479999,3593.817,"OFF",-7.5280454708199862,-158.64239131086001,-1.990891,"ON",63692.522685165008,88218.827124140007,3687.212,null,3323.3441783388821,0,3306.6598300091232,0,3334.9527702393684,9964.9567785873733,3366.4151159644975,0,3335.1189216569664,0,3397.4619147520189,10098.995952373483,298.34882166111811,0,287.15716999087681,0,352.25922976063157,255.27788403550267,0,258.69807834303356,0,289.75008524798113,900.52850004272159,766.48932625661246,null,null,10891.882702999999,null,103480.2117000001,14.808534918154638,13975.752803626472,274.0357330279337,12893.039899800009,236.79901165802883,-37.23672136990487,null,null,null,null,null,null,null,null,null,9964.9567785873733,90.817497497360364,0,12.212536735087269,0,9.7317074178081384]
[2635.0098479673843,0,2186.906342285205,0,0,4821.9161902525893,5063.7806419999997,"2013-08-15T11:00:00",79,67,"ON",50642.677123690002,71471.927294690002,2670.4520000000002,"OFF",582.69653228850223,8903.6470942100004,165.84129999999999,"ON",44163.317303700002,66192.429876708004,2235.2849999999999,"OFF",-9.3937329949400148,-166.36581278614003,-3.8158750000000001,"OFF",2.9730565905599904,-113.41539484340001,-3.9817830000000001,null,2567.8956239102959,0,2186.5659565742399,0,0,4754.4615804845362,2686.1652753285089,0,2301.257308750859,0,0,4987.4225840793679,102.55637608970437,0,48.719043425759992,0,0,-15.713275328508644,0,-65.972308750859156,0,0,94.802151032647203,-138.15885256218496,null,null,5063.7806419999997,null,109285.23110000021,14.580480970883762,14990.620860619818,311.66395364716806,13438.71172340002,255.1906851643509,-56.473268482817161,null,null,null,null,null,null,null,null,null,4754.4615804845362,67.11422405708845,0,0.34038571096516534,0,0]
[0,2442.1113672047491,2687.3462401431261,0,2678.0161204025749,7807.4737277504501,7908.1668379999992,"2013-08-16T03:00:00",73,66,"OFF",-10.31397960192,-75.14639166260001,1.4625189999999999,"ON",41576.060649899999,71809.700656098008,2453.4839999999999,"ON",55524.169464209997,72050.157238584012,2755.645,"OFF",-6.4944655440699934,-166.53970446726004,-1.7696810000000001,"ON",55145.547837765,73432.564020152,2699.3449999999998,null,0,2448.7001331955025,2680.6704189985853,0,2675.1744745429833,7804.5450267370716,0,2529.5776497022598,2819.0540266025919,0,2800.630291274369,8149.2619675792212,0,4.7838668044973929,74.974581001414663,0,24.170525457016538,0,-76.093649702259881,-63.409026602591894,0,-101.28529127436923,59.336064689359489,-285.38087615279011,null,null,7908.1668379999992,null,91919.663300000131,13.92769847899832,13199.548143378675,247.03593112239545,11806.348350200013,202.44302254882635,-44.592908573569105,null,null,null,null,null,null,null,null,null,7804.5450267370716,0,-6.5887659907534726,6.6758211445408051,0,2.8416458595916083]
[3007.064045273627,0,2996.2892581663928,0,2835.271021433326,8838.6243248733463,9580.0359130000015,"2013-08-16T23:00:00",77,66,"ON",59055.464581749984,71036.588508506,3266.0920000000001,"OFF",-15.511268523729994,-107.40209538526001,-8.8484060000000007,"ON",61579.617520339991,78354.933804283995,3197.4520000000002,"OFF",-8.9114483958500088,-158.81636320032001,-1.7696810000000001,"ON",59072.965559009986,73177.990769826007,3127.11,null,2921.839953263363,0,2984.8438018738798,0,2829.5511380883418,8736.2348932255845,3086.7763494225933,0,3106.5194072518038,0,2975.5167467169763,9168.812503391373,344.25204673663711,0,212.60819812612044,0,297.55886191165837,179.31565057740681,0,90.932592748196384,0,151.59325328302384,799.89852400539678,367.3209138396079,null,null,9580.0359130000015,null,103480.2117000001,14.321759899917355,14450.767562525223,291.31959442704795,12893.039899800009,236.79901165802883,-54.520582769019114,null,null,null,null,null,null,null,null,null,8736.2348932255845,85.22409201026403,0,11.445456292512972,0,5.7198833449842823]
[1915.1136840334825,0,1955.653221493927,0,2014.5801847768014,5885.3470903042107,6222.6758109999992,"2013-08-17T09:00:00",75,65,"ON",34725.536336789984,70565.123885986002,2127.723,"OFF",-15.867731801999987,-108.27901316648001,-8.8484060000000007,"ON",39693.166384514989,77341.300907534009,2046.8240000000001,"OFF",-9.5596835561000066,-158.64239131086001,-3.9817830000000001,"ON",37412.48169574498,73291.236925072008,2060.9589999999998,null,1876.9080679706206,0,1956.8818512137379,0,2019.9550775627674,5853.7449967471257,1934.7924556445901,0,2009.614879267071,0,2078.3905891138825,6022.7979240255436,250.81493202937941,0,89.942148786262123,0,41.003922437232404,192.93054435540989,0,37.209120732929023,0,-17.431589113882637,329.91037999762818,160.85745271921056,null,null,6222.6758109999992,null,97681.6875,14.063260229152098,13891.755668079453,271.03952069327056,12347.978625,219.18889743802484,-51.850623255245722,null,null,null,null,null,null,null,null,null,5853.7449967471257,38.205616062861964,0,-1.2286297198108969,0,-5.3748927859660398]
[3008.2057393091704,0,2951.8075823855156,0,2876.2841505094261,8836.2974722041126,9390.4120450000009,"2013-08-18",76,65,"ON",59841.601609080004,72303.840176336016,3248.7150000000001,"OFF",-18.098441999040016,-107.8489360474,-8.8484060000000007,"ON",61393.206226954979,73067.968989848014,3129.3719999999998,"OFF",-10.716293700699993,-158.78155278076002,-1.806549,"ON",60993.188512375003,71974.969940668016,3022.98,null,2921.3290569983474,0,2940.534396813272,0,2869.0252088724583,8730.8886626840776,3080.1626824053596,0,3101.9162204190011,0,3034.1949042595852,9216.2738070839459,327.38594300165278,0,188.83760318672785,0,153.95479112754174,168.5523175946405,0,27.455779580998751,0,-11.214904259585182,615.80159510134581,130.41645070147757,null,null,9390.4120450000009,null,100578.26240000024,14.161995028004071,14203.968042795634,282.26746644577236,12620.256665600022,227.89072423119586,-54.376742214576495,null,null,null,null,null,null,null,null,null,8730.8886626840776,86.876682310823071,0,11.273185572243619,0,7.2589416369678474]
[0,0,0,0,0,0,-17.410977200000001,"2013-08-18T15:00:00",88,69,"OFF",1.471929835775007,-73.754793005267999,0.78355680000000005,"OFF",-21.619690408999983,-108.13744544638001,-8.8484060000000007,"OFF",0.54570329162500675,-36.738235032734003,-1.7696810000000001,"OFF",-11.305269571260013,-158.99025488144002,-1.7696810000000001,"OFF",2.7042877238300154,-115.50426064202001,-5.8067659999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-62.612987802353587,-62.612987802353587,null,null,-17.410977200000001,null,134683.69280000008,15.567925515142619,17302.715467002443,407.23547204101828,15826.167123200006,344.6224842386647,-62.612987802353587,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2158.6422342802516,0,2049.9811114337176,0,2026.7903560605896,6235.4137017745597,6409.1139130000001,"2013-08-19T07:00:00",75,68,"ON",39110.862608289994,76384.118640476008,2211.6959999999999,"OFF",-20.367167124550022,-108.54618714702001,-8.8484060000000007,"ON",40448.473888680019,75701.641917084009,2201.4830000000002,"OFF",-12.119248347989988,-159.19903719046002,-1.7696810000000001,"ON",35707.93866611999,68834.436450470006,2006.5530000000001,null,2113.0187470645601,0,2051.0034153505244,0,2032.5914074183938,6196.6135698334783,2167.5701741065086,0,2111.3059849689121,0,2099.2839273497552,6378.1600864251759,98.67725293543981,0,150.47958464947578,0,-26.038407418393717,44.12582589349131,0,90.177015031088104,0,-92.73092734975512,177.55758783288971,-3.988928758807873,null,null,6409.1139130000001,null,97681.6875,14.245800860991078,13713.751645578501,264.749739771657,12347.978625,219.18889743802484,-45.560842333632166,null,null,null,null,null,null,null,null,null,6196.6135698334783,45.623487215691512,0,-1.0223039168067771,0,-5.8010513578042264]
[3117.1822544127122,0,3232.6105909219932,0,3013.9741905251585,9363.7670358598625,10258.337587,"2013-08-19T22:00:00",83,67,"ON",60457.257576430013,71318.937906973995,3479.1489999999999,"OFF",-21.586571842559977,-105.38469521758002,-8.8484060000000007,"ON",65280.773001225025,71947.979834258018,3464.6550000000002,"OFF",-2.8207707115000069,-159.40773929114002,-3.779007,"ON",62451.741494199996,72378.361745030008,3327.1610000000001,null,3028.5399201379009,0,3217.7390951138964,0,3005.4502898633964,9251.7293051151937,3199.5364988431052,0,3412.330671287832,0,3175.8462629923051,9787.7134331232428,450.60907986209895,0,246.91590488610382,0,321.71071013660367,279.61250115689472,0,52.324328712168153,0,151.31473700769493,955.87906005520972,419.89493204716103,null,null,10258.337587,null,120794.73630000022,14.972802495456683,16135.22068920016,357.26604376216687,14520.60521220002,293.9094089325701,-63.356634829596771,null,null,null,null,null,null,null,null,null,9251.7293051151937,88.642334274811219,0,14.871495808096824,0,8.5239006617621271]
[2623.1947735510444,0,2462.3490870768928,0,2531.3428526849457,7616.8867133128824,7662.1776730000001,"2013-08-20T13:00:00",92,69,"ON",49012.809435225019,69776.459341268011,2631.61,"OFF",-20.49473530944999,-112.02361972772002,-8.8484060000000007,"ON",49096.176521399997,71345.607180024002,2579.8539999999998,"OFF",-5.4646536716099989,-166.99199929652002,-3.7329210000000002,"ON",48915.901842500018,72341.425804460014,2463.2950000000001,null,2559.1305049148873,0,2459.6756314711424,0,2532.2833308440349,7551.0894672300647,2679.7681539285704,0,2571.6540634971011,0,2637.2116735086297,7888.6338909343012,72.479495085112831,0,120.17836852885739,0,-68.988330844034863,-48.1581539285703,0,8.1999365028987086,0,-173.91667350862963,60.001302703060674,-277.5431210011759,null,null,7662.1776730000001,null,145103.97120000015,15.923118847725004,18225.571584015615,449.2034682420192,16805.673292800013,385.53523817514451,-63.668230066874685,null,null,null,null,null,null,null,null,null,7551.0894672300647,64.064268636157067,0,2.6734556057504051,0,-0.94047815908925259]
[2408.3169388118986,0,2324.9154586988629,0,2305.2306686433035,7038.463066154065,7369.6739130000005,"2013-08-21T05:00:00",74,68,"ON",44962.864523600023,71008.339131158005,2570.703,"OFF",-20.93166381412496,-105.06578685774001,-8.8484060000000007,"ON",46707.077741625006,74389.080557988011,2419.3029999999999,"OFF",-9.4901918088750072,-165.80916690654001,-1.7696810000000001,"ON",43673.774736134998,72978.552732416007,2390.2860000000001,null,2352.2157264994821,0,2323.451647771627,0,2308.6055598790713,6984.2729341501799,2447.5632106491807,0,2409.968650988465,0,2389.578452315021,7247.1103139526676,218.48727350051786,0,95.851352228372889,0,81.680440120928779,123.13978935081923,0,9.3343490115348686,0,0.70754768497909026,352.82860889123697,89.991229088750657,null,null,7369.6739130000005,null,94794.23760000011,14.147377103652154,13400.962864774267,253.89383129991543,12076.55833440001,210.7033743413329,-43.19045695858253,null,null,null,null,null,null,null,null,null,6984.2729341501799,56.101212312416465,0,1.4638109272359543,0,-3.3748912357677909]
[2466.0331229260601,0,2974.3149811491157,0,2553.4860144696113,7993.8341185447871,8588.4789130000008,"2013-08-21T14:00:00",95,74,"ON",42495.09862383498,62639.529268902006,2702.5859999999998,"OFF",-19.941987918875046,-108.18821732560001,-8.8484060000000007,"ON",56254.849188005021,73900.563642384004,2988.7150000000001,"OFF",-9.403377105920006,-158.64239131086001,-1.7696810000000001,"ON",45783.094291299996,63584.503826612003,2907.7959999999998,null,2413.8936065786088,0,2967.0853957008521,0,2556.0005244008485,7936.9795266803085,2539.992920426379,0,3098.1022722839657,0,2695.4325396233839,8333.5277323337286,288.69239342139099,0,21.629604299148014,0,351.79547559915136,162.5930795736208,0,-109.38727228396556,0,212.36346037661588,615.66545861305008,219.11725295963089,null,null,8588.4789130000008,null,152358.63750000007,16.474641166456294,18496.140335998891,461.92122538107543,17487.611925000008,415.4692106744352,-46.452014706640227,null,null,null,null,null,null,null,null,null,7936.9795266803085,52.139516347451263,0,7.2295854482636059,0,-2.5145099312371713]
[3177.5337777726581,0,3067.8716065508265,0,2967.3878698666463,9212.7932541901318,9436.470913000001,"2013-08-22T12:00:00",93,75,"ON",55938.845899220003,71549.304280288008,3371.4270000000001,"OFF",-19.817652632700032,-107.1531286979,-8.8484060000000007,"ON",57369.46066665501,75610.838055370012,3088.2779999999998,"OFF",-10.500592355119995,-159.89484453996002,-1.7696810000000001,"ON",54719.87160128,73137.726183146005,2987.384,null,3097.99718007722,0,3059.8006620353694,0,2964.8127105599765,9122.610552672566,3244.3794766802853,0,3184.5168576985789,0,3092.2733109735309,9521.1696453523946,273.4298199227801,0,28.477337964630351,0,22.57128944002352,127.04752331971486,0,-96.238857698579068,0,-104.88931097353088,280.07623120451689,-118.48286147531218,null,null,9436.470913000001,null,147581.8293000001,16.37266221907614,18027.835342263315,440.02764432353058,17038.591954200008,395.6254282006135,-44.402216122917082,null,null,null,null,null,null,null,null,null,9122.610552672566,79.536597695438104,0,8.0709445154570858,0,2.5751593066697751]
[3309.4524660715688,0,3231.3560965436304,0,3215.9031234503168,9756.7116860655151,10289.664913000001,"2013-08-23T03:00:00",83,72,"ON",60406.980206939996,70054.830406072011,3487.7919999999999,"OFF",-19.48244606779997,-108.5447433969,-8.8484060000000007,"ON",62044.44804090001,73267.382964756005,3485.1109999999999,"OFF",-11.039107918229988,-166.99199929652002,-1.7696810000000001,"ON",62618.019122069993,71583.440949792013,3327.38,null,3220.0979310975281,0,3219.4342026860227,0,3207.1661526867865,9646.6982864703368,3403.3360490982195,0,3384.5886799726563,0,3387.0506787002796,10174.975407771155,267.69406890247183,0,265.6767973139772,0,120.21384731321359,84.455950901780398,0,100.52232002734354,0,-59.670678700279495,603.36860945797366,75.091488157155425,null,null,10289.664913000001,null,120794.73630000022,15.277036881854986,15813.896010616025,344.12551300425912,14520.60521220002,293.9094089325701,-50.216104071689017,null,null,null,null,null,null,null,null,null,9646.6982864703368,89.354534974040689,0,11.921893857607756,0,8.7369707635302802]
[3070.6518107155007,0,0,0,0,3070.6518107155007,3314.1853499999997,"2013-08-23T18:00:00",97,73,"ON",55284.239864060008,84918.013308120004,3334.1680000000001,"OFF",-17.688391398989953,-106.09790777686001,-8.8484060000000007,"OFF",-0.93609364350000179,-36.877404523468002,-3.7974410000000001,"OFF",-12.674865080569996,-158.64239131086001,-1.7696810000000001,"check",10086.006756539999,68751.316547728013,-5.5671220000000003,null,2992.8620593753612,0,0,0,0,2992.8620593753612,3056.1981681693587,0,0,0,0,3056.1981681693587,341.30594062463888,0,0,0,0,277.9698318306414,0,0,0,0,292.94635857027453,229.61024977627704,null,null,3314.1853499999997,null,156871.89770000021,16.567636621378568,18937.148524560904,483.05196062883738,17911.85838380002,434.69237857447303,-48.359582054364353,null,null,null,null,null,null,null,null,null,2992.8620593753612,77.789751340139446,0,0,0,0]
[3410.3224109841854,0,3461.3524916055762,0,3357.0035795801423,10228.678482169904,10372.793913000001,"2013-08-24T10:00:00",90,75,"ON",60124.523090825001,90289.485629580013,3470.5419999999999,"OFF",-17.889410080440051,-112.02369993606001,-8.8484060000000007,"ON",64142.872071739992,92695.816037919998,3542.884,"OFF",-11.728530103149987,-159.89484453996002,-1.7696810000000001,"ON",63123.823516074997,88151.291701860013,3369.9859999999999,null,3321.1407568326968,0,3447.4538789390231,0,3347.7733549092932,10116.367990681014,3366.7594664238263,0,3485.6149315886782,0,3409.6725203398819,10262.046918352386,149.40124316730316,0,95.430121060976944,0,22.212645090706701,103.78253357617359,0,57.269068411321769,0,-39.686520339882009,221.74584361718723,76.066915945813776,null,null,10372.793913000001,null,139988.10000000021,16.113816734026962,17374.915243313204,410.44023003176642,16324.78140000002,365.14206432996684,-45.298165701799576,null,null,null,null,null,null,null,null,null,10116.367990681014,89.181654151488601,0,13.898612666553163,0,9.2302246708491111]
[3359.352363525426,0,3343.3764835819629,0,3225.47758164569,9928.2064287530793,10388.979626,"2013-08-25T01:00:00",84,72,"ON",61310.756612569981,90418.701265320007,3551.3229999999999,"OFF",-17.103591442739994,-110.29577166744001,-8.8484060000000007,"ON",63993.970513305001,95192.781870460007,3458.491,"OFF",-12.665010169349996,-166.99199929652002,-3.6499679999999999,"ON",62826.621962260004,88402.183389380007,3391.6640000000002,null,3267.8457727412283,0,3329.66319044593,0,3216.5558026245822,9814.0647658117396,3314.3656035499553,0,3353.8682728576155,0,3276.0730076356222,9944.3068840431915,283.47722725877156,0,128.82780955406997,0,175.10819737541806,236.9573964500446,0,104.62272714238452,0,115.59099236437805,536.19479141514648,405.95267318369412,null,null,10388.979626,null,123629.28960000002,15.373657566481736,16083.263083671325,355.12332981578862,14787.053222400002,303.90488704267557,-51.218442773113054,null,null,null,null,null,null,null,null,null,9814.0647658117396,91.50659078419767,0,13.713293136032917,0,8.9217790211077954]
[0,0,0,0,0,0,-17.229976000000001,"2013-08-25T16:00:00",96,73,"OFF",-11.509620014459996,-73.058993676602014,0.72491399999999995,"OFF",-15.452640888949981,-106.09790777686001,-8.8484060000000007,"OFF",-0.54461415700000226,-33.398399859304,-1.7696810000000001,"OFF",-12.802135725470009,-166.99199929652002,-1.7696810000000001,"OFF",-14.183872578470003,-118.98177343106001,-5.5671220000000003,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-49.076635108355333,-49.076635108355333,null,null,-17.229976000000001,null,154650.08640000015,16.491902314700525,18754.669224804758,474.24815069675356,17703.008121600014,425.17151558839822,-49.076635108355333,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3300.0906011177835,3052.3389515553649,3160.7915276158355,0,0,9513.221080288984,9875.0131969999984,"2013-08-26T08:00:00",81,72,"ON",60236.517257279978,88591.876113480001,3416.1619999999998,"ON",49346.089412299996,93029.402523979996,3230.067,"ON",60796.267187759986,93238.184833000007,3236.1210000000001,"OFF",-11.986312446639992,-166.99199929652002,-1.7696810000000001,"OFF",-96.247245766629973,-119.67758078056001,-5.5671220000000003,null,3211.1390474312698,3055.4136720509996,3149.9609504932496,0,0,9416.5136699755203,3265.6882002390635,3077.4358249241109,3181.2477412188309,0,0,9524.3717663820062,205.02295256873003,174.65332794900041,86.160049506750511,0,0,150.47379976093634,152.63117507588913,54.87325878116917,0,0,418.04514395482204,310.18704754833573,null,null,9875.0131969999984,null,115066.74090000021,15.081788185318956,15259.031553302078,322.05669624917562,13982.17364460002,274.2655101795167,-47.79118606965892,null,null,null,null,null,null,null,null,null,9416.5136699755203,88.951553686513762,-3.074720495634665,10.830577122585964,0,0]
[3300.9517067343986,0,3224.2404019678597,0,3048.850493295492,9574.0426019977494,10836.147097999999,"2013-08-26T20:00:00",87,69,"ON",62430.878151800003,66179.339875620004,3627.826,"OFF",-14.180732304260021,-110.63216544540002,-8.8484060000000007,"ON",63813.745290994993,68171.001186994006,3564.5250000000001,"OFF",-11.593696999640027,-158.64239131086001,-2.101496,"ON",61471.759261664985,70034.080508514016,3654.7460000000001,null,3207.266777198899,0,3210.739748396395,0,3041.1441407361067,9459.1506663314012,3440.793237130878,0,3434.1444505539075,0,3227.0312600010107,10101.968947685797,420.55922280110099,0,353.78525160360505,0,613.6018592638934,187.03276286912205,0,130.38054944609257,0,427.71473999898944,1325.9570244580775,683.13874310368215,null,null,10836.147097999999,null,131970.16469999996,15.475430185181473,17055.443773882063,396.36084777478715,15571.095481799995,334.37153856426528,-61.989309210521867,null,null,null,null,null,null,null,null,null,9459.1506663314012,93.684929535499577,0,13.500653571464682,0,7.7063525593853228]
[2670.0937124556426,2968.5370919098332,0,0,2748.7503632997614,8387.3811676652367,9413.7206380000007,"2013-08-27T14:00:00",93,73,"ON",47387.582196860021,61971.113067512008,2971.69,"ON",47386.168172725003,62996.504506906007,3156.4549999999999,"OFF",0.12540272650000397,-33.398399859304,-1.7696810000000001,"OFF",-10.627678549810005,-165.73954606742004,-1.7696810000000001,"ON",51207.84753888,66013.717674354019,3289.1149999999998,null,2608.787175107142,2972.6764912516865,0,0,2748.4153363042824,8329.8790026631104,2770.0963914058243,3133.2170694736506,0,0,2904.6965932711541,8808.010054150629,362.90282489285801,183.77850874831347,0,0,540.69966369571739,201.59360859417575,23.237930526349373,0,0,384.41840672884564,1036.7250498381975,558.59399835067939,null,null,9413.7206380000007,null,147581.8293000001,16.250968464516816,18162.834987002494,446.28137569930482,17038.591954200008,395.6254282006135,-50.655947498691319,null,null,null,null,null,null,null,null,null,8329.8790026631104,61.306537348500569,-4.1393993418532773,0,0,0.33502699547898374]
[0,2531.8801543672607,2231.2239728020072,0,2228.7600725547131,6991.8641997239811,7375.7609921000003,"2013-08-28T05:00:00",73,68,"OFF",1.042309151639994,-73.754793005267999,0.42767309999999997,"ON",42226.294688835005,69390.007538314007,2680.1219999999998,"ON",44628.650471539979,93455.389017720008,2371.152,"OFF",-10.612896182979993,-158.64239131086001,-1.7696810000000001,"ON",41549.795973959983,72123.756411367998,2325.8290000000002,null,0,2538.2559262460177,2230.695996542338,0,2232.9315314320215,7001.8834542203767,0,2632.4654061171354,2246.6782544955145,0,2309.5427910018666,7188.686451614516,0,141.86607375398216,140.45600345766206,0,92.897468567978649,0,47.656593882864399,124.47374550448558,0,16.286208998133588,334.47329776929553,147.67030037515619,null,null,7375.7609921000003,null,91919.663300000131,14.04939223355764,13085.215612451284,243.18927055915373,11806.348350200013,202.44302254882635,-40.746248010327378,null,null,null,null,null,null,null,null,null,7001.8834542203767,0,-6.3757718787569502,0.52797625966923079,0,-4.171458877308396]
[3188.1573982121045,0,3339.5227396808327,0,3100.826440444016,9628.5065783369537,10616.335098,"2013-08-28T20:00:00",90,71,"ON",58879.817514244998,90494.016896580011,3560.1689999999999,"OFF",-11.960795919150002,-101.94608347344001,-8.8484060000000007,"ON",64558.656113700003,95846.800674819999,3495.5819999999999,"OFF",-8.3018931518600088,-166.99199929652002,-2.101496,"ON",60923.335718875001,88033.144817039996,3571.5340000000001,null,3102.5395661405855,0,3325.2860245659281,0,3093.5597992268022,9521.3853899333153,3144.9153508472095,0,3346.3977848534905,0,3151.4214945687067,9642.7346302694077,457.62943385941435,0,170.29597543407181,0,477.97420077319794,415.25364915279033,0,149.18421514650936,0,420.11250543129336,1048.6584723029694,927.30923196687831,null,null,10616.335098,null,139988.10000000021,15.870429224908323,17641.375417911404,422.38320209368163,16324.78140000002,365.14206432996684,-57.241137763714789,null,null,null,null,null,null,null,null,null,9521.3853899333153,85.617832071518933,0,14.236715114904655,0,7.2666412172138735]
[3107.8857245091694,0,3015.942055060279,0,2897.8888890408471,9021.7166686102955,9240.0529130000014,"2013-08-29T12:00:00",97,72,"ON",56671.022172149977,89010.483439940013,3189.4639999999999,"OFF",-5.2925182324599964,-109.93635809590002,-8.8484060000000007,"ON",58182.617100674994,91884.187845460008,3014.5790000000002,"OFF",-8.8660999942199936,-159.89484453996002,-1.7696810000000001,"ON",55475.366490599998,87264.829128180005,3046.6280000000002,null,3027.1520033284537,0,3007.2572710714799,0,2894.800223401282,8929.2094978012155,3073.3244147995224,0,3042.0804933731197,0,2946.36762367853,9061.772531851173,162.31199667154624,0,7.3217289285203151,0,151.82777659871817,116.13958520047754,0,-27.501493373119501,0,100.26037632147018,269.71157028307425,137.14853623311774,null,null,9240.0529130000014,null,156871.89770000021,16.50678974409891,19006.954123963573,486.4423104901835,17911.85838380002,434.69237857447303,-51.749931915710476,null,null,null,null,null,null,null,null,null,8929.2094978012155,80.733721180715747,0,8.684783988799154,0,3.0886656395650789]
[3236.3362063309937,0,3121.5109651119164,0,2876.1807102091325,9234.027881652044,9902.3509129999984,"2013-08-30T03:00:00",81,69,"ON",61229.713718359999,89626.804324500001,3453.6019999999999,"OFF",-11.274013681840005,-104.70637328620001,-8.8484060000000007,"ON",61960.68761442,93954.204684180018,3261.5419999999999,"OFF",-8.3011817010500089,-158.64239131086001,-1.7696810000000001,"ON",57436.433263440005,87998.334397480008,3197.8249999999998,null,3145.5326581409831,0,3109.6978098669524,0,2871.6898646298919,9126.9203326378283,3195.9331860638845,0,3138.4185641118902,0,2923.0702521881221,9257.4220023638954,308.06934185901673,0,151.8441901330475,0,326.13513537010795,257.66881393611538,0,123.12343588810973,0,274.75474781187768,730.90995039237123,600.40828066630183,null,null,9902.3509129999984,null,115066.74090000021,14.899247553479974,15445.980139194937,329.40422714931765,13982.17364460002,274.2655101795167,-55.138716969800953,null,null,null,null,null,null,null,null,null,9126.9203326378283,90.803548190010588,0,11.813155244964037,0,4.490845579240613]
[3238.7199508338954,0,3295.9021544553029,0,3174.6043794560919,9709.2264847452898,10641.880626000002,"2013-08-30T19:00:00",94,70,"ON",60541.340943180003,89832.057466560014,3533.2190000000001,"OFF",-16.03404211185001,-105.76159420724001,-8.8484060000000007,"ON",64437.519839419991,91743.261792080011,3509.6460000000002,"OFF",-9.3667242141899809,-158.64239131086001,-3.6499679999999999,"ON",63436.647499319995,88069.479195060005,3611.5140000000001,null,3149.3803639446833,0,3281.7967561552573,0,3165.16544992117,9596.3425700211119,3197.6308010240668,0,3325.4477272836907,0,3227.610561665711,9750.6890899734681,383.83863605531678,0,227.84924384474289,0,446.34855007883016,335.58819897593321,0,184.19827271630948,0,383.90343833428915,997.98616495531837,843.63964500296038,null,null,10641.880626000002,null,150001.30160000012,16.150899758699293,18574.977721498832,465.66214061334779,17266.022350400013,405.61187558977639,-60.050265023571399,null,null,null,null,null,null,null,null,null,9596.3425700211119,89.339586889212114,0,14.105398300045636,0,9.4389295349219537]
[2885.8672536279769,0,2774.9999409104362,0,2696.1353137124834,8357.0025082508964,8446.934913000001,"2013-08-31T09:00:00",89,73,"ON",51722.620721099986,89310.302214860014,2822.0770000000002,"OFF",-17.814665304800013,-110.27275187386002,-8.8484060000000007,"ON",53104.039987529985,96032.56319026,2818.66,"OFF",-8.2811029781900007,-159.89484453996002,-1.7696810000000001,"ON",49955.308973130006,88146.639618140005,2816.8159999999998,null,2815.7491622259208,0,2769.9523101851246,0,2696.5220911220058,8282.2235635330508,2852.9988486414736,0,2783.4720702335062,0,2735.1257596202527,8371.5966784952325,6.3278377740793985,0,48.707689814875266,0,120.293908877994,-30.921848641473389,0,35.187929766493653,0,81.690240379747138,124.20664652311865,34.833531560937388,null,null,8446.934913000001,null,137357.58810000028,15.902457401227565,17275.014123213081,406.00942458523065,16077.513281400026,354.88663464140063,-51.122789943830014,null,null,null,null,null,null,null,null,null,8282.2235635330508,70.118091402056052,0,5.047630725311592,0,-0.38677740952243767]
[3261.4459400420869,0,3363.4310080137611,0,3117.3109606458702,9742.1879087017187,10513.524912999999,"2013-09-01",87,70,"ON",60963.303240800007,89016.739690460017,3500.308,"OFF",-19.678203368104992,-110.99157901694002,-8.8484060000000007,"ON",65615.487567685006,90494.337729940002,3479.4879999999998,"OFF",-13.086660006225022,-159.89484453996002,-1.7696810000000001,"ON",62153.887757805016,87752.896877080013,3544.3470000000002,null,3171.1067526974889,0,3348.1805755706778,0,3109.0067950948601,9628.2941233630263,3224.4674530323496,0,3401.0915359255332,0,3170.7480297819056,9796.307018739788,329.20124730251109,0,131.30742442932205,0,435.34020490514013,275.84054696765043,0,78.396464074466621,0,373.59897021809456,836.7703252464803,668.75742986971864,null,null,10513.524912999999,null,131970.16469999996,15.536277062461135,16988.647173249403,393.45008995475831,15571.095481799995,334.37153856426528,-59.078551390493033,null,null,null,null,null,null,null,null,null,9628.2941233630263,90.339187344598031,0,15.250432443083355,0,8.3041655510101009]
[3309.6974348351614,0,3247.8591473748493,0,3080.8267049744636,9638.3832871844752,10565.559913000001,"2013-09-01T01:00:00",88,71,"ON",61126.414422050002,89285.197004440008,3492.1280000000002,"OFF",-18.154758539000003,-107.15304848956001,-8.8484060000000007,"ON",62957.266166924986,94421.739098040009,3521.1129999999998,"OFF",-7.2066014548499941,-158.64239131086001,-1.7696810000000001,"ON",60474.00651485999,88084.157321280014,3562.9369999999999,null,3218.8011223211033,0,3235.1245766592015,0,3073.9338209734478,9527.8595199537522,3271.0791708264419,0,3262.4621788866289,0,3130.6628597326817,9664.204209445752,273.32687767889684,0,285.98842334079836,0,489.00317902655206,221.04882917355826,0,258.65082111337097,0,432.27414026731822,991.62706192942619,855.28237243742637,null,null,10565.559913000001,null,134683.69280000008,15.689619269701939,17168.510017331824,401.31390235548571,15826.167123200006,344.6224842386647,-56.691418116821012,null,null,null,null,null,null,null,null,null,9527.8595199537522,90.896312514058081,0,12.734570715647806,0,6.8928840010157728]
[0,0,0,0,0,0,-15.584255000000002,"2013-09-01T16:00:00",103,74,"OFF",-6.7626134595900043,-73.754793005267999,1.412058,"OFF",-18.846002010779998,-103.33785858912,-8.8484060000000007,"OFF",-0.33398957387500006,-71.667395019270003,-1.7696810000000001,"OFF",-8.2946205435800238,-166.99199929652002,-1.7696810000000001,"OFF",-5.5975473322250053,-118.95386092874001,-4.6085450000000003,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-39.199924007030233,-39.199924007030233,null,null,-15.584255000000002,null,168530.34230000025,17.025881882006715,19796.958943795613,525.68106678058132,19007.752176200025,486.48114277355108,-39.199924007030233,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3102.3746135427245,0,3076.6541303178906,0,2867.5592180022327,9046.5879618628478,9398.572913,"2013-09-02T07:00:00",77,74,"ON",55210.446066000004,89116.358448740008,3074.654,"OFF",1.5330107778000008,-106.81673491994002,-8.8484060000000007,"ON",58102.813165040003,94336.557840960013,3217.0039999999999,"OFF",-7.6932865089500115,-158.64239131086001,-1.7696810000000001,"ON",53220.007890450004,87961.919811120009,3117.5329999999999,null,3024.6038594800007,0,3068.0197057877849,0,2865.9811257275478,8958.6046909953329,3068.0734684148129,0,3091.6854977781245,0,2910.6386436907619,9070.3976098836993,50.050140519999331,0,148.98429421221499,0,251.5518742724521,6.5805315851871455,0,125.31850222187541,0,206.89435630923799,413.34958763476152,301.55666874639564,null,null,9398.572913,null,103480.2117000001,14.808534918154638,13975.752803626472,274.0357330279337,12893.039899800009,236.79901165802883,-37.23672136990487,null,null,null,null,null,null,null,null,null,8958.6046909953329,77.770754062723881,0,8.6344245301056617,0,1.5780922746848773]
[3321.4266173097612,0,3481.3190481984961,0,3170.4581784885809,9973.2038439968383,10615.051913000001,"2013-09-02T23:00:00",85,74,"ON",59227.619455800006,89928.708516259998,3526.9920000000002,"OFF",-9.0111426751499994,-107.15328911458001,-8.8484060000000007,"ON",65087.919003450021,93078.570236400017,3497.1669999999999,"OFF",-8.4715873450600263,-165.73954606742004,-1.7696810000000001,"ON",59971.667544945012,88351.491718500009,3601.511,null,3234.5194553736619,0,3466.5213774062418,0,3163.948414102063,9864.9892468819671,3280.505288929513,0,3503.5759474218626,0,3218.6076270908293,10002.688863442205,292.47254462633828,0,30.645622593758162,0,437.56258589793697,246.48671107048722,0,-6.4089474218626492,0,382.90337290917068,713.92244406164275,576.22282750140459,null,null,10615.051913000001,null,126439.21250000014,15.591132435598475,16219.375086739386,360.75120410155813,15051.185975000013,313.99289504516747,-46.758309056390658,null,null,null,null,null,null,null,null,null,9864.9892468819671,86.907161936099328,0,14.797670792254394,0,6.5097643865178725]
[3115.757771876993,0,3068.738053822794,0,2979.5273316033604,9164.0231573031469,9225.103912999999,"2013-09-03T14:00:00",96,74,"ON",55460.555289989992,89089.08761314,3079.7049999999999,"OFF",-3.1798830285000004,-108.54482360524,-8.8484060000000007,"ON",57961.124964909999,93322.082756639997,3032.1089999999999,"OFF",-7.4783493142400141,-158.64239131086001,-1.7696810000000001,"ON",55760.257883880004,88308.500048260001,3123.9079999999999,null,3037.4330161743578,0,3060.2146472466529,0,2976.2309856085003,9073.8786490295097,3081.4276141507885,0,3088.2882195078455,0,3023.6537017655219,9193.3695354241572,42.27198382564211,0,-28.105647246653007,0,147.6770143914996,-1.7226141507885586,0,-56.179219507845573,0,100.25429823447803,116.07062419294772,-3.4202622016970849,null,null,9225.103912999999,null,154650.08640000015,16.552749191980187,18685.728226333325,470.9442423659392,17703.008121600014,425.17151558839822,-45.772726777540981,null,null,null,null,null,null,null,null,null,9073.8786490295097,78.32475570263523,0,8.523406576141042,0,3.2963459948600757]
[2590.6344289339554,0,2648.3065242839534,0,2567.3000668656236,7806.2410200835329,8058.3196260000004,"2013-09-04T06:00:00",76,69,"ON",48316.41256995,88672.806328539999,2693.4760000000001,"OFF",-13.004639721325013,-109.2405507464,-8.8484060000000007,"ON",52916.064395999994,93020.419189900014,2676.1819999999998,"OFF",-8.081158950550007,-159.89484453996002,-3.6499679999999999,"ON",49836.061422629995,87879.305220919996,2701.16,null,2527.956379980631,0,2643.3811482285505,0,2567.7417034724367,7739.0792316816187,2562.3494299050421,0,2667.6170449312176,0,2606.8681861515338,7836.8346609877935,165.51962001936909,0,32.800851771449288,0,133.41829652756314,131.12657009495797,0,8.5649550687821829,0,94.291813848466063,286.01466167116661,188.25923236499131,null,null,8058.3196260000004,null,100578.26240000024,14.405382537122712,13963.983551399593,273.61483087841077,12620.256665600022,227.89072423119586,-45.72410664721491,null,null,null,null,null,null,null,null,null,7739.0792316816187,62.678048953324378,0,4.9253760554029213,0,-0.44163660681306283]
[3304.5742238125472,0,3101.0677062601467,0,3150.1335485648797,9555.7754786375735,10325.209912999999,"2013-09-05",83,72,"ON",60318.191986950013,89100.958447460012,3499.933,"OFF",-15.436669369874977,-107.15328911458001,-8.8484060000000007,"ON",59727.191234759994,92817.973339740012,3248.471,"OFF",-9.0148722635999992,-165.73954606742004,-1.7696810000000001,"ON",61175.331905759995,87797.733339140002,3587.424,null,3215.4297033205585,0,3091.137555398584,0,3142.6436836220382,9449.2109423411803,3267.3838438291727,0,3123.3251850443344,0,3202.4073206570133,9593.1163495305209,284.50329667944152,0,157.33344460141598,0,444.78031637796175,232.54915617082725,0,125.14581495566563,0,385.01667934298666,836.40095358713029,692.49554639779058,null,null,10325.209912999999,null,120794.73630000022,15.277036881854986,15813.896010616025,344.12551300425912,14520.60521220002,293.9094089325701,-50.216104071689017,null,null,null,null,null,null,null,null,null,9449.2109423411803,89.144520491988715,0,9.9301508615626517,0,7.4898649428414501]
[3443.8279110844605,0,3383.2365126424456,0,3303.4237019815564,10130.488125708463,10618.539097999999,"2013-09-05T11:00:00",91,76,"ON",60032.40140997502,88674.490703680014,3561.0639999999999,"OFF",-16.646899923839996,-112.71958749390001,-8.8484060000000007,"ON",62238.503694179992,90948.717976040003,3516.5419999999999,"OFF",-7.9168138134400037,-159.89484453996002,-2.101496,"ON",61197.476652425008,87772.868753740011,3551.8829999999998,null,3354.7001517564931,0,3371.0938905476546,0,3295.8696748053344,10021.663717109481,3408.8270448710859,0,3416.4754493499045,0,3356.249087926577,10181.551582147567,206.36384824350671,0,145.44810945234531,0,256.01332519466541,152.23695512891391,0,100.06655065009545,0,195.63391207342283,565.66371449387884,405.77584945579366,null,null,10618.539097999999,null,142571.47790000017,16.262722545089108,17533.531363486592,417.52764425519103,16567.618922600017,375.36607585855251,-42.161568396638529,null,null,null,null,null,null,null,null,null,10021.663717109481,89.127759327967397,0,12.142622094791022,0,7.5540271762220073]
[3073.7314179511663,0,3008.2905482729357,0,2877.6656177187733,8959.6875839428758,9789.5420979999999,"2013-09-06T03:00:00",80,67,"ON",59613.985489770006,89469.194936400017,3396.6840000000002,"OFF",-20.632536849279983,-106.09798798520001,-8.8484060000000007,"ON",61151.97706865998,93997.356771100007,3100.3890000000001,"OFF",-7.5689670674099814,-158.64239131086001,-2.101496,"ON",59209.596752739992,88021.193774380008,3303.4189999999999,null,2987.0564696538604,0,2997.2044394640279,0,2871.830141712845,8856.0910508307334,3035.4057290973938,0,3024.8543813430665,0,2926.1301524150749,8986.3902628555352,409.62753034613979,0,103.1845605359722,0,431.58885828715484,361.27827090260644,0,75.534618656933617,0,377.28884758492495,886.00427624747113,755.70506422266931,null,null,9789.5420979999999,null,112180.80000000005,14.679181478474124,15284.339956489324,323.04614131908619,13710.895200000004,264.64946839729043,-58.396672921795755,null,null,null,null,null,null,null,null,null,8856.0910508307334,86.674948297305946,0,11.086108808907738,0,5.8354760059282853]
[3111.5834429629354,0,0,0,0,3111.5834429629354,3324.9359249999998,"2013-09-06T18:00:00",96,72,"ON",56740.841164700018,81863.759929260006,3342.5590000000002,"OFF",-19.281367500720009,-108.11570898624001,-8.8484060000000007,"OFF",-0.1149399455549997,-75.14639166260001,-2.175233,"OFF",-7.7254335455499934,-160.72981335936001,-1.7696810000000001,"check",6365.16975774,68148.358372611998,-4.8297549999999996,null,3030.6926497231311,0,0,0,0,3030.6926497231311,3113.9078602465611,0,0,0,0,3113.9078602465611,311.86635027686907,0,0,0,0,228.65113975343911,0,0,0,0,259.44903418390629,176.23382366047633,null,null,3324.9359249999998,null,154650.08640000015,16.431055437420866,18824.120822791785,477.588831681361,17703.008121600014,425.17151558839822,-52.417316092962778,null,null,null,null,null,null,null,null,null,3030.6926497231311,80.890793239804225,0,0,0,0]
[3084.0001261367333,0,3079.433032303255,0,3010.4104904835913,9173.8436489235792,9103.3398880000004,"2013-09-07T09:00:00",86,74,"ON",54866.024823449996,89282.389712540011,3039.39,"OFF",-21.147496914300014,-109.50724347690002,-8.8484060000000007,"ON",58152.503166030001,93605.940071900011,2992.5239999999999,"OFF",-8.769052833730008,-164.90457724801999,-2.3227060000000002,"ON",56451.481155299996,88173.910453740013,3082.5970000000002,null,3006.9890753036993,0,3070.7595434142222,0,3006.6180440612006,9084.3666627791226,3049.1743269296412,0,3097.7386088274743,0,3055.8626511464986,9202.7755869036137,32.400924696300535,0,-78.23554341422232,0,75.978955938799572,-9.7843269296413382,0,-105.21460882747442,0,26.734348853501615,-17.191348546195172,-135.6002726706871,null,null,9103.3398880000004,null,129220.75440000021,15.685946134355177,16475.991093324286,371.49060160934556,15312.650913600019,324.1549158422726,-47.33568576707296,null,null,null,null,null,null,null,null,null,9084.3666627791226,77.011050833034005,0,8.6734888890327966,0,3.7924464223906398]
[3104.6297319411324,0,3143.4864897240323,0,3025.0825641455181,9273.1987858106822,9823.2419129999998,"2013-09-08T01:00:00",78,70,"ON",58014.177645360003,89299.073047259997,3198.0639999999999,"OFF",-20.416481007000009,-106.0330192298,-8.8484060000000007,"ON",61725.45147840499,94616.244322540006,3358.346,"OFF",-8.7770632428500051,-164.90457724801999,-1.7696810000000001,"ON",60059.373264900009,88104.369822960012,3277.45,null,3021.1587577793234,0,3131.869698383322,0,3018.5395931760077,9171.5680493386535,3067.9870860602759,0,3157.1056473399822,0,3074.2795764419193,9299.3723098421779,176.90524222067643,0,226.47630161667803,0,258.91040682399216,130.07691393972391,0,201.24035266001783,0,203.17042355808053,614.70190556447892,486.89764506095463,null,null,9823.2419129999998,null,106383.78480000014,14.664120753719914,14509.398358986275,293.49298014688463,13165.975771200012,245.90293505001699,-47.590045096867641,null,null,null,null,null,null,null,null,null,9171.5680493386535,83.470974161808954,0,11.616791340710279,0,6.5429709695104066]
[0,0,0,0,0,0,-17.316291800000002,"2013-09-08T16:00:00",97,73,"OFF",-13.143662593440013,-73.754793005267999,0.85980920000000005,"OFF",-20.291277933820055,-111.32324050284001,-8.8484060000000007,"OFF",1.0431612426999588E-2,-75.14639166260001,-3.5762309999999999,"OFF",-8.098286470050013,-158.64239131086001,-1.7696810000000001,"OFF",-17.674896147860007,-119.67758078056001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-48.359582054364353,-48.359582054364353,null,null,-17.316291800000002,null,156871.89770000021,16.567636621378568,18937.148524560904,483.05196062883738,17911.85838380002,434.69237857447303,-48.359582054364353,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3061.6133659864995,0,2961.7203517914113,0,2895.6162775187563,8918.9499952966671,9090.858913,"2013-09-09T13:00:00",92,73,"ON",55113.033299800016,72051.191926169995,3106.9319999999998,"OFF",-18.209380863780005,-103.67417215874002,-8.8484060000000007,"ON",56600.194597759997,77206.863708860008,2894.712,"OFF",-8.2584158641599856,-160.72981335936001,-1.7696810000000001,"ON",54633.597522559998,74719.972043824018,3099.8330000000001,null,2984.2014093343842,0,2954.2395629412126,0,2893.1046796929263,8831.5456519685231,3122.198368454809,0,3064.8439084784745,0,3009.6660278214481,9196.7083047547312,122.73059066561564,0,-59.527562941212636,0,206.72832030707377,-15.266368454809253,0,-170.13190847847454,0,90.166972178551987,218.96894270335162,-146.19371008285697,null,null,9090.858913,null,145103.97120000015,16.166506356843648,17951.184751623761,436.49764350326967,16805.673292800013,385.53523817514451,-50.962405328125158,null,null,null,null,null,null,null,null,null,8831.5456519685231,77.41195665211535,0,7.4807888501986781,0,2.5115978258299947]
[0,3200.7304958408722,0,3547.244261617072,3022.2514825764888,9770.2262400344334,10995.5650608,"2013-09-09T22:00:00",83,71,"OFF",-10.259831926079988,-74.450592333934011,0.62674180000000002,"ON",52355.558400859991,71666.785435886006,3487.7190000000001,"OFF",0.47101337235000201,-41.052200495464007,-1.7696810000000001,"ON",58391.067309120001,72959.840126694005,3866.5320000000002,"ON",59148.142770479993,73598.218304754002,3642.4569999999999,null,0,3201.9722630991837,0,3539.508804112304,3016.431072581785,9757.9121397932722,0,3333.6807751421129,0,3691.8923261618484,3160.9394419937312,10186.512543297693,0,285.74673690081636,0,327.02319588769615,626.02592741821491,0,154.03822485788714,0,174.63967383815179,481.5175580062687,1186.0145778108097,757.4141743063899,null,null,10995.5650608,null,120794.73630000022,15.216190004575326,15877.133009469346,346.69069132848784,14520.60521220002,293.9094089325701,-52.781282395917742,null,null,null,null,null,null,null,null,null,9757.9121397932722,0,-1.2417672583114836,0,7.7354575047679646,5.820409994703823]
[0,3134.3053269712282,0,3334.2815728490141,2831.3061598669115,9299.8930596871542,9628.6049496000014,"2013-09-10T13:00:00",90,72,"OFF",-14.835412283940009,-75.842190991265994,0.66363059999999996,"ON",50704.141473749994,72716.520106470009,3100.4430000000002,"OFF",2.3293427625004377E-2,-33.398399859304,-1.7696810000000001,"ON",53978.44674463501,75599.360241916002,3419.5219999999999,"ON",53923.512858105001,73715.330501988006,3109.7460000000001,null,0,3136.5847358848141,0,3329.8622374426054,2829.2716669694755,9295.7186402968946,0,3253.7762091831637,0,3443.0235399167691,2948.7618514200103,9645.5616005199445,0,-36.141735884813897,0,89.659762557394515,280.47433303052458,0,-153.33320918316349,0,-23.501539916769161,160.98414857998978,279.78834527651776,-70.054614946530307,null,null,9628.6049496000014,null,139988.10000000021,15.931276102187983,17573.997098797929,419.34607875655428,16324.78140000002,365.14206432996684,-54.204014426587435,null,null,null,null,null,null,null,null,null,9295.7186402968946,0,-2.2794089135859394,0,4.4193354064086634,2.0344928974359391]
[3164.4922487863082,0,3026.3594339961419,3488.0173729134035,0,9678.8690556958536,10420.141811000001,"2013-09-11T05:00:00",75,69,"ON",59876.766241109988,69916.374769564005,3437.2640000000001,"OFF",-14.293559903445001,-108.97385801590001,-8.8484060000000007,"ON",60211.599335175,73738.029462208011,3251.45,"ON",58605.420851294984,74186.193561958004,3744.2579999999998,"OFF",-5.8272452571200164,-119.67758078056001,-3.9817830000000001,null,3076.8792259051643,0,3016.0518901991036,3480.1241502554522,0,9573.0552663597191,3257.0260242050726,0,3166.806539453959,3623.7061914768915,0,10047.538755135924,360.38477409483585,0,235.39810980089624,264.13384974454766,0,180.23797579492748,0,84.643460546040842,120.55180852310832,0,816.3991738052905,341.9156850290874,null,null,10420.141811000001,null,97681.6875,14.30664773827074,13655.426384574825,262.70645727301411,12347.978625,219.18889743802484,-43.517559834989271,null,null,null,null,null,null,null,null,null,9573.0552663597191,87.613022881143934,0,10.307543797038306,7.8932226579513554,0]
[3309.1995403266992,0,3280.8442402725891,0,3161.11058586012,9751.1543664594083,10738.518811,"2013-09-11T20:00:00",86,72,"ON",60402.37865816,72456.661126538005,3584.306,"OFF",-17.818232676959997,-100.61951773818001,-8.8484060000000007,"ON",62910.443895449986,77575.990510374002,3542.1759999999999,"OFF",-6.3207134462500001,-160.72981335936001,-3.9817830000000001,"ON",61417.313191230009,74944.386958310002,3624.8670000000002,null,3219.8558957621408,0,3268.1397111650845,0,3153.4153219612631,9641.4109288884883,3382.6267904808374,0,3402.5711384892288,0,3298.9081911432986,10084.106120113365,364.45010423785925,0,274.03628883491547,0,471.4516780387371,201.67920951916267,0,139.60486151077112,0,325.95880885670158,1057.1476007068745,614.45240948199807,null,null,10738.518811,null,129220.75440000021,15.564252379795857,16604.813549251263,376.94538624690989,15312.650913600019,324.1549158422726,-52.79047040463729,null,null,null,null,null,null,null,null,null,9641.4109288884883,89.343644564558417,0,12.704529107504641,0,7.6952638988568651]
[3013.9656086145478,0,2876.5872738214648,0,2883.7752302839149,8774.328112719928,9271.5659130000004,"2013-09-12T12:00:00",93,72,"ON",54880.72109183998,71028.038299462001,3090.5410000000002,"OFF",-20.056544808029994,-108.96912572384001,-8.8484060000000007,"ON",55598.603687240015,74685.835374319999,3031.0810000000001,"OFF",-6.882153535460005,-158.64239131086001,-1.7696810000000001,"ON",55148.148218700007,74270.733152318018,3160.5619999999999,null,2937.2074283869861,0,2869.8403469306681,0,2880.9139417611236,8687.9617170787787,3080.8601878735394,0,2992.156588397409,0,3002.3290881750363,9075.3458644459843,153.3335716130141,0,161.24065306933198,0,279.64805823887627,9.6808121264607507,0,38.924411602591135,0,158.23291182496359,540.3864552345085,153.00230786730168,null,null,9271.5659130000004,null,147581.8293000001,16.190121587237158,18231.095857407323,449.4612558873273,17038.591954200008,395.6254282006135,-53.835827686713799,null,null,null,null,null,null,null,null,null,8687.9617170787787,76.758180227561752,0,6.746926890796658,0,2.8612885227912557]
[3250.6801398061912,0,3322.2446551372204,0,3044.7502476701557,9617.6750426135677,10546.193912999999,"2013-09-13T03:00:00",80,71,"ON",60041.834322029979,70065.458011122013,3513.23,"OFF",-18.911584063620005,-106.88170367534001,-8.8484060000000007,"ON",64258.78288160501,71706.424397514013,3444.8980000000001,"OFF",-8.8697889984200042,-166.99199929652002,-1.7696810000000001,"ON",59659.165289115001,73014.92721460601,3598.6840000000002,null,3162.3521149654971,0,3308.2947004714069,0,3038.5218483743693,9509.1686638112733,3342.8973054540702,0,3500.1646782171497,0,3190.0394992030488,10033.101482874268,350.87788503450292,0,136.6032995285932,0,560.16215162563094,170.33269454592983,0,-55.266678217149547,0,408.64450079695143,998.92123693413737,474.98841787114208,null,null,10546.193912999999,null,112180.80000000005,14.922568987592765,15035.05195295418,313.37156765188007,13710.895200000004,264.64946839729043,-48.722099254589637,null,null,null,null,null,null,null,null,null,9509.1686638112733,88.32802484069407,0,13.949954665813493,0,6.2283992957864029]
[3245.7883723933769,3187.1864838405395,0,3447.2579571578885,0,{"$f":"SUM(A5444:E5444)","v":9880.2328133918054},{"$f":"N5444+R5444+V5444+Z5444+AD5444","v":10903.476536000002},"2013-09-13T22:00:00",84,72,"ON",59242.037059769988,71108.824139510005,3525.672,"ON",51567.755695000014,70168.846561382015,3495.18,"OFF",-0.10689131179499889,-33.398399859304,-1.7696810000000001,"ON",56010.679101999995,70980.980066384,3888.3760000000002,"OFF",-104.04674953756998,-121.06919547956002,-3.9817830000000001,null,3159.1693787840391,3188.9334094943583,0,3441.3740956168863,0,{"$f":"SUM(AF5444:AJ5444)","v":9789.4768838952841},3326.4492620549481,3326.5395084192205,0,3596.1540643307449,0,{"$f":"SUM(AL5444:AP5444)","v":10249.142834804914},{"$f":"IF($K5444=\"ON\",$N5444-AF5444,0)","v":366.50262121596097},{"$f":"IF($O5444=\"ON\",$R5444-AG5444,0)","v":306.24659050564151},{"$f":"IF($S5444=\"ON\",$V5444-AH5444,0)","v":0},{"$f":"IF($W5444=\"ON\",$Z5444-AI5444,0)","v":447.00190438311392},{"$f":"IF($AA5444=\"ON\",$AD5444-AJ5444,0)","v":0},{"$f":"IF($K5444=\"ON\",$N5444-AL5444,0)","v":199.2227379450519},{"$f":"IF($O5444=\"ON\",$R5444-AM5444,0)","v":168.64049158077933},{"$f":"IF($S5444=\"ON\",$V5444-AN5444,0)","v":0},{"$f":"IF($W5444=\"ON\",$Z5444-AO5444,0)","v":292.22193566925534},{"$f":"IF($AA5444=\"ON\",$AD5444-AP5444,0)","v":0},{"$f":"SUM(AR5444:AV5444)+BN5444","v":1068.5326733316033},{"$f":"SUM(AW5444:BA5444)+BN5444","v":608.86672242197346},null,null,{"$f":"N5444+R5444+V5444+Z5444+AD5444","v":10903.476536000002},null,123629.28960000002,{"$f":"19.5285952781395+42*-0.3035722016559+BH5444*0.0000340867411548605+J5444*0.0608468772796604","v":15.373657566481736},{"$f":"BH5444*1000/(500*BI5444)","v":16083.263083671325},{"$f":"0.00000128*BJ5444^2+0*BJ5444+24.024","v":355.12332981578862},{"$f":"0.094*BH5444 + 3165.9","v":14787.053222400002},{"$f":"0.00000128*BL5444^2+0*BL5444+24.024","v":303.90488704267557},{"$f":"BM5444-BK5444","v":-51.218442773113054},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF5444:AJ5444)","v":9789.4768838952841},{"$f":"A5444-AF5444","v":86.618993609337849},{"$f":"B5444-AG5444","v":-1.7469256538188347},{"$f":"C5444-AH5444","v":0},{"$f":"D5444-AI5444","v":5.8838615410022612},{"$f":"E5444-AJ5444","v":0}]
[2977.0125997740915,3136.8505522704645,0,3378.4475157442384,0,9492.3106677887954,10298.726536,"2013-09-14T08:00:00",78,66,"ON",58456.734923599986,70064.824365235996,3128.6149999999998,"ON",54257.619562154985,70471.649086550009,3351.471,"OFF",1.6872512227999487E-2,-33.398399859304,-1.7696810000000001,"ON",58561.536457750015,70424.695124314007,3824.3919999999998,"OFF",-104.62777942209998,-121.74527157742001,-3.9817830000000001,null,2893.1586990957107,3136.8120248237506,0,3370.6155736254655,0,9400.5862975449272,3062.4902623639564,3285.7273582161724,0,3542.9911132950947,0,9891.2087338752244,235.45630090428904,214.65897517624944,0,453.77642637453437,0,66.124737636043392,65.74364178382757,0,281.40088670490513,0,847.12891350386076,356.50647717356406,null,null,10298.726536,null,106383.78480000014,14.420733244601273,14754.282323310754,302.66572400122902,13165.975771200012,245.90293505001699,-56.76278895121203,null,null,null,null,null,null,null,null,null,9400.5862975449272,83.853900678380796,3.8527446713942481E-2,0,7.8319421187729859,0]
[2567.7556223556226,2871.4281883250078,0,2860.6691398663634,0,8299.8529505469924,8513.9934069999999,"2013-09-15T05:00:00",76,66,"ON",49886.216839699999,68578.716220882008,2620.2170000000001,"ON",49675.198507664987,69712.244544264016,2764.9609999999998,"OFF",1.2695679278750047,-67.492591026439996,-1.7696810000000001,"ON",48366.381582219998,66907.431081970004,3135.931,"OFF",-4.5804056400199817,-118.28596608156001,-5.3459120000000002,null,2502.3009741421074,2874.2890496706323,0,2859.6947242751326,0,8236.2847480878718,2633.869171197724,3003.0412442493543,0,2997.5589688669647,0,8634.4693843140431,117.91602585789269,-109.32804967063248,0,276.23627572486748,0,-13.652171197723874,-238.08024424935456,0,138.37203113303531,0,232.65237100263909,-165.53226522353174,null,null,8513.9934069999999,null,100578.26240000024,14.222841905283731,14143.201909969317,280.06260514068447,12620.256665600022,227.89072423119586,-52.171880909488607,null,null,null,null,null,null,null,null,null,8236.2847480878718,65.454648213515156,-2.8608613456244711,0,0.97441559123080879,0]
[3326.3311315096803,3359.7157034389948,0,3537.1487465026303,0,10223.195581451306,11167.679563999998,"2013-09-15T20:00:00",88,71,"ON",61429.99200123499,68378.00287086601,3604.3359999999998,"ON",54897.440031199978,69971.534044982007,3590.4279999999999,"OFF",0.21782692499999992,-67.492591026439996,-1.7696810000000001,"ON",58213.926751630002,68860.191348444001,3979.5149999999999,"OFF",-8.1871131711599947,-118.28596608156001,-4.8297549999999996,null,3234.7092286528432,3359.2149335278446,0,3529.5568511601823,0,10123.48101334087,3439.6766775100996,3517.0108304021805,0,3714.6396813724073,0,10671.327189284688,369.62677134715659,231.21306647215533,0,449.95814883981757,0,164.65932248990021,73.417169597819338,0,264.87531862759261,0,994.10656854230842,446.26039259849114,null,null,11167.679563999998,null,134683.69280000008,15.689619269701939,17168.510017331824,401.31390235548571,15826.167123200006,344.6224842386647,-56.691418116821012,null,null,null,null,null,null,null,null,null,10123.48101334087,91.621902856837096,0.50076991115020064,0,7.5918953424479696,0]
[3117.4348699094799,3167.6516020504346,0,3381.2404449513101,0,9666.3269169112245,10441.918406999999,"2013-09-16T12:00:00",92,73,"ON",56165.670494079997,69428.659937360018,3294.748,"ON",50691.596780149986,70889.069329578007,3457.5880000000002,"OFF",-0.45674558612500438,-75.14639166260001,-1.7696810000000001,"ON",54233.849139794991,67093.209639078006,3696.6979999999999,"OFF",-11.565841337644995,-117.59015873206,-5.3459120000000002,null,3037.6855924061751,3169.9417547578664,0,3376.6403707368449,0,9584.2677179008861,3200.6564262237739,3298.4630037770448,0,3551.0901031477151,0,10050.209533148534,257.0624075938249,287.64624524213377,0,320.05762926315492,0,94.091573776226141,159.12499622295536,0,145.60789685228474,0,813.80387677098838,347.86206152334108,null,null,10441.918406999999,null,145103.97120000015,16.166506356843648,17951.184751623761,436.49764350326967,16805.673292800013,385.53523817514451,-50.962405328125158,null,null,null,null,null,null,null,null,null,9584.2677179008861,79.749277503304711,-2.2901527074318437,0,4.6000742144651667,0]
[3127.788150210386,0,3143.9706787594355,3313.4069811042195,0,9585.1658100740406,10470.185839,"2013-09-17T03:00:00",81,69,"ON",59178.268752599994,69776.034237066007,3354.49,"OFF",-9.1613888983800145,-105.76159420724001,-8.8484060000000007,"ON",62368.889864490026,75146.463850106011,3309.3519999999999,"ON",55424.650908774995,66711.209398994004,3820.0219999999999,"OFF",-13.600485788610008,-118.98177343106001,-4.8297549999999996,null,3041.7996437434526,0,3131.7939828727549,3307.9700278734622,0,9481.5636544896697,3218.8512525902447,0,3282.2709290360576,3492.244660534072,0,9993.3668421603743,312.69035625654715,0,177.55801712724497,512.05197212653775,0,135.63874740975507,0,27.081070963942238,327.77733946592798,0,947.16162854052891,435.35844086982434,null,null,10470.185839,null,115066.74090000021,14.899247553479974,15445.980139194937,329.40422714931765,13982.17364460002,274.2655101795167,-55.138716969800953,null,null,null,null,null,null,null,null,null,9481.5636544896697,85.988506466933359,0,12.176695886680591,5.4369532307573536,0]
[3280.6852980603103,0,3243.9608183400273,0,3080.5375170523848,9605.1836334527216,10602.946837,"2013-09-17T19:00:00",89,71,"ON",60594.716548299977,73058.023155688003,3557.4810000000002,"OFF",-14.339867670199986,-106.88170367534001,-8.8484060000000007,"ON",62888.579925919985,76043.417674658005,3462.953,"OFF",-7.2181275337599953,-158.64239131086001,-3.4287570000000001,"ON",60467.496949564993,76002.631733768008,3594.79,null,3191.0527278101968,0,3231.2890723108894,0,3073.6500094104499,9495.991809531537,3349.6604867889901,0,3377.5384408623049,0,3206.5124879209479,9933.7114155722429,366.42827218980347,0,231.66392768911055,0,521.13999058955005,207.82051321101017,0,85.414559137695051,0,388.27751207905203,1062.1953044012257,624.475698360519,null,null,10602.946837,null,137357.58810000028,15.780763646668245,17408.230827790172,411.92352070863888,16077.513281400026,354.88663464140063,-57.036886067238243,null,null,null,null,null,null,null,null,null,9495.991809531537,89.632570250113531,0,12.671746029137921,0,6.887507641934917]
[2959.7755034168122,0,2771.0137262059952,0,2719.8588909347527,8450.6481205575601,9029.8529129999988,"2013-09-18T10:00:00",88,73,"ON",53162.951226210011,70604.401910084009,3082.6579999999999,"OFF",-16.387285272614999,-110.62743315334001,-8.8484060000000007,"ON",53027.953900940003,77094.419637014013,2977.1390000000001,"OFF",-3.4865486810006271E-2,-164.90457724801999,-1.7696810000000001,"ON",50521.771199359995,74240.558774810008,2980.674,null,2886.602307844691,0,2766.0153941774229,0,2719.9241183085283,8372.5418203306417,3024.3159231143677,0,2863.4042596173031,0,2822.1569448072387,8709.8771275389099,196.05569215530886,0,211.12360582257725,0,260.74988169147173,58.342076885632196,0,113.73474038269705,0,158.51705519276129,617.0231297820003,279.68782257373306,null,null,9029.8529129999988,null,134683.69280000008,15.81131302426126,17036.370425825884,395.52853412602218,15826.167123200006,344.6224842386647,-50.906049887357483,null,null,null,null,null,null,null,null,null,8372.5418203306417,73.173195572121131,0,4.9983320285723494,0,-6.5227373775542219E-2]
[2534.5179010440665,0,0,0,0,2534.5179010440665,3023.2807969999994,"2013-09-18T18:00:00",93,70,"ON",46447.055945299988,59389.463269600004,3043.6689999999999,"OFF",-17.316818608214991,-106.18116403378001,-8.8484060000000007,"OFF",-0.32159920362499478,-75.14639166260001,-3.5762309999999999,"OFF",-1.9838410586400124,-164.90457724801999,-3.9817830000000001,"OFF",-398.09404349999778,32652.566568146005,-3.9817830000000001,null,2475.3786090388003,0,0,0,0,2475.3786090388003,2647.2257409787412,0,0,0,0,2647.2257409787412,568.29039096119959,0,0,0,0,396.44325902125865,0,0,0,0,507.98608877480831,336.13895683486737,null,null,3023.2807969999994,null,147581.8293000001,16.068427832677838,18369.16851315942,455.92973038700478,17038.591954200008,395.6254282006135,-60.304302186391283,null,null,null,null,null,null,null,null,null,2475.3786090388003,59.13929200526627,0,0,0,0]
[0,0,0,0,0,0,-16.922614899999999,"2013-09-19T16:00:00",89,73,"OFF",-1.9472924321400056,-75.14639166260001,0.81106509999999998,"OFF",-18.622859170739975,-107.42463392880001,-8.8484060000000007,"OFF",-1.55994527225,-75.14639166260001,-1.7696810000000001,"OFF",-4.6330994248699877,-166.99199929652002,-1.7696810000000001,"OFF",-1.2280884898450002,-119.54531722790001,-5.3459120000000002,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-51.122789943830014,-51.122789943830014,null,null,-16.922614899999999,null,137357.58810000028,15.902457401227565,17275.014123213081,406.00942458523065,16077.513281400026,354.88663464140063,-51.122789943830014,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2643.2853225478989,0,2576.5206330389096,0,2509.8279337393456,7729.6338893261545,8043.9209129999999,"2013-09-20T07:00:00",73,72,"ON",47467.027037569991,73000.281171722017,2682.5320000000002,"OFF",-19.687554473850021,-108.5447433969,-8.8484060000000007,"ON",49776.628990424979,75260.856984614002,2689.6129999999998,"OFF",-8.2097734469800141,-164.90457724801999,-1.7696810000000001,"ON",46116.758859794987,75438.847311908001,2682.3939999999998,null,2581.9363986881667,0,2573.4823149901763,0,2512.1758403428612,7667.5945540212042,2678.9313385177638,0,2668.072221836409,0,2592.0041965964783,7939.0077569506511,100.59560131183343,0,116.13068500982354,0,170.21815965713859,3.600661482236319,0,21.540778163590858,0,90.389803403521455,353.59884597764938,82.185643048202479,null,null,8043.9209129999999,null,91919.663300000131,14.292779742676283,12862.39135492176,235.7886225499725,11806.348350200013,202.44302254882635,-33.345600001146153,null,null,null,null,null,null,null,null,null,7667.5945540212042,61.348923859732167,0,3.0383180487333448,0,-2.3479066035156393]
[2885.0636056164408,0,2783.4884851045394,0,2781.6242716792949,8450.1763624002742,9520.456913,"2013-09-20T23:00:00",69,64,"ON",58117.074884119989,72428.483936696008,3168.9830000000002,"OFF",-18.936524738560014,-110.36074042284001,-8.8484060000000007,"ON",58751.238795080018,74577.995261190008,3026.0810000000001,"OFF",-8.7251273337199944,-164.90457724801999,-1.7696810000000001,"ON",59573.59834538,75273.963027370002,3336.011,null,2802.2942397999955,0,2774.4083539385583,0,2775.5272067538581,8352.2298004924123,2950.6820814407861,0,2910.4119920883031,0,2907.9976112575823,8769.091684786672,366.68876020000471,0,251.67264606144181,0,560.48379324614189,218.3009185592141,0,115.66900791169701,0,428.01338874241765,1141.844549240044,724.98266494578445,null,null,9520.456913,null,80625.134100000141,13.421011031132586,12014.763107335926,208.79780163251255,10744.662605400013,171.79715136496822,-37.00065026754433,null,null,null,null,null,null,null,null,null,8352.2298004924123,82.769365816445315,0,9.080131165981129,0,6.0970649254368254]
[2029.068029002254,0,2330.6467314310362,0,0,4359.7147604332904,5362.544104999999,"2013-09-21T14:00:00",82,61,"ON",40410.925191000002,62400.219665678007,2548.0949999999998,"OFF",-19.157565873779976,-106.45258905634,-8.8484060000000007,"ON",51013.211331719991,71080.975803862006,2829.6019999999999,"OFF",-9.2212193485300205,-164.90457724801999,-2.3227060000000002,"OFF",-2.8086792327999999,-118.98177343106001,-3.9817830000000001,null,1981.8300785097317,0,2326.8778416697733,0,0,4308.707920179505,2094.2681643801243,0,2447.9666094051831,0,0,4542.234773785307,566.26492149026808,0,502.7241583302266,0,0,453.82683561987551,0,381.63539059481673,0,0,990.74601789720737,757.21916429140492,null,null,5362.544104999999,null,117939.30320000008,14.510388822813997,16255.843263768329,362.26712347673879,14252.194500800008,284.02406155345153,-78.243061923287257,null,null,null,null,null,null,null,null,null,4308.707920179505,47.237950492522259,0,3.7688897612629262,0,0]
[2235.6349357110316,0,0,0,2136.4133608617462,4372.0482965727779,4884.3752069999991,"2013-09-22T05:00:00",62,55,"ON",50461.393226150023,62900.142207230005,2475.2489999999998,"OFF",-17.113897211839994,-107.15786098996001,-8.8484060000000007,"OFF",1.4627855316999613E-2,-67.492591026439996,-1.7696810000000001,"OFF",-9.5319652523200062,-164.90457724801999,-2.3227060000000002,"ON",49921.47485999998,68560.893927734011,2422.067,null,2170.3923585310999,0,0,0,2136.7674967787311,4307.1598553098311,2340.5486845291703,0,0,0,2264.679022606249,4605.2277071354192,304.85664146889985,0,0,0,285.29950322126888,134.70031547082954,0,0,0,157.38797739375104,561.99769315408946,263.92984132850131,null,null,4884.3752069999991,null,62221.807200000039,12.246079695187058,10161.91446548472,156.20256717289934,9014.7498768000041,128.0441156368201,-28.158451536079241,null,null,null,null,null,null,null,null,null,4307.1598553098311,65.242577179931686,0,0,0,-0.35413591698488744]
[2560.7211341403313,0,0,0,2452.4677618973274,5013.1888960376582,5577.1081299999996,"2013-09-22T21:00:00",70,59,"ON",55042.563481080011,64346.218369090006,2807.69,"OFF",-17.548255849019974,-106.72882657930001,-8.8484060000000007,"OFF",0.24421208962500376,-67.492591026439996,-1.7696810000000001,"OFF",-10.176961286659983,-164.90457724801999,-3.9817830000000001,"ON",55556.029284910001,69123.138349466011,2784.018,null,2485.4701388295889,0,0,0,2449.3679678882363,4934.8381067178252,2677.5755925601861,0,0,0,2604.8282918155091,5282.4038843756953,322.21986117041115,0,0,0,334.65003211176372,130.11440743981393,0,0,0,179.18970818449088,607.8560493823345,260.29027172446445,null,null,5577.1081299999996,null,83410.700000000012,13.211727508537386,12626.766627770703,228.10110140439545,11006.505800000001,179.08725750455508,-49.013843899840367,null,null,null,null,null,null,null,null,null,4934.8381067178252,75.250995310742383,0,0,0,3.0997940090910561]
[2740.4668691344132,0,0,0,2485.3089544936806,5225.7758236280933,5744.0772319999996,"2013-09-23T12:00:00",80,63,"ON",55853.271729564985,68395.648705665997,2939.2840000000001,"OFF",-18.41315402915998,-103.24978983180002,-8.8484060000000007,"OFF",-0.2492364424599964,-33.398399859304,-1.7696810000000001,"OFF",-8.8022538715299863,-164.90457724801999,-1.7696810000000001,"ON",52716.285000924989,72200.38745940401,2817.181,null,2662.8808505637435,0,0,0,2484.0531546875841,5146.9340052513271,2828.9060195320417,0,0,0,2605.42857241308,5434.3345919451222,276.40314943625663,0,0,0,333.12784531241596,110.37798046795842,0,0,0,211.75242758692002,540.96629434703163,253.56570765323744,null,null,5744.0772319999996,null,112180.80000000005,14.435793969355482,15542.033952290967,333.21416879893144,13710.895200000004,264.64946839729043,-68.564700401641005,null,null,null,null,null,null,null,null,null,5146.9340052513271,77.586018570669694,0,0,0,1.2557998060965474]
[2647.4713222593182,2930.2942405591807,0,0,2547.9946249736026,8125.7601877921006,8698.1126130000011,"2013-09-23T23:00:00",72,63,"ON",53839.467108180004,61266.715404798008,2861.8130000000001,"ON",52555.219807349989,60766.407863214008,2897.029,"OFF",2.107446429199997E-2,-33.398399859304,-1.7696810000000001,"OFF",-9.6299873639200015,-158.64239131086001,-2.3227060000000002,"ON",54416.572206869991,64941.556751906006,2943.3629999999998,null,2574.2249379383043,2931.3983081453071,0,0,2545.6505749880353,8051.2738210716461,2785.6470631771858,3145.8652183833187,0,0,2727.5116332078619,8659.023914768366,287.58806206169584,-34.369308145307059,0,0,397.71242501196457,76.165936822814274,-248.83621838331874,0,0,215.85136679213792,603.28571635493824,-4.4643773417816135,null,null,8698.1126130000011,null,89061.715200000035,13.647739710040611,13051.49674483864,242.06120611908304,11537.701228800002,194.41574354566797,-47.645462573415074,null,null,null,null,null,null,null,null,null,8051.2738210716461,73.24638432101392,-1.104067586126348,0,0,2.3440499855673806]
[2630.7992827427183,0,0,0,0,2630.7992827427183,3082.7422919999999,"2013-09-24T18:00:00",88,63,"ON",53473.461562799996,61773.239092732008,3100.6640000000002,"OFF",-1.8489126035950081,-112.85874896380001,-8.8484060000000007,"OFF",-5.1681194625003125E-2,-33.398399859304,-1.404684,"OFF",-10.515585522189998,-166.99199929652002,-2.3227060000000002,"OFF",131.30483633999867,42642.010002604002,-5.3459120000000002,null,2558.3283174169424,0,0,0,0,2558.3283174169424,2762.3674393417141,0,0,0,0,2762.3674393417141,542.33568258305786,0,0,0,0,338.29656065828613,0,0,0,0,461.09681844647878,257.05769652170704,null,null,3082.7422919999999,null,134683.69280000008,15.202844251464656,17718.223060401942,425.86134837524378,15826.167123200006,344.6224842386647,-81.238864136579082,null,null,null,null,null,null,null,null,null,2558.3283174169424,72.470965325775978,0,0,0,0]
[2831.897937553978,0,0,0,0,2831.897937553978,5516.6561299999994,"2013-09-25T09:00:00",82,66,"ON",55509.901308810004,66548.482718801999,2954.4009999999998,"OFF",1.764719680920007,-107.1531286979,-8.8484060000000007,"OFF",-0.56082235400000435,-33.398399859304,-1.7696810000000001,"OFF",-10.014144451290017,-158.64239131086001,-3.9817830000000001,"check",4282.1662978780005,5342.5708503078004,2576.855,null,2754.6251022243587,0,0,0,0,2754.6251022243587,2934.1184806983024,0,0,0,0,2934.1184806983024,199.77589777564117,0,0,0,0,20.282519301697448,0,0,0,0,135.28256849747044,-44.210809976473286,null,null,5516.6561299999994,null,117939.30320000008,14.814623209212298,15922.011857400586,348.51739083162227,14252.194500800008,284.02406155345153,-64.493329278170734,null,null,null,null,null,null,null,null,null,2754.6251022243587,77.272835329619284,0,0,0,0]
[2784.1187047199078,0,2601.5685066826109,0,0,5385.6872114025191,5761.9099269999997,"2013-09-25T10:00:00",83,64,"ON",56013.996840539992,65808.953803168013,2992.701,"OFF",-4.6955338505099684,-112.02378014440001,-8.8484060000000007,"ON",55022.58855185,73080.842428418007,2788.2330000000002,"OFF",-10.800613796700002,-158.64239131086001,-3.9817830000000001,"OFF",1.1453773534000151,-166.99199929652002,-6.1938839999999997,null,2706.0337130043226,0,2595.2483240507781,0,0,5301.2820370551008,2894.3644998923019,0,2723.7589616574028,0,0,5618.1234615497051,286.66728699567739,0,192.98467594922204,0,0,98.336500107698157,0,64.474038342597396,0,0,408.01885601093255,91.177431516328681,null,null,5761.9099269999997,null,120794.73630000022,14.790261863617703,16334.360731927405,365.54251586653697,14520.60521220002,293.9094089325701,-71.633106933966872,null,null,null,null,null,null,null,null,null,5301.2820370551008,78.084991715585147,0,6.3201826318327221,0,0]
[2608.7673507778818,0,0,0,2572.4636523686036,5181.2310031464858,5803.3521299999993,"2013-09-26T01:00:00",75,60,"ON",55324.669410009992,63547.046531832006,2808.299,"OFF",-22.325855780934983,-109.93162580384001,-8.8484060000000007,"OFF",0.56228624462499477,-67.492591026439996,-1.7696810000000001,"OFF",-9.1590596277600049,-160.72981335936001,-3.9817830000000001,"ON",57920.521308219984,59274.091593344005,3009.6529999999998,null,2532.7657246119788,0,0,0,2567.6685060061945,5100.4342306181734,2734.1888680683564,0,0,0,2829.395099189358,5563.5839672577149,275.53327538802114,0,0,0,441.98449399380524,74.110131931643537,0,0,0,180.25790081064179,654.62254642033781,191.47280978079672,null,null,5803.3521299999993,null,97681.6875,13.759025842753797,14198.924926279449,282.08412039951344,12347.978625,219.18889743802484,-62.895222961488599,null,null,null,null,null,null,null,null,null,5100.4342306181734,76.001626165902962,0,0,0,4.7951463624090138]
[0,0,0,0,0,0,-16.466065,"2013-09-26T16:00:00",94,68,"OFF",-1.1326281204250019,-75.842190991265994,1.3044830000000001,"OFF",-9.2519796440400235,-109.93635809590002,-8.8484060000000007,"OFF",-4.7396445321250029,-33.398399859304,-1.7696810000000001,"OFF",-9.3894115900200283,-164.90457724801999,-2.3227060000000002,"OFF",3.1347574604850221,-116.19862424140001,-4.8297549999999996,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-66.78155514818377,-66.78155514818377,null,null,-16.466065,null,150001.30160000012,16.029206004139972,18715.99897852186,472.39343073796016,17266.022350400013,405.61187558977639,-66.78155514818377,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3104.7815942685352,3076.6490833857711,0,0,3022.8163148720741,9204.2469925263795,10195.181396,"2013-09-27T08:00:00",75,68,"ON",59471.22223462502,66173.829562662009,3368.8719999999998,"ON",52045.072795740001,69229.735233326006,3335.4349999999999,"OFF",0.13959167585999444,-33.398399859304,-1.7696810000000001,"OFF",-9.5163923845900058,-160.76462377892,-2.3319230000000002,"ON",61755.961225279993,62666.992604518004,3494.9760000000001,null,3018.2755667703059,3078.0865012007662,0,0,3014.8799219880598,9111.2419899591314,3229.2787123058879,3223.6478828008972,0,0,3276.553005024311,9729.4796001310951,350.59643322969396,257.34849879923377,0,0,480.09607801194034,139.59328769411195,111.78711719910279,0,0,218.42299497568911,1042.480167707236,424.24255753527166,null,null,10195.181396,null,{"$f":" -0.6251*I5765^3 + 145.21*I5765^2 - 8340.3*I5765 + 170112","v":97681.6875},14.245800860991078,13713.751645578501,264.749739771657,12347.978625,219.18889743802484,-45.560842333632166,null,null,null,null,null,null,null,null,null,9111.2419899591314,86.506027498229287,-1.4374178149951149,0,0,7.9363928840143672]
[3282.1377863346152,0,3236.9709509750583,0,3139.6899026473352,9658.7986399570091,10379.370810999999,"2013-09-27T23:00:00",82,73,"ON",59208.006755339993,68898.55499746601,3439.038,"OFF",-10.713802423050018,-111.32291966948002,-8.8484060000000007,"ON",61531.037757479986,77028.191610676004,3424.0010000000002,"OFF",-8.780040796240014,-160.76462377892,-3.9817830000000001,"ON",60115.15986864001,68280.437446090014,3529.1619999999998,null,3195.4372631410788,0,3225.4924241721515,0,3133.0723040686435,9554.0019913818724,3381.5855107134985,0,3358.2149994893803,0,3327.5410336243822,10067.34154382726,243.60073685892121,0,198.50857582784874,0,396.08969593135635,57.452489286501532,0,65.786000510619942,0,201.62096637561763,791.58949101862549,278.2499385732383,null,null,10379.370810999999,null,117939.30320000008,15.240551350169921,15477.038919420083,330.63357915295234,14252.194500800008,284.02406155345153,-46.609517599500805,null,null,null,null,null,null,null,null,null,9554.0019913818724,86.700523193536355,0,11.478526802906799,0,6.6175985786917408]
[3167.6208565129823,0,3185.1798966246051,0,2980.6866144467172,9333.4873675843046,10450.840054,"2013-09-28T14:00:00",74,71,"ON",58495.14158896001,68204.383898102009,3404.1759999999999,"OFF",-14.400675812639999,-107.14807557248001,-8.8484060000000007,"ON",61846.998167729995,76913.63003865401,3551.183,"OFF",-8.7459175073900042,-164.86976682846,-3.41954,"ON",58198.193683210011,68258.364110922004,3507.7489999999998,null,3082.890796417058,0,3173.4447367849425,0,2975.6067673735397,9231.9423005755398,3269.7795759673854,0,3308.013522986344,0,3157.2997721187326,9735.092871072462,321.2852035829419,0,377.73826321505749,0,532.1422326264601,134.3964240326145,0,243.16947701365598,0,350.44922788126723,1193.7943028492832,690.64373235236133,null,null,10450.840054,null,94794.23760000011,14.329917735491136,13230.255658093794,248.07477091650927,12076.55833440001,210.7033743413329,-37.371396575176362,null,null,null,null,null,null,null,null,null,9231.9423005755398,84.730060095924273,0,11.735159839662629,0,5.0798470731774614]
[1669.0071125300847,0,1389.7126628563808,0,1647.6439185647546,4706.3636939512198,5276.5116709999993,"2013-09-29T05:00:00",65,61,"ON",30069.070288950017,65862.532974288013,1820.7650000000001,"OFF",-15.75246221394001,-107.8489360474,-8.8484060000000007,"ON",25343.849947114995,67296.465593472007,1771.105,"OFF",-8.9951360911299876,-158.64239131086001,-2.3319230000000002,"ON",27682.663190699976,63020.238154712009,1695.8219999999999,null,1638.0479061289755,0,1392.6938502353632,0,1654.2672640128915,4685.0090203772297,1691.8798887591095,0,1428.5494431990239,0,1706.4240979786259,4826.8534299367593,182.71709387102464,0,378.41114976463678,0,41.554735987108415,128.88511124089064,0,342.55555680097609,0,-10.602097978626034,573.13710945350545,431.29269989397631,null,null,5276.5116709999993,null,69836.662499999977,12.870726560407837,10852.0155676102,174.7647896059573,9730.5462749999988,145.21891943669294,-29.545870169264361,null,null,null,null,null,null,null,null,null,4685.0090203772297,30.959206401109213,0,-2.9811873789824404,0,-6.6233454481368881]
[2441.6797781280802,0,2377.5598928879263,0,2348.4953790512727,7167.7350500672792,7648.3419130000002,"2013-09-29T20:00:00",76,60,"ON",51483.240480880013,65243.605318678005,2599.4279999999999,"OFF",-17.771125695569999,-105.76159420724001,-8.8484060000000007,"ON",52737.920120759998,71016.736944356002,2496.8960000000002,"OFF",-9.6404434869599758,-164.86976682846,-1.7696810000000001,"ON",51598.697512569997,62522.569467514004,2562.636,null,2373.7413897722809,0,2372.7481343380196,0,2347.9123325784803,7094.4018566887808,2535.1800232412766,0,2502.5396807235747,0,2528.618271243336,7566.3379752081873,225.68661022771903,0,124.14786566198063,0,214.72366742151962,64.247976758723325,0,-5.6436807235745619,0,34.017728756663928,498.71793702162222,26.781818502215629,null,null,7648.3419130000002,null,100578.26240000024,13.857760641605768,14515.803094192532,293.73093052079292,12620.256665600022,227.89072423119586,-65.840206289597063,null,null,null,null,null,null,null,null,null,7094.4018566887808,67.938388355799361,0,4.811758549906699,0,0.58304647279237543]
[2617.0260831100686,0,2372.3870210157452,0,0,4989.4131041258133,5400.1063590000003,"2013-09-30T12:00:00",82,64,"ON",52419.764282760014,64041.506885430012,2767.5030000000002,"OFF",-17.112912531090011,-107.85406938116002,-8.8484060000000007,"ON",50079.156915719999,67977.739191764005,2650.2080000000001,"OFF",-8.2748053210199863,-166.99199929652002,-3.41954,"OFF",-1.2221745228700185,-166.99199929652002,-5.3366949999999997,null,2546.6319984381225,0,2369.1582059802386,0,0,4915.7902044183611,2724.567307379144,0,2504.9807238281028,0,0,5229.5480312072468,220.87100156187762,0,281.04979401976152,0,0,42.935692620856116,0,145.2272761718973,0,0,432.0299924135191,118.27216562463337,null,null,5400.1063590000003,null,117939.30320000008,14.692929454652978,16053.885450685382,353.91486472157158,14252.194500800008,284.02406155345153,-69.890803168120044,null,null,null,null,null,null,null,null,null,4915.7902044183611,70.394084671946075,0,3.2288150355066136,0,0]
[2956.6066936258153,0,0,3463.7886743944478,0,6420.395368020263,6770.74413,"2013-10-01T03:00:00",69,65,"ON",58806.509940359996,92220.020165039998,3084.8760000000002,"OFF",-17.622069399674988,-109.93635809590002,-8.8484060000000007,"OFF",0.19274169525000096,-67.318643199481997,-1.7696810000000001,"ON",60805.688544300006,89415.936598639993,3700.4679999999998,"OFF",-6.3696650660299783,-119.67758078056001,-3.9817830000000001,null,2872.1127549852572,0,0,3454.0798344370087,0,6326.1925894222659,2905.6666656493403,0,0,3506.1393937068228,0,6411.8060593561631,212.76324501474301,0,0,246.38816556299116,0,179.2093343506599,0,0,194.32860629317702,0,423.81485407659233,338.20138414269508,null,null,6770.74413,null,80625.134100000141,13.481857908412247,11960.53758283458,207.13370786611006,10744.662605400013,171.79715136496822,-35.336556501141843,null,null,null,null,null,null,null,null,null,6326.1925894222659,84.493938640558099,0,0,9.7088399574390678,0]
[0,0,0,0,0,0,-17.118027000000001,"2013-10-01T18:00:00",85,70,"OFF",-2.8160650064250055,-111.18881132500002,1.1686780000000001,"OFF",-17.731532986960012,-128.44467317592,-8.8484060000000007,"OFF",-6.691719825000172E-3,-41.226148322422006,-1.7696810000000001,"OFF",-4.035717894739995,-166.99199929652002,-2.3319230000000002,"OFF",1202.9302336699905,38572.014247652005,-5.3366949999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-57.522760319971781,-57.522760319971781,null,null,-17.118027000000001,null,126439.21250000014,15.347744926479834,16476.585075616094,371.51565536513925,15051.185975000013,313.99289504516747,-57.522760319971781,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[2834.1416240948934,0,2776.1026911151789,0,2761.1018949416944,8371.3462101517671,8813.6220539999995,"2013-10-02T10:00:00",80,73,"ON",50701.500192330008,66708.514398770014,2911.2979999999998,"OFF",-17.961476217409977,-108.81368196092001,-8.8484060000000007,"ON",53125.077448350021,70485.493046033997,2932.0430000000001,"OFF",-6.5879818005400015,-158.64239131086001,-3.41954,"ON",51499.903617829994,63276.439634340008,2982.549,null,2766.1507565839097,0,2771.0414022059704,0,2760.5928854958129,8297.7850442856925,2916.2910209829356,0,2909.112007374973,0,2938.9835439435733,8764.3865723014824,145.14724341609008,0,161.00159779402975,0,221.9561145041871,-4.9930209829358319,0,22.930992625027102,0,43.565456056426683,484.04501605560915,17.443488039820181,null,null,8813.6220539999995,null,112180.80000000005,15.044262742152085,14913.432704905359,308.70940805598821,13710.895200000004,264.64946839729043,-44.059939658697772,null,null,null,null,null,null,null,null,null,8297.7850442856925,67.990867510983662,0,5.0612889092085425,0,0.50900944588147468]
[3237.329956946217,0,3154.9428017595565,0,3240.0324103604767,9632.3051690662505,10526.668670999999,"2013-10-03T03:00:00",76,73,"ON",58389.443307089983,67101.158285572004,3482.8879999999999,"OFF",-18.094906791500005,-107.14807557248001,-8.8484060000000007,"ON",60087.574751709988,69359.071181576001,3422.1759999999999,"OFF",-8.6787249308900005,-164.86976682846,-2.3319230000000002,"ON",62298.451214550019,62987.649506170004,3632.7849999999999,null,3152.5284784985474,0,3144.7039176633534,0,3231.5632841241768,9528.7956802860772,3349.1759177723807,0,3332.4561994470369,0,3496.626959176961,10178.259076396378,330.35952150145249,0,277.47208233664651,0,401.22171587582307,133.71208222761925,0,89.719800552963079,0,136.15804082303885,971.5541542818828,322.09075817158197,null,null,10526.668670999999,null,100578.26240000024,14.648770046241355,13731.973685505023,265.38988966323507,12620.256665600022,227.89072423119586,-37.499165432039206,null,null,null,null,null,null,null,null,null,9528.7956802860772,84.801478447669524,0,10.238884096203037,0,8.4691262362998714]
[0,0,0,0,0,0,-18.965109500000001,"2013-10-03T16:00:00",91,74,"OFF",-1.7577284883199982,-74.450592333934011,0.55668649999999997,"OFF",-18.349170984744998,-108.112821486,-8.8484060000000007,"OFF",-0.89100581225000297,-75.14639166260001,-3.5670139999999999,"OFF",-9.5791054559900086,-160.76462377892,-1.7696810000000001,"OFF",3.6035235688899974,-117.59015873206,-5.3366949999999997,null,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,-48.11750293216727,-48.11750293216727,null,null,-18.965109500000001,null,142571.47790000017,16.141028790529788,17665.723759026965,423.48357879071978,16567.618922600017,375.36607585855251,-48.11750293216727,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[3230.2507317075415,0,3201.9414166006309,0,3092.6087987712558,9524.8009470794277,10394.976671,"2013-10-04T07:00:00",75,72,"ON",58955.66017977499,70272.331361650009,3341.3319999999999,"OFF",-17.664953710199981,-110.63216544540002,-8.8484060000000007,"ON",61526.081586899993,72724.741461320009,3508.9319999999998,"OFF",-10.972047091880009,-166.99199929652002,-2.3319230000000002,"ON",59899.245146020017,66270.336237349999,3555.893,null,3144.2976134897426,0,3190.4779958555009,0,3086.1769895566886,9420.9525989019312,3316.8072068628367,0,3357.3572767321848,0,3297.5072008032848,9971.6716843983049,197.03438651025726,0,318.45400414449887,0,469.71601044331146,24.524793137163215,0,151.57472326781499,0,258.3857991967152,947.66299313492834,396.94390763855415,null,null,10394.976671,null,97681.6875,14.489188370109721,13483.38982209813,256.73030540116406,12347.978625,219.18889743802484,-37.541407963139221,null,null,null,null,null,null,null,null,null,9420.9525989019312,85.953118217798874,0,11.463420745129952,0,6.4318092145672381]
[3304.1426271647852,0,3219.1267251121694,0,3122.0354719392421,9645.3048242161967,10690.120913000001,"2013-10-04T22:00:00",81,71,"ON",61024.830612374994,69624.296099454004,3551.163,"OFF",-15.968715473040008,-107.8489360474,-8.8484060000000007,"ON",62449.882382340002,74114.960535204009,3519.2739999999999,"OFF",-11.241950449170005,-158.64239131086001,-1.7696810000000001,"ON",61397.992730940008,65889.049851492004,3630.3020000000001,null,3213.4884562613847,0,3206.8531354464876,0,3114.3683284448011,9534.7099201526744,3404.1386526616907,0,3366.7718784470167,0,3339.9669903882627,10110.87752149697,337.67454373861528,0,312.42086455351227,0,515.933671555199,147.02434733830933,0,152.50212155298323,0,290.33500961173741,1115.8184597514005,539.6508584071039,null,null,10690.120913000001,null,115066.74090000021,15.020941308039296,15320.842887311706,324.47613027544281,13982.17364460002,274.2655101795167,-50.210620095926117,null,null,null,null,null,null,null,null,null,9534.7099201526744,90.654170903400427,0,12.273589665681811,0,7.6671434944410066]
[1711.3298243238271,0,0,0,1712.636380884449,3423.9662052082758,3436.8832320000001,"2013-10-05T14:00:00",63,53,"ON",35461.534450150008,71215.573419216016,1724.2739999999999,"OFF",-15.321717244259981,-108.54987673066002,-8.8484060000000007,"OFF",0.28588027237499897,-33.398399859304,-1.7696810000000001,"OFF",-11.62753043816002,-160.76462377892,-1.7696810000000001,"ON",34726.748204150004,67737.467088460005,1724.9970000000001,null,1672.7010476565104,0,0,0,1718.4659549511809,3391.1670026076913,1730.0606828119803,0,0,0,1783.3866850095417,3513.4473678215218,51.572952343489533,0,0,0,6.5310450488191236,-5.7866828119804268,0,0,0,-58.389685009541608,23.769442333455117,-98.510922880375574,null,null,3436.8832320000001,null,64707.210300000093,12.209105232762928,10599.828417623821,167.84014397832385,9248.3777682000091,133.50558891947031,-34.334555058853539,null,null,null,null,null,null,null,null,null,3391.1670026076913,38.628776667316743,0,0,0,-5.8295740667319933]
[0,0,0,0,2013.292382730089,2013.292382730089,3134.64813,"2013-10-06T05:00:00",53,50,"check",14564.828196269998,43323.323705066003,1119.172,"OFF",-18.853798325985025,-107.8489360474,-8.8484060000000007,"OFF",-0.41287571187500094,-41.226148322422006,-1.7696810000000001,"OFF",-12.171447757420005,-160.76462377892,-3.9817830000000001,"ON",45795.339797020002,69910.824352436015,2030.076,null,0,0,0,0,2015.6762668497176,2015.6762668497176,0,0,0,0,2116.7478379023514,2116.7478379023514,0,0,0,0,14.399733150282373,0,0,0,0,-86.671837902351399,6.7024737994522923,-94.369097253181479,null,null,3134.64813,null,42907.977300000086,11.283499788278451,7605.4376931125289,98.062633604885548,7199.249866200008,90.365374254055467,-7.6972593508300804,null,null,null,null,null,null,null,null,null,2015.6762668497176,0,0,0,0,-2.3838841196286467]
[2248.561272542735,0,0,0,2156.333248153167,4404.8945206959015,4868.1082319999996,"2013-10-06T20:00:00",68,51,"ON",50794.064453035011,66367.348224580011,2402.6080000000002,"OFF",-23.31650964045005,-107.1531286979,-8.8484060000000007,"OFF",0.2123812518749939,-41.226148322422006,-1.7696810000000001,"OFF",-12.579267171730022,-158.64239131086001,-1.7696810000000001,"ON",50570.590843499987,58789.063740530008,2477.8879999999999,null,2182.6545766925938,0,0,0,2156.3306046408634,4338.9851813334571,2330.6022802235766,0,0,0,2357.8006996213526,4688.4029798449292,219.95342330740641,0,0,0,321.55739535913654,72.005719776423575,0,0,0,120.08730037864734,484.69020487508669,135.27240636361469,null,null,4868.1082319999996,null,77871.196800000151,12.536128878595186,12423.483765065837,221.58297454189369,10485.792499200013,164.76236075043747,-56.820613791456225,null,null,null,null,null,null,null,null,null,4338.9851813334571,65.906695850141205,0,0,0,2.6435123036208097E-3]
[1964.0158264473603,0,0,0,1919.1115826380842,3883.1274090854445,4190.3664219999991,"2013-10-07T12:00:00",78,57,"ON",41541.984018195006,71094.474867484008,2100.1990000000001,"OFF",-30.831362597750008,-113.14645627938,-8.8484060000000007,"OFF",-0.22997603847000342,-33.398399859304,-1.3963890000000001,"OFF",-10.462358461589991,-160.76462377892,-3.9817830000000001,"ON",40662.580226520004,62727.726359566004,2104.3939999999998,null,1915.1871840582301,0,0,0,1923.4721829426742,3838.6593670009042,1994.5411671497029,0,0,0,2034.4269022484643,4028.9680693981672,185.01181594177001,0,0,0,180.9218170573256,105.65783285029715,0,0,0,69.967097751535448,286.73867999690623,96.429977599643223,null,null,4190.3664219999991,null,106383.78480000014,13.873111349084329,15336.687225107846,325.09788805220637,13165.975771200012,245.90293505001699,-79.194953002189379,null,null,null,null,null,null,null,null,null,3838.6593670009042,48.828642389130209,0,0,0,-4.3606003045899797]
[2192.0568100222536,0,0,0,2147.076271020936,4339.13308104319,4635.8623729999999,"2013-10-08T08:00:00",60,54,"ON",49328.884657349998,75859.315471856011,2321.306,"OFF",-4.7393522510399855,-107.58513081714,-8.8484060000000007,"OFF",-0.33477421924999945,-75.14639166260001,-1.7696810000000001,"OFF",-9.6938861866699888,-164.86976682846,-3.41954,"ON",50269.548105525013,68872.439161962,2328.5940000000001,null,2129.0505732501001,0,0,0,2147.2403647253882,4276.2909379754883,2216.3331355894247,0,0,0,2275.0578272186785,4491.3909628081037,192.25542674989993,0,0,0,181.35363527461186,104.97286441057531,0,0,0,53.536172781321511,350.65338769529978,135.55336286268482,null,null,4635.8623729999999,null,57428.400000000081,12.021841187431155,9554.0107550316879,140.86127552929429,8564.1696000000084,117.9056012000823,-22.955674329211988,null,null,null,null,null,null,null,null,null,4276.2909379754883,63.006236772153443,0,0,0,-0.16409370445217064]
[0,0,0,0,2522.1894594060345,2522.1894594060345,2993.3082689999997,"2013-10-08T18:00:00",75,58,"OFF",-6.1629330626400103,-73.754793005267999,1.7526040000000001,"OFF",-8.2052689263999792,-104.36484617448001,-8.8484060000000007,"OFF",0.1196777303100031,-67.318643199481997,-1.3963890000000001,"OFF",-10.363282348789999,-166.99199929652002,-3.41954,"ON",58534.39309392,58412.004334190002,3005.22,null,0,0,0,0,2516.947054235075,2516.947054235075,0,0,0,0,2793.1079452358076,2793.1079452358076,0,0,0,0,488.27294576492477,0,0,0,0,212.11205476419218,420.75153579215964,144.59064479142708,null,null,2993.3082689999997,null,97681.6875,13.637332088194475,14325.63009660237,286.71030741078994,12347.978625,219.18889743802484,-67.521409972765099,null,null,null,null,null,null,null,null,null,2516.947054235075,0,0,0,0,5.2424051709595005]
[0,0,0,0,2402.8172629288997,2402.8172629288997,2643.8304109999999,"2013-10-09T09:00:00",67,60,"OFF",-8.5422922665449992,-75.14639166260001,1.478421,"OFF",-11.903738507324988,-107.14807557248001,-8.8484060000000007,"OFF",-0.32214962650000306,-41.226148322422006,-1.7696810000000001,"OFF",-8.850474426430015,-166.99199929652002,-2.3319230000000002,"ON",53170.149286969994,68638.88049671601,2655.3020000000001,null,0,0,0,0,2401.2798628457645,2401.2798628457645,0,0,0,0,2547.185550392338,2547.185550392338,0,0,0,0,254.02213715423568,0,0,0,0,108.11644960766216,216.64083966368838,70.735152117114865,null,null,2643.8304109999999,null,75152.638700000127,12.99108398784298,11569.879583617156,195.36750538163341,10230.248037800013,157.98620789108611,-37.381297490547297,null,null,null,null,null,null,null,null,null,2401.2798628457645,0,0,0,0,1.5374000831352532]
[2491.3127594068187,0,0,0,2314.8506380276367,4806.163397434455,5315.2691299999997,"2013-10-10",64,59,"ON",53439.310220799991,70251.822089112,2695.4720000000002,"OFF",-14.505108671559972,-109.93635809590002,-8.8484060000000007,"OFF",-0.66788545874999539,-67.318643199481997,-1.7696810000000001,"OFF",-9.6951121195499788,-160.76462377892,-3.9817830000000001,"ON",51551.634080045005,64269.563258552007,2634.3969999999999,null,2419.4610972390396,0,0,0,2314.2940531544236,4733.7551503934628,2557.3614737691064,0,0,0,2481.155432808881,5038.5169065779874,276.01090276096056,0,0,0,320.1029468455763,138.11052623089381,0,0,0,153.24156719111897,566.87816532272609,262.11640913820202,null,null,5315.2691299999997,null,67246.745600000082,12.660750978865622,10622.868376805443,168.46602566519439,9487.0940864000077,139.23034138138365,-29.235684283810741,null,null,null,null,null,null,null,null,null,4733.7551503934628,71.851662167779068,0,0,0,0.55658487321306893]
[0,0,0,0,3039.0154124348451,3039.0154124348451,3583.8107380000001,"2013-10-10T16:00:00",84,68,"OFF",-2.0552838871200017,-76.537990319932007,2.1383649999999998,"OFF",-15.005751067619986,-108.81873508634001,-8.8484060000000007,"OFF",2.0260246250023511E-3,-75.14639166260001,-1.7696810000000001,"OFF",-9.0546081088400285,-160.76462377892,-3.41954,"ON",62131.934684870015,56573.990118920003,3595.71,null,0,0,0,0,3030.7559113793013,3030.7559113793013,0,0,0,0,3373.3208393261502,3373.3208393261502,0,0,0,0,564.95408862069871,0,0,0,0,222.3891606738498,502.99775487326184,160.43282692641293,null,null,3583.8107380000001,null,{"$f":" -0.6251*I6085^3 + 145.21*I6085^2 - 8340.3*I6085 + 170112","v":123629.28960000002},15.130270057363095,16341.980563636567,365.86122079011244,14787.053222400002,303.90488704267557,-61.956333747436872,null,null,null,null,null,null,null,null,null,3030.7559113793013,0,0,0,0,8.2595010555437511]
[3168.2888588421783,0,0,0,2913.9238834366934,6082.2127422788717,6804.9293729999999,"2013-10-11T07:00:00",71,67,"ON",61439.724142350009,67156.526102674005,3447.451,"OFF",-16.035333853550007,-106.03045256292,-8.8484060000000007,"OFF",5.7116615638499658E-2,-67.318643199481997,-1.7696810000000001,"OFF",-8.4039995181099911,-166.99199929652002,-3.41954,"ON",60081.120271845022,56952.73390040001,3371.5160000000001,null,3077.3260549847064,0,0,0,2907.392245113931,5984.718300098637,3292.6613702514378,0,0,0,3221.8713901876527,6514.5327604390905,370.12494501529363,0,0,0,464.12375488606904,154.78962974856222,0,0,0,149.64460981234743,796.81086532667655,266.99640498622352,null,null,6804.9293729999999,null,86224.143900000025,13.79440366074769,12501.322423288642,224.06631978370484,11270.969526600002,186.62848520901872,-37.437834574686121,null,null,null,null,null,null,null,null,null,5984.718300098637,90.962803857471954,0,0,0,6.5316383227623191]
[3492.2697104994195,0,0,0,3338.2971672085068,6830.5668777079263,7195.9372319999993,"2013-10-11T23:00:00",79,73,"ON",62961.361119134992,95621.816281120016,3533.2139999999999,"OFF",-17.468521378200016,-106.45732134840001,-8.8484060000000007,"OFF",-0.68325045475000445,-41.226148322422006,-1.7696810000000001,"OFF",-8.7954292137599932,-164.86976682846,-1.7696810000000001,"ON",64399.712790439982,83812.902799600008,3675.1109999999999,null,3396.5877275045509,0,0,0,3327.9286109421537,6724.516338446705,3417.8249802081664,0,0,0,3420.3206891941486,6838.1456694023145,136.62627249544903,0,0,0,347.18238905784619,115.38901979183356,0,0,0,254.79031080585128,441.2163527100268,327.58702175441641,null,null,7195.9372319999993,null,109285.23110000021,14.945562234561725,14624.438931748889,297.78299400761932,13438.71172340002,255.1906851643509,-42.592308843268427,null,null,null,null,null,null,null,null,null,6724.516338446705,95.681982994868576,0,0,0,10.368556266353153]
[3305.3674138449987,0,3240.0875832414026,0,3093.3349187135573,9638.7899157999582,10458.054913,"2013-10-12T07:00:00",76,73,"ON",59629.776120000002,69671.827561737999,3448.0740000000001,"OFF",-18.982742118434967,-108.80854862716001,-8.8484060000000007,"ON",61585.466458100018,68233.186712996016,3448.127,"OFF",-8.3825242436599918,-158.64239131086001,-1.7696810000000001,"ON",59093.192204799998,60271.586572086002,3572.4720000000002,null,3217.6800908380137,0,3228.5611813619666,0,3087.5414920408525,9533.7827642408338,3399.7572845408617,0,3436.8645607607164,0,3355.1233710757078,10191.745216377287,230.39390916198636,0,219.56581863803331,0,484.93050795914769,48.316715459138322,0,11.262439239283594,0,217.34862892429237,897.39107032712809,239.42861819067508,null,null,10458.054913,null,100578.26240000024,14.648770046241355,13731.973685505023,265.38988966323507,12620.256665600022,227.89072423119586,-37.499165432039206,null,null,null,null,null,null,null,null,null,9533.7827642408338,87.687323006985025,0,11.52640187943598,0,5.7934266727047543]
[2971.6515054648439,0,0,0,0,2971.6515054648439,3035.0002069999991,"2013-10-13T04:00:00",71,68,"ON",56869.50781024999,60103.582183122002,3051.9319999999998,"OFF",-15.805348931610029,-105.32959208800001,-8.8484060000000007,"OFF",0,-33.398399859304,-1.7696810000000001,"OFF",-10.747222942500022,-158.64239131086001,-2.3319230000000002,"OFF",-2.8657358363200114,-166.99199929652002,-3.9817830000000001,null,2891.0741612118818,0,0,0,0,2891.0741612118818,3141.8276155520612,0,0,0,0,3141.8276155520612,160.85783878811799,0,0,0,0,-89.895615552061372,0,0,0,0,125.17316244186884,-125.58029189831052,null,null,3035.0002069999991,null,86224.143900000025,13.855250538027352,12446.421472256716,222.31316155526787,11270.969526600002,186.62848520901872,-35.684676346249148,null,null,null,null,null,null,null,null,null,2891.0741612118818,80.577344252962121,0,0,0,0]
[0,2977.7403809819798,0,2152.5386187728882,0,5130.278999754868,4798.5514069999999,"2013-10-13T20:00:00",74,69,"OFF",27.990934491999873,1771.7869910154002,1.6429720000000001,"ON",49778.244283494991,63084.813889246005,2975.9580000000001,"OFF",3.8604552450000065,-33.398399859304,-1.7696810000000001,"ON",30404.63824737502,62950.898044782007,1828.914,"OFF",-0.31147641370998741,-166.22665131624001,-6.1938839999999997,null,0,2980.5550012942144,0,2157.1529390528863,0,5137.7079403471007,0,3156.1591720547781,0,2223.0179265048669,0,5379.1770985596449,0,-4.5970012942143512,0,-328.23893905288628,0,0,-180.201172054778,0,-394.10392650486688,0,-374.0617728755899,-615.53093108813414,null,null,4798.5514069999999,null,94794.23760000011,14.208223980931816,13343.57309220617,251.92920686982214,12076.55833440001,210.7033743413329,-41.225832528489235,null,null,null,null,null,null,null,null,null,5137.7079403471007,0,-2.8146203122346378,0,-4.6143202799980827,0]
[0,3333.4529725165144,0,3540.3525145456024,0,6873.8054870621163,7385.7244769999998,"2013-10-14T11:00:00",72,71,"OFF",-5.4284225092200069,-75.14639166260001,1.6061300000000001,"ON",54483.159919409984,68149.360976862008,3505.7689999999998,"OFF",-0.23823941587499686,-41.226148322422006,-1.7696810000000001,"ON",58270.178608044997,63250.115257152007,3884.9580000000001,"OFF",-5.4592779723249922,-166.99199929652002,-4.8389720000000001,null,0,3333.248728300764,0,3532.7151246953899,0,6865.9638529961539,0,3502.5402823778354,0,3771.5984549983309,0,7274.1387373761663,0,172.52027169923576,0,352.24287530461015,0,0,3.2287176221643676,0,113.35954500166918,0,491.87694394642256,83.702059566410156,null,null,7385.7244769999998,null,89061.715200000035,14.134514728277894,12602.019512112538,227.30194660309135,11537.701228800002,194.41574354566797,-32.886203057423387,null,null,null,null,null,null,null,null,null,6865.9638529961539,0,0.20424421575035012,0,7.6373898502124575,0]
[0,3214.0695468540266,0,3441.176653505398,2957.07967249174,9612.3258728511646,10815.219079999999,"2013-10-15T03:00:00",73,70,"OFF",-10.008604254824998,-73.754793005267999,1.716761,"ON",53148.999148765004,67920.582728680005,3472.377,"OFF",0.30966556725000138,-67.318643199481997,-1.7696810000000001,"ON",57132.768885860001,63992.323131342004,3798.9589999999998,"ON",58490.711275789996,61396.05937388201,3543.9360000000001,null,0,3214.7868610605601,0,3434.4486703264247,2951.7816467520779,9601.0171781390636,0,3377.0176035530126,0,3656.180395282377,3200.2984606776567,10233.496459513046,0,257.59013893943984,0,364.51032967357514,592.15435324792224,0,95.359396446987375,0,142.77860471762278,343.6375393223434,1177.2565613072845,544.77727993330086,null,null,10815.219079999999,null,91919.663300000131,14.17108598811696,12972.846735540037,239.4412831024791,11806.348350200013,202.44302254882635,-36.998260553652756,null,null,null,null,null,null,null,null,null,9601.0171781390636,0,-0.71731420653350142,0,6.727983178973318,5.29802573966208]
[0,0,0,0,2081.2336611749556,2081.2336611749556,2363.5165260000003,"2013-10-15T19:00:00",56,54,"OFF",-17.291691552640003,-75.981360482000014,1.8236270000000001,"OFF",-11.601320087279982,-103.24730337326001,-8.8484060000000007,"OFF",0.39305785335000154,-33.398399859304,-3.5670139999999999,"OFF",-0.58743219892499299,-166.99199929652002,-1.7696810000000001,"ON",48097.214862155,72175.755478190011,2375.8780000000002,null,0,0,0,0,2082.535816175402,2082.535816175402,0,0,0,0,2182.2634746841059,2182.2634746841059,0,0,0,0,293.34218382459812,0,0,0,0,193.6145253158943,281.81297626455523,182.08531775585141,null,null,2363.5165260000003,null,48656.198400000052,11.722825422133701,8301.104323900101,112.22666623522937,7739.5826496000045,100.69745867518647,-11.529207560042906,null,null,null,null,null,null,null,null,null,2082.535816175402,0,0,0,0,-1.3021550004464189]
[0,0,0,0,2012.4454938425965,2012.4454938425965,2153.7154183000002,"2013-10-16T10:00:00",58,53,"OFF",-23.560088823600008,-74.450103063060013,0.99042830000000004,"OFF",-12.63281248736002,-107.85406938116002,-8.8484060000000007,"OFF",5.3929730625001213E-2,-67.318643199481997,-1.7696810000000001,"OFF",-2.4158243151899912,-166.99199929652002,-2.3319230000000002,"ON",45766.240072109984,71751.541588764012,2165.6750000000002,null,0,0,0,0,2014.8422387938995,2014.8422387938995,0,0,0,0,2107.1284074069399,2107.1284074069399,0,0,0,0,150.83276120610071,0,0,0,0,58.546592593060268,132.83360906355108,40.547440450510621,null,null,2153.7154183000002,null,52896.528800000029,11.806517589609925,8960.5640949623448,126.79738739190829,8138.1737072000033,108.79823524935864,-17.999152142549647,null,null,null,null,null,null,null,null,null,2014.8422387938995,0,0,0,0,-2.3967449513029351]
[0,0,0,0,1888.1859313820908,1888.1859313820908,2446.8192319999998,"2013-10-17T02:00:00",52,48,"OFF",7318.7460516949986,11837.355358884,428.28,"OFF",-12.506806732770006,-110.34445812982001,-8.8484060000000007,"OFF",0.15881456612499975,-41.226148322422006,-1.7696810000000001,"OFF",-3.884231572269992,-160.76462377892,-1.7696810000000001,"ON",41379.178142170022,60876.349434852011,2030.9269999999999,null,0,0,0,0,1892.2906747304316,1892.2906747304316,0,0,0,0,2016.1371891915851,2016.1371891915851,0,0,0,0,138.63632526956826,0,0,0,0,14.789810808414813,131.59869069457102,7.7521762334175861,null,null,2446.8192319999998,null,41170.179200000071,11.102570159705023,7416.3330846438703,94.426555420650587,7035.8968448000069,87.388920845653359,-7.0376345749972273,null,null,null,null,null,null,null,null,null,1892.2906747304316,0,0,0,0,-4.1047433483408895]
[2224.5998323603581,0,0,0,2115.1574245432384,4339.7572569035965,4843.0771299999997,"2013-10-17T13:00:00",68,55,"ON",50176.227474120002,68560.541011038018,2459.5349999999999,"OFF",-14.117802362730007,-107.15826203166,-8.8484060000000007,"OFF",-0.38553583401000396,-41.226148322422006,-1.7696810000000001,"OFF",-4.3339211842499861,-166.99199929652002,-3.9817830000000001,"ON",49223.366510599997,65016.711966486007,2398.1419999999998,null,2159.9239319802828,0,0,0,2115.8838599668939,4275.8077919471762,2290.4125617169634,0,0,0,2262.0070182480144,4552.4195799649779,299.6110680197171,0,0,0,282.25814003310597,169.12243828303644,0,0,0,136.13498175198538,532.50200770458764,255.89021968678645,null,null,4843.0771299999997,null,77871.196800000151,12.779516387713828,12186.876942364608,214.12956109867284,10485.792499200013,164.76236075043747,-49.367200348235372,null,null,null,null,null,null,null,null,null,4275.8077919471762,64.675900380075291,0,0,0,-0.7264354236554027]
[0,0,0,0,2100.9047758579709,2100.9047758579709,2263.2934700000001,"2013-10-18T07:00:00",56,53,"OFF",-9.5324633204400016,-74.450592333934011,1.58534,"OFF",-15.302165437125014,-110.63721857082001,-8.8484060000000007,"OFF",-0.2474560712500016,-33.398399859304,-1.7696810000000001,"OFF",-5.8856744509499928,-164.86976682846,-3.9817830000000001,"ON",48752.047971364998,71523.348861464008,2276.308,null,0,0,0,0,2101.875891562534,2101.875891562534,0,0,0,0,2207.704726620218,2207.704726620218,0,0,0,0,174.43210843746601,0,0,0,0,68.603273379781967,161.98009730834121,56.151262250657155,null,null,2263.2934700000001,null,48656.198400000052,11.661978544854041,8344.4156946198564,113.14946980431128,7739.5826496000045,100.69745867518647,-12.452011129124813,null,null,null,null,null,null,null,null,null,2101.875891562534,0,0,0,0,-0.97111570456308982]
[0,0,0,0,2180.3050717712445,2180.3050717712445,2385.7925499999997,"2013-10-18T23:00:00",52,49,"OFF",-10.771637810400009,-72.685487499724019,1.53142,"OFF",-15.30651094127998,-110.35817375596001,-8.8484060000000007,"OFF",0.46407675037500146,-33.398399859304,-1.7696810000000001,"OFF",-8.8669294388400122,-164.86976682846,-3.9817830000000001,"ON",51345.338331015024,72191.652771178007,2398.8609999999999,null,0,0,0,0,2179.8631863604232,2179.8631863604232,0,0,0,0,2293.377588618544,2293.377588618544,0,0,0,0,218.99781363957663,0,0,0,0,105.48341138145588,212.72555424442606,99.211151986305296,null,null,2385.7925499999997,null,41170.179200000071,11.163417036984683,7375.9099142497716,93.661180240803944,7035.8968448000069,87.388920845653359,-6.2722593951505843,null,null,null,null,null,null,null,null,null,2179.8631863604232,0,0,0,0,0.44188541082121446]
[0,0,0,0,2098.7669985120906,2098.7669985120906,2312.8799770000001,"2013-10-19T14:00:00",64,50,"OFF",-10.749990286259996,-74.450592333934011,1.7526040000000001,"OFF",-13.062823419044994,-106.72625991242001,-8.8484060000000007,"OFF",-0.47527258587500193,-75.14639166260001,-1.7696810000000001,"OFF",-5.5091588722799898,-158.64239131086001,-3.41954,"ON",48681.128173524994,71941.130042022007,2325.165,null,0,0,0,0,2099.7744665628543,2099.7744665628543,0,0,0,0,2203.131419097037,2203.131419097037,0,0,0,0,225.39053343714568,0,0,0,0,122.03358090296297,182.799485600531,79.44253306634829,null,null,2312.8799770000001,null,67246.745600000082,12.113129083348678,11103.117144593278,181.82138921799833,9487.0940864000077,139.23034138138365,-42.591047836614678,null,null,null,null,null,null,null,null,null,2099.7744665628543,0,0,0,0,-1.0074680507636913]
[2084.1124256333346,0,0,0,2050.3857194028146,4134.4981450361493,4348.3809899999997,"2013-10-20T05:00:00",44,42,"ON",46446.523135550007,76995.250045438006,2217.0549999999998,"OFF",-14.358651728480011,-105.07083998316001,-8.8484060000000007,"OFF",-0.2175224357499948,-41.226148322422006,-1.7696810000000001,"OFF",-4.9104071405900118,-158.64239131086001,-2.3319230000000002,"ON",47059.948340174989,71759.121276894002,2144.2759999999998,null,2026.6280486067542,0,0,0,2052.1910861813835,4078.8191347881375,2099.1829732796623,0,0,0,2149.6926740859644,4248.8756473656267,190.42695139324564,0,0,0,92.084913818616315,117.87202672033754,0,0,0,-5.416674085964587,284.2359209558652,114.17940837837618,null,null,4348.3809899999997,null,31016.841600000043,10.391394705397946,5969.7167664871658,69.64002338825982,6081.4831104000041,71.364079132263043,1.7240557440032234,null,null,null,null,null,null,null,null,null,4078.8191347881375,57.484377026580432,0,0,0,-1.8053667785688958]
[2121.4576465227451,0,0,0,2046.4633324366368,4167.9209789593824,4322.6821299999992,"2013-10-20T06:00:00",46,43,"ON",47456.642344860004,76859.280867470006,2231.8890000000001,"OFF",-13.735091676919998,-107.8489360474,-8.8484060000000007,"OFF",-4.6891344500005545E-2,-33.398399859304,-1.7696810000000001,"OFF",-5.0401283382799962,-158.64239131086001,-3.9817830000000001,"ON",46927.131223549979,71707.202418412009,2105.393,null,2062.0657847451243,0,0,0,2048.3312631457825,4110.3970478909068,2138.4194063924301,0,0,0,2145.536904558583,4283.9563109510127,169.82321525487578,0,0,0,57.061736854217543,93.469593607570005,0,0,0,-40.143904558583017,226.93792749048964,53.37866443038331,null,null,4322.6821299999992,null,32877.826400000049,10.515676489848337,6253.1072407447627,74.073728210245861,6256.415681600005,74.126703591642183,5.2975381396322518E-2,null,null,null,null,null,null,null,null,null,4110.3970478909068,59.391861777620761,0,0,0,-1.8679307091456394]
[2213.6227570952346,0,0,0,0,2213.6227570952346,2413.0694489999992,"2013-10-20T21:00:00",60,52,"ON",49891.482563649981,69299.789197482009,2429.4389999999999,"OFF",-15.112159398480001,-105.49265564322,-8.8484060000000007,"OFF",0.64926477000000127,-75.14639166260001,-1.7696810000000001,"OFF",-3.3795230976500017,-158.64239131086001,-1.7696810000000001,"OFF",-0.44545754519001296,-130.33983583344002,-3.9817830000000001,null,2149.5103003258205,0,0,0,0,2149.5103003258205,2274.0941739173136,0,0,0,0,2274.0941739173136,279.92869967417937,0,0,0,0,155.34482608268627,0,0,0,0,254.57119511183646,129.98732152034336,null,null,2413.0694489999992,null,57428.400000000081,11.900147432871835,9651.7123546495459,143.2631057624252,8564.1696000000084,117.9056012000823,-25.357504562342896,null,null,null,null,null,null,null,null,null,2149.5103003258205,64.112456769414166,0,0,0,0]
[2818.8630364174655,0,0,0,0,2818.8630364174655,3017.0622949999997,"2013-10-21T12:00:00",72,63,"ON",57515.905701674972,58911.573959046007,3035.3490000000002,"OFF",-15.345476054479995,-108.81368196092001,-8.8484060000000007,"OFF",-3.0878125424999868E-2,-41.226148322422006,-1.7696810000000001,"OFF",-3.4891919225100252,-160.76462377892,-2.3319230000000002,"OFF",-4.0845481101600001,-166.99199929652002,-5.3366949999999997,null,2737.6002428460747,0,0,0,0,2737.6002428460747,3004.8997585697334,0,0,0,0,3004.8997585697334,297.74875715392545,0,0,0,0,30.449241430266738,0,0,0,0,250.10329458051038,-17.196221143148335,null,null,3017.0622949999997,null,89061.715200000035,13.647739710040611,13051.49674483864,242.06120611908304,11537.701228800002,194.41574354566797,-47.645462573415074,null,null,null,null,null,null,null,null,null,2737.6002428460747,81.26279357139083,0,0,0,0]
[2011.0815695435499,0,0,0,0,2011.0815695435499,2101.2234009999997,"2013-10-22T03:00:00",48,46,"ON",44429.076498600014,71680.78179121601,2120.1,"OFF",-15.089598795104996,-109.23549762098,-8.8484060000000007,"OFF",-2.6796065624999945E-2,-33.398399859304,-1.7696810000000001,"OFF",-4.9161627048600041,-164.86976682846,-3.41954,"OFF",-6.1030612936299971,-120.37338813006001,-4.8389720000000001,null,1957.3182379155649,0,0,0,0,1957.3182379155649,2045.190377667539,0,0,0,0,2045.190377667539,162.78176208443506,0,0,0,0,74.909622332460913,0,0,0,0,161.81192493207462,73.939785180100472,null,null,2101.2234009999997,null,35210.380800000043,10.777726299749748,6533.9163049292883,78.669839718170635,6475.6757952000044,77.700002565810195,-0.96983715236044077,null,null,null,null,null,null,null,null,null,1957.3182379155649,53.763331627985053,0,0,0,0]
[2557.9834657875413,0,0,0,0,2557.9834657875413,2912.6304489999993,"2013-10-22T18:00:00",72,56,"ON",57489.344165045004,60650.731395266012,2929,"OFF",-15.26101710724498,-104.37503263366001,-8.8484060000000007,"OFF",1.869095549999971E-2,-41.226148322422006,-1.7696810000000001,"OFF",-4.524326501029968,-158.64239131086001,-1.7696810000000001,"OFF",-7.4010685944000203,-118.98177343106001,-3.9817830000000001,null,2477.8541456961993,0,0,0,0,2477.8541456961993,2722.751700492584,0,0,0,0,2722.751700492584,451.14585430380066,0,0,0,0,206.24829950741605,0,0,0,0,389.22640035738243,144.32884556099782,null,null,2912.6304489999993,null,89061.715200000035,13.221811569082988,13471.938354991547,256.33519749208619,11537.701228800002,194.41574354566797,-61.91945394641823,null,null,null,null,null,null,null,null,null,2477.8541456961993,80.129320091341924,0,0,0,0]
[2237.4457013935794,0,0,2613.2822850012744,0,4850.7279863948534,4960.0679410000002,"2013-10-23T10:00:00",70,57,"ON",48863.087707720013,69512.806506854016,2385.8380000000002,"OFF",-15.791333710320011,-105.49770876864001,-8.8484060000000007,"OFF",0.12108132137499698,-41.226148322422006,-1.7696810000000001,"ON",48718.025525610006,69022.332507754007,2589.6869999999999,"OFF",-8.4323996353000261,-120.24288916088001,-4.8389720000000001,null,2175.1100685311467,0,0,2612.0911453448107,0,4787.2012138759574,2293.8043380157087,0,0,2736.9810925850998,0,5030.7854306008085,210.72793146885351,0,0,-22.404145344810786,0,92.033661984291484,0,0,-147.29409258509986,0,135.49782834236009,-108.08638838249101,null,null,4960.0679410000002,null,83410.700000000012,13.090033753978064,12744.153539657831,231.91321528623772,11006.505800000001,179.08725750455508,-52.825957781682632,null,null,null,null,null,null,null,null,null,4787.2012138759574,62.335632862432703,0,0,1.1911396564637471,0]
[0,0,0,2579.8477313303642,0,2579.8477313303642,2616.3595569999998,"2013-10-24T01:00:00",60,54,"OFF",-2.9965694937300014,-72.363194347936002,1.5853390000000001,"OFF",4.2323442179699757,-105.33464521342002,-8.8484060000000007,"OFF",1.4569008300000514E-2,-33.398399859304,-1.7696810000000001,"ON",49333.626822269995,61406.446353912012,2630.7289999999998,"OFF",-9.8282546733000036,-121.06919547956002,-5.3366949999999997,null,0,0,0,2578.3158289266516,0,2578.3158289266516,0,0,0,2757.6030219636177,0,2757.6030219636177,0,0,0,52.413171073348167,0,0,0,0,-126.87402196361791,0,29.457496744136179,-149.82969629282991,null,null,2616.3595569999998,null,{"$f":" -0.6251*I6405^3 + 145.21*I6405^2 - 8340.3*I6405 + 170112","v":57428.400000000081},12.021841187431155,9554.0107550316879,140.86127552929429,8564.1696000000084,117.9056012000823,-22.955674329211988,null,null,null,null,null,null,null,null,null,2578.3158289266516,0,0,0,1.5319024037125928,0]
[0,0,2004.5436835430721,0,0,2004.5436835430721,4462.5627139999997,"2013-10-24T17:00:00",76,61,"OFF",-8.7157378503,-75.14639166260001,1.532367,"check",-2030.7269299200148,62887.501372846011,2409.2649999999999,"ON",43143.412097179993,108747.26945540002,2058.3739999999998,"OFF",0.59184802382999591,-166.99199929652002,-1.7696810000000001,"OFF",-11.096150894080026,-116.19862424140001,-4.8389720000000001,null,0,0,2004.5651789262724,0,0,2004.5651789262724,0,0,1987.6421877939554,0,0,1987.6421877939554,0,0,53.808821073727358,0,0,0,0,70.731812206044424,0,0,-9.6784266274576112,7.2445645048594542,null,null,4462.5627139999997,null,100578.26240000024,13.91860751888543,14452.345504179331,291.37797193238083,12620.256665600022,227.89072423119586,-63.48724770118497,null,null,null,null,null,null,null,null,null,2004.5651789262724,0,0,-2.1495383200317519E-2,0,0]
[0,2222.9701510223613,2117.4405372059141,0,0,4340.4106882282758,4417.3852470000011,"2013-10-25T08:00:00",54,49,"OFF",-13.881275399700007,-73.059482947476013,1.786759,"ON",43654.725273609991,82011.904733240008,2042.9169999999999,"ON",49867.869129924991,82587.479781080008,2380.94,"OFF",-1.2489650719700016,-166.99199929652002,-3.41954,"OFF",-10.444712217729997,-119.67758078056001,-4.8389720000000001,null,0,2228.6587000492559,2114.3055455552549,0,0,4342.9642456045112,0,2277.3647481391204,2173.4433657009986,0,0,4450.8081138401194,0,-185.741700049256,266.63445444474519,0,0,0,-234.44774813912045,207.49663429900147,0,0,69.976234928782148,-37.867633306826022,null,null,4417.3852470000011,null,44737.413600000087,11.285012432616197,7928.6423239905353,104.48911245027077,7371.2168784000078,93.572592983563723,-10.916519466707044,null,null,null,null,null,null,null,null,null,4342.9642456045112,0,-5.6885490268946342,3.1349916506592308,0,0]
[0,0,2029.412271630981,0,0,2029.412271630981,2188.422086,"2013-10-25T23:00:00",58,52,"OFF",-19.281918535719992,-73.754793005267999,1.8058149999999999,"OFF",-10.118035925550009,-103.40523359472,-8.8484060000000007,"ON",47583.460900249993,77304.509341976009,2202.866,"OFF",-2.8643536611200049,-158.64239131086001,-3.41954,"OFF",-10.431084859300016,-118.98177343106001,-3.9817830000000001,null,0,0,2027.4618182945974,0,0,2027.4618182945974,0,0,2102.4376596751567,0,0,2102.4376596751567,0,0,175.40418170540261,0,0,0,0,100.42834032484325,0,0,156.3374639213387,81.361622540779337,null,null,2188.422086,null,52896.528800000029,11.745670712330265,9006.9830996489254,127.86495303342255,8138.1737072000033,108.79823524935864,-19.066717784063911,null,null,null,null,null,null,null,null,null,2027.4618182945974,0,0,1.950453336383589,0,0]
[0,0,2871.5742524415514,0,0,2871.5742524415514,3099.1011830000007,"2013-10-26T17:00:00",76,67,"OFF",-23.151282783750013,-74.450592333934011,1.695919,"OFF",-14.366075525230022,-108.27692774964001,-8.8484060000000007,"ON",58542.858708479987,64943.008522860007,3113.4430000000002,"OFF",-4.9374422713699992,-160.79935399013999,-2.3411409999999999,"OFF",-10.183457501909993,-118.23375045222002,-4.8481889999999996,null,0,0,2862.6382036548325,0,0,2862.6382036548325,0,0,3078.3524806220462,0,0,3078.3524806220462,0,0,250.80479634516769,0,0,0,0,35.090519377954024,0,0,200.80965943039683,-14.904617536816829,null,null,3099.1011830000007,null,{"$f":" -0.6251*I6469^3 + 145.21*I6469^2 - 8340.3*I6469 + 170112","v":100578.26240000024},14.283688782563392,14082.953490666881,277.88586114596671,12620.256665600022,227.89072423119586,-49.995136914770853,null,null,null,null,null,null,null,null,null,2862.6382036548325,0,0,8.9360487867188567,0,0]
[0,0,2103.8465616634448,2538.6444516685906,0,4642.4910133320354,4905.8668379999999,"2013-10-27T05:00:00",61,59,"OFF",-25.161576839369989,-73.058993676602014,1.897216,"OFF",-16.252426568000001,-102.01875222948001,-8.8484060000000007,"ON",46866.296109920004,80002.733941244005,2319.886,"ON",45581.176759274997,75936.684436620009,2597.7710000000002,"OFF",-10.921075423160017,-118.41478067560001,-4.8389720000000001,null,0,0,2102.2610145624758,2539.0259736328348,0,4641.2869881953102,0,0,2164.5178779411885,2616.2814705522869,0,4780.7993484934759,0,0,217.62498543752417,58.745026367165337,0,0,0,155.36812205881142,-18.510470552286733,0,256.26514354283393,116.75278324466912,null,null,4905.8668379999999,null,59794.286900000065,12.406720948191431,9639.0153610598427,142.94958992735695,8786.5629686000066,122.84472166550138,-20.104868261855572,null,null,null,null,null,null,null,null,null,4641.2869881953102,0,0,1.5855471009690518,-0.38152196424425711,0]
[0,0,0,2642.3088054571699,0,2642.3088054571699,2602.2277050000002,"2013-10-27T20:00:00",63,59,"OFF",-28.417986769860015,-73.058993676602014,1.699676,"OFF",-16.743531603749997,-107.15754015660001,-8.8484060000000007,"OFF",0.3102159901250014,-33.398399859304,-1.7696810000000001,"ON",48031.422875019976,59182.758356586004,2617.34,"OFF",-10.567358443599986,-119.72947557654001,-6.1938839999999997,null,0,0,0,2641.4880574875715,0,2641.4880574875715,0,0,0,2829.3828347447211,0,2829.3828347447211,0,0,0,-24.14805748757135,0,0,0,0,-212.04283474472095,0,-50.2526780304905,-238.1474552876401,null,null,2602.2277050000002,null,64707.210300000093,12.574186496440891,10292.071032716971,159.61020946238946,9248.3777682000091,133.50558891947031,-26.10462054291915,null,null,null,null,null,null,null,null,null,2641.4880574875715,0,0,0,0.82074796959841478,0]
[0,0,0,3001.3330961010438,0,3001.3330961010438,3008.0763510000002,"2013-10-28T12:00:00",71,66,"OFF",-31.239956952990006,-73.058993676602014,1.7159150000000001,"OFF",-16.078389226259993,-109.2405507464,-8.8484060000000007,"OFF",-0.27835159632999684,-33.398399859304,-1.7696810000000001,"ON",51262.301928959983,58596.058411988008,3022.306,"OFF",-11.269087608399973,-118.28596608156001,-5.327477,null,0,0,0,2998.6933418233448,0,2998.6933418233448,0,0,0,3221.0176857523552,0,3221.0176857523552,0,0,0,23.612658176655259,0,0,0,0,-198.71168575235515,0,-15.601688447329138,-237.92603237633955,null,null,3008.0763510000002,null,86224.143900000025,13.73355678346803,12556.709854477553,225.84283183300312,11270.969526600002,186.62848520901872,-39.214346623984397,null,null,null,null,null,null,null,null,null,2998.6933418233448,0,0,0,2.6397542776990122,0]
[0,0,0,3239.9050376460523,2587.4791263598054,5827.3841640058581,6006.8454949999996,"2013-10-29T03:00:00",71,68,"OFF",-30.909560383455027,-75.14639166260001,1.8065819999999999,"OFF",-18.729658953750018,-103.93508988876,-8.8484060000000007,"OFF",0.12285242721000283,-75.14639166260001,-1.7696810000000001,"ON",54673.657138099996,69452.562022680009,3271.5309999999999,"ON",51152.018688275006,70680.335145562014,2744.1260000000002,null,0,0,0,3235.0110294092674,2587.1690845784765,5822.1801139877443,0,0,0,3392.5386213974853,2711.4774612041047,6104.0160826015899,0,0,0,36.519970590732555,156.95691542152372,0,0,0,-121.00762139748531,32.648538795895547,157.79220966600712,-124.04375894783891,null,null,6006.8454949999996,null,86224.143900000025,13.855250538027352,12446.421472256716,222.31316155526787,11270.969526600002,186.62848520901872,-35.684676346249148,null,null,null,null,null,null,null,null,null,5822.1801139877443,0,0,0,4.8940082367848845,0.31004178132889137]
[0,0,0,3435.7545736696811,2888.7838512676781,6324.5384249373592,6979.1976240000004,"2013-10-29T19:00:00",74,70,"OFF",-31.745742748279998,-75.145790100050007,1.749711,"OFF",-19.518233677624998,-108.53928922978001,-8.8484060000000007,"OFF",0.25910710440499757,-41.400104170214007,-1.7696810000000001,"ON",57035.225944609992,69655.208393690002,3713.7,"ON",56893.628345320001,70450.827001486003,3274.366,null,0,0,0,3429.1022247080505,2884.6885049905109,6313.7907296985613,0,0,0,3599.7495296443062,3040.8359762099749,6640.5855058542811,0,0,0,284.59777529194935,389.67749500948912,0,0,0,113.9504703556936,233.5300237900251,634.98898288212592,308.19420672640615,null,null,6979.1976240000004,null,94794.23760000011,14.269070858211474,13286.672768248049,249.98966176064545,12076.55833440001,210.7033743413329,-39.286287419312544,null,null,null,null,null,null,null,null,null,6313.7907296985613,0,0,0,6.6523489616306506,4.0953462771672093]
[0,0,0,3419.4256708701437,2921.6589275242172,6341.0845983943609,6809.7162840000001,"2013-10-30T10:00:00",72,69,"OFF",-32.861917167724975,-72.363194347936002,1.5853710000000001,"OFF",-18.05907093126001,-109.23509657928,-8.8484060000000007,"OFF",2.2416555226499608E-2,-67.144695372523998,-1.7696810000000001,"ON",57369.438396420002,69261.978986006012,3552.5940000000001,"ON",58513.08534655501,70360.111368946003,3266.1550000000002,null,0,0,0,3412.5199417359504,2916.3510120892925,6328.8709538252424,0,0,0,3588.1719249311705,3082.0018879442418,6670.1738128754123,0,0,0,140.07405826404965,349.80398791070775,0,0,0,-35.577924931170401,184.15311205575836,453.44579437284631,112.14293532267683,null,null,6809.7162840000001,null,89061.715200000035,14.012820973718572,12711.461220697491,230.84799534757909,11537.701228800002,194.41574354566797,-36.432251801911121,null,null,null,null,null,null,null,null,null,6328.8709538252424,0,0,0,6.9057291341932796,5.3079154349247801]
[0,0,0,0,2628.1805031338299,2628.1805031338299,2859.0561400000001,"2013-10-31T01:00:00",68,67,"OFF",-34.234270433549973,-75.14639166260001,1.6295500000000001,"OFF",-18.335735720830034,-109.23509657928,-8.8484060000000007,"OFF",7.6637602000002789E-2,-33.398399859304,-1.7696810000000001,"OFF",-1.5686436359299942,-158.64239131086001,-3.410323,"ON",53019.07394662498,63776.827384264005,2871.4549999999999,null,0,0,0,0,2626.734406317431,2626.734406317431,0,0,0,0,2809.7561457684806,2809.7561457684806,0,0,0,0,244.72059368256896,0,0,0,0,61.698854231519363,215.34748138790786,32.325741936858265,null,null,2859.0561400000001,null,77871.196800000151,13.509678915069752,11528.208374091928,194.13547304509856,10485.792499200013,164.76236075043747,-29.373112294661098,null,null,null,null,null,null,null,null,null,2626.734406317431,0,0,0,0,1.4460968163989492]
[2227.7058076464505,0,0,0,2200.5007410103694,4428.2065486568199,4876.726772,"2013-10-31T22:00:00",54,49,"ON",50256.60057639001,79865.818304864006,2382.7350000000001,"OFF",-17.220136515444999,-108.5447433969,-8.8484060000000007,"OFF",-0.31153112131000038,-33.398399859304,-1.7696810000000001,"OFF",-4.2122630957399965,-164.83503661724001,-2.3411409999999999,"ON",51992.735029550007,72187.104958300013,2506.951,null,2162.8704343716972,0,0,0,2199.6805980587496,4362.5510324304469,2234.5904526223517,0,0,0,2316.0996023560629,4550.690054978415,219.8645656283029,0,0,0,307.27040194125038,148.14454737764845,0,0,0,190.85139764393716,516.2184481028462,328.07942555487858,null,null,4876.726772,null,44737.413600000087,11.285012432616197,7928.6423239905353,104.48911245027077,7371.2168784000078,93.572592983563723,-10.916519466707044,null,null,null,null,null,null,null,null,null,4362.5510324304469,64.835373274753238,0,0,0,0.82014295161980044]
[2011.7115626683656,0,0,0,0,2011.7115626683656,2216.8565830000002,"2013-11-01T07:00:00",50,48,"ON",48792.191918894998,75619.829410284001,2234.6640000000002,"OFF",-17.567304243089996,-105.4952223101,-8.8484060000000007,"OFF",-0.41621338250000356,-33.398399859304,-1.7696810000000001,"OFF",-4.7927542566400003,-158.64239131086001,-2.3411409999999999,"OFF",1.4377924464400154,-118.98177343106001,-4.8481889999999996,null,1982.4772281280764,0,0,0,0,1982.4772281280764,2067.5953631719963,0,0,0,0,2067.5953631719963,252.18677187192384,0,0,0,0,167.06863682800395,0,0,0,0,249.15421984179125,164.03608479787135,null,null,2216.8565830000002,null,37984.500000000058,10.993980737412199,6910.0539481099695,85.142522324211427,6736.4430000000057,82.109970294078821,-3.0325520301326065,null,null,null,null,null,null,null,null,null,1982.4772281280764,29.234334540289183,0,0,0,0]
[2191.7600787367141,0,0,0,0,2191.7600787367141,2710.039295,"2013-11-01T22:00:00",63,53,"ON",53843.600867374989,67981.982212949995,2728.326,"OFF",-16.282637802,-106.02788589604002,-8.8484060000000007,"OFF",7.7688697199999922E-4,-33.398399859304,-1.7696810000000001,"OFF",-5.0635008148900011,-160.79935399013999,-2.3411409999999999,"OFF",-4.253391490529979,-119.67758078056001,-5.327477,null,2156.0837220197755,0,0,0,0,2156.0837220197755,2308.289242554732,0,0,0,0,2308.289242554732,572.24227798022457,0,0,0,0,420.03675744526799,0,0,0,0,537.90772292137103,385.70220238641446,null,null,2710.039295,null,64707.210300000093,12.209105232762928,10599.828417623821,167.84014397832385,9248.3777682000091,133.50558891947031,-34.334555058853539,null,null,null,null,null,null,null,null,null,2156.0837220197755,35.676356716938699,0,0,0,0]
[2254.3729603423253,0,0,0,0,2254.3729603423253,2736.5947549999996,"2013-11-02T14:00:00",67,50,"ON",55520.094143460003,67425.953937568018,2754.31,"OFF",-16.904506928100002,-105.75614004012002,-8.8484060000000007,"OFF",-4.6159222874998483E-2,-67.144695372523998,-1.7696810000000001,"OFF",-9.3069359961200053,-164.83503661724001,-1.7696810000000001,"OFF",-7.6583207206800141,-120.50212251576001,-5.327477,null,2216.4053344435433,0,0,0,0,2216.4053344435433,2382.6305118497858,0,0,0,0,2382.6305118497858,537.90466555645662,0,0,0,0,371.67948815021418,0,0,0,0,483.27035408658207,317.04517668033964,null,null,2736.5947549999996,null,75152.638700000127,12.382615215046375,12138.411376730915,212.62051936096066,10230.248037800013,157.98620789108611,-54.634311469874547,null,null,null,null,null,null,null,null,null,2216.4053344435433,37.967625898781989,0,0,0,0]
[1889.9281948023579,0,0,0,0,1889.9281948023579,2148.9024489999993,"2013-11-03T05:00:00",47,42,"ON",45152.417165960018,76423.051768712001,2165.2719999999999,"OFF",-17.43470898573003,-110.20272999304002,-8.8484060000000007,"OFF",1.6102795499999916E-2,-33.398399859304,-1.7696810000000001,"OFF",-8.2968602961300046,-166.99199929652002,-1.7696810000000001,"OFF",-9.6017451508300073,-120.37338813006001,-3.9817830000000001,null,1864.9122156409965,0,0,0,0,1864.9122156409965,1934.5754232610132,0,0,0,0,1934.5754232610132,300.35978435900347,0,0,0,0,230.69657673898678,0,0,0,0,298.42747435848918,228.76426673847249,null,null,2148.9024489999993,null,33987.03270000004,10.492638840604116,6478.2621829082664,77.742887565439204,6360.681073800004,75.810577564924898,-1.9323100005143061,null,null,null,null,null,null,null,null,null,1864.9122156409965,25.015979161361429,0,0,0,0]
[0,1970.6457555975937,1604.8356535221099,0,0,3575.4814091197036,4013.9032540000003,"2013-11-03T21:00:00",61,52,"OFF",-1.9536718460249998,-75.14639166260001,1.329412,"ON",40363.239559455003,83618.397575100011,2133.29,"ON",37724.752609499992,79561.106821204012,1886.3810000000001,"OFF",-8.789790307339981,-166.99199929652002,-1.7696810000000001,"OFF",-9.6052075044800009,-118.28596608156001,-5.327477,null,0,1950.0463832874,1587.4031537173803,0,0,3537.4495370047803,0,1986.4083023447779,1627.7811789529364,0,0,3614.1894812977143,0,183.24361671259999,298.97784628261979,0,0,0,146.88169765522207,258.59982104706364,0,0,453.51046157937202,376.77051728643795,null,null,4013.9032540000003,null,59794.286900000065,11.980792807233808,9981.6911722064415,151.55572308134913,8786.5629686000066,122.84472166550138,-28.711001415847747,null,null,null,null,null,null,null,null,null,3537.4495370047803,0,20.599372310193758,17.432499804729559,0,0]
[0,0,1940.3923702467168,0,0,1940.3923702467168,2474.5439929999998,"2013-11-04T12:00:00",57,55,"OFF",-6.9084057597299964,-74.449990771384009,2.1045050000000001,"OFF",-0.85585681440000871,-107.41950059504001,-8.8484060000000007,"ON",48016.90964939999,77514.061651060008,2488.6799999999998,"OFF",-8.2012887373199987,-166.99199929652002,-3.410323,"OFF",-10.234740520549984,-117.59015873206,-3.9817830000000001,null,0,0,1912.1063843050117,0,0,1912.1063843050117,0,0,1986.1664358440851,0,0,1986.1664358440851,0,0,576.57361569498812,0,0,0,0,502.51356415591476,0,0,563.3824706459726,489.32241910689925,null,null,2474.5439929999998,null,50738.045700000075,11.854635689452406,8560.0345770463373,117.81496570909295,7935.2762958000076,104.62382066007743,-13.191145049015518,null,null,null,null,null,null,null,null,null,1912.1063843050117,0,0,28.285985941705121,0,0]
[0,0,2362.4877665085419,0,0,2362.4877665085419,2735.6307620000002,"2013-11-05T07:00:00",63,62,"OFF",-11.317985061425009,-75.842190991265994,2.2120380000000002,"OFF",-6.0907736966999968,-109.93090392878001,-8.8484060000000007,"ON",53848.135194209994,74785.68673678601,2748.8850000000002,"OFF",-8.3212604239099779,-160.79935399013999,-1.7696810000000001,"OFF",-12.424584850439988,-118.28596608156001,-4.8481889999999996,null,0,0,2326.3823867505166,0,0,2326.3823867505166,0,0,2436.3863371361904,0,0,2436.3863371361904,0,0,422.5026132494836,0,0,0,0,312.49866286380984,0,0,400.25053478755103,290.24658440187727,null,null,2735.6307620000002,null,64707.210300000093,12.756727128279872,10144.79805820308,155.75766738140285,9248.3777682000091,133.50558891947031,-22.252078461932541,null,null,null,null,null,null,null,null,null,2326.3823867505166,0,0,36.105379758025265,0,0]
[0,0,2930.2921250061377,0,2719.0733293970025,5649.3654544031397,7030.9248360000001,"2013-11-05T18:00:00",68,67,"OFF",-13.196098548375,-73.058993676602014,1.528565,"OFF",-7.5728056534900006,-112.71958749390001,-8.8484060000000007,"ON",62512.680155199989,74072.883240039999,3479.4989999999998,"OFF",-7.653208113320022,-158.64239131086001,-3.410323,"ON",59047.049345999985,71628.710536888015,3562.1559999999999,null,0,0,2880.8667067436927,0,2675.8684536585029,5556.7351604021951,0,0,3037.3507891063314,0,2830.7438310808602,5868.094620187192,0,0,598.63229325630709,0,886.28754634149709,0,0,442.14821089366842,0,731.41216891913973,1455.5467273031431,1144.1872675181471,null,null,7030.9248360000001,null,77871.196800000151,13.509678915069752,11528.208374091928,194.13547304509856,10485.792499200013,164.76236075043747,-29.373112294661098,null,null,null,null,null,null,null,null,null,5556.7351604021951,0,0,49.425418262444964,0,43.204875738499595]
[0,0,0,0,2010.3480347432589,2010.3480347432589,2358.0630960000003,"2013-11-06T09:00:00",50,48,"OFF",-16.215351875369993,-74.450592333934011,1.4009659999999999,"OFF",-10.078755516044993,-107.8489360474,-8.8484060000000007,"OFF",-4.7197231270001617E-2,-41.400104170214007,-1.7696810000000001,"OFF",-8.9338228209999766,-166.99199929652002,-3.9817830000000001,"ON",49825.850996375026,74887.655599428006,2371.2620000000002,null,0,0,0,0,1980.2427736339866,1980.2427736339866,0,0,1969.9878941091019,0,2071.4345914810478,4041.4224855901498,0,0,0,0,391.01922636601353,0,0,0,0,299.82740851895232,387.98667433588093,296.79485648881973,null,null,2358.0630960000003,null,{"$f":" -0.6251*I6725^3 + 145.21*I6725^2 - 8340.3*I6725 + 170112","v":37984.500000000058},10.993980737412199,6910.0539481099695,85.142522324211427,6736.4430000000057,82.109970294078821,-3.0325520301326065,null,null,null,null,null,null,null,null,null,1980.2427736339866,0,0,0,0,30.105261109272305]
[0,0,0,0,1824.0020331247747,1824.0020331247747,2340.3159410000003,"2013-11-07T01:00:00",43,40,"OFF",-22.824738536389997,-72.682704270325999,1.4953510000000001,"OFF",-11.44172369871999,-106.46277551552001,-8.8484060000000007,"OFF",0.14643590699999823,-67.144695372523998,-1.7696810000000001,"OFF",-8.1046895273399855,-158.64239131086001,-3.410323,"ON",42820.522522500003,74698.283708688003,2352.8490000000002,null,0,0,0,0,1801.6964698549507,1801.6964698549507,0,0,1969.9878941091019,0,1869.9114814093252,3839.8993755184274,0,0,0,0,551.15253014504947,0,0,0,0,482.93751859067493,552.70002254803364,484.4850109936591,null,null,2340.3159410000003,null,30272.564300000085,10.244330963166089,5910.1105594589499,68.733640736036079,6011.521044200008,70.281133139020227,1.5474924029841475,null,null,null,null,null,null,null,null,null,1801.6964698549507,0,0,0,0,22.305563269824006]
[0,0,0,0,1894.832605291316,1894.832605291316,2345.125618,"2013-11-07T16:00:00",63,50,"OFF",-26.892780322649983,-157.94080896088002,1.6494880000000001,"OFF",-11.781950163100021,-107.8489360474,-8.8484060000000007,"OFF",-0.12008587574999723,-41.400104170214007,-1.7696810000000001,"OFF",-5.8079945625099754,-164.83503661724001,-3.9817830000000001,"ON",45559.691471239996,64599.500265142,2358.076,null,0,0,0,0,1869.6227928275723,1869.6227928275723,0,0,1969.9878941091019,0,1994.7724416270223,3964.760335736124,0,0,0,0,488.45320717242771,0,0,0,0,363.3035583729777,449.71980325508929,324.57015445563928,null,null,2345.125618,null,64707.210300000093,12.026564600923948,10760.7138775156,172.23899283680873,9248.3777682000091,133.50558891947031,-38.733403917338421,null,null,null,null,null,null,null,null,null,1869.6227928275723,0,0,0,0,25.209812463743674]
[0,0,0,0,1843.8585565545116,1843.8585565545116,2288.5359129999997,"2013-11-08T07:00:00",42,41,"OFF",-28.87257107196001,-73.754793005267999,1.752783,"OFF",-11.732109097640006,-105.75614004012002,-8.8484060000000007,"OFF",-0.20684188974999973,-67.144695372523998,-1.7696810000000001,"OFF",-5.1246592345199975,-164.83503661724001,-3.9817830000000001,"ON",43598.64808721999,74377.787223716005,2301.3829999999998,null,0,0,0,0,1820.7468547083079,1820.7468547083079,0,0,1969.9878941091019,0,1892.6411328177353,3862.6290269268375,0,0,0,0,480.63614529169195,0,0,0,0,408.74186718226451,483.4287284778315,411.53445036840407,null,null,2288.5359129999997,null,29657.431200000021,10.28420995769026,5767.5662636239704,66.602970374775509,5953.6985328000019,69.395553560915062,2.7925831861395523,null,null,null,null,null,null,null,null,null,1820.7468547083079,0,0,0,0,23.111701846203687]
[0,0,0,0,1844.509858407059,1844.509858407059,2156.2904189999999,"2013-11-08T23:00:00",57,50,"OFF",-28.406958928849992,-166.99199929652002,1.917187,"OFF",-10.984929731040015,-106.88683700910001,-8.8484060000000007,"OFF",0.432409868375002,-33.398399859304,-1.7696810000000001,"OFF",-5.2880030704899834,-160.79935399013999,-1.7696810000000001,"ON",43624.032477209985,60923.142980408003,2166.761,null,0,0,0,0,1821.3716064310538,1821.3716064310538,0,0,1969.9878941091019,0,1955.9595801512905,3925.9474742603925,0,0,0,0,345.38939356894616,0,0,0,0,210.80141984870943,327.19232175689427,192.60434803665754,null,null,2156.2904189999999,null,50738.045700000075,11.550401303054105,8785.5035281906876,122.82089247212932,7935.2762958000076,104.62382066007743,-18.197071812051888,null,null,null,null,null,null,null,null,null,1821.3716064310538,0,0,0,0,23.138251976005222]
[0,0,0,0,2259.7905158023736,2259.7905158023736,3030.191777,"2013-11-09T14:00:00",69,59,"OFF",-31.232404254149973,-166.99199929652002,1.953991,"OFF",-10.714071120389995,-109.93635809590002,-8.8484060000000007,"OFF",-6.681546355500019E-2,-41.400104170214007,-2.193667,"OFF",-5.9478341717200269,-160.79935399013999,-2.3411409999999999,"ON",53907.113094040011,64949.393106724005,3041.6210000000001,null,0,0,0,0,2224.3116172340669,2224.3116172340669,0,0,1969.9878941091019,0,2397.9488870311566,4367.936781140259,0,0,0,0,817.30938276593315,0,0,0,0,643.67211296884352,771.63793264237449,598.00066284528486,null,null,3030.191777,null,80625.134100000141,13.116776644734284,12293.437066699922,217.46860148852684,10744.662605400013,171.79715136496822,-45.671450123558628,null,null,null,null,null,null,null,null,null,2224.3116172340669,0,0,0,0,35.478898568306704]
[0,0,0,0,1987.3241565332451,1987.3241565332451,2405.1943160000001,"2013-11-09T22:00:00",60,54,"OFF",-29.695666959069992,-74.450592333934011,2.2120700000000002,"OFF",-10.828560289680011,-112.71413332678001,-8.8484060000000007,"OFF",-0.34233960599999597,-67.144695372523998,-2.193667,"OFF",-4.4712838906399819,-160.79935399013999,-1.7696810000000001,"ON",48993.962053110023,74138.806474686004,2415.7939999999999,null,0,0,0,0,1958.209298736381,1958.209298736381,0,0,1969.9878941091019,0,2049.9624819809092,4019.9503760900111,0,0,0,0,457.58470126361885,0,0,0,0,365.83151801909071,434.62902693440685,342.87584368987871,null,null,2405.1943160000001,null,57428.400000000081,12.021841187431155,9554.0107550316879,140.86127552929429,8564.1696000000084,117.9056012000823,-22.955674329211988,null,null,null,null,null,null,null,null,null,1958.209298736381,0,0,0,0,29.114857796864044]
[1966.4408071038999,0,0,0,0,1966.4408071038999,2279.2734489999993,"2013-11-10T20:00:00",59,52,"ON",47462.133191934998,110735.47378732001,2295.643,"OFF",-10.031486592599977,-26.724127533726001,-8.8484060000000007,"OFF",-3.4583144785000276E-2,-67.144695372523998,-1.7696810000000001,"OFF",-4.7046661063499933,-164.83503661724001,-1.7696810000000001,"OFF",4.5848631871700087,-118.98177343106001,-3.9817830000000001,null,1938.7886993526356,0,0,0,0,1938.7886993526356,1914.7401619322372,0,1969.9878941091019,0,0,3884.7280560413392,356.85430064736443,0,0,0,0,380.90283806776279,0,0,0,0,334.71483061709205,358.76336803749041,null,null,2279.2734489999993,null,55127.89710000006,11.821730785993527,9326.5356990392647,135.36386322618091,8347.9223274000051,113.2243931959085,-22.139470030272406,null,null,null,null,null,null,null,null,null,1938.7886993526356,27.652107751264339,0,0,0,0]
[1814.7024422355257,0,0,0,0,1814.7024422355257,2395.3724009999996,"2013-11-11T11:00:00",64,55,"ON",42799.082671099983,64409.727332702001,2414.2489999999998,"OFF",-11.527164375420009,-110.20272999304002,-8.8484060000000007,"OFF",-0.22668053549999762,-33.398399859304,-1.7696810000000001,"OFF",-4.4073850678899955,-160.79935399013999,-3.410323,"OFF",-2.6806768329599957,-166.99199929652002,-4.8481889999999996,null,1792.228096313456,0,0,0,0,1792.228096313456,1904.6945229240637,0,1969.9878941091019,0,0,3874.6824170331656,622.02090368654376,0,0,0,0,509.55447707593612,0,0,0,0,587.06743271352696,474.60100610291931,null,null,2395.3724009999996,null,67246.745600000082,12.417363469746979,10831.082743746138,174.18381235440046,9487.0940864000077,139.23034138138365,-34.953470973016806,null,null,null,null,null,null,null,null,null,1792.228096313456,22.474345922069688,0,0,0,0]
[1880.2527251726344,0,0,0,0,1880.2527251726344,2237.0983466999996,"2013-11-12T03:00:00",62,58,"ON",42291.770526749991,75913.528288861999,2252.7249999999999,"OFF",-10.757859081989984,-109.93635809590002,-8.8484060000000007,"OFF",-0.46295248237500236,-67.144695372523998,-0.1603773,"OFF",-4.6349439269699921,-158.64239131086001,-1.7696810000000001,"OFF",-6.858980333849984,-166.99199929652002,-4.8481889999999996,null,1858.1814801261307,0,0,0,0,1858.1814801261307,1921.3896266327984,0,1969.9878941091019,0,0,3891.3775207419003,394.54351987386917,0,0,0,0,331.33537336720156,0,0,0,0,370.23920072375734,307.03105421708972,null,null,2237.0983466999996,null,62221.807200000039,12.428620327026039,10012.6652134829,152.34843478693193,9014.7498768000041,128.0441156368201,-24.304319150111837,null,null,null,null,null,null,null,null,null,1858.1814801261307,22.071245046503691,0,0,0,0]
[1733.5982339480552,0,0,0,0,1733.5982339480552,1967.222755,"2013-11-12T18:00:00",46,35,"ON",40159.801490970007,75467.537835126015,1984.9380000000001,"OFF",-10.35404558930002,-109.50692264354001,-8.8484060000000007,"OFF",-1.3790805073999757E-2,-33.398399859304,-1.7696810000000001,"OFF",-4.4599006776800003,-166.99199929652002,-1.7696810000000001,"OFF",-8.8988348661100023,-166.99199929652002,-5.327477,null,1713.8029197269263,0,0,0,0,1713.8029197269263,1771.8814141048883,0,1969.9878941091019,0,0,3741.8693082139903,271.13508027307375,0,0,0,0,213.05658589511177,0,0,0,0,266.21159585589385,208.13310147793183,null,null,1967.222755,null,32877.826400000049,10.028901471611054,6556.6156957604489,79.050188008822118,6256.415681600005,74.126703591642183,-4.9234844171799352,null,null,null,null,null,null,null,null,null,1713.8029197269263,19.79531422112882,0,0,0,0]
[1629.9521895537621,0,0,0,0,1629.9521895537621,1874.2557870000001,"2013-11-13T09:00:00",36,31,"ON",36611.223018999983,73091.774825159999,1895.6210000000001,"OFF",-10.409725969760043,-107.8489360474,-8.8484060000000007,"OFF",-0.35154455024999698,-41.400104170214007,-1.7696810000000001,"OFF",-4.3316287316399897,-166.99199929652002,-4.553242,"OFF",-11.034976366050003,-159.33819866036001,-6.1938839999999997,null,1613.4767301250911,0,0,0,0,1613.4767301250911,1668.2337246496579,0,1969.9878941091019,0,0,3638.2216187587601,282.14426987490901,0,0,0,0,227.38727535034218,0,0,0,0,280.53169524990574,225.7747007253389,null,null,1874.2557870000001,null,28888.694400000008,9.6495374525758404,5987.581175155392,69.913444261216284,5881.4372736000005,68.300869636213008,-1.6125746250032762,null,null,null,null,null,null,null,null,null,1613.4767301250911,16.475459428671002,0,0,0,0]
[1668.395881661259,0,0,0,0,1668.395881661259,1796.8635519999998,"2013-11-13T10:00:00",41,34,"ON",37952.27450891499,72573.452490412004,1819.0029999999999,"OFF",-9.6517020719549826,-104.36997950824001,-8.8484060000000007,"OFF",-0.46801168837500223,-67.144695372523998,-1.7696810000000001,"OFF",-4.2181128024000181,-158.64239131086001,-6.1938839999999997,"OFF",-10.869877310179994,-163.96004383618003,-5.327477,null,1650.7035848963578,0,0,0,0,1650.7035848963578,1711.0799359798855,0,1969.9878941091019,0,0,3681.0678300889876,168.2994151036421,0,0,0,0,107.92306402011445,0,0,0,0,167.98974485805778,107.61339377453012,null,null,1796.8635519999998,null,29175.192900000024,9.8418438846255771,5928.8062769571079,69.016952153198076,5908.3681326000024,68.707281907613748,-0.30967024558432854,null,null,null,null,null,null,null,null,null,1650.7035848963578,17.69229676490113,0,0,0,0]
[0,0,1666.0019448790515,0,0,1666.0019448790515,1914.9482648000001,"2013-11-14T11:00:00",50,41,"OFF",-2.5807415992000116,-74.450592333934011,0.74323680000000003,"OFF",0.57693646856999914,-102.54892935688001,-8.8484060000000007,"ON",39734.82821512501,79125.535430834003,1931.0170000000001,"OFF",-4.1157429358499895,-166.99199929652002,-3.9817830000000001,"OFF",-12.311851635300009,-166.99199929652002,-3.9817830000000001,null,0,0,1646.6677555105939,0,0,1646.6677555105939,0,0,1692.6654636854773,0,0,1692.6654636854773,0,0,284.34924448940615,0,0,0,0,238.35153631452272,0,0,276.29084895432243,230.29314077943897,null,null,1914.9482648000001,null,37984.500000000058,10.568052596454578,7188.5524136666936,90.168365829162568,6736.4430000000057,82.109970294078821,-8.0583955350837471,null,null,null,null,null,null,null,null,null,1646.6677555105939,0,0,19.334189368457601,0,0]
[0,0,2132.9487784466714,0,0,2132.9487784466714,2366.6773669000004,"2013-11-14T16:00:00",61,46,"OFF",-10.61936521358,-74.450592333934011,0.84210289999999999,"OFF",-15.933142773080029,-104.36452534112001,-8.8484060000000007,"ON",53260.148428159991,76663.299809514006,2381.873,"OFF",-4.3439341956500011,-158.64239131086001,-2.3411409999999999,"OFF",-11.919650890420009,-166.99199929652002,-4.8481889999999996,null,0,0,2098.0445189571628,0,0,2098.0445189571628,0,0,2193.9988681820187,0,0,2193.9988681820187,0,0,283.82848104283721,0,0,0,0,187.87413181798138,0,0,246.97486641169456,151.02051718683873,null,null,2366.6773669000004,null,59794.286900000065,11.615711543555845,10295.415253002335,159.69833629664402,8786.5629686000066,122.84472166550138,-36.853614631142634,null,null,null,null,null,null,null,null,null,2098.0445189571628,0,0,34.904259489508604,0,0]
[0,0,1934.2877213582371,2600.4678360051048,0,4534.7555573633417,5247.301175999999,"2013-11-15T07:00:00",54,52,"OFF",-13.080928668749989,-70.971595690604005,1.0964659999999999,"OFF",-18.263134585100001,-102.28801162686,-8.8484060000000007,"ON",47843.855593389999,78600.587887202011,2324.096,"ON",52861.731518124994,72452.987584566014,2937.1509999999998,"OFF",-11.718424476219996,-162.39975099816002,-6.1938839999999997,null,0,0,1906.2074466620429,2565.0409581536055,0,4471.2484048156484,0,0,1975.1887991304925,2686.8450768979537,0,4662.0338760284467,0,0,417.88855333795709,372.11004184639432,0,0,0,348.90720086950751,250.30592310204611,0,781.62337625526447,590.83790504246667,null,null,5247.301175999999,null,44737.413600000087,11.46755306445518,7802.4341110167852,101.94781191265062,7371.2168784000078,93.572592983563723,-8.3752189290868984,null,null,null,null,null,null,null,null,null,4471.2484048156484,0,0,28.080274696194238,35.426877851499285,0]
[0,0,0,2504.0283175068084,0,2504.0283175068084,2701.1749889999996,"2013-11-15T22:00:00",63,60,"OFF",-14.87399256092999,-108.68976007562,1.308859,"OFF",-18.282894907940015,-109.80914766866002,-8.8484060000000007,"OFF",-1.6808390721000249E-2,-166.99199929652002,-1.7696810000000001,"ON",46756.253846399981,54333.626807708002,2714.4659999999999,"OFF",6047.9635354500033,38012.705451164002,-3.9817830000000001,null,0,0,0,2476.1019536287945,0,2476.1019536287945,0,0,1705.9388681028674,2689.7669888890259,0,4395.7058569918936,0,0,0,238.3640463712054,0,0,0,0,24.69901111097397,0,213.56217388361443,-0.10286137661699968,null,null,2701.1749889999996,null,64707.210300000093,12.63503337372055,10242.50722353988,158.30746140706128,9248.3777682000091,133.50558891947031,-24.80187248759097,null,null,null,null,null,null,null,null,null,2476.1019536287945,0,0,0,27.926363878013944,0]
[0,0,0,0,2708.8321591467397,2708.8321591467397,3388.0410910000001,"2013-11-16T14:00:00",76,68,"OFF",-16.591999972860016,-74.450592333934011,1.072319,"OFF",-19.477706584359993,-105.33215875488001,-8.8484060000000007,"OFF",-0.23247754237499865,-41.400104170214007,-1.7696810000000001,"OFF",-0.80596836760999679,-166.99199929652002,-2.3411409999999999,"ON",57848.76452690499,61827.997326450008,3399.9279999999999,null,0,0,0,0,2667.293485102532,2667.293485102532,0,0,1705.9388681028674,0,2900.3517111780247,4606.2905792808924,0,0,0,0,732.63451489746785,0,0,0,0,499.57628882197514,684.78848072757182,451.73025465207917,null,null,3388.0410910000001,null,100578.26240000024,14.344535659843054,14023.216196752192,275.73675840109183,12620.256665600022,227.89072423119586,-47.846034169895972,null,null,null,null,null,null,null,null,null,2667.293485102532,0,0,0,0,41.53867404420771]
[2825.3582744274718,0,0,0,2683.8700781664147,5509.2283525938865,6590.4212319999988,"2013-11-17T05:00:00",73,70,"ON",56340.558147520016,71293.896863226008,3269.0169999999998,"OFF",-18.682178010195003,-110.20818416016002,-8.8484060000000007,"OFF",-0.19825763512499603,-33.398399859304,-1.7696810000000001,"OFF",-3.3156506249299853,-164.83503661724001,-1.7696810000000001,"ON",55411.869038789991,66682.711375792001,3333.7919999999999,null,2785.1178549772344,0,0,0,2645.6245067823024,5430.7423617595368,2931.7433780597039,0,1705.9388681028674,0,2818.8318649785087,7456.5141111410803,483.89914502276542,0,0,0,688.16749321769748,337.27362194029593,0,0,0,514.96013502149117,1135.0683776868102,815.2354964081344,null,null,6590.4212319999988,null,91919.663300000131,14.17108598811696,12972.846735540037,239.4412831024791,11806.348350200013,202.44302254882635,-36.998260553652756,null,null,null,null,null,null,null,null,null,5430.7423617595368,40.240419450237368,0,0,0,38.245571384112282]
[1985.0916805500167,0,0,0,1971.8156996729151,3956.9073802229318,4866.5784337000005,"2013-11-17T20:00:00",68,55,"ON",48013.258570000013,72769.770423395996,2422.6170000000002,"OFF",-19.46111369782998,-105.06578685774001,-8.8484060000000007,"OFF",9.7278839849998466E-2,-41.400104170214007,-0.1603773,"OFF",-5.6206721992399995,-166.99199929652002,-3.9817830000000001,"ON",48428.627395320007,69642.888392666006,2456.9520000000002,null,1956.789675366414,0,0,0,1943.3639709824388,3900.1536463488528,2052.5045687066299,0,1705.9388681028674,0,2055.56036153166,5814.0037983411567,465.82732463358616,0,0,0,513.58802901756144,370.11243129337026,0,0,0,401.39163846834026,930.04815330291217,722.1368694134751,null,null,4866.5784337000005,null,77871.196800000151,12.779516387713828,12186.876942364608,214.12956109867284,10485.792499200013,164.76236075043747,-49.367200348235372,null,null,null,null,null,null,null,null,null,3900.1536463488528,28.30200518360266,0,0,0,28.45172869047633]
[1966.0644521521976,0,0,0,0,1966.0644521521976,2370.8238069999993,"2013-11-18T12:00:00",70,50,"ON",47450.965605119993,60137.085206740005,2388.8339999999998,"OFF",-19.594718996929998,-107.8489360474,-8.8484060000000007,"OFF",-2.3962505538000032E-2,-33.398399859304,-1.7696810000000001,"OFF",-6.4485374417800001,-158.64239131086001,-3.410323,"OFF",-8.3971697740018461E-2,-117.59015873206,-3.9817830000000001,null,1938.4254299699855,0,0,0,0,1938.4254299699855,2104.755206248602,0,1705.9388681028674,0,0,3810.6940743514697,450.40857003001429,0,0,0,0,284.07879375139782,0,0,0,0,383.36370278884442,217.03392651022793,null,null,2370.8238069999993,null,83410.700000000012,12.664105613020443,13172.773908998728,246.13212474572498,11006.505800000001,179.08725750455508,-67.044867241169896,null,null,null,null,null,null,null,null,null,1938.4254299699855,27.639022182212102,0,0,0,0]
[1732.8257837381968,0,0,0,0,1732.8257837381968,1942.0309889999999,"2013-11-19T02:00:00",60,49,"ON",40134.115187639996,71307.299676840004,1958.972,"OFF",-18.753414801580032,-108.53928922978001,-8.8484060000000007,"OFF",-0.24528230233000206,-33.398399859304,-1.7696810000000001,"OFF",-6.1291487281500059,-166.99199929652002,-2.3411409999999999,"OFF",-3.8079339453399963,-118.28596608156001,-3.9817830000000001,null,1713.0556585634533,0,0,0,0,1713.0556585634533,1784.9281711281735,0,1705.9388681028674,0,0,3490.867039231041,245.91634143654665,0,0,0,0,174.04382887182646,0,0,0,0,216.81480948097698,144.94229691625679,null,null,1942.0309889999999,null,57428.400000000081,11.717606801032852,9802.0698211068211,147.00713315565196,8564.1696000000084,117.9056012000823,-29.101531955569655,null,null,null,null,null,null,null,null,null,1713.0556585634533,19.770125174743498,0,0,0,0]
[1916.9562912888823,0,0,0,0,1916.9562912888823,2193.8223469999994,"2013-11-19T18:00:00",62,48,"ON",45977.55271687502,60104.777287388009,2212.404,"OFF",-16.889022499799978,-106.19640361838,-8.8484060000000007,"OFF",-2.9783851223000226E-2,-41.400104170214007,-1.7696810000000001,"OFF",-7.3013298127000121,-166.99199929652002,-3.9817830000000001,"OFF",-6.371974622550006,-120.37338813006001,-3.9817830000000001,null,1891.0147467171305,0,0,0,0,1891.0147467171305,2047.2979762541995,0,1705.9388681028674,0,0,3753.2368443570667,321.3892532828695,0,0,0,0,165.10602374580048,0,0,0,0,283.53331108552209,127.25008154845304,null,null,2193.8223469999994,null,62221.807200000039,11.820151554229435,10528.089578976016,165.90005783416754,9014.7498768000041,128.0441156368201,-37.855942197347446,null,null,null,null,null,null,null,null,null,1891.0147467171305,25.94154457175182,0,0,0,0]
[1709.3785257717184,1995.5024021635936,0,0,0,3704.8809279353118,4143.9786519999998,"2013-11-20T09:00:00",54,45,"ON",39349.219395799992,70558.723260454004,2008.684,"ON",40996.928303264998,80717.422333980008,2147.2399999999998,"OFF",-0.25374494537500064,-33.398399859304,-1.7696810000000001,"OFF",-6.7703029075000103,-166.99199929652002,-3.9817830000000001,"OFF",-8.5805659995999992,-118.23262753546001,-6.1938839999999997,null,1690.3699253020432,1974.246160339429,0,0,0,3664.6160856414722,1762.0374156023975,2020.0272705841151,1705.9388681028674,0,0,5488.0035542893802,318.31407469795681,172.99383966057076,0,0,0,246.64658439760251,127.21272941588472,0,0,0,476.80495756258944,359.3563570175491,null,null,4143.9786519999998,null,44737.413600000087,11.041624923497556,8103.4112116586939,108.07554977950186,7371.2168784000078,93.572592983563723,-14.502956795938132,null,null,null,null,null,null,null,null,null,3664.6160856414722,19.00860046967523,21.25624182416459,0,0,0]
[0,1966.261553320832,0,0,0,1966.261553320832,2117.5596860000001,"2013-11-21",62,58,"OFF",-7.3372382408250099,-73.058993676602014,1.970985,"ON",38223.75985658999,69383.855558636002,2125.027,"OFF",0.1592010332499976,-33.398399859304,-1.7696810000000001,"OFF",-7.1720829155499901,-164.83503661724001,-2.3411409999999999,"OFF",-9.9992122197100013,-119.67758078056001,-5.327477,null,0,1947.6885274879912,0,0,0,1947.6885274879912,0,2021.7587435405665,1705.9388681028674,0,0,3727.6976116434339,0,177.33847251200882,0,0,0,0,103.26825645943359,0,0,0,153.03415336189698,78.96393730932175,null,null,2117.5596860000001,null,62221.807200000039,12.428620327026039,10012.6652134829,152.34843478693193,9014.7498768000041,128.0441156368201,-24.304319150111837,null,null,null,null,null,null,null,null,null,1947.6885274879912,0,18.573025832840813,0,0,0]
[0,2912.147102866641,2870.060025593491,0,0,5782.2071284601316,6852.5079190000006,"2013-11-21T16:00:00",75,70,"OFF",-9.7221311232749912,-74.449990771384009,1.4953829999999999,"ON",50549.633493975016,71162.467477302009,3431.8119999999999,"ON",59324.227222919988,75956.760584122007,3424.9520000000002,"OFF",-7.4706814555100136,-166.99199929652002,-1.7696810000000001,"OFF",-10.677149830234994,-120.37338813006001,-3.9817830000000001,null,0,2878.6482903040851,2825.4621228804517,0,0,5704.1104131845368,0,3001.4377296060247,2953.0351265074355,0,0,5954.4728561134598,0,553.1637096959148,599.48987711954851,0,0,0,430.37427039397517,471.91687349256472,0,0,1111.1534043557306,860.79096142680726,null,null,6852.5079190000006,null,97681.6875,14.367494615550399,13597.59514289652,260.68907989775749,12347.978625,219.18889743802484,-41.500182459732656,null,null,null,null,null,null,null,null,null,5704.1104131845368,0,33.498812562555941,44.597902713039275,0,0]
[0,0,1518.5032841892275,0,0,1518.5032841892275,1881.9429342999999,"2013-11-22T07:00:00",37,35,"OFF",-13.119916952700006,-74.450592333934011,0.92490629999999996,"OFF",-1.4846268197250148,-105.76159420724001,-8.8484060000000007,"ON",34761.954366959995,80467.573354880005,1897.83,"OFF",-6.9525081155599997,-166.99199929652002,-3.9817830000000001,"OFF",-11.452499949100018,-120.37338813006001,-3.9817830000000001,null,0,0,1503.6847500592703,0,0,1503.6847500592703,0,0,1536.1064367508129,0,0,1536.1064367508129,0,0,394.14524994072963,0,0,0,0,361.72356324918701,0,0,395.07319373201165,362.65150704046903,null,null,1881.9429342999999,null,28650.199700000056,9.8847954545887777,5796.8219639183117,67.036025448148166,5859.0187718000052,67.963969239430199,0.92794379128203275,null,null,null,null,null,null,null,null,null,1503.6847500592703,0,0,14.818534129957243,0,0]
[0,0,1488.7064620773672,0,0,1488.7064620773672,1630.2118679999999,"2013-11-22T22:00:00",36,35,"OFF",-15.201152633099985,-73.754793005267999,1.1407050000000001,"OFF",-5.4109384501200051,-112.71958749390001,-8.8484060000000007,"ON",33701.544595600011,79318.508676040001,1647.3209999999999,"OFF",-6.9049990114700099,-164.83503661724001,-4.553242,"OFF",-10.354361908835019,-166.99199929652002,-4.8481889999999996,null,0,0,1474.7692417484623,0,0,1474.7692417484623,0,0,1507.5292956817666,0,0,1507.5292956817666,0,0,172.55175825153765,0,0,0,0,139.79170431823331,0,0,173.16936887973455,140.40931494643021,null,null,1630.2118679999999,null,28888.694400000008,9.8929249616944812,5840.2736322892088,67.683259008016108,5881.4372736000005,68.300869636213008,0.61761062819689982,null,null,null,null,null,null,null,null,null,1474.7692417484623,0,0,13.937220328904914,0,0]
[0,0,1538.2719742457336,0,0,1538.2719742457336,1644.2068999999999,"2013-11-23T15:00:00",41,38,"OFF",-17.726066289580007,-70.971595690604005,1.605278,"OFF",-8.6083875916799855,-108.27837149976,-8.8484060000000007,"ON",35454.344373720007,77126.117972982,1660.28,"OFF",-6.2660371340000012,-158.64239131086001,-3.9817830000000001,"OFF",-8.6570235464300165,-157.80742249145999,-4.8481889999999996,null,0,0,1522.8626121914685,0,0,1522.8626121914685,0,0,1564.0822523218455,0,0,1564.0822523218455,0,0,137.41738780853143,0,0,0,0,96.197747678154428,0,0,139.25314881779107,98.03350868741407,null,null,1644.2068999999999,null,29175.192900000024,10.08523139374422,5785.7260306584812,66.871520898354106,5908.3681326000024,68.707281907613748,1.8357610092596417,null,null,null,null,null,null,null,null,null,1522.8626121914685,0,0,15.409362054265102,0,0]
[0,0,1303.3657636311143,0,0,1303.3657636311143,1477.922456,"2013-11-24T04:00:00",36,32,"OFF",-18.094591951030001,-73.754793005267999,1.478529,"OFF",-10.626843828864992,-108.27837149976,-8.8484060000000007,"ON",26573.778214939997,75469.968147828011,1495.4680000000001,"OFF",-5.455062260690025,-160.79935399013999,-3.9817830000000001,"OFF",-8.3276320384600133,-166.99199929652002,-6.1938839999999997,null,0,0,1294.6228852235083,0,0,1294.6228852235083,0,0,1320.2456783365958,0,0,1320.2456783365958,0,0,200.84511477649176,0,0,0,0,175.22232166340427,0,0,199.80584003393147,174.18304692084399,null,null,1477.922456,null,28888.694400000008,9.7103843298555006,5950.0619993338405,69.340144378773275,5881.4372736000005,68.300869636213008,-1.0392747425602664,null,null,null,null,null,null,null,null,null,1294.6228852235083,0,0,8.7428784076059856,0,0]
[0,0,1420.9692064516064,0,0,1420.9692064516064,1481.7154720000001,"2013-11-24T20:00:00",34,31,"OFF",-19.188961396990006,-70.971595690604005,1.1745969999999999,"OFF",-9.0481844139000049,-106.45443384816001,-8.8484060000000007,"ON",31209.961089590015,75754.178379784003,1499.27,"OFF",-5.0929074483699921,-166.99199929652002,-4.553242,"OFF",-7.0850377043599995,-166.99199929652002,-5.327477,null,0,0,1408.9913419525758,0,0,1408.9913419525758,0,0,1443.5677529796862,0,0,1443.5677529796862,0,0,90.278658047424187,0,0,0,0,55.702247020313735,0,0,87.284551327458331,52.708140300347878,null,null,1481.7154720000001,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1408.9913419525758,0,0,11.977864499030602,0,0]
[0,0,1338.5992548748814,0,0,1338.5992548748814,1683.7997350000001,"2013-11-25T11:00:00",37,35,"OFF",-20.12306996049001,-73.058993676602014,1.428383,"OFF",-9.152052777399998,-108.8086288355,-8.8484060000000007,"ON",28008.789051749987,75386.880328422005,1699.7639999999999,"OFF",-4.2229875579499918,-158.64239131086001,-4.5624589999999996,"OFF",-5.0981603547000178,-166.99199929652002,-3.9817830000000001,null,0,0,1328.9116894779131,0,0,1328.9116894779131,0,0,1357.4339506425385,0,0,1357.4339506425385,0,0,370.85231052208678,0,0,0,0,342.33004935746135,0,0,371.7802543133688,343.25799314874337,null,null,1683.7997350000001,null,28650.199700000056,9.8847954545887777,5796.8219639183117,67.036025448148166,5859.0187718000052,67.963969239430199,0.92794379128203275,null,null,null,null,null,null,null,null,null,1328.9116894779131,0,0,9.6875653969682389,0,0]
[0,0,1440.2627860871273,0,0,1440.2627860871273,1533.2177459999998,"2013-11-26T02:00:00",37,35,"OFF",-20.204359803039996,-70.971595690604005,1.0397650000000001,"OFF",-7.9646856602599883,-107.8489360474,-8.8484060000000007,"ON",31931.686480980003,75989.637982688,1551.4970000000001,"OFF",-2.2623608757400091,-160.83416440970004,-5.6132070000000001,"OFF",-2.58741508283999,-166.99199929652002,-4.8574060000000001,null,0,0,1427.7333756745697,0,0,1427.7333756745697,0,0,1463.4399827846505,0,0,1463.4399827846505,0,0,123.76362432543033,0,0,0,0,88.057017215349561,0,0,124.69156811671236,88.984961006631593,null,null,1533.2177459999998,null,28650.199700000056,9.8847954545887777,5796.8219639183117,67.036025448148166,5859.0187718000052,67.963969239430199,0.92794379128203275,null,null,null,null,null,null,null,null,null,1427.7333756745697,0,0,12.529410412557581,0,0]
[0,0,1441.9346050242546,0,0,1441.9346050242546,1749.530855,"2013-11-26T18:00:00",47,39,"OFF",-20.221645422720012,-71.667395019270003,1.8635029999999999,"OFF",-7.0484018024000088,-104.62800973802001,-8.8484060000000007,"ON",31993.759056270006,75575.907323300009,1765.06,"OFF",-2.3206471421000119,-164.80022619768002,-4.5624589999999996,"OFF",-2.0777264058599809,-166.99199929652002,-3.9817830000000001,null,0,0,1429.3571501931219,0,0,1429.3571501931219,0,0,1466.0208388846495,0,0,1466.0208388846495,0,0,335.70284980687802,0,0,0,0,299.03916111535045,0,0,331.85151125967957,295.187822568152,null,null,1749.530855,null,33987.03270000004,10.310098208765135,6592.9600304109508,79.66191611212335,6360.681073800004,75.810577564924898,-3.851338547198452,null,null,null,null,null,null,null,null,null,1429.3571501931219,0,0,12.577454831132627,0,0]
[0,0,1328.59072329895,0,0,1328.59072329895,1476.4520649999999,"2013-11-27T09:00:00",35,28,"OFF",-21.685340822219988,-70.971595690604005,1.3779710000000001,"OFF",-8.1057204021499878,-109.03385385422001,-8.8484060000000007,"ON",27605.450895619993,75845.744220728011,1495.1949999999999,"OFF",-1.4813723365700029,-161.66913322910003,-6.1938839999999997,"OFF",-2.8396697987000024,-166.99199929652002,-5.0786160000000002,null,0,0,1319.1737814430983,0,0,1319.1737814430983,0,0,1346.2150266088654,0,0,1346.2150266088654,0,0,176.02121855690166,0,0,0,0,148.97997339113454,0,0,172.01082942038261,144.96958425461548,null,null,1476.4520649999999,null,29282.587499999994,9.4804233528792441,6177.4852050476729,72.870494026986108,5918.4632249999995,68.860104890467056,-4.010389136519052,null,null,null,null,null,null,null,null,null,1319.1737814430983,0,0,9.4169418558517464,0,0]
[0,0,1513.4870365158345,0,0,1513.4870365158345,1670.395231,"2013-11-28T01:00:00",32,28,"OFF",-21.565417902629999,-70.971595690604005,1.5484709999999999,"OFF",-8.6235047009499848,-107.1531286979,-8.8484060000000007,"ON",34584.870689769996,71423.465415662009,1686.7739999999999,"OFF",-2.2839152002799983,-158.64239131086001,-3.9817830000000001,"OFF",-3.2394056459800122,-117.59015873206,-5.0970510000000004,null,0,0,1498.8176572484888,0,0,1498.8176572484888,0,0,1551.8144228118952,0,0,1551.8144228118952,0,0,187.9563427515111,0,0,0,0,134.95957718810473,0,0,180.48168395098048,127.48491838757413,null,null,1670.395231,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1498.8176572484888,0,0,14.669379267345676,0,0]
[0,0,0,1974.1889814663159,0,1974.1889814663159,2054.175475,"2013-11-28T20:00:00",45,38,"OFF",-23.964979359420003,-69.579997033272008,1.8430260000000001,"OFF",-9.8086568873300006,-108.5447433969,-8.8484060000000007,"OFF",-0.11239166662500143,-33.398399859304,-2.4240940000000002,"ON",35124.432368609996,65258.852924112005,2068.7020000000002,"OFF",-3.9133443222300026,-119.67758078056001,-5.0970510000000004,null,0,0,0,1958.4609177678544,0,1958.4609177678544,0,0,1489.566015047717,2034.1862435402031,0,3523.7522585879201,0,0,0,110.2410822321458,0,0,0,0,34.515756459797103,0,108.60632501798136,32.880999245632665,null,null,2054.175475,null,31886.51250000007,10.17765144313752,6265.9863482552601,74.280108693147241,6163.2321750000065,72.645351478982803,-1.6347572141644378,null,null,null,null,null,null,null,null,null,1958.4609177678544,0,0,0,15.728063698461483,0]
[0,0,0,1666.7013615322353,0,1666.7013615322353,1975.9957570000001,"2013-11-29T06:00:00",34,31,"OFF",-26.055295139429997,-71.921222332034006,1.645627,"OFF",-8.78193788992,-105.76159420724001,-8.8484060000000007,"OFF",4.2047326831500142E-2,-33.398399859304,-1.7696810000000001,"ON",23802.476922810005,65916.954332978014,1988.95,"OFF",-3.4459811167600041,-117.59015873206,-3.9817830000000001,null,0,0,0,1659.2624005140017,0,1659.2624005140017,0,0,1489.566015047717,1693.9892264531811,0,3183.5552415008979,0,0,0,329.68759948599836,0,0,0,0,294.96077354681893,0,326.69349276603248,291.96666682685304,null,null,1975.9957570000001,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1659.2624005140017,0,0,0,7.4389610182336128,0]
[0,0,0,1853.6186884021954,0,1853.6186884021954,1797.3952959999999,"2013-11-29T23:00:00",46,41,"OFF",-24.035772614040006,-70.971595690604005,1.8199989999999999,"OFF",-9.3124836805650268,-109.2405507464,-8.8484060000000007,"OFF",4.8387181276001189E-2,-45.748847969168004,-1.7696810000000001,"ON",30986.159126780003,65139.919997560006,1811.2719999999999,"OFF",-5.7840707290099775,-116.28412633184,-5.0786160000000002,null,0,0,0,1841.2937617993837,0,1841.2937617993837,0,0,1489.566015047717,1900.9124276870371,0,3390.478442734754,0,0,0,-30.021761799383739,0,0,0,0,-89.640427687037118,0,-31.147621322580264,-90.766287210233642,null,null,1797.3952959999999,null,32877.826400000049,10.393982735289017,6326.3192247520783,75.252563114838708,6256.415681600005,74.126703591642183,-1.1258595231965245,null,null,null,null,null,null,null,null,null,1841.2937617993837,0,0,0,12.324926602811729,0]
[0,0,0,2208.2776403240509,0,2208.2776403240509,2212.7701080000002,"2013-11-30T14:00:00",67,58,"OFF",-26.465153281070016,-72.363194347936002,1.548079,"OFF",-9.3759653446800115,-106.45740155674001,-8.8484060000000007,"OFF",-0.74318799249999867,-33.398399859304,-1.7696810000000001,"ON",40252.663429649983,64870.644558512009,2228.0340000000001,"OFF",-5.8841745021500182,-118.98177343106001,-6.1938839999999997,null,0,0,0,2187.6138047740296,0,2187.6138047740296,0,0,1489.566015047717,2288.9042209002105,0,3778.4702359479274,0,0,0,40.420195225970474,0,0,0,0,-60.87022090021037,0,-0.21689299595720968,-101.50730912213805,null,null,2212.7701080000002,null,75152.638700000127,12.869390233283658,11679.2850846399,198.62329611301379,10230.248037800013,157.98620789108611,-40.637088221927684,null,null,null,null,null,null,null,null,null,2187.6138047740296,0,0,0,20.663835550021304,0]
[0,0,0,1992.7817858570231,0,1992.7817858570231,2078.2072640000001,"2013-12-01T05:00:00",53,52,"OFF",-26.737454491090006,-70.275796361938006,1.672134,"OFF",-10.723048476079999,-107.6239516537,-8.8484060000000007,"OFF",-8.0799437600001904E-3,-75.14639166260001,-1.7696810000000001,"ON",35734.919565929995,65075.21592968201,2091.1350000000002,"OFF",-6.833165063970017,-120.37338813006001,-3.9817830000000001,null,0,0,0,1976.5145534690596,0,1976.5145534690596,0,0,1489.566015047717,2055.4829289919762,0,3545.0489440396932,0,0,0,114.62044653094063,0,0,0,0,35.652071008023995,0,108.49474676450133,29.526371241584698,null,null,2078.2072640000001,null,42907.977300000086,11.405193542837774,7524.2874465633977,96.491074020494764,7199.249866200008,90.365374254055467,-6.1256997664392969,null,null,null,null,null,null,null,null,null,1976.5145534690596,0,0,0,16.267232387963531,0]
[0,0,0,2224.1229760290812,1897.3245794855804,4121.4475555146619,4652.3864599999997,"2013-12-01T21:00:00",57,55,"OFF",-26.705360154550004,-73.500965692503996,1.645235,"OFF",-10.706411471850025,-106.47560884992001,-8.8484060000000007,"OFF",-7.9650971909999244E-2,-33.398399859304,-3.327369,"ON",42827.092689659999,73346.684950514013,2336.8919999999998,"ON",45654.262510799999,74387.981703729994,2326.0250000000001,null,0,0,0,2200.8786967186443,1872.0111734041034,4072.8898701227477,0,0,1489.566015047717,2277.1718825061166,1950.7247150838591,5717.4626126376925,0,0,0,136.01330328135555,454.01382659589672,0,0,0,59.720117493883208,375.30028491614098,576.83598482823675,421.82925736100867,null,null,4652.3864599999997,null,50738.045700000075,11.854635689452406,8560.0345770463373,117.81496570909295,7935.2762958000076,104.62382066007743,-13.191145049015518,null,null,null,null,null,null,null,null,null,4072.8898701227477,0,0,0,23.244279310436923,25.313406081477069]
[0,0,0,0,1822.7592554782075,1822.7592554782075,2051.82647,"2013-12-02T12:00:00",63,55,"OFF",-30.314629163770018,-70.971595690604005,1.7328129999999999,"OFF",-12.753256129470017,-109.2405507464,-8.8484060000000007,"OFF",-7.3155129361999929E-2,-33.398399859304,-3.327369,"OFF",0.65382329438998998,-163.96525737828,-2.5715680000000001,"ON",42771.546482500002,66207.444877956004,2064.8409999999999,null,0,0,0,0,1800.5039316032569,1800.5039316032569,0,0,1489.566015047717,0,1903.310350648954,3392.8763656966712,0,0,0,0,264.33706839674301,0,0,0,0,161.53064935104589,232.82717449440477,130.02075544870766,null,null,2051.82647,null,64707.210300000093,12.330798987322249,10495.217765941683,165.01548282180855,9248.3777682000091,133.50558891947031,-31.509893902338234,null,null,null,null,null,null,null,null,null,1800.5039316032569,0,0,0,0,22.255323874950591]
[0,0,0,0,1757.7076039288627,1757.7076039288627,1918.516372,"2013-12-03T04:00:00",48,46,"OFF",-29.03683715898001,-73.754793005267999,1.501242,"OFF",-10.708546959210025,-105.96829109942,-8.8484060000000007,"OFF",2.7902062064995764E-2,-45.748847969168004,-1.7696810000000001,"OFF",-2.8631679097699845,-161.66913322910003,-3.9817830000000001,"ON",40160.666184639987,74575.885781848017,1931.615,null,0,0,0,0,1738.0451246227299,1738.0451246227299,0,0,1489.566015047717,0,1798.5565802926633,3288.12259534038,0,0,0,0,193.56987537727014,0,0,0,0,133.05841970733672,192.6000382249097,132.08858255497628,null,null,1918.516372,null,35210.380800000043,10.777726299749748,6533.9163049292883,78.669839718170635,6475.6757952000044,77.700002565810195,-0.96983715236044077,null,null,null,null,null,null,null,null,null,1738.0451246227299,0,0,0,0,19.662479306132809]
[0,0,0,0,1867.8682229698557,1867.8682229698557,2045.6109160000001,"2013-12-03T12:00:00",68,53,"OFF",-31.248014938019995,-72.363194347936002,1.658684,"OFF",-11.236467212100042,-105.06578685774001,-8.8484060000000007,"OFF",-0.2321160901049984,-33.398399859304,-1.7696810000000001,"OFF",-5.7858549379150048,-158.64239131086001,-1.7696810000000001,"ON",44528.735682275001,65183.096146982003,2056.34,null,0,0,0,0,1843.77331097916,1843.77331097916,0,0,1489.566015047717,0,1960.3216629920869,3449.8876780398041,0,0,0,0,212.56668902084016,0,0,0,0,96.01833700791326,159.52652377214329,42.978171759216394,null,null,2045.6109160000001,null,77871.196800000151,12.657822633154508,12304.042971187304,217.80252599913433,10485.792499200013,164.76236075043747,-53.040165248696866,null,null,null,null,null,null,null,null,null,1843.77331097916,0,0,0,0,24.094911990695664]
[1765.610191428058,0,0,0,1743.1870191917594,3508.7972106198176,4155.761129999999,"2013-12-04T09:00:00",58,52,"ON",41214.954853599993,75780.582965312016,2114.1849999999999,"OFF",-10.42367299617,-108.52645589538001,-8.8484060000000007,"OFF",-0.25215223237500273,-45.748847969168004,-1.7696810000000001,"OFF",-5.8847258498699908,-163.96525737828,-3.9817830000000001,"ON",39564.642646830005,74201.537417400003,2056.1759999999999,null,1744.7654543333531,0,0,0,1724.0930237751882,3468.858478108541,1804.8932346047065,0,1489.566015047717,0,1784.0235080083412,5078.4827576607649,369.41954566664685,0,0,0,332.08297622481177,309.2917653952934,0,0,0,272.15249199165874,682.43580410739469,562.37753960288819,null,null,4155.761129999999,null,52896.528800000029,11.745670712330265,9006.9830996489254,127.86495303342255,8138.1737072000033,108.79823524935864,-19.066717784063911,null,null,null,null,null,null,null,null,null,3468.858478108541,20.844737094704897,0,0,0,19.093995416571261]
[1620.2681663886538,0,0,0,0,1620.2681663886538,1871.6132339999999,"2013-12-05T01:00:00",46,40,"ON",36268.491852974999,64660.987978586003,1889.393,"OFF",-10.2502225032,-106.45732134840001,-8.8484060000000007,"OFF",-0.14137670099999836,-75.14639166260001,-1.7696810000000001,"OFF",-6.3475114267599864,-158.64239131086001,-3.1798959999999998,"OFF",-2.0090801797500006,-118.28596608156001,-3.9817830000000001,null,1604.0963701447636,0,0,0,0,1604.0963701447636,1684.0555642872041,0,1489.566015047717,0,0,3173.6215793349211,285.29662985523646,0,0,0,0,205.33743571279592,0,0,0,0,283.56567316051905,203.60647901807855,null,null,1871.6132339999999,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,1604.0963701447636,16.171796243890185,0,0,0,0]
[0,1580.887481466847,0,0,0,1580.887481466847,1796.1569122000003,"2013-12-05T16:00:00",31,29,"OFF",-2.0060541339300046,-73.058993676602014,1.425508,"ON",29227.493744364987,73689.703937358005,1804.1780000000001,"OFF",0.13151708448000105,-33.398399859304,-0.36776180000000003,"OFF",-6.7419977258900028,-158.64239131086001,-3.9817830000000001,"OFF",-3.2230117770900026,-121.06919547956002,-5.0970510000000004,null,0,1570.0474059877895,0,0,0,1570.0474059877895,0,1604.9632843755146,1489.566015047717,0,0,3094.5292994232314,0,234.13059401221062,0,0,0,0,199.21471562448551,0,0,0,225.62475814878081,190.7088797610557,null,null,1796.1569122000003,null,32487.155900000012,9.650503523722751,6732.738000694053,82.046094062066885,6219.6926546000013,73.540258198637076,-8.5058358634298088,null,null,null,null,null,null,null,null,null,1570.0474059877895,0,10.840075479057532,0,0,0]
[0,0,1380.0939654113104,0,0,1380.0939654113104,1579.127594,"2013-12-06T07:00:00",27,26,"OFF",-5.7085553463000034,-73.058993676602014,1.2170479999999999,"OFF",-3.8706339982000131,-105.57310460824,-8.8484060000000007,"ON",29646.767440069998,75136.566140950003,1597.248,"OFF",-6.84816199676,-161.66913322910003,-5.3919969999999999,"OFF",-3.6482997600000027,-121.06919547956002,-5.0970510000000004,null,0,0,1369.2662050004046,0,0,1369.2662050004046,0,0,1401.582141272894,0,0,1401.582141272894,0,0,227.98179499959542,0,0,0,0,195.66585872710607,0,0,205.84000278037334,173.52406650788399,null,null,1579.127594,null,38478.146700000041,9.6721762445445219,7956.4610336175765,105.05474838972785,6782.8457898000033,82.912956170505765,-22.141792219222083,null,null,null,null,null,null,null,null,null,1369.2662050004046,0,0,10.827760410905739,0,0]
[0,0,0,1836.3201089894762,0,1836.3201089894762,2253.0284850000003,"2013-12-06T23:00:00",25,23,"OFF",-7.5362968619650017,-75.856692659138005,1.3268690000000001,"OFF",-6.2424630522899864,-166.15703047712,-8.8484060000000007,"OFF",-7.5642156374994718E-2,-166.99199929652002,-2.4240940000000002,"ON",30364.31263212,68112.384932122019,2269.1680000000001,"OFF",3.7359713124996356E-2,-124.04203739332002,-6.1938839999999997,null,0,0,0,1824.4689824751426,0,1824.4689824751426,0,0,1412.4518539855485,1874.5811450058045,0,3287.032998991353,0,0,0,444.69901752485748,0,0,0,0,394.58685499419562,0,410.33253924600785,360.22037671534599,null,null,2253.0284850000003,null,42593.562500000029,9.6299167258247635,8846.0915525418659,124.18826976761927,7169.6948750000029,89.821791488769676,-34.366478278849598,null,null,null,null,null,null,null,null,null,1824.4689824751426,0,0,0,11.8511265143336,0]
[0,0,1453.9521680288562,0,0,1453.9521680288562,2171.8234790000006,"2013-12-07T14:00:00",25,23,"OFF",-13.580515611669993,-71.667395019270003,1.327653,"OFF",-6.4565189368300047,-105.27248374992,-8.8484060000000007,"ON",32437.817300625,74764.728297544018,2191.732,"OFF",-2.1017047428299969,-166.99199929652002,-6.1938839999999997,"OFF",-0.71409905343000823,-121.76500282906001,-6.1938839999999997,null,0,0,1441.0281951781283,0,0,1441.0281951781283,0,0,1480.3828173902634,0,0,1480.3828173902634,0,0,750.7038048218717,0,0,0,0,711.34918260973654,0,0,716.33732654302207,676.98270433088692,null,null,2171.8234790000006,null,42593.562500000029,9.6299167258247635,8846.0915525418659,124.18826976761927,7169.6948750000029,89.821791488769676,-34.366478278849598,null,null,null,null,null,null,null,null,null,1441.0281951781283,0,0,12.923972850727978,0,0]
[0,0,1411.5169551429774,0,0,1411.5169551429774,2207.5250070000002,"2013-12-08T01:00:00",26,25,"OFF",-15.501884981850003,-70.971595690604005,1.3856980000000001,"OFF",-7.1752006226249936,-109.25883824792001,-8.8484060000000007,"ON",30852.686103360003,73473.446211050017,2224.85,"OFF",-2.7552381868899887,-166.99199929652002,-4.7836689999999997,"OFF",-1.5047405593499996,-119.67758078056001,-5.0786160000000002,null,0,0,1399.8073106043769,0,0,1399.8073106043769,0,0,1437.9519455971085,0,0,1437.9519455971085,0,0,825.04268939562303,0,0,0,0,786.89805440289138,0,0,797.78576265594938,759.64112766321773,null,null,2207.5250070000002,null,40439.402400000021,9.6781821826492553,8356.8177653234343,113.41459604841647,6967.2038256000014,86.157669308742783,-27.256926739673688,null,null,null,null,null,null,null,null,null,1399.8073106043769,0,0,11.709644538600514,0,0]
[0,0,1433.7478931816622,0,0,1433.7478931816622,1888.7090440000002,"2013-12-08T05:00:00",26,25,"OFF",-15.856944402600003,-71.667395019270003,1.3174980000000001,"OFF",-6.8349355986600182,-107.8489360474,-8.8484060000000007,"ON",31689.093536130003,74935.026645032005,1906.729,"OFF",-3.0746269005199829,-166.99199929652002,-5.3919969999999999,"OFF",-0.985966976750002,-120.45897042884,-5.0970510000000004,null,0,0,1421.4053259494926,0,0,1421.4053259494926,0,0,1458.6477428749745,0,0,1458.6477428749745,0,0,485.32367405050741,0,0,0,0,448.08125712502556,0,0,458.0667473108337,420.82433038535186,null,null,1888.7090440000002,null,40439.402400000021,9.6781821826492553,8356.8177653234343,113.41459604841647,6967.2038256000014,86.157669308742783,-27.256926739673688,null,null,null,null,null,null,null,null,null,1421.4053259494926,0,0,12.342567232169586,0,0]
[0,0,1432.5376850400935,0,0,1432.5376850400935,1971.387395,"2013-12-08T20:00:00",32,31,"OFF",-17.583058818639998,-70.275796361938006,1.6594679999999999,"OFF",-6.6437530587999989,-107.1531286979,-8.8484060000000007,"ON",31643.905392270008,75336.068345032007,1988.752,"OFF",-3.4019733232099942,-166.99199929652002,-3.9817830000000001,"OFF",-1.54969035075499,-121.06919547956002,-6.1938839999999997,null,0,0,1420.2297587456299,0,0,1420.2297587456299,0,0,1456.5761012665669,0,0,1456.5761012665669,0,0,568.5222412543701,0,0,0,0,532.17589873343309,0,0,563.1064567172732,526.76011419633619,null,null,1971.387395,null,31434.163200000039,9.7363041886792132,6457.1037615175974,77.392561903366015,6120.7113408000041,71.976777366269161,-5.4157845370968545,null,null,null,null,null,null,null,null,null,1420.2297587456299,0,0,12.307926294463641,0,0]
[0,0,0,1741.3364179183668,0,1741.3364179183668,2148.5492309999995,"2013-12-09T13:00:00",33,30,"OFF",-20.482006320140005,-123.72770090886,1.5484709999999999,"OFF",11.853377861850017,-141.57790655918001,-8.8484060000000007,"OFF",-0.85974881962500049,-33.398399859304,-3.9817830000000001,"ON",26802.681319294999,67399.003935328001,2164.9279999999999,"OFF",-2.0798490473599909,-145.62778606245999,-5.0970510000000004,null,0,0,0,1732.0123839735859,0,1732.0123839735859,0,0,1332.4441863622908,1772.735628932614,0,3105.179815294905,0,0,0,432.915616026414,0,0,0,0,392.19237106738592,0,428.20848925124801,387.48524429221993,null,null,2148.5492309999995,null,30551.57130000004,9.645372629758878,6334.9696217519358,75.392755338905431,6037.7477022000039,70.685628563739428,-4.7071267751660031,null,null,null,null,null,null,null,null,null,1732.0123839735859,0,0,0,9.324033944780922,0]
[0,0,0,1823.0541310680487,0,1823.0541310680487,1792.5366369999999,"2013-12-10T04:00:00",23,20,"OFF",-20.831540131170005,-70.971595690604005,1.58534,"OFF",5.0308150037199955,-105.76159420724001,-8.8484060000000007,"OFF",-6.4605478027999347E-2,-45.748847969168004,-1.7696810000000001,"ON",29882.15780353501,69456.195460482006,1806.6479999999999,"OFF",-0.4103066019499863,-119.67758078056001,-5.0786160000000002,null,0,0,0,1811.5636701859835,0,1811.5636701859835,0,0,1332.4441863622908,1857.1874049888115,0,3189.6315913511025,0,0,0,-4.9156701859835721,0,0,0,0,-50.539404988811611,0,-55.335571704160714,-100.95930650698875,null,null,1792.5366369999999,null,47495.598300000012,9.6144705194322402,9880.0237005261006,148.97103145338554,7630.4862402000017,98.551129935208394,-50.419901518177141,null,null,null,null,null,null,null,null,null,1811.5636701859835,0,0,0,11.490460882065236,0]
[0,0,0,1991.9378530433239,0,1991.9378530433239,2132.0986559999997,"2013-12-10T20:00:00",31,28,"OFF",-22.218239895880011,-71.667395019270003,1.7595259999999999,"OFF",3.092699551199996,-105.96829109942,-8.8484060000000007,"OFF",-1.900733757999807E-3,-33.398399859304,-1.7696810000000001,"ON",35707.356645100001,68193.732230550013,2144.9389999999999,"OFF",-3.4479812953249955,-119.67758078056001,-3.9817830000000001,null,0,0,0,1975.6951709917203,0,1975.6951709917203,0,0,1332.4441863622908,2044.1628203605749,0,3376.6070067228657,0,0,0,169.24382900827959,0,0,0,0,100.77617963942498,0,159.99935069805207,91.53170132919746,null,null,2132.0986559999997,null,32487.155900000012,9.589656646443089,6775.4575784629087,82.784736508864597,6219.6926546000013,73.540258198637076,-9.244478310227521,null,null,null,null,null,null,null,null,null,1975.6951709917203,0,0,0,16.242682051603651,0]
[0,0,1529.3069926879527,0,0,1529.3069926879527,1790.8347480000002,"2013-12-11T11:00:00",39,34,"OFF",-24.287378542649993,-73.754793005267999,1.400606,"OFF",-1.8603153371250178,-105.55481710672001,-8.8484060000000007,"ON",35141.423486595013,71160.245706283997,1807.048,"OFF",1.883421094310004,-166.99199929652002,-4.7836689999999997,"OFF",-5.1451980903400161,-118.98177343106001,-3.9817830000000001,null,0,0,1514.1661591573463,0,0,1514.1661591573463,0,0,1569.5805495250088,0,0,1569.5805495250088,0,0,292.88184084265367,0,0,0,0,237.46745047499121,0,0,293.30956200394019,237.89517163627775,null,null,1790.8347480000002,null,28624.403100000054,9.8230692552822418,5827.9957834172064,67.499884609956794,5856.5938914000053,67.927605771243336,0.42772116128654147,null,null,null,null,null,null,null,null,null,1514.1661591573463,0,0,15.140833530606415,0,0]
[0,0,0,1774.5212841804146,0,1774.5212841804146,2098.2646560000003,"2013-12-12T02:00:00",30,28,"OFF",-24.296519462040006,-73.754793005267999,1.5736270000000001,"OFF",-3.6459898899999943,-107.1531286979,-8.8484060000000007,"OFF",0.31848404437500455,-33.398399859304,-1.7696810000000001,"ON",28076.980102259997,68481.896733668007,2113.5030000000002,"OFF",-7.3005282694399858,-113.50378443408002,-6.1938839999999997,null,0,0,0,1764.3294234740745,0,1764.3294234740745,0,0,1531.8574046691319,1806.6814567295758,0,3338.5388613987079,0,0,0,349.17357652592568,0,0,0,0,306.8215432704244,0,337.80828737836498,295.4562541228637,null,null,2098.2646560000003,null,33714.300000000047,9.631485989739506,7000.8511741420052,86.759253967981437,6335.0442000000039,75.393964820420734,-11.365289147560702,null,null,null,null,null,null,null,null,null,1764.3294234740745,0,0,0,10.191860706340094,0]
[0,0,0,1941.7552957077492,0,1941.7552957077492,2359.1545900000006,"2013-12-12T17:00:00",45,39,"OFF",-25.059748080990012,-71.667395019270003,1.404293,"OFF",-6.9028284936599906,-106.45732134840001,-8.8484060000000007,"OFF",0.24127352968500149,-33.398399859304,-1.7696810000000001,"ON",34042.731671759997,68890.927184332002,2373.4470000000001,"OFF",-8.7635801497299948,-118.89627134062002,-5.0786160000000002,null,0,0,0,1926.9590047002393,0,1926.9590047002393,0,0,1531.8574046691319,1987.3229457068478,0,3519.1803503759797,0,0,0,446.48799529976077,0,0,0,0,386.12405429315231,0,445.44880212814917,385.08486112154071,null,null,2359.1545900000006,null,31886.51250000007,10.238498320417181,6228.747908550873,73.684544650594404,6163.2321750000065,72.645351478982803,-1.0391931716116005,null,null,null,null,null,null,null,null,null,1926.9590047002393,0,0,0,14.796291007509808,0]
[0,0,0,1871.2673716774443,0,1871.2673716774443,2187.775967,"2013-12-13T08:00:00",44,39,"OFF",-27.539506837530002,-72.363194347936002,1.4666699999999999,"OFF",-8.077776691419972,-106.45732134840001,-8.8484060000000007,"OFF",-0.44688617690999838,-33.398399859304,-1.7696810000000001,"ON",31612.830954870005,68180.738479470005,2202.0059999999999,"OFF",-9.0436839220700076,-120.37338813006001,-5.0786160000000002,null,0,0,0,1858.4550924254386,0,1858.4550924254386,0,0,1531.8574046691319,1912.4684377072881,0,3444.32584237642,0,0,0,343.55090757456128,0,0,0,0,289.53756229271175,0,343.62909363691392,289.6157483550644,null,null,2187.775967,null,31016.841600000043,10.208854073558966,6076.4589985342182,71.285893069910372,6081.4831104000041,71.364079132263043,7.8186062352671115E-2,null,null,null,null,null,null,null,null,null,1858.4550924254386,0,0,0,12.812279252005737,0]
[0,0,0,0,0,0,-19.123072000000001,"2013-12-13T23:00:00",47,46,"OFF",-23.479938006299996,-89.604506405980004,1.0162690000000001,"OFF",-10.017347427879983,4378.1987076522,-8.8484060000000007,"OFF",-2.551608203874999,-166.99199929652002,-3.327369,"OFF",-1.4224536694899865,-166.99199929652002,-3.9817830000000001,"check",7372.8218551250066,62536.405406164005,-3.9817830000000001,null,0,0,0,0,0,0,0,0,1531.8574046691319,0,0,1531.8574046691319,0,0,0,0,0,0,0,0,0,0,0.47571419705829499,0.47571419705829499,null,null,-19.123072000000001,null,33987.03270000004,10.736026349722758,6331.3988980434469,75.334863367866603,6360.681073800004,75.810577564924898,0.47571419705829499,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,0,1819.1472725590477,1819.1472725590477,2473.6570387000002,"2013-12-14T15:00:00",42,37,"OFF",-27.721409865930013,-73.058993676602014,0.92669369999999995,"OFF",-10.438469955759976,-107.17141619942001,-8.8484060000000007,"OFF",-0.14542875025000307,-62.795943552736006,-1.7696810000000001,"OFF",-2.0962766366499963,-163.96525737828,-2.5715680000000001,"ON",42629.017425715007,74120.406681490014,2485.92,null,0,0,0,0,1797.0378178830158,1797.0378178830158,0,0,1531.8574046691319,0,1866.7457279192706,3398.6031325884023,0,0,0,0,688.88218211698427,0,0,0,0,619.17427208072945,689.5855359784847,619.87762594222988,null,null,2473.6570387000002,null,29657.431200000021,10.040822448571618,5907.3709055016725,68.692199699414601,5953.6985328000019,69.395553560915062,0.7033538615004602,null,null,null,null,null,null,null,null,null,1797.0378178830158,0,0,0,0,22.109454676031874]
[0,0,0,0,1699.2080419805347,1699.2080419805347,2173.4075699999999,"2013-12-15T06:00:00",27,26,"OFF",-32.282588558439983,-72.355799138988004,1.1875530000000001,"OFF",-11.860817700600006,-102.28255745974,-8.8484060000000007,"OFF",-0.5636213128750025,-75.14639166260001,-1.7696810000000001,"OFF",-3.008014024679996,-158.64239131086001,-3.1798959999999998,"ON",37727.89554338,74660.545684718003,2186.018,null,0,0,0,0,1681.8114524123775,1681.8114524123775,0,0,1531.8574046691319,0,1735.0998834919826,3266.9572881611148,0,0,0,0,504.20654758762248,0,0,0,0,450.91811650801742,482.06475536840037,428.77632428879531,null,null,2173.4075699999999,null,38478.146700000041,9.6721762445445219,7956.4610336175765,105.05474838972785,6782.8457898000033,82.912956170505765,-22.141792219222083,null,null,null,null,null,null,null,null,null,1681.8114524123775,0,0,0,0,17.396589568157196]
[0,0,0,0,1844.8656755548568,1844.8656755548568,2345.4420779999996,"2013-12-15T22:00:00",42,38,"OFF",-30.923841857370007,-72.363194347936002,1.330948,"OFF",-10.55586441689001,-107.1531286979,-8.8484060000000007,"OFF",-0.33635522112500199,-62.795943552736006,-1.7696810000000001,"OFF",-3.9121099040100034,-166.99199929652002,-3.9817830000000001,"ON",43637.896721154983,74574.867135930006,2358.7109999999998,null,0,0,0,0,1821.712915914824,1821.712915914824,0,0,1531.8574046691319,0,1892.9886638633973,3424.846068532529,0,0,0,0,536.99808408517583,0,0,0,0,465.72233613660251,538.23793043164324,466.96218248306991,null,null,2345.4420779999996,null,29657.431200000021,10.10166932585128,5871.7881655665378,68.155707214447688,5953.6985328000019,69.395553560915062,1.2398463464673739,null,null,null,null,null,null,null,null,null,1821.712915914824,0,0,0,0,23.152759640032855]
[0,0,0,0,2428.5060930019658,2428.5060930019658,3682.1036599999998,"2013-12-16T13:00:00",63,49,"OFF",-32.190082045199993,-72.363194347936002,0.90253000000000005,"OFF",-10.342099350480019,-106.43911405522,-8.8484060000000007,"OFF",8.3895564555000551E-2,-62.795943552736006,-1.7696810000000001,"OFF",-3.4197859434900124,-166.99199929652002,-3.9817830000000001,"ON",63644.926714215027,74549.810050514017,3695.8009999999999,null,0,0,0,0,2379.3634701813653,2379.3634701813653,0,0,1531.8574046691319,0,2531.0871693072809,4062.9445739764128,0,0,0,0,1316.4375298186346,0,0,0,0,1164.7138306927191,1276.1929170505268,1124.4692179246113,null,null,3682.1036599999998,null,64707.210300000093,11.965717723644286,10815.433189124711,173.75020168757803,9248.3777682000091,133.50558891947031,-40.244612768107714,null,null,null,null,null,null,null,null,null,2379.3634701813653,0,0,0,0,49.142622820600536]
[0,0,0,0,1704.5987663088613,1704.5987663088613,1897.8224710000002,"2013-12-17T02:00:00",43,39,"OFF",-30.836273199130016,-71.667395019270003,1.0474540000000001,"OFF",-11.775524907029981,-102.30084496126001,-8.8484060000000007,"OFF",-0.16389719437499872,-33.398399859304,-1.7696810000000001,"OFF",-3.6449205998100083,-158.64239131086001,-3.1798959999999998,"ON",37955.664596189999,75339.862199514013,1910.5730000000001,null,0,0,0,0,1686.9961444696323,1686.9961444696323,0,0,1531.8574046691319,0,1738.99014635255,3270.8475510216822,0,0,0,0,223.57685553036777,0,0,0,0,171.58285364745007,224.58846661898116,172.59446473606346,null,null,1897.8224710000002,null,30272.564300000085,10.183484085886429,5945.4237949771377,69.269522050406849,6011.521044200008,70.281133139020227,1.0116110886133782,null,null,null,null,null,null,null,null,null,1686.9961444696323,0,0,0,0,17.602621839228959]
[0,0,0,0,1956.3670267180203,1956.3670267180203,2376.083251,"2013-12-17T19:00:00",58,48,"OFF",-32.226887258100014,-71.667395019270003,1.043121,"OFF",-9.1135774549400015,-107.1531286979,-8.8484060000000007,"OFF",-0.25722314949999797,-33.398399859304,-1.7696810000000001,"OFF",-4.3004302961200089,-166.99199929652002,-3.9817830000000001,"ON",47861.382006749984,68655.988935638015,2389.64,null,0,0,0,0,1928.5726093611001,1928.5726093611001,0,0,1531.8574046691319,0,2043.3970954574438,3575.2545001265757,0,0,0,0,461.06739063889972,0,0,0,0,346.24290454255606,437.55964420667544,322.73515811033178,null,null,2376.083251,null,52896.528800000029,11.502283203211622,9197.5702328787156,132.30598168158289,8138.1737072000033,108.79823524935864,-23.507746432224252,null,null,null,null,null,null,null,null,null,1928.5726093611001,0,0,0,0,27.794417356920121]
[0,0,0,0,1801.3188890407514,1801.3188890407514,2530.3164220000003,"2013-12-18T10:00:00",53,47,"OFF",-34.244472637969977,-71.406164476724001,1.3751899999999999,"OFF",-9.8242200346400139,-105.06578685774001,-8.8484060000000007,"OFF",-5.9270003624998749E-2,-33.398399859304,-1.7696810000000001,"OFF",-4.357952411609995,-161.66913322910003,-1.7696810000000001,"ON",41921.402988644979,73515.499443712004,2541.3290000000002,null,0,0,0,0,1779.9262232734061,1779.9262232734061,0,0,1531.8574046691319,0,1849.5253596623929,3381.3827643315249,0,0,0,0,761.40277672659408,0,0,0,0,691.80364033760725,751.25056237120566,681.65142598221883,null,null,2530.3164220000003,null,42907.977300000086,11.100959156439471,7730.4990848669013,100.51758860944383,7199.249866200008,90.365374254055467,-10.152214355388367,null,null,null,null,null,null,null,null,null,1779.9262232734061,0,0,0,0,21.392665767345306]
[1853.8176965750288,0,0,0,0,{"$f":"SUM(A7748:E7748)","v":1853.8176965750288},{"$f":"N7748+R7748+V7748+Z7748+AD7748","v":2167.7994009999998},"2013-12-19T02:00:00",55,51,"ON",44033.478068249984,64747.163819082001,2186.6759999999999,"OFF",-10.269118200599966,-108.5447433969,-8.8484060000000007,"OFF",-4.8601164600001147E-3,-62.795943552736006,-1.7696810000000001,"OFF",-3.5566743493399886,-163.96525737828,-3.1798959999999998,"OFF",-1.0295909969100061,-116.19862424140001,-5.0786160000000002,null,1830.0282566781132,0,0,0,0,{"$f":"SUM(AF7748:AJ7748)","v":1830.0282566781132},1947.340483997172,0,1531.8574046691319,0,0,{"$f":"SUM(AL7748:AP7748)","v":3479.1978886663037},{"$f":"IF($K7748=\"ON\",$N7748-AF7748,0)","v":356.64774332188676},{"$f":"IF($O7748=\"ON\",$R7748-AG7748,0)","v":0},{"$f":"IF($S7748=\"ON\",$V7748-AH7748,0)","v":0},{"$f":"IF($W7748=\"ON\",$Z7748-AI7748,0)","v":0},{"$f":"IF($AA7748=\"ON\",$AD7748-AJ7748,0)","v":0},{"$f":"IF($K7748=\"ON\",$N7748-AL7748,0)","v":239.33551600282794},{"$f":"IF($O7748=\"ON\",$R7748-AM7748,0)","v":0},{"$f":"IF($S7748=\"ON\",$V7748-AN7748,0)","v":0},{"$f":"IF($W7748=\"ON\",$Z7748-AO7748,0)","v":0},{"$f":"IF($AA7748=\"ON\",$AD7748-AP7748,0)","v":0},{"$f":"SUM(AR7748:AV7748)+BN7748","v":344.95933393462838},{"$f":"SUM(AW7748:BA7748)+BN7748","v":227.64710661556958},null,null,{"$f":"N7748+R7748+V7748+Z7748+AD7748","v":2167.7994009999998},null,46654.737500000047,{"$f":"19.5285952781395+42*-0.3035722016559+BH7748*0.0000340867411548605+J7748*0.0608468772796604","v":11.472061510664844},{"$f":"BH7748*1000/(500*BI7748)","v":8133.6275013219047},{"$f":"0.00000128*BJ7748^2+0*BJ7748+24.024","v":108.70354730273282},{"$f":"0.094*BH7748 + 3165.9","v":7551.4453250000042},{"$f":"0.00000128*BL7748^2+0*BL7748+24.024","v":97.015137915474455},{"$f":"BM7748-BK7748","v":-11.688409387258361},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF7748:AJ7748)","v":1830.0282566781132},{"$f":"A7748-AF7748","v":23.78943989691561},{"$f":"B7748-AG7748","v":0},{"$f":"C7748-AH7748","v":0},{"$f":"D7748-AI7748","v":0},{"$f":"E7748-AJ7748","v":0}]
[2408.1463602149961,0,2011.3166437841091,0,0,4419.4630039991052,5332.0888620000005,"2013-12-19T17:00:00",71,62,"ON",53251.063285770004,61115.081538028011,2868.39,"OFF",-0.50631590879999955,-107.1531286979,-8.8484060000000007,"ON",45183.656701574997,66227.368629611999,2479.4140000000002,"OFF",-2.7633803461600084,-158.64239131086001,-1.7696810000000001,"OFF",-3.8242782848899961,-117.50465664162,-5.0970510000000004,null,2372.7940561790956,0,1986.0174283940335,0,0,4358.8114845731288,2577.1314256724399,0,2102.8259549453264,0,0,4679.9573806177668,495.59594382090427,0,493.39657160596676,0,0,291.25857432755993,0,376.58804505467378,0,0,942.4301079942685,621.28421194963119,null,null,5332.0888620000005,null,86224.143900000025,13.490169274349389,12783.256035778466,233.19089264162122,11270.969526600002,186.62848520901872,-46.562407432602498,null,null,null,null,null,null,null,null,null,4358.8114845731288,35.352304035900488,0,25.299215390075688,0,0]
[0,0,2445.2994093883503,0,0,2445.2994093883503,3324.3056799999999,"2013-12-20T08:00:00",63,61,"OFF",-4.5157342007050127,-93.779350502980009,2.8527049999999998,"OFF",-6.1831083684499708,-120.73865691042,-8.8484060000000007,"ON",56463.688033145008,53432.421941136003,3337.97,"OFF",-4.0268115846000141,-166.99199929652002,-2.5715680000000001,"OFF",-6.9113207239999994,-118.98177343106001,-5.0970510000000004,null,0,0,2405.5873708842364,0,0,2405.5873708842364,0,0,2721.6082441263943,0,0,2721.6082441263943,0,0,932.38262911576339,0,0,0,0,616.36175587360549,0,0,908.86481876857965,592.84394552642175,null,null,3324.3056799999999,null,64707.210300000093,12.695880251000212,10193.418498083629,157.02339926665408,9248.3777682000091,133.50558891947031,-23.517810347183769,null,null,null,null,null,null,null,null,null,2405.5873708842364,0,0,39.712038504113934,0,0]
[0,0,1665.0955022400399,0,0,1665.0955022400399,1931.6636270000001,"2013-12-21",35,34,"OFF",-7.0924363089300018,-73.754793005267999,3.050497,"OFF",-10.059270124949995,-109.72966120372001,-8.8484060000000007,"ON",39705.537242420018,73592.51549178001,1943.213,"OFF",-7.2467062005099745,-158.64239131086001,-1.7696810000000001,"OFF",-8.8038100773000121,-118.98177343106001,-3.9817830000000001,null,0,0,1645.7897746210976,0,0,1645.7897746210976,0,0,1708.3404007219845,0,0,1708.3404007219845,0,0,297.42322537890232,0,0,0,0,234.87259927801551,0,0,296.96822699798895,234.41760089710215,null,null,1931.6636270000001,null,29282.587499999994,9.8455046165572071,5948.4178090283758,69.315103271380409,5918.4632249999995,68.860104890467056,-0.45499838091335221,null,null,null,null,null,null,null,null,null,1645.7897746210976,0,0,19.305727618942228,0,0]
[0,0,1703.7944639134569,0,0,1703.7944639134569,2020.7143410000001,"2013-12-21T15:00:00",51,50,"OFF",-7.6491238586699986,-73.754793005267999,2.8254139999999999,"OFF",-4.4747533156200063,-107.13492140472,-8.8484060000000007,"ON",40943.429204745,71109.34549372,2036.913,"OFF",-8.2457412379299733,-158.64239131086001,-3.9817830000000001,"OFF",-7.7832169465399907,-118.28596608156001,-6.1938839999999997,null,0,0,1683.2664487914701,0,0,1683.2664487914701,0,0,1758.628811699203,0,0,1758.628811699203,0,0,353.6465512085299,0,0,0,0,278.28418830079704,0,0,350.12516362296628,274.76280071523342,null,null,2020.7143410000001,null,39527.769900000014,11.168279533584904,7078.5781786949956,88.160024360828118,6881.5103706000009,84.638636775264473,-3.5213875855636445,null,null,null,null,null,null,null,null,null,1683.2664487914701,0,0,20.528015121986755,0,0]
[0,0,1490.3969725030538,0,0,1490.3969725030538,1748.5701320000001,"2013-12-22T07:00:00",35,33,"OFF",-6.5061649573900189,-74.450592333934011,2.631103,"OFF",-8.6027181717199852,-106.43911405522,-8.8484060000000007,"ON",33762.262842879987,72734.703337148007,1762.751,"OFF",-8.2938827427400135,-158.64239131086001,-1.7696810000000001,"OFF",-8.2549168184699688,-120.37338813006001,-6.1938839999999997,null,0,0,1476.4100559665599,0,0,1476.4100559665599,0,0,1523.7363939418192,0,0,1523.7363939418192,0,0,286.34094403344011,0,0,0,0,239.01460605818079,0,0,285.32089964787224,237.99456167261292,null,null,1748.5701320000001,null,29282.587499999994,9.7846577392775451,5985.4086428499004,69.880149276034928,5918.4632249999995,68.860104890467056,-1.0200443855678714,null,null,null,null,null,null,null,null,null,1476.4100559665599,0,0,13.986916536493936,0,0]
[0,0,1526.9209140415937,0,0,1526.9209140415937,1826.828332,"2013-12-22T21:00:00",33,30,"OFF",-6.0345265911299908,-71.667395019270003,2.5811999999999999,"OFF",-10.741696052509992,-106.43911405522,-8.8484060000000007,"ON",35057.839143384997,74106.450430330005,1840.248,"OFF",-11.450508476820003,-161.70394364866002,-3.1706789999999998,"OFF",-7.7475565693400137,-119.67758078056001,-3.9817830000000001,null,0,0,1511.8513861503513,0,0,1511.8513861503513,0,0,1559.3707060146355,0,0,1559.3707060146355,0,0,328.3966138496487,0,0,0,0,280.87729398536453,0,0,323.68948707448271,276.17016721019854,null,null,1826.828332,null,30551.57130000004,9.645372629758878,6334.9696217519358,75.392755338905431,6037.7477022000039,70.685628563739428,-4.7071267751660031,null,null,null,null,null,null,null,null,null,1511.8513861503513,0,0,15.069527891242387,0,0]
[0,0,0,1941.6685889407761,0,1941.6685889407761,2263.4464289999996,"2013-12-23T12:00:00",38,34,"OFF",-14.911982627570007,-72.363194347936002,3.3185669999999998,"OFF",-12.340331016749982,-108.5447433969,-8.8484060000000007,"OFF",-0.18387544849499812,-62.795943552736006,-1.7696810000000001,"ON",34039.810488490009,68155.745560726005,2275.8429999999998,"OFF",-8.1388018506199824,-120.37338813006001,-5.0970510000000004,null,0,0,0,1926.8747735590352,0,1926.8747735590352,0,0,1463.033293423611,1989.3322889828451,0,3452.3655824064563,0,0,0,348.9682264409646,0,0,0,0,286.51071101715479,0,349.47685521470839,287.01933979089858,null,null,2263.4464289999996,null,28563.352800000052,9.820988249508714,5816.798080667475,67.332979086408727,5850.8551632000053,67.841607860152536,0.50862877374380844,null,null,null,null,null,null,null,null,null,1926.8747735590352,0,0,0,14.793815381740842,0]
[0,0,0,1754.922396769852,0,1754.922396769852,2075.5427549999995,"2013-12-24T04:00:00",26,25,"OFF",-19.970898332400001,-73.058993676602014,3.5026250000000001,"OFF",-13.943051741905018,-108.05346731440001,-8.8484060000000007,"OFF",0.28810538612499803,-33.398399859304,-1.7696810000000001,"ON",27328.514349759997,68502.101214514012,2086.64,"OFF",-8.8383820361899978,-118.28596608156001,-3.9817830000000001,null,0,0,0,1745.245139524209,0,1745.245139524209,0,0,1463.033293423611,1785.417440029878,0,3248.4507334534892,0,0,0,341.39486047579089,0,0,0,0,301.22255997012189,0,314.13793373611719,273.96563323044819,null,null,2075.5427549999995,null,40439.402400000021,9.6781821826492553,8356.8177653234343,113.41459604841647,6967.2038256000014,86.157669308742783,-27.256926739673688,null,null,null,null,null,null,null,null,null,1745.245139524209,0,0,0,9.6772572456429771,0]
[0,0,0,1938.9484534432586,0,1938.9484534432586,2081.0212999999999,"2013-12-24T19:00:00",46,40,"OFF",-23.81178431015999,-72.111837452044,3.0471699999999999,"OFF",-12.684373800959996,-104.36997950824001,-8.8484060000000007,"OFF",9.0866618875000832E-2,-33.398399859304,-1.7696810000000001,"ON",33948.086783590006,69587.095471362001,2092.5740000000001,"OFF",-8.5278820375699578,-118.28596608156001,-3.9817830000000001,null,0,0,0,1924.2322602634401,0,1924.2322602634401,0,0,1463.033293423611,1982.3286294524069,0,3445.3619228760181,0,0,0,168.34173973655993,0,0,0,0,110.24537054759321,0,166.61078304184255,108.51441385287583,null,null,2081.0212999999999,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,1924.2322602634401,0,0,0,14.716193179818447,0]
[0,0,0,0,0,0,-14.992103,"2013-12-25T10:00:00",47,43,"OFF",-27.803452386780016,-166.99199929652002,3.58955,"OFF",-12.851162592454999,-166.99199929652002,-8.8484060000000007,"OFF",-0.49403380812500736,-166.99199929652002,-1.7696810000000001,"OFF",2.1851289378100027,-166.99199929652002,-3.9817830000000001,"OFF",-8.2240895860899972,-120.37338813006001,-3.9817830000000001,null,0,0,0,0,0,0,0,0,1463.033293423611,0,0,1463.033293423611,0,0,0,0,0,0,0,0,0,0,-1.3146555314168893,-1.3146555314168893,null,null,-14.992103,null,33987.03270000004,10.553485717883778,6440.911298606512,77.125233096341788,6360.681073800004,75.810577564924898,-1.3146555314168893,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,0,0,0,1331.8585239999998,"2013-12-26T02:00:00",34,32,"OFF",0.44078330183999503,-79.877841535030015,2.9388230000000002,"check",19939.347734204996,54359.718580710003,1338.3579999999999,"OFF",-1.8701937967500179E-2,-45.922803816960005,-1.7696810000000001,"OFF",-2.2607008238499882,-163.93044695872001,-2.5807850000000001,"OFF",1.9723366721099933,-119.67758078056001,-5.0878329999999998,null,0,0,0,0,0,0,0,0,1463.033293423611,0,0,1463.033293423611,0,0,0,0,0,0,0,0,0,0,-2.3886834235928092,-2.3886834235928092,null,null,1331.8585239999998,null,29835.629600000044,9.7426622649083274,6124.7385547713593,72.039900626307542,5970.4491824000042,69.651217202714733,-2.3886834235928092,null,null,null,null,null,null,null,null,null,0,0,0,0,0,0]
[0,0,0,2158.9646767274239,0,2158.9646767274239,2429.2481839999996,"2013-12-26T17:00:00",50,42,"OFF",-4.2409582784100044,-72.614551243828004,2.9490539999999998,"OFF",-4.1198433831499974,-107.1531286979,-8.8484060000000007,"OFF",7.6239423749984575E-3,-33.398399859304,-1.7696810000000001,"ON",40915.260223550009,70534.636695952009,2440.8989999999999,"OFF",-3.4076886641000059,-118.37299213046002,-3.9817830000000001,null,0,0,0,2137.7317639131356,0,2137.7317639131356,0,0,1509.7879541167799,2217.8933455787928,0,3727.6812996955728,0,0,0,303.16723608686425,0,0,0,0,223.00565442120705,0,295.86398141194013,215.70239974628294,null,null,2429.2481839999996,null,37984.500000000058,10.628899473734236,7147.40036705889,89.413224969002954,6736.4430000000057,82.109970294078821,-7.3032546749241334,null,null,null,null,null,null,null,null,null,2137.7317639131356,0,0,0,21.232912814288284,0]
[0,0,0,2115.6707160617443,0,2115.6707160617443,2196.8012569999996,"2013-12-26T21:00:00",41,37,"OFF",-5.4645482714900027,-73.058993676602014,2.7651270000000001,"OFF",-6.9251842607999814,-113.41531463506001,-8.8484060000000007,"OFF",-5.6182960952000274E-2,-45.922803816960005,-1.7696810000000001,"ON",39610.061800000003,70420.243561444004,2208.636,"OFF",-2.9174009304300013,-118.98177343106001,-3.9817830000000001,null,0,0,0,2095.7552457624711,0,2095.7552457624711,0,0,1509.7879541167799,2171.3494392660145,0,3681.1373933827945,0,0,0,112.88075423752889,0,0,0,0,37.286560733985425,0,114.19477740700671,38.600583903463246,null,null,2196.8012569999996,null,29175.192900000024,10.024384516464558,5820.8447315805197,67.393258738135927,5908.3681326000024,68.707281907613748,1.3140231694778208,null,null,null,null,null,null,null,null,null,2095.7552457624711,0,0,0,19.915470299273238,0]
[0,0,0,2067.3809448581383,0,2067.3809448581383,2189.795944,"2013-12-26T22:00:00",43,39,"OFF",-6.0669099572900027,-74.450592333934011,2.8388640000000001,"OFF",-7.2162147653700055,-105.27023791640001,-8.8484060000000007,"OFF",0.28001299875000063,-62.621995725778007,-1.7696810000000001,"ON",38118.787978325003,70596.004096885998,2202.663,"OFF",-3.7892122473100263,-118.37299213046002,-5.0878329999999998,null,0,0,0,2048.9158352231134,0,2048.9158352231134,0,0,1509.7879541167799,2118.4008313130703,0,3628.1887854298502,0,0,0,153.74716477688662,0,0,0,0,84.262168686929726,0,154.75877586550001,85.273779775543105,null,null,2189.795944,null,30272.564300000085,10.183484085886429,5945.4237949771377,69.269522050406849,6011.521044200008,70.281133139020227,1.0116110886133782,null,null,null,null,null,null,null,null,null,2048.9158352231134,0,0,0,18.465109635024874,0]
[0,0,0,2007.6045481383817,0,2007.6045481383817,2139.3237589999999,"2013-12-26T23:00:00",39,36,"OFF",-6.3063173733300006,-74.450592333934011,3.1706789999999998,"OFF",-7.7880798169499972,-104.16544824124001,-8.8484060000000007,"OFF",0.39621078099999524,-33.398399859304,-1.7696810000000001,"ON",36216.792052019999,70780.948487258007,2151.8589999999999,"OFF",-3.2074386649900006,-120.28644228950002,-5.0878329999999998,null,0,0,0,1990.90493704092,0,1990.90493704092,0,0,1509.7879541167799,2053.172757030206,0,3562.9607111469859,0,0,0,160.95406295907992,0,0,0,0,98.686242969793966,0,162.43929997940299,100.17147999011704,null,null,2139.3237589999999,null,28624.403100000054,9.9447630098415623,5756.678780916689,66.442368750920267,5856.5938914000053,67.927605771243336,1.4852370203230691,null,null,null,null,null,null,null,null,null,1990.90493704092,0,0,0,16.699611097461684,0]
[0,0,0,1984.1079398965917,0,1984.1079398965917,2087.2725030000001,"2013-12-27",42,38,"OFF",-6.643906690220005,-70.971595690604005,2.9490539999999998,"OFF",-8.1139823316750217,-107.1531286979,-8.8484060000000007,"OFF",0.30249835874999814,-62.621995725778007,-2.4333119999999999,"ON",35450.967036240021,71020.859653032006,2100.6930000000002,"OFF",-4.1061526985499714,-120.37338813006001,-5.0878329999999998,null,0,0,0,1968.0926842992617,0,1968.0926842992617,0,0,1509.7879541167799,2027.1104263796042,0,3536.8983804963841,0,0,0,132.60031570073852,0,0,0,0,73.582573620396033,0,133.84016204720589,74.822419966863407,null,null,2087.2725030000001,null,29657.431200000021,10.10166932585128,5871.7881655665378,68.155707214447688,5953.6985328000019,69.395553560915062,1.2398463464673739,null,null,null,null,null,null,null,null,null,1968.0926842992617,0,0,0,16.015255597329997,0]
[0,0,0,1909.7236319496285,0,1909.7236319496285,2060.3746799999999,"2013-12-27T01:00:00",38,35,"OFF",-7.0726168223499837,-72.363194347936002,3.26755,"OFF",-8.1707790341700086,-109.93635809590002,-8.8484060000000007,"OFF",-5.9024070000012223E-3,-33.398399859304,-1.7696810000000001,"ON",32952.476787,70989.682671274,2071.7069999999999,"OFF",-3.2919948380500013,-118.98177343106001,-3.9817830000000001,null,0,0,0,1895.8361403332826,0,1895.8361403332826,0,0,1509.7879541167799,1947.0778651878954,0,3456.8658193046754,0,0,0,175.87085966671725,0,0,0,0,124.62913481210444,0,176.91119191453521,125.66946705992241,null,null,2060.3746799999999,null,28563.352800000052,9.8818351267883742,5780.9814540557363,66.801275612334564,5850.8551632000053,67.841607860152536,1.0403322478179717,null,null,null,null,null,null,null,null,null,1895.8361403332826,0,0,0,13.887491616345869,0]
[0,0,0,1916.8780524874592,0,{"$f":"SUM(A7940:E7940)","v":1916.8780524874592},{"$f":"N7940+R7940+V7940+Z7940+AD7940","v":2042.139324},"2013-12-27T02:00:00",35,33,"OFF",-7.2165090661300129,-72.363194347936002,2.8028249999999999,"OFF",-7.959537050000014,-103.85969404916001,-8.8484060000000007,"OFF",0.27018618288000323,-33.398399859304,-2.4333119999999999,"ON",33197.949833200015,70413.56220672201,2054.6,"OFF",-3.9751028664499928,-118.28596608156001,-3.9817830000000001,null,0,0,0,1902.7885916304201,0,{"$f":"SUM(AF7940:AJ7940)","v":1902.7885916304201},0,0,1509.7879541167799,1956.2498178033156,0,{"$f":"SUM(AL7940:AP7940)","v":3466.0377719200956},{"$f":"IF($K7940=\"ON\",$N7940-AF7940,0)","v":0},{"$f":"IF($O7940=\"ON\",$R7940-AG7940,0)","v":0},{"$f":"IF($S7940=\"ON\",$V7940-AH7940,0)","v":0},{"$f":"IF($W7940=\"ON\",$Z7940-AI7940,0)","v":151.81140836957979},{"$f":"IF($AA7940=\"ON\",$AD7940-AJ7940,0)","v":0},{"$f":"IF($K7940=\"ON\",$N7940-AL7940,0)","v":0},{"$f":"IF($O7940=\"ON\",$R7940-AM7940,0)","v":0},{"$f":"IF($S7940=\"ON\",$V7940-AN7940,0)","v":0},{"$f":"IF($W7940=\"ON\",$Z7940-AO7940,0)","v":98.350182196684273},{"$f":"IF($AA7940=\"ON\",$AD7940-AP7940,0)","v":0},{"$f":"SUM(AR7940:AV7940)+BN7940","v":150.79136398401192},{"$f":"SUM(AW7940:BA7940)+BN7940","v":97.330137811116401},null,null,{"$f":"N7940+R7940+V7940+Z7940+AD7940","v":2042.139324},null,29282.587499999994,{"$f":"19.5285952781395+42*-0.3035722016559+BH7940*0.0000340867411548605+J7940*0.0608468772796604","v":9.7846577392775451},{"$f":"BH7940*1000/(500*BI7940)","v":5985.4086428499004},{"$f":"0.00000128*BJ7940^2+0*BJ7940+24.024","v":69.880149276034928},{"$f":"0.094*BH7940 + 3165.9","v":5918.4632249999995},{"$f":"0.00000128*BL7940^2+0*BL7940+24.024","v":68.860104890467056},{"$f":"BM7940-BK7940","v":-1.0200443855678714},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF7940:AJ7940)","v":1902.7885916304201},{"$f":"A7940-AF7940","v":0},{"$f":"B7940-AG7940","v":0},{"$f":"C7940-AH7940","v":0},{"$f":"D7940-AI7940","v":14.089460857039057},{"$f":"E7940-AJ7940","v":0}]
[0,0,0,1953.4048372443795,0,1953.4048372443795,2027.9730220000001,"2013-12-27T03:00:00",33,32,"OFF",-7.5474917929599989,-70.971595690604005,3.0969419999999999,"OFF",-9.2456702022799693,-107.64448498874,-8.8484060000000007,"OFF",2.8644825040001601E-2,-33.398399859304,-1.7696810000000001,"ON",34433.765294129997,70567.754719538018,2040.5820000000001,"OFF",-3.8081462094900034,-120.37338813006001,-5.0878329999999998,null,0,0,0,1938.2751803848982,0,1938.2751803848982,0,0,1509.7879541167799,1995.264742617228,0,3505.0526967340079,0,0,0,102.30681961510186,0,0,0,0,45.317257382772141,0,98.871786706448887,41.88222447411917,null,null,2027.9730220000001,null,{"$f":" -0.6251*I7941^3 + 145.21*I7941^2 - 8340.3*I7941 + 170112","v":30551.57130000004},9.7670663843181984,6256.0384250183888,74.120661472392399,6037.7477022000039,70.685628563739428,-3.4350329086529712,null,null,null,null,null,null,null,null,null,1938.2751803848982,0,0,0,15.129656859481202,0]
[0,0,0,1922.4187854088918,0,1922.4187854088918,2036.752426,"2013-12-27T04:00:00",36,34,"OFF",-8.1605315325600127,-73.754793005267999,3.0862959999999999,"OFF",-10.105043436599978,-108.56367256514001,-8.8484060000000007,"OFF",3.9574815776999617E-2,-33.398399859304,-1.7696810000000001,"ON",33387.272484300018,70550.221176413994,2048.2660000000001,"OFF",-3.9481744830500056,-117.59015873206,-3.9817830000000001,null,0,0,0,1908.1725041903644,0,1908.1725041903644,0,0,1509.7879541167799,1961.8743009887201,0,3471.6622551054998,0,0,0,140.09349580963567,0,0,0,0,86.391699011280025,0,140.16905425675372,86.467257458398066,null,null,2036.752426,null,28888.694400000008,9.832078084414821,5876.4167965249399,68.225311189094967,5881.4372736000005,68.300869636213008,7.5558447118041272E-2,null,null,null,null,null,null,null,null,null,1908.1725041903644,0,0,0,14.246281218527429,0]
[0,0,0,1915.812301401626,0,1915.812301401626,2006.8352049999999,"2013-12-27T05:00:00",32,30,"OFF",-8.0662130732400126,-73.058993676602014,2.7380749999999998,"OFF",-9.2573265275899974,-108.73034549566,-8.8484060000000007,"OFF",0.33115548162499914,-33.398399859304,-1.7696810000000001,"ON",33161.455778620009,70768.002861182002,2018.6969999999999,"OFF",-3.6413065875899848,-117.59015873206,-3.9817830000000001,null,0,0,0,1901.7529642355696,0,1901.7529642355696,0,0,1509.7879541167799,1954.1925391776092,0,3463.9804932943889,0,0,0,116.94403576443028,0,0,0,0,64.504460822390683,0,110.85489366887633,58.41531872683673,null,null,2006.8352049999999,null,31434.163200000039,9.675457311399553,6497.7111031154127,78.065919461823114,6120.7113408000041,71.976777366269161,-6.089142095553953,null,null,null,null,null,null,null,null,null,1901.7529642355696,0,0,0,14.059337166056366,0]
[0,0,0,1911.1312681540494,0,1911.1312681540494,1982.890304,"2013-12-27T06:00:00",32,31,"OFF",-8.7312668907099962,-73.754793005267999,2.7792750000000002,"OFF",-10.235385911525,-107.66341415698001,-8.8484060000000007,"OFF",-0.13048535474999462,-33.398399859304,-1.7696810000000001,"ON",33000.864504300007,70569.559407188004,1996.923,"OFF",-4.9199009215299938,-117.59015873206,-6.1938839999999997,null,0,0,0,1897.2040859045435,0,1897.2040859045435,0,0,1509.7879541167799,1949.6518537084878,0,3459.439807825268,0,0,0,99.718914095456512,0,0,0,0,47.271146291512196,0,94.303129558359657,41.855361754415341,null,null,1982.890304,null,31434.163200000039,9.7363041886792132,6457.1037615175974,77.392561903366015,6120.7113408000041,71.976777366269161,-5.4157845370968545,null,null,null,null,null,null,null,null,null,1897.2040859045435,0,0,0,13.927182249505904,0]
[0,0,0,1947.7589162833358,0,1947.7589162833358,1990.7597369999999,"2013-12-27T07:00:00",33,31,"OFF",-9.3180445120200073,-73.754793005267999,2.677657,"OFF",-10.28981765694,-105.96604526590001,-8.8484060000000007,"OFF",-0.35628358901999913,-33.398399859304,-1.7696810000000001,"ON",34244.608467559992,70994.142254978011,2003.788,"OFF",-4.0394716801599788,-119.59063494000002,-5.0878329999999998,null,0,0,0,1932.7910100824229,0,1932.7910100824229,0,0,1509.7879541167799,1988.0144072952089,0,3497.8023614119888,0,0,0,70.996989917577139,0,0,0,0,15.773592704791099,0,66.931890925785495,11.708493712999456,null,null,1990.7597369999999,null,30551.57130000004,9.7062195070385382,6295.2566192935019,74.750727555531071,6037.7477022000039,70.685628563739428,-4.0650989917916434,null,null,null,null,null,null,null,null,null,1932.7910100824229,0,0,0,14.967906200912921,0]
[0,0,0,1834.2026538207901,0,1834.2026538207901,2089.1422889999999,"2013-12-27T08:00:00",35,33,"OFF",-9.0034100005500086,-72.355366013952008,2.6811590000000001,"OFF",-10.920745359680028,-111.12344152790001,-8.8484060000000007,"OFF",-2.5259437175000368E-2,-75.14639166260001,-1.7696810000000001,"ON",30287.664298080006,70829.506616294006,2101.0610000000001,"OFF",-5.7243395971999904,-119.76460682946001,-3.9817830000000001,null,0,0,0,1822.409253225308,0,1822.409253225308,0,0,1509.7879541167799,1866.2531062543608,0,3376.0410603711407,0,0,0,278.65174677469213,0,0,0,0,234.80789374563938,0,277.63170238912426,233.7878493600715,null,null,2089.1422889999999,null,29282.587499999994,9.7846577392775451,5985.4086428499004,69.880149276034928,5918.4632249999995,68.860104890467056,-1.0200443855678714,null,null,null,null,null,null,null,null,null,1822.409253225308,0,0,0,11.793400595482126,0]
[0,0,0,2009.513229407567,0,2009.513229407567,2142.8329409999997,"2013-12-27T09:00:00",41,38,"OFF",-9.5647710396700099,-72.37102268192001,3.1338110000000001,"OFF",-10.913584101349992,-107.8489360474,-8.8484060000000007,"OFF",-0.49292840446000258,-33.398399859304,-1.7696810000000001,"ON",36278.536237319982,70655.422435158005,2154.299,"OFF",-4.7714433750200191,-120.37338813006001,-3.9817830000000001,null,0,0,0,1992.7577815436459,0,1992.7577815436459,0,0,1509.7879541167799,2055.6159608108196,0,3565.4039149275995,0,0,0,161.54121845635404,0,0,0,0,98.683039189180363,0,163.37697946561369,100.51880019844,null,null,2142.8329409999997,null,29175.192900000024,10.08523139374422,5785.7260306584812,66.871520898354106,5908.3681326000024,68.707281907613748,1.8357610092596417,null,null,null,null,null,null,null,null,null,1992.7577815436459,0,0,0,16.755447863921063,0]
[0,0,0,1974.685767780426,0,1974.685767780426,2098.5654039999999,"2013-12-27T10:00:00",45,41,"OFF",-10.094128811639996,-71.667395019270003,3.181324,"OFF",-10.881916594080016,-108.5447433969,-8.8484060000000007,"OFF",-0.25782041687500445,-33.398399859304,-1.7696810000000001,"ON",35140.833412475004,70941.108500570001,2111.09,"OFF",-4.2777169621200084,-118.28596608156001,-5.0878329999999998,null,0,0,0,1958.9433446903565,0,1958.9433446903565,0,0,1509.7879541167799,2017.1799653132844,0,3526.9679194300643,0,0,0,152.14665530964362,0,0,0,0,93.91003468671579,0,152.26726390072255,94.030643277794724,null,null,2098.5654039999999,null,31886.51250000007,10.360192074976503,6155.583268966061,72.524742887903869,6163.2321750000065,72.645351478982803,0.12060859107893407,null,null,null,null,null,null,null,null,null,1958.9433446903565,0,0,0,15.742423090069451,0]
[0,0,0,2043.2163725961479,0,2043.2163725961479,2186.1602120000002,"2013-12-27T11:00:00",50,44,"OFF",-10.300253077030005,-73.754793005267999,3.2071320000000001,"OFF",-10.864550343839982,-105.04685768950002,-8.8484060000000007,"OFF",-0.58308520262499786,-33.398399859304,-1.7696810000000001,"ON",37357.654475255011,70371.541057395996,2198.6590000000001,"OFF",-5.2824480897299937,-120.37338813006001,-5.0878329999999998,null,0,0,0,2025.4690758696186,0,2025.4690758696186,0,0,1509.7879541167799,2092.9757758805936,0,3602.7637299973735,0,0,0,173.18992413038154,0,0,0,0,105.68322411940653,0,167.35866676698845,99.851966756013425,null,null,2186.1602120000002,null,37984.500000000058,10.750593228293559,7066.4937633454365,87.941227657471927,6736.4430000000057,82.109970294078821,-5.8312573633931066,null,null,null,null,null,null,null,null,null,2025.4690758696186,0,0,0,17.747296726529385,0]
[0,0,0,2146.5731967446877,0,2146.5731967446877,2295.4314409999997,"2013-12-27T12:00:00",53,46,"OFF",-10.495432422540016,-73.058993676602014,3.0969419999999999,"OFF",-11.247383759699984,-101.81021054548,-8.8484060000000007,"OFF",-0.10819998123099911,-62.621995725778007,-2.4333119999999999,"ON",40544.641668634998,70822.696928228004,2307.598,"OFF",-5.215075448519995,-118.98177343106001,-3.9817830000000001,null,0,0,0,2125.7189574829431,0,2125.7189574829431,0,0,1509.7879541167799,2203.355059957245,0,3713.1430140740249,0,0,0,181.87904251705686,0,0,0,0,104.24294004275498,0,170.88132549200793,93.245223017706067,null,null,2295.4314409999997,null,42907.977300000086,11.040112279159811,7773.1052393364844,101.36309127910438,7199.249866200008,90.365374254055467,-10.997717025048914,null,null,null,null,null,null,null,null,null,2125.7189574829431,0,0,0,20.854239261744624,0]
[0,0,0,2234.8955388409577,0,2234.8955388409577,2418.1713210000003,"2013-12-27T13:00:00",54,45,"OFF",-10.115065066189997,-74.450592333934011,2.999241,"OFF",-11.757366882309995,-107.64448498874,-8.8484060000000007,"OFF",-0.7924215619999988,-33.398399859304,-1.7696810000000001,"ON",43137.425574109984,70717.206919460004,2430.8780000000002,"OFF",-4.8094386578699835,-116.28557008196,-5.0878329999999998,null,0,0,0,2211.3155677765958,0,2211.3155677765958,0,0,1509.7879541167799,2299.5741832550116,0,3809.3621373717915,0,0,0,219.56243222340436,0,0,0,0,131.30381674498858,0,205.05947542746623,116.80085994905045,null,null,2418.1713210000003,null,44737.413600000087,11.041624923497556,8103.4112116586939,108.07554977950186,7371.2168784000078,93.572592983563723,-14.502956795938132,null,null,null,null,null,null,null,null,null,2211.3155677765958,0,0,0,23.579971064361871,0]
[0,0,0,2222.0559397461247,0,2222.0559397461247,2456.370543,"2013-12-27T14:00:00",55,46,"OFF",-10.291137237720003,-73.058993676602014,2.8624130000000001,"OFF",-11.552922865119985,-108.05346731440001,-8.8484060000000007,"OFF",9.7549129260003378E-2,-62.621995725778007,-1.7696810000000001,"ON",42767.364912859994,70873.067765747997,2468.1080000000002,"OFF",-4.9129811102399996,-118.11207440044001,-3.9817830000000001,null,0,0,0,2198.8759730299098,0,2198.8759730299098,0,0,1509.7879541167799,2284.9786712818855,0,3794.7666253986654,0,0,0,269.23202697009037,0,0,0,0,183.12932871811472,0,252.86708733365907,166.76438908168342,null,null,2456.370543,null,46654.737500000047,11.167827124266543,8355.2041020807137,113.38007755190577,7551.4453250000042,97.015137915474455,-16.364939636431316,null,null,null,null,null,null,null,null,null,2198.8759730299098,0,0,0,23.179966716214949,0]
[0,0,0,2177.4314284667248,0,2177.4314284667248,2518.4461970000002,"2013-12-27T15:00:00",56,46,"OFF",-10.311025858155004,-72.363194347936002,2.940067,"OFF",-11.999710753279993,-108.34029233824,-8.8484060000000007,"OFF",8.3667219490001291E-2,-62.621995725778007,-1.7696810000000001,"ON",41463.321240320001,70273.149486718001,2530.1060000000002,"OFF",-5.5310518622099938,-119.76460682946001,-3.9817830000000001,null,0,0,0,2155.6318678984835,0,2155.6318678984835,0,0,1509.7879541167799,2238.9829424752174,0,3748.7708965919974,0,0,0,374.47413210151672,0,0,0,0,291.12305752478278,0,355.13704226176554,271.78596768503161,null,null,2518.4461970000002,null,48656.198400000052,11.236050403896417,8660.7298207076656,120.03454851493765,7739.5826496000045,100.69745867518647,-19.337089839751187,null,null,null,null,null,null,null,null,null,2155.6318678984835,0,0,0,21.799560568241304,0]
[0,0,0,2321.1455930509428,0,2321.1455930509428,2612.8322599999997,"2013-12-27T16:00:00",57,46,"OFF",-10.540693290045004,-73.058993676602014,2.8251300000000001,"OFF",-11.726477766405015,-105.06578685774001,-8.8484060000000007,"OFF",-0.13439687049999632,-33.398399859304,-1.7696810000000001,"ON",45567.373403424994,70374.316265960006,2624.607,"OFF",-5.2582499766300055,-119.67758078056001,-3.9817830000000001,null,0,0,0,2294.8475747407233,0,2294.8475747407233,0,0,1509.7879541167799,2394.9534828020714,0,3904.7414369188514,0,0,0,329.75942525927667,0,0,0,0,229.65351719792852,0,307.26330002424299,207.15739196289485,null,null,2612.8322599999997,null,50738.045700000075,11.307013793935463,8974.6146285261493,127.1199458951111,7935.2762958000076,104.62382066007743,-22.496125235033674,null,null,null,null,null,null,null,null,null,2294.8475747407233,0,0,0,26.298018310219504,0]
[0,0,0,2333.0684636438259,0,2333.0684636438259,2673.3027889999998,"2013-12-27T17:00:00",56,46,"OFF",-10.693079104859997,-72.363194347936002,3.0596589999999999,"OFF",-11.524586768749998,-104.57443056690002,-8.8484060000000007,"OFF",5.4622146226500481E-2,-33.398399859304,-1.7696810000000001,"ON",45895.975512944999,70141.086454908,2684.8429999999998,"OFF",-6.3942028017700148,-118.37299213046002,-3.9817830000000001,null,0,0,0,2306.3906332924557,0,2306.3906332924557,0,0,1509.7879541167799,2409.0931917204143,0,3918.8811458371943,0,0,0,378.45236670754412,0,0,0,0,275.74980827958552,0,359.11527686779294,256.41271843983435,null,null,2673.3027889999998,null,48656.198400000052,11.236050403896417,8660.7298207076656,120.03454851493765,7739.5826496000045,100.69745867518647,-19.337089839751187,null,null,null,null,null,null,null,null,null,2306.3906332924557,0,0,0,26.677830351370176,0]
[0,0,0,2294.5933075104481,0,2294.5933075104481,2558.3260329999998,"2013-12-27T18:00:00",53,44,"OFF",-10.091058673049993,-73.754793005267999,3.0609030000000002,"OFF",-12.340340628570019,-104.86125559074002,-8.8484060000000007,"OFF",-0.15810018750000598,-45.922803816960005,-1.7696810000000001,"ON",44829.360719575001,70237.946046292011,2569.8649999999998,"OFF",-6.3510282736600052,-114.02425635234002,-3.9817830000000001,null,0,0,0,2269.1376474558137,0,2269.1376474558137,0,0,1509.7879541167799,2366.6683702253285,0,3876.4563243421085,0,0,0,300.72735254418603,0,0,0,0,203.19662977467124,0,287.99602649483796,190.46530372532317,null,null,2558.3260329999998,null,42907.977300000086,10.91841852460049,7859.7421784708704,103.09670030340355,7199.249866200008,90.365374254055467,-12.731326049348084,null,null,null,null,null,null,null,null,null,2269.1376474558137,0,0,0,25.455660054634336,0]
[0,0,0,2231.0986315813548,0,2231.0986315813548,2490.1476069999999,"2013-12-27T19:00:00",48,41,"OFF",-10.28412685867,-72.363194347936002,3.096527,"OFF",-12.618010355600008,-106.45732134840001,-8.8484060000000007,"OFF",6.602045407050007E-2,-45.922803816960005,-1.7696810000000001,"ON",43028.225455379994,70185.201041908003,2502.7570000000001,"OFF",-6.6565612911699761,-119.59063494000002,-5.0878329999999998,null,0,0,0,2207.6370780339098,0,2207.6370780339098,0,0,1509.7879541167799,2297.7384104697262,0,3807.5263645865061,0,0,0,295.11992196609026,0,0,0,0,205.01858953027386,0,290.92926647501446,200.82793403919806,null,null,2490.1476069999999,null,35210.380800000043,10.473491913351447,6723.713751115688,81.890658056886011,6475.6757952000044,77.700002565810195,-4.190655491075816,null,null,null,null,null,null,null,null,null,2207.6370780339098,0,0,0,23.461553547444964,0]
[0,0,0,2173.1256938814249,0,2173.1256938814249,2379.994647,"2013-12-27T20:00:00",49,42,"OFF",-10.455429760350007,-74.442772020784005,2.6416179999999998,"OFF",-12.450999859200007,-104.55550139866,-8.8484060000000007,"OFF",9.4860112499321248E-4,-33.398399859304,-1.7696810000000001,"ON",41335.985021759996,70420.516269800006,2394.165,"OFF",-6.6530801591099884,-116.89443159090001,-6.1938839999999997,null,0,0,0,2151.4584991553797,0,2151.4584991553797,0,0,1509.7879541167799,2233.7157833811493,0,3743.5037374979293,0,0,0,242.70650084462022,0,0,0,0,160.44921661885064,0,237.39383772482262,155.13655349905304,null,null,2379.994647,null,36544.120100000058,10.579801616918271,6908.2807831787659,85.111159525423403,6601.047289400005,79.798496405625798,-5.3126631197976053,null,null,null,null,null,null,null,null,null,2151.4584991553797,0,0,0,21.667194726045182,0]
[0,0,0,2136.9230375817028,0,2136.9230375817028,2405.5982450000001,"2013-12-27T21:00:00",49,43,"OFF",-10.146527002010004,-71.675223353253998,3.1231650000000002,"OFF",-12.517796189599999,-106.27179945798001,-8.8484060000000007,"OFF",6.2334815995999014E-2,-33.398399859304,-1.7696810000000001,"ON",40254.391007224986,70576.385136922006,2418.181,"OFF",-7.3288914608999942,-116.98137743146002,-5.0878329999999998,null,0,0,0,2116.3628192189535,0,2116.3628192189535,0,0,1509.7879541167799,2193.8226566057037,0,3703.6106107224837,0,0,0,301.81818078104652,0,0,0,0,224.3583433942963,0,297.20215480074972,219.7423174139995,null,null,2405.5982450000001,null,36544.120100000058,10.640648494197933,6868.7768644790049,84.414522385922595,6601.047289400005,79.798496405625798,-4.6160259802967971,null,null,null,null,null,null,null,null,null,2116.3628192189535,0,0,0,20.56021836274931,0]
[0,0,0,2156.6195059209972,0,2156.6195059209972,2330.3165399999998,"2013-12-27T22:00:00",45,41,"OFF",-10.487153839819999,-72.363194347936002,2.8024100000000001,"OFF",-14.040435574999986,-106.45732134840001,-8.8484060000000007,"OFF",0.13447884837500571,-45.922803816960005,-1.7696810000000001,"ON",40845.296207799998,70220.131773978006,2342.114,"OFF",-7.3332169485399845,-118.37299213046002,-3.9817830000000001,null,0,0,0,2135.4583563113219,0,2135.4583563113219,0,0,1509.7879541167799,2216.5697585769681,0,3726.357712693748,0,0,0,206.65564368867808,0,0,0,0,125.54424142303196,0,206.77625227975702,125.6648500141109,null,null,2330.3165399999998,null,31886.51250000007,10.360192074976503,6155.583268966061,72.524742887903869,6163.2321750000065,72.645351478982803,0.12060859107893407,null,null,null,null,null,null,null,null,null,2135.4583563113219,0,0,0,21.161149609675249,0]
[0,0,0,2033.2934245068527,0,2033.2934245068527,2167.2852120000002,"2013-12-27T23:00:00",42,39,"OFF",-10.724885540819983,-73.058993676602014,3.1938140000000002,"OFF",-13.235923132474991,-107.1531286979,-8.8484060000000007,"OFF",8.1909065146500343E-2,-33.398399859304,-2.4333119999999999,"ON",37042.099552500018,70407.025227012011,2181.567,"OFF",-6.6566037439999901,-118.199020241,-6.1938839999999997,null,0,0,0,2015.8392943940648,0,2015.8392943940648,0,0,1509.7879541167799,2082.1151273687033,0,3591.9030814854832,0,0,0,165.72770560593517,0,0,0,0,99.451872631296737,0,167.49443675726476,101.21860378262633,null,null,2167.2852120000002,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,2015.8392943940648,0,0,0,17.45413011278788,0]
[0,0,0,2030.2364636529846,0,2030.2364636529846,2145.3780169999995,"2013-12-28",43,40,"OFF",-11.009991135079996,-73.754793005267999,3.009887,"OFF",-12.328415535205004,-104.36997950824001,-8.8484060000000007,"OFF",-4.1429565040499605E-2,-33.398399859304,-1.7696810000000001,"ON",36944.527281305025,70602.677430774012,2156.9679999999998,"OFF",-6.7041160631999839,-119.67758078056001,-3.9817830000000001,null,0,0,0,2012.8724587852348,0,2012.8724587852348,0,0,1509.7879541167799,2078.1848388253306,0,3587.9727929421106,0,0,0,144.09554121476503,0,0,0,0,78.783161174669203,0,145.64303361774918,80.330653577653351,null,null,2145.3780169999995,null,30272.564300000085,10.244330963166089,5910.1105594589499,68.733640736036079,6011.521044200008,70.281133139020227,1.5474924029841475,null,null,null,null,null,null,null,null,null,2012.8724587852348,0,0,0,17.364004867749827,0]
[0,0,0,1977.7229815578767,0,1977.7229815578767,2080.6956969999997,"2013-12-28T01:00:00",42,39,"OFF",-11.54257156628999,-75.14639166260001,3.3185669999999998,"OFF",-13.046770289759996,-107.13419952966001,-8.8484060000000007,"OFF",8.3789161600499332E-2,-75.14639166260001,-1.7696810000000001,"ON",35240.997341100003,69943.068105116006,2091.9769999999999,"OFF",-6.8894973324000128,-118.98177343106001,-3.9817830000000001,null,0,0,0,1961.89271281636,0,1961.89271281636,0,0,1509.7879541167799,2023.34496603516,0,3533.1329201519402,0,0,0,130.08428718363984,0,0,0,0,68.63203396483982,0,131.85101833496944,70.398765116169415,null,null,2080.6956969999997,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1961.89271281636,0,0,0,15.830268741516647,0]
[0,0,0,1927.9740784870189,0,1927.9740784870189,2078.3701109999997,"2013-12-28T02:00:00",40,38,"OFF",-12.260928964410004,-72.363194347936002,2.7780309999999999,"OFF",-13.070702906249986,-105.76159420724001,-8.8484060000000007,"OFF",-1.2858814151999989E-2,-45.922803816960005,-1.7696810000000001,"ON",33576.41360303999,70262.016569126004,2091.2979999999998,"OFF",-6.3147735568399899,-117.67718478096002,-5.0878329999999998,null,0,0,0,1913.5702129953249,0,1913.5702129953249,0,0,1509.7879541167799,1968.6269010302371,0,3478.4148551470171,0,0,0,177.72778700467484,0,0,0,0,122.67109896976262,0,179.98471050366499,124.92802246875277,null,null,2078.3701109999997,null,28829.600000000006,10.073451258016961,5723.8774004204279,65.960348793655953,5875.8824000000004,68.217272292646101,2.2569234989901474,null,null,null,null,null,null,null,null,null,1913.5702129953249,0,0,0,14.403865491693978,0]
[0,0,0,1908.0666725312039,0,1908.0666725312039,2095.3187229999999,"2013-12-28T03:00:00",41,39,"OFF",-12.462086056050005,-73.310350572494002,3.1946430000000001,"OFF",-12.386551971299999,-108.76820383214002,-8.8484060000000007,"OFF",-0.17715418787500442,-62.621995725778007,-1.7696810000000001,"ON",32895.46125831001,70406.608143644014,2107.83,"OFF",-6.7221933663499955,-118.199020241,-5.0878329999999998,null,0,0,0,1894.2258720270738,0,1894.2258720270738,0,0,1509.7879541167799,1946.7595264024767,0,3456.5474805192566,0,0,0,213.60412797292611,0,0,0,0,161.07047359752323,0,215.95226828084594,163.41861390544307,null,null,2095.3187229999999,null,29175.192900000024,10.14607827102388,5751.0285492910634,66.359141599693913,5908.3681326000024,68.707281907613748,2.3481403079198344,null,null,null,null,null,null,null,null,null,1894.2258720270738,0,0,0,13.840800504130129,0]
[0,0,0,1905.9088538505393,0,1905.9088538505393,2042.9131010000001,"2013-12-28T04:00:00",41,38,"OFF",-12.917614853340002,-72.807636780710013,3.3550209999999998,"OFF",-12.927408469300005,-103.46972110008001,-8.8484060000000007,"OFF",-0.18380170779999888,-45.922803816960005,-1.7696810000000001,"ON",32821.11812739999,70710.38921056001,2055.2640000000001,"OFF",-7.38157072191001,-116.19862424140001,-5.0878329999999998,null,0,0,0,1892.1288099405883,0,1892.1288099405883,0,0,1509.7879541167799,1943.6687643065993,0,3453.4567184233792,0,0,0,163.1351900594118,0,0,0,0,111.59523569340081,0,164.97095106867144,113.43099670266045,null,null,2042.9131010000001,null,29175.192900000024,10.08523139374422,5785.7260306584812,66.871520898354106,5908.3681326000024,68.707281907613748,1.8357610092596417,null,null,null,null,null,null,null,null,null,1892.1288099405883,0,0,0,13.780043909951019,0]
[0,0,0,1931.2569131661471,0,1931.2569131661471,2044.991587,"2013-12-28T05:00:00",37,35,"OFF",-13.121351563949988,-73.754793005267999,2.9855070000000001,"OFF",-14.287270174439994,-109.2405507464,-8.8484060000000007,"OFF",0.24001950687500437,-33.398399859304,-1.7696810000000001,"ON",33687.867504374983,70662.376498236001,2057.712,"OFF",-8.032372605810016,-117.59015873206,-5.0878329999999998,null,0,0,0,1916.7597608140875,0,1916.7597608140875,0,0,1509.7879541167799,1971.1130400648244,0,3480.9009941816043,0,0,0,140.9522391859125,0,0,0,0,86.598959935175571,0,141.88018297719452,87.526903726457604,null,null,2044.991587,null,28650.199700000056,9.8847954545887777,5796.8219639183117,67.036025448148166,5859.0187718000052,67.963969239430199,0.92794379128203275,null,null,null,null,null,null,null,null,null,1916.7597608140875,0,0,0,14.497152352059629,0]
[0,0,0,1940.0185005170831,0,1940.0185005170831,2041.6869340000003,"2013-12-28T06:00:00",35,34,"OFF",-13.659600125174997,-73.754793005267999,3.0138039999999999,"OFF",-14.384964953424991,-106.66185261540001,-8.8484060000000007,"OFF",-0.46116068024999946,-45.922803816960005,-1.7696810000000001,"ON",33984.187887844993,70576.385136922006,2053.2730000000001,"OFF",-7.502433928920003,-120.37338813006001,-3.9817830000000001,null,0,0,0,1925.2717821010649,0,1925.2717821010649,0,0,1509.7879541167799,1980.7931333886311,0,3490.5810875054112,0,0,0,128.00121789893524,0,0,0,0,72.479866611369062,0,127.54621951802189,72.024868230455709,null,null,2041.6869340000003,null,29282.587499999994,9.8455046165572071,5948.4178090283758,69.315103271380409,5918.4632249999995,68.860104890467056,-0.45499838091335221,null,null,null,null,null,null,null,null,null,1925.2717821010649,0,0,0,14.746718416018211,0]
[0,0,0,1957.7268705827319,0,1957.7268705827319,2051.8299079999997,"2013-12-28T07:00:00",37,35,"OFF",-13.941238044704994,-72.363194347936002,3.217778,"OFF",-14.129765935739997,-101.38229905158001,-8.8484060000000007,"OFF",-0.1352517826250014,-62.621995725778007,-1.7696810000000001,"ON",34578.118568500002,70523.640132538014,2063.212,"OFF",-8.5969103391499999,-119.67758078056001,-3.9817830000000001,null,0,0,0,1942.4731571854252,0,1942.4731571854252,0,0,1509.7879541167799,2000.0535690167951,0,3509.8415231335748,0,0,0,120.73884281457481,0,0,0,0,63.15843098320488,0,121.66678660585684,64.086374774486913,null,null,2051.8299079999997,null,28650.199700000056,9.8847954545887777,5796.8219639183117,67.036025448148166,5859.0187718000052,67.963969239430199,0.92794379128203275,null,null,null,null,null,null,null,null,null,1942.4731571854252,0,0,0,15.253713397306683,0]
[0,0,0,1997.2421777319703,0,1997.2421777319703,2041.8859417999997,"2013-12-28T08:00:00",36,35,"OFF",-13.721804472529998,-74.450592333934011,3.2941880000000001,"OFF",-14.589556274749999,-100.19513541124002,-8.8484060000000007,"OFF",-3.381206595999893E-2,-33.398399859304,-0.37605719999999998,"ON",35880.366785899998,70197.729584616012,2051.7979999999998,"OFF",-7.7786320408999838,-118.28596608156001,-3.9817830000000001,null,0,0,0,1980.8450700858011,0,1980.8450700858011,0,0,1509.7879541167799,2043.7299888102534,0,3553.5179429270333,0,0,0,70.952929914198648,0,0,0,0,8.0680111897463576,0,71.570540542395548,8.6856218179432574,null,null,2041.8859417999997,null,28888.694400000008,9.8929249616944812,5840.2736322892088,67.683259008016108,5881.4372736000005,68.300869636213008,0.61761062819689982,null,null,null,null,null,null,null,null,null,1980.8450700858011,0,0,0,16.397107646169161,0]
[0,0,0,1972.8257756372768,0,1972.8257756372768,2039.3741450000002,"2013-12-28T09:00:00",42,40,"OFF",-14.811137976640007,-73.754793005267999,2.9130150000000001,"OFF",-14.624590786860017,-108.74927466390001,-8.8484060000000007,"OFF",4.3102803139995031E-3,-45.922803816960005,-1.7696810000000001,"ON",35079.401637870003,70637.888892033996,2051.0610000000001,"OFF",-7.8580499230449892,-121.06919547956002,-3.9817830000000001,null,0,0,0,1957.1371014724823,0,1957.1371014724823,0,0,1509.7879541167799,2016.0359817819253,0,3525.8239358987053,0,0,0,93.923898527517849,0,0,0,0,35.02501821807482,0,96.208134851517087,37.309254542074058,null,null,2039.3741450000002,null,29657.431200000021,10.2233630804106,5801.893362630899,67.111317236915824,5953.6985328000019,69.395553560915062,2.284236323999238,null,null,null,null,null,null,null,null,null,1957.1371014724823,0,0,0,15.68867416479452,0]
[0,0,0,2037.9429062486006,0,2037.9429062486006,2063.5533620000001,"2013-12-28T10:00:00",48,44,"OFF",-15.491235337060012,-73.058993676602014,2.8992819999999999,"OFF",-14.908951705315017,-109.93635809590002,-8.8484060000000007,"OFF",-0.66098760612499441,-75.14639166260001,-1.7696810000000001,"ON",37190.176607439986,70358.876160510001,2076.36,"OFF",-7.1329669494299797,-119.67758078056001,-5.0878329999999998,null,0,0,0,2020.3515277374954,0,2020.3515277374954,0,0,1509.7879541167799,2087.3048268713869,0,3597.0927809881669,0,0,0,56.008472262504711,0,0,0,0,-10.944826871386795,0,53.783378092663952,-13.169921041227553,null,null,2063.5533620000001,null,35210.380800000043,10.656032545190428,6608.5347713942847,79.925096735650953,6475.6757952000044,77.700002565810195,-2.2250941698407587,null,null,null,null,null,null,null,null,null,2020.3515277374954,0,0,0,17.591378511105177,0]
[0,0,0,2338.6577500136364,0,2338.6577500136364,2481.394949,"2013-12-28T11:00:00",53,47,"OFF",-15.54224899514001,-70.275796361938006,3.280869,"OFF",-15.451039799235026,-106.25287028974,-8.8484060000000007,"OFF",-0.31119824819999969,-33.398399859304,-1.7696810000000001,"ON",46049.435269529989,69934.437687732003,2493.8200000000002,"OFF",-7.5783820417900092,-118.28596608156001,-5.0878329999999998,null,0,0,0,2311.8015399372302,0,2311.8015399372302,0,0,1509.7879541167799,2416.2224796712444,0,3926.0104337880243,0,0,0,182.01846006276992,0,0,0,0,77.597520328755763,0,171.86624570738155,67.445305973367397,null,null,2481.394949,null,42907.977300000086,11.100959156439471,7730.4990848669013,100.51758860944383,7199.249866200008,90.365374254055467,-10.152214355388367,null,null,null,null,null,null,null,null,null,2311.8015399372302,0,0,0,26.856210076406114,0]
[0,0,0,2356.973828149823,0,2356.973828149823,2419.8765259999996,"2013-12-28T12:00:00",57,49,"OFF",-15.693391241099999,-73.754793005267999,3.1333959999999998,"OFF",-15.351430175359994,-105.76159420724001,-8.8484060000000007,"OFF",5.7312776965499516E-2,-33.398399859304,-1.7696810000000001,"ON",46549.745208199987,70178.246978830008,2431.3429999999998,"OFF",-7.9841037381000177,-118.98177343106001,-3.9817830000000001,null,0,0,0,2329.5316153195586,0,2329.5316153195586,0,0,1509.7879541167799,2434.995784573186,0,3944.783738689966,0,0,0,101.81138468044128,0,0,0,0,-3.6527845731861817,0,82.565116336964266,-22.899052916663194,null,null,2419.8765259999996,null,50738.045700000075,11.489554425774443,8832.0301762407325,123.87008900355444,7935.2762958000076,104.62382066007743,-19.246268343477013,null,null,null,null,null,null,null,null,null,2329.5316153195586,0,0,0,27.442212830264452,0]
[0,0,0,2255.40371721266,0,2255.40371721266,2375.9279139999999,"2013-12-28T13:00:00",58,50,"OFF",-15.802218391119997,-71.667395019270003,2.889465,"OFF",-15.793164286375005,-109.22162157816001,-8.8484060000000007,"OFF",-4.6434606659999959E-3,-33.398399859304,-2.4333119999999999,"ON",43723.904053199985,70040.336759034006,2389.4079999999999,"OFF",-7.6172623240999942,-118.98177343106001,-5.0878329999999998,null,0,0,0,2231.1822926520385,0,2231.1822926520385,0,0,1509.7879541167799,2324.8581869690106,0,3834.6461410857905,0,0,0,158.22570734796136,0,0,0,0,64.549813030989299,0,136.97334448297113,43.297450165999066,null,null,2375.9279139999999,null,52896.528800000029,11.623976957770942,9101.279018733303,130.05059811434887,8138.1737072000033,108.79823524935864,-21.252362864990232,null,null,null,null,null,null,null,null,null,2231.1822926520385,0,0,0,24.221424560621472,0]
[0,0,0,2398.5137420941724,0,2398.5137420941724,2485.4883610000002,"2013-12-28T14:00:00",59,50,"OFF",-15.513606512529998,-73.058993676602014,2.5443319999999998,"OFF",-15.195070764900022,-109.2405507464,-8.8484060000000007,"OFF",0.14536432665000029,-45.922803816960005,-1.7696810000000001,"ON",47670.16493183998,69708.161939758007,2499.7559999999999,"OFF",-8.2205235483700108,-121.06919547956002,-6.1938839999999997,null,0,0,0,2369.7344349011264,0,2369.7344349011264,0,0,1509.7879541167799,2482.8694563319859,0,3992.6574104487659,0,0,0,130.02156509887345,0,0,0,0,16.886543668013928,0,105.5539262951219,-7.5810951357376268,null,null,2485.4883610000002,null,55127.89710000006,11.700037031434206,9423.5423275822577,137.69203199966006,8347.9223274000051,113.2243931959085,-24.467638803751555,null,null,null,null,null,null,null,null,null,2369.7344349011264,0,0,0,28.779307193045952,0]
[0,0,0,2331.5591337734522,0,2331.5591337734522,2404.9819240000002,"2013-12-28T15:00:00",59,49,"OFF",-15.973532542440013,-73.754793005267999,2.7278440000000002,"OFF",-15.21437670417002,-103.67417215874002,-8.8484060000000007,"OFF",-0.61831226662500394,-33.398399859304,-1.7696810000000001,"ON",45854.471547000008,69873.206640976001,2417.96,"OFF",-8.7039339235800046,-117.59015873206,-5.0878329999999998,null,0,0,0,2304.9294371900214,0,2304.9294371900214,0,0,1509.7879541167799,2408.7711969294646,0,3918.5591510462446,0,0,0,113.03056280997862,0,0,0,0,9.188803070535414,0,87.37135943986064,-16.470400299582565,null,null,2404.9819240000002,null,55127.89710000006,11.639190154154544,9472.8063327193704,138.88359656602648,8347.9223274000051,113.2243931959085,-25.659203370117979,null,null,null,null,null,null,null,null,null,2304.9294371900214,0,0,0,26.629696583430814,0]
[0,0,0,2316.8491111553958,0,2316.8491111553958,2447.4637479999997,"2013-12-28T16:00:00",58,48,"OFF",-16.172434489750014,-74.450592333934011,2.6416179999999998,"OFF",-15.293837861509996,-110.63216544540002,-8.8484060000000007,"OFF",5.7150289999999939E-3,-33.398399859304,-1.7696810000000001,"ON",45448.539573689995,70164.747915208005,2459.422,"OFF",-8.6813896414500018,-117.59015873206,-3.9817830000000001,null,0,0,0,2290.6877246610497,0,2290.6877246610497,0,0,1509.7879541167799,2391.2827212072957,0,3901.0706753240756,0,0,0,168.73427533895028,0,0,0,0,68.139278792704317,0,145.22652890672603,44.631532360480065,null,null,2447.4637479999997,null,52896.528800000029,11.502283203211622,9197.5702328787156,132.30598168158289,8138.1737072000033,108.79823524935864,-23.507746432224252,null,null,null,null,null,null,null,null,null,2290.6877246610497,0,0,0,26.161386494346061,0]
[0,0,0,2359.0157468970706,0,2359.0157468970706,2550.256738,"2013-12-28T17:00:00",58,48,"OFF",-16.686478663005001,-75.14639166260001,2.7047089999999998,"OFF",-15.300909362585001,-105.78052337548,-8.8484060000000007,"OFF",-5.5737926080001311E-2,-45.922803816960005,-1.7696810000000001,"ON",46605.278786859999,70090.707596554013,2564.364,"OFF",-8.7843370265999869,-118.98177343106001,-6.1938839999999997,null,0,0,0,2331.508068407722,0,2331.508068407722,0,0,1509.7879541167799,2437.6701540070248,0,3947.4581081238048,0,0,0,232.85593159227801,0,0,0,0,126.69384599297518,0,209.34818516005376,103.18609956075093,null,null,2550.256738,null,52896.528800000029,11.502283203211622,9197.5702328787156,132.30598168158289,8138.1737072000033,108.79823524935864,-23.507746432224252,null,null,null,null,null,null,null,null,null,2331.508068407722,0,0,0,27.507678489348564,0]
[0,0,0,2265.5557543894897,0,2265.5557543894897,2656.6539439999997,"2013-12-28T18:00:00",55,47,"OFF",-16.483340316590002,-73.754793005267999,3.1938140000000002,"OFF",-14.743793614999992,-104.35105034,-8.8484060000000007,"OFF",-3.3687928039998122E-2,-75.14639166260001,-1.7696810000000001,"ON",44012.169061944995,69943.340813472008,2668.06,"OFF",-8.5830707165700115,-119.67758078056001,-3.9817830000000001,null,0,0,0,2241.0156566404089,0,2241.0156566404089,0,0,1509.7879541167799,2336.3691019937419,0,3846.1570561105218,0,0,0,427.04434335959104,0,0,0,0,331.69089800625807,0,411.64520020909862,316.29175485576565,null,null,2656.6539439999997,null,46654.737500000047,11.228674001546203,8309.9282236844028,112.41428106596688,7551.4453250000042,97.015137915474455,-15.399143150492421,null,null,null,null,null,null,null,null,null,2241.0156566404089,0,0,0,24.540097749080815,0]
[0,0,0,2249.1305768617062,0,2249.1305768617062,2575.9023119999997,"2013-12-28T19:00:00",54,46,"OFF",-16.499334784800006,-73.058993676602014,2.852182,"OFF",-15.656751188450002,-107.1531286979,-8.8484060000000007,"OFF",2.3278500033001095E-2,-45.922803816960005,-1.7696810000000001,"ON",43545.10324122,69758.260068921998,2587.65,"OFF",-8.6970141122900113,-120.98224963900002,-3.9817830000000001,null,0,0,0,2225.1056917891365,0,2225.1056917891365,0,0,1509.7879541167799,2319.2815883067283,0,3829.0695424235082,0,0,0,362.54430821086362,0,0,0,0,268.36841169327181,0,348.96011258566483,254.78421606807302,null,null,2575.9023119999997,null,44737.413600000087,11.102471800777217,8059.0006266655482,107.1567886087625,7371.2168784000078,93.572592983563723,-13.584195625198774,null,null,null,null,null,null,null,null,null,2225.1056917891365,0,0,0,24.024885072569759,0]
[0,0,0,2221.0964159348273,0,2221.0964159348273,2492.4648849999999,"2013-12-28T20:00:00",54,46,"OFF",-16.803824128649993,-74.450592333934011,3.0467550000000001,"OFF",-14.506918710829989,-104.38890867648001,-8.8484060000000007,"OFF",-4.0883533883999998E-2,-45.922803816960005,-1.7696810000000001,"ON",42739.619168520003,69519.046715706005,2504.018,"OFF",-9.0077263750599972,-119.76460682946001,-3.9817830000000001,null,0,0,0,2197.94629231513,0,2197.94629231513,0,0,1509.7879541167799,2289.7239315106194,0,3799.5118856273994,0,0,0,306.07170768487003,0,0,0,0,214.29406848938061,0,292.48751205967125,200.70987286418182,null,null,2492.4648849999999,null,44737.413600000087,11.102471800777217,8059.0006266655482,107.1567886087625,7371.2168784000078,93.572592983563723,-13.584195625198774,null,null,null,null,null,null,null,null,null,2197.94629231513,0,0,0,23.150123619697297,0]
[0,0,0,2189.6332461247403,0,2189.6332461247403,2438.6793970000003,"2013-12-28T21:00:00",51,45,"OFF",-17.072534273335009,-75.14639166260001,2.8753169999999999,"OFF",-15.701208173859996,-107.83000687916001,-8.8484060000000007,"OFF",4.1152893249998115E-2,-33.398399859304,-1.7696810000000001,"ON",41822.706511590011,69476.881191367997,2451.5100000000002,"OFF",-8.8213159985299807,-119.67758078056001,-5.0878329999999998,null,0,0,0,2167.4577794745637,0,2167.4577794745637,0,0,1509.7879541167799,2255.5384337308246,0,3765.3263878476046,0,0,0,284.0522205254365,0,0,0,0,195.97156626917558,0,276.88843380502141,188.80777954876049,null,null,2438.6793970000003,null,39527.769900000014,10.864045147186603,7276.8051613327989,91.802423495679577,6881.5103706000009,84.638636775264473,-7.1637867204151036,null,null,null,null,null,null,null,null,null,2167.4577794745637,0,0,0,22.175466650176531,0]
[0,0,0,2118.3177245423003,0,2118.3177245423003,2341.2886020000001,"2013-12-28T22:00:00",48,43,"OFF",-16.815851345159988,-73.754793005267999,2.654522,"OFF",-15.543724623375024,-106.47633072498,-8.8484060000000007,"OFF",0.14929136603999885,-33.398399859304,-1.7696810000000001,"ON",39690.703032090001,69677.12933301201,2354.34,"OFF",-8.5969103391499999,-118.98177343106001,-5.0878329999999998,null,0,0,0,2098.3221599240737,0,2098.3221599240737,0,0,1509.7879541167799,2176.9732614491645,0,3686.7612155659444,0,0,0,256.01784007592642,0,0,0,0,177.36673855083563,0,253.14883569705538,174.49773417196459,null,null,2341.2886020000001,null,35210.380800000043,10.595185667910767,6646.4867919474727,80.569006944681234,6475.6757952000044,77.700002565810195,-2.8690043788710398,null,null,null,null,null,null,null,null,null,2098.3221599240737,0,0,0,19.995564618226581,0]
[0,0,0,2078.5099090706331,0,2078.5099090706331,2246.8154139999997,"2013-12-28T23:00:00",48,42,"OFF",-17.812329515025002,-73.754793005267999,2.9263340000000002,"OFF",-15.062895253124973,-103.6552429905,-8.8484060000000007,"OFF",0.10903188685999866,-33.398399859304,-1.7696810000000001,"ON",38465.922691125008,69701.063501668003,2259.5949999999998,"OFF",-8.2712696986150007,-118.98177343106001,-5.0878329999999998,null,0,0,0,2059.7123962275286,0,2059.7123962275286,0,0,1509.7879541167799,2133.5568112787664,0,3643.3447653955463,0,0,0,199.88260377247116,0,0,0,0,126.03818872123338,0,196.358499216919,122.51408416568123,null,null,2246.8154139999997,null,35210.380800000043,10.534338790631107,6684.877238107244,81.224107121362351,6475.6757952000044,77.700002565810195,-3.5241045555521566,null,null,null,null,null,null,null,null,null,2059.7123962275286,0,0,0,18.797512843104414,0]
[0,0,0,2065.6193476974818,0,2065.6193476974818,2213.4647919999998,"2013-12-29",46,40,"OFF",-17.534785563680011,-74.450592333934011,2.7647119999999998,"OFF",-15.548431044040006,-106.45732134840001,-8.8484060000000007,"OFF",-8.6702578500000543E-2,-33.398399859304,-1.7696810000000001,"ON",38063.645724094997,69495.104526216004,2226.4059999999999,"OFF",-8.9732122242699912,-117.59015873206,-5.0878329999999998,null,0,0,0,2047.2067500931216,0,2047.2067500931216,0,0,1509.7879541167799,2120.2472280732445,0,3630.0351821900244,0,0,0,179.19924990687832,0,0,0,0,106.15877192675543,0,177.46829321216094,104.42781523203806,null,null,2213.4647919999998,null,32877.826400000049,10.333135858009356,6363.5718821050814,75.857660286359561,6256.415681600005,74.126703591642183,-1.7309566947173778,null,null,null,null,null,null,null,null,null,2047.2067500931216,0,0,0,18.412597604360144,0]
[0,0,0,1902.8848956375466,0,1902.8848956375466,2070.188885,"2013-12-29T01:00:00",45,40,"OFF",-18.094525122935007,-74.450592333934011,3.0467550000000001,"OFF",-14.741914564159977,-105.78052337548,-8.8484060000000007,"OFF",-2.9146653023999974E-2,-62.621995725778007,-1.7696810000000001,"ON",32716.755850214999,69813.507573514013,2081.7420000000002,"OFF",-9.4824763729499857,-117.59015873206,-3.9817830000000001,null,0,0,0,1889.1899038052079,0,1889.1899038052079,0,0,1509.7879541167799,1942.6683019498205,0,3452.4562560666004,0,0,0,192.55209619479228,0,0,0,0,139.0736980501797,0,192.09794278664469,138.61954464203211,null,null,2070.188885,null,31886.51250000007,10.299345197696841,6191.9494662885154,73.099504887130408,6163.2321750000065,72.645351478982803,-0.45415340814760441,null,null,null,null,null,null,null,null,null,1889.1899038052079,0,0,0,13.694991832338701,0]
[0,0,0,1917.7260171284756,0,1917.7260171284756,2074.7080829999995,"2013-12-29T02:00:00",42,39,"OFF",-18.794484420374996,-74.450592333934011,2.7059530000000001,"OFF",-14.918337112279989,-102.28255745974,-8.8484060000000007,"OFF",0.10348447356000194,-33.398399859304,-1.7696810000000001,"ON",33226.968257100016,69921.082999122009,2086.6019999999999,"OFF",-9.7259009001700019,-118.28596608156001,-3.9817830000000001,null,0,0,0,1903.6125790148319,0,1903.6125790148319,0,0,1509.7879541167799,1958.4458217716126,0,3468.2337758883923,0,0,0,182.98942098516795,0,0,0,0,128.15617822838726,0,184.75615213649755,129.92290937971686,null,null,2074.7080829999995,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1903.6125790148319,0,0,0,14.113438113643724,0]
[0,0,0,1912.1671538102737,0,1912.1671538102737,2134.619952,"2013-12-29T03:00:00",42,39,"OFF",-18.725464369289991,-73.754793005267999,3.3408720000000001,"OFF",-15.967616584429988,-103.8786232174,-8.8484060000000007,"OFF",-1.9908915999953603E-4,-33.398399859304,-1.7696810000000001,"ON",33036.44475504,72346.214242358008,2146.9850000000001,"OFF",-9.5325282595200083,-117.59015873206,-5.0878329999999998,null,0,0,0,1898.2107483277057,0,1898.2107483277057,0,0,1509.7879541167799,1946.3649203383866,0,3456.1528744551665,0,0,0,248.77425167229444,0,0,0,0,200.62007966161354,0,250.54098282362403,202.38681081294314,null,null,2134.619952,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1898.2107483277057,0,0,0,13.956405482568016,0]
[0,0,0,1921.3726933244848,0,1921.3726933244848,2050.9351449999995,"2013-12-29T04:00:00",42,39,"OFF",-19.619536788749986,-73.058993676602014,2.9130150000000001,"OFF",-15.196601099119974,-109.73190703724001,-8.8484060000000007,"OFF",-0.19116069337499841,-33.398399859304,-1.7696810000000001,"ON",33351.580315275009,72214.151210548007,2062.6219999999998,"OFF",-9.1550573561500048,-118.28596608156001,-3.9817830000000001,null,0,0,0,1907.1560467706852,0,1907.1560467706852,0,0,1509.7879541167799,1956.5353219253166,0,3466.3232760420965,0,0,0,155.46595322931466,0,0,0,0,106.08667807468328,0,157.23268438064426,107.85340922601287,null,null,2050.9351449999995,null,29657.431200000021,10.16251620313094,5836.6315206194613,67.628822409585467,5953.6985328000019,69.395553560915062,1.7667311513295942,null,null,null,null,null,null,null,null,null,1907.1560467706852,0,0,0,14.216646553799592,0]
[0,0,0,1820.1273998395568,0,1820.1273998395568,2036.1049760000001,"2013-12-29T05:00:00",40,37,"OFF",-19.628822447780006,-73.058993676602014,3.1098460000000001,"OFF",-15.094482254640013,-108.05346731440001,-8.8484060000000007,"OFF",-0.11943005274999709,-33.398399859304,-1.7696810000000001,"ON",29775.154545389996,72440.988416901993,2047.595,"OFF",-9.1009527897399973,-119.67758078056001,-3.9817830000000001,null,0,0,0,1808.7161885392723,0,1808.7161885392723,0,0,1509.7879541167799,1847.88994638803,0,3357.6779005048102,0,0,0,238.87881146072777,0,0,0,0,199.70505361197002,0,240.62448950650446,201.4507316577467,null,null,2036.1049760000001,null,28829.600000000006,10.012604380737301,5758.6615637113737,66.471594246869415,5875.8824000000004,68.217272292646101,1.7456780457766854,null,null,null,null,null,null,null,null,null,1808.7161885392723,0,0,0,11.411211300284549,0]
[0,0,0,1747.3460783489891,0,1747.3460783489891,2032.0062679999999,"2013-12-29T06:00:00",38,36,"OFF",-20.401089765214987,-73.754793005267999,3.0596589999999999,"OFF",-15.651272507849995,-106.25287028974,-8.8484060000000007,"OFF",-0.16822239884000434,-45.922803816960005,-3.318152,"ON",27036.001268345015,72931.109499306011,2046.201,"OFF",-9.762695960750003,-117.59015873206,-5.0878329999999998,null,0,0,0,1737.8661589554649,0,1737.8661589554649,0,0,1509.7879541167799,1769.6058901239001,0,3279.3938442406798,0,0,0,308.3348410445351,0,0,0,0,276.59510987609997,0,309.89714496590898,278.15741379747385,null,null,2032.0062679999999,null,28563.352800000052,9.9426820040680362,5745.6032061195147,66.279303938778682,5850.8551632000053,67.841607860152536,1.5623039213738537,null,null,null,null,null,null,null,null,null,1737.8661589554649,0,0,0,9.4799193935241419,0]
[0,0,0,1732.6491852933882,0,1732.6491852933882,2039.470086,"2013-12-29T07:00:00",38,36,"OFF",-20.948178482250004,-73.058993676602014,2.7659560000000001,"OFF",-14.986862616555024,-105.76159420724001,-8.8484060000000007,"OFF",-3.6217238160001601E-2,-33.398399859304,-1.7696810000000001,"ON",26463.347865869993,72673.656769574009,2051.3040000000001,"OFF",-9.8225659940800067,-118.98177343106001,-3.9817830000000001,null,0,0,0,1723.5494639413812,0,1723.5494639413812,0,0,1509.7879541167799,1754.4147409409534,0,3264.2026950577333,0,0,0,327.7545360586189,0,0,0,0,296.88925905904671,0,329.31683997999278,298.45156298042059,null,null,2039.470086,null,28563.352800000052,9.9426820040680362,5745.6032061195147,66.279303938778682,5850.8551632000053,67.841607860152536,1.5623039213738537,null,null,null,null,null,null,null,null,null,1723.5494639413812,0,0,0,9.099721352007009,0]
[0,0,0,1951.6884806930943,0,1951.6884806930943,2045.9668620000002,"2013-12-29T08:00:00",40,38,"OFF",-21.024504486789997,-73.746972692118007,2.8624130000000001,"OFF",-15.901026166545007,-103.8786232174,-8.8484060000000007,"OFF",-0.11714638337500449,-45.922803816960005,-2.4333119999999999,"ON",34376.332275249995,72937.790854028004,2059.4740000000002,"OFF",-9.8536839184700202,-118.98177343106001,-5.0878329999999998,null,0,0,0,1936.6080326998051,0,1936.6080326998051,0,0,1509.7879541167799,1987.1142398442391,0,3496.9021939610193,0,0,0,122.86596730019505,0,0,0,0,72.359760155761023,0,125.1228907991852,74.616683654751171,null,null,2045.9668620000002,null,28829.600000000006,10.073451258016961,5723.8774004204279,65.960348793655953,5875.8824000000004,68.217272292646101,2.2569234989901474,null,null,null,null,null,null,null,null,null,1936.6080326998051,0,0,0,15.080447993289226,0]
[0,0,0,1964.6302584958621,0,1964.6302584958621,2045.4480779999999,"2013-12-29T09:00:00",44,41,"OFF",-21.028475487099996,-73.762621339252007,3.1839979999999999,"OFF",-14.72641579628999,-109.22162157816001,-8.8484060000000007,"OFF",8.864444849000383E-3,-62.621995725778007,-1.7696810000000001,"ON",34807.887925029987,72840.786887632014,2057.9699999999998,"OFF",-10.468188632719999,-120.37338813006001,-5.0878329999999998,null,0,0,0,1949.1779778426512,0,1949.1779778426512,0,0,1509.7879541167799,2001.1872358066116,0,3510.9751899233916,0,0,0,108.79202215734858,0,0,0,0,56.782764193388175,0,109.9771390692767,57.967881105316295,null,null,2045.4480779999999,null,31016.841600000043,10.330547828118286,6004.8783696788278,70.178962220334924,6081.4831104000041,71.364079132263043,1.1851169119281195,null,null,null,null,null,null,null,null,null,1949.1779778426512,0,0,0,15.452280653210892,0]
[0,0,0,1965.2082073467909,0,1965.2082073467909,2077.0373159999999,"2013-12-29T10:00:00",46,43,"OFF",-21.597234867090005,-75.14639166260001,2.9121860000000002,"OFF",-15.990783211044985,-108.35922150648001,-8.8484060000000007,"OFF",1.665907388999342E-3,-62.621995725778007,-1.7696810000000001,"ON",34827.079818510014,73298.215050651997,2088.7249999999999,"OFF",-10.747087213204987,-119.67758078056001,-3.9817830000000001,null,0,0,0,1949.7392795779997,0,1949.7392795779997,0,0,1509.7879541167799,2000.6032932292483,0,3510.3912473460282,0,0,0,138.98572042200021,0,0,0,0,88.121706770751643,0,139.03869580339654,88.174682152147966,null,null,2077.0373159999999,null,32877.826400000049,10.515676489848337,6253.1072407447627,74.073728210245861,6256.415681600005,74.126703591642183,5.2975381396322518E-2,null,null,null,null,null,null,null,null,null,1949.7392795779997,0,0,0,15.468927768791218,0]
[0,0,0,2181.6833000838892,0,2181.6833000838892,2276.1725460000002,"2013-12-29T11:00:00",47,43,"OFF",-21.610851000210001,-75.14639166260001,3.2310970000000001,"OFF",-15.415176942879993,-109.2405507464,-8.8484060000000007,"OFF",-0.4512647796249955,-33.398399859304,-2.4333119999999999,"ON",41588.798577259993,72528.928840877998,2289.3110000000001,"OFF",-8.8299763758499843,-120.37338813006001,-5.0878329999999998,null,0,0,0,2159.7528843974405,0,2159.7528843974405,0,0,1509.7879541167799,2234.7864476397044,0,3744.5744017564843,0,0,0,129.55811560255961,0,0,0,0,54.524552360295729,0,128.24346007114272,53.20989682887884,null,null,2276.1725460000002,null,33987.03270000004,10.553485717883778,6440.911298606512,77.125233096341788,6360.681073800004,75.810577564924898,-1.3146555314168893,null,null,null,null,null,null,null,null,null,2159.7528843974405,0,0,0,21.930415686448669,0]
[0,0,0,2158.1804756842739,0,2158.1804756842739,2387.9644369999996,"2013-12-29T12:00:00",50,45,"OFF",-21.713849600940005,-72.363194347936002,3.0973570000000001,"OFF",-16.458242795539999,-105.76159420724001,-8.8484060000000007,"OFF",-3.1620034799947113E-4,-75.14639166260001,-1.7696810000000001,"ON",40891.874173609998,72898.408559087999,2400.5729999999999,"OFF",-8.931820715020006,-117.59015873206,-5.0878329999999998,null,0,0,0,2136.9715647486614,0,2136.9715647486614,0,0,1509.7879541167799,2208.1864005913353,0,3717.9743547081152,0,0,0,263.60143525133844,0,0,0,0,192.38659940866455,0,258.48760674962779,187.27277090695389,null,null,2387.9644369999996,null,37984.500000000058,10.811440105573219,7026.7234760740748,87.223798795789492,6736.4430000000057,82.109970294078821,-5.113828501710671,null,null,null,null,null,null,null,null,null,2136.9715647486614,0,0,0,21.208910935612494,0]
[0,0,0,2077.8231816179004,0,2077.8231816179004,2348.2860719999999,"2013-12-29T13:00:00",44,40,"OFF",-22.676012411389991,-74.450592333934011,3.0969419999999999,"OFF",-16.22083066099999,-102.28255745974,-8.8484060000000007,"OFF",-3.8769676001999924E-2,-45.922803816960005,-1.7696810000000001,"ON",38444.563318799999,72775.112298840002,2359.7890000000002,"OFF",-10.364646180349983,-118.28596608156001,-3.9817830000000001,null,0,0,0,2059.0462127766295,0,2059.0462127766295,0,0,1509.7879541167799,2122.4772709957892,0,3632.2652251125692,0,0,0,300.74278722337067,0,0,0,0,237.31172900421097,0,301.37935748792381,237.94829926876412,null,null,2348.2860719999999,null,31016.841600000043,10.269700950838626,6040.4566303300589,70.727508867709915,6081.4831104000041,71.364079132263043,0.6365702645531286,null,null,null,null,null,null,null,null,null,2059.0462127766295,0,0,0,18.7769688412709,0]
[0,0,0,2090.3013478582416,0,2090.3013478582416,2297.3676599999999,"2013-12-29T14:00:00",41,38,"OFF",-22.202456227909998,-73.058993676602014,3.12358,"OFF",-16.275200927310017,-106.45732134840001,-8.8484060000000007,"OFF",0.1036317451250002,-45.922803816960005,-1.7696810000000001,"ON",38831.435771439981,73351.088388379998,2309.9499999999998,"OFF",-9.8570801448699825,-116.89443159090001,-5.0878329999999998,null,0,0,0,2071.1504221901469,0,2071.1504221901469,0,0,1509.7879541167799,2133.9722862514054,0,3643.7602403681854,0,0,0,238.79957780985296,0,0,0,0,175.9777137485944,0,240.6353388191126,177.81347475785404,null,null,2297.3676599999999,null,29175.192900000024,10.08523139374422,5785.7260306584812,66.871520898354106,5908.3681326000024,68.707281907613748,1.8357610092596417,null,null,null,null,null,null,null,null,null,2071.1504221901469,0,0,0,19.150925668094715,0]
[0,0,0,1984.4294111011038,0,1984.4294111011038,2139.782995,"2013-12-29T15:00:00",38,35,"OFF",-22.623550701674993,-74.006149901160001,2.5168650000000001,"OFF",-14.901377075200026,-105.27023791640001,-8.8484060000000007,"OFF",0.26078333150000466,-62.621995725778007,-1.7696810000000001,"ON",35461.517283690024,73518.09017309401,2151.866,"OFF",-9.4244009015099834,-121.06919547956002,-3.9817830000000001,null,0,0,0,1968.404830548739,0,1968.404830548739,0,0,1509.7879541167799,2020.5060935673407,0,3530.2940476841204,0,0,0,183.46116945126096,0,0,0,0,131.35990643265927,0,184.50150169907891,132.40023868047723,null,null,2139.782995,null,28563.352800000052,9.8818351267883742,5780.9814540557363,66.801275612334564,5850.8551632000053,67.841607860152536,1.0403322478179717,null,null,null,null,null,null,null,null,null,1968.404830548739,0,0,0,16.024580552364796,0]
[0,0,0,1967.2781633506888,0,1967.2781633506888,2092.9877299999998,"2013-12-29T16:00:00",37,34,"OFF",-22.663713503059995,-74.895034766708008,2.9125999999999999,"OFF",-16.495752026805,-106.45732134840001,-8.8484060000000007,"OFF",0.31543915187500332,-75.14639166260001,-1.7696810000000001,"ON",34895.760806329992,73368.902660694002,2104.6750000000002,"OFF",-9.888155616429982,-117.59015873206,-3.9817830000000001,null,0,0,0,1951.7495838155701,0,1951.7495838155701,0,0,1509.7879541167799,2002.6250363729312,0,3512.4129904897109,0,0,0,152.92541618443011,0,0,0,0,102.04996362706902,0,153.31890025931796,102.44344770195686,null,null,2092.9877299999998,null,28650.199700000056,9.8239485773091175,5832.7259094525198,67.570485164542362,5859.0187718000052,67.963969239430199,0.39348407488783721,null,null,null,null,null,null,null,null,null,1951.7495838155701,0,0,0,15.528579535118752,0]
[0,0,0,1947.1427759737655,0,1947.1427759737655,2029.1140260000002,"2013-12-29T17:00:00",35,32,"OFF",-22.917569692080011,-71.667395019270003,2.754896,"OFF",-16.423324582125002,-111.12344152790001,-8.8484060000000007,"OFF",-1.6571241875000906E-2,-75.14639166260001,-1.7696810000000001,"ON",34223.925287050006,73386.155474628002,2040.9590000000001,"OFF",-10.772023537030003,-120.37338813006001,-3.9817830000000001,null,0,0,0,1932.192500567696,0,1932.192500567696,0,0,1509.7879541167799,1981.1270584320855,0,3490.9150125488654,0,0,0,108.76649943230404,0,0,0,0,59.831941567914555,0,107.17076853963133,58.236210675241836,null,null,2029.1140260000002,null,29282.587499999994,9.7238108619978867,6022.8624179519456,70.455835783139776,5918.4632249999995,68.860104890467056,-1.5957308926727194,null,null,null,null,null,null,null,null,null,1932.192500567696,0,0,0,14.950275406069522,0]
[0,0,0,1945.4266523920601,0,{"$f":"SUM(A8004:E8004)","v":1945.4266523920601},{"$f":"N8004+R8004+V8004+Z8004+AD8004","v":2024.0444900000002},"2013-12-29T18:00:00",32,30,"OFF",-23.46184922972499,-72.363194347936002,3.1573600000000002,"OFF",-16.264419846674972,-109.93635809590002,-8.8484060000000007,"OFF",0.21410278724999943,-75.14639166260001,-1.7696810000000001,"ON",34166.274651780011,73205.951397150013,2035.4870000000001,"OFF",-9.7970117558000087,-118.98177343106001,-3.9817830000000001,null,0,0,0,1930.5254617329538,0,{"$f":"SUM(AF8004:AJ8004)","v":1930.5254617329538},0,0,1509.7879541167799,1979.7521009304558,0,{"$f":"SUM(AL8004:AP8004)","v":3489.5400550472359},{"$f":"IF($K8004=\"ON\",$N8004-AF8004,0)","v":0},{"$f":"IF($O8004=\"ON\",$R8004-AG8004,0)","v":0},{"$f":"IF($S8004=\"ON\",$V8004-AH8004,0)","v":0},{"$f":"IF($W8004=\"ON\",$Z8004-AI8004,0)","v":104.96153826704631},{"$f":"IF($AA8004=\"ON\",$AD8004-AJ8004,0)","v":0},{"$f":"IF($K8004=\"ON\",$N8004-AL8004,0)","v":0},{"$f":"IF($O8004=\"ON\",$R8004-AM8004,0)","v":0},{"$f":"IF($S8004=\"ON\",$V8004-AN8004,0)","v":0},{"$f":"IF($W8004=\"ON\",$Z8004-AO8004,0)","v":55.734899069544326},{"$f":"IF($AA8004=\"ON\",$AD8004-AP8004,0)","v":0},{"$f":"SUM(AR8004:AV8004)+BN8004","v":98.872396171492355},{"$f":"SUM(AW8004:BA8004)+BN8004","v":49.645756973990373},null,null,{"$f":"N8004+R8004+V8004+Z8004+AD8004","v":2024.0444900000002},null,31434.163200000039,{"$f":"19.5285952781395+42*-0.3035722016559+BH8004*0.0000340867411548605+J8004*0.0608468772796604","v":9.675457311399553},{"$f":"BH8004*1000/(500*BI8004)","v":6497.7111031154127},{"$f":"0.00000128*BJ8004^2+0*BJ8004+24.024","v":78.065919461823114},{"$f":"0.094*BH8004 + 3165.9","v":6120.7113408000041},{"$f":"0.00000128*BL8004^2+0*BL8004+24.024","v":71.976777366269161},{"$f":"BM8004-BK8004","v":-6.089142095553953},null,null,null,null,null,null,null,null,null,{"$f":"SUM(AF8004:AJ8004)","v":1930.5254617329538},{"$f":"A8004-AF8004","v":0},{"$f":"B8004-AG8004","v":0},{"$f":"C8004-AH8004","v":0},{"$f":"D8004-AI8004","v":14.901190659106305},{"$f":"E8004-AJ8004","v":0}]
[0,0,0,1942.4264626151912,0,1942.4264626151912,1998.3306570000002,"2013-12-29T19:00:00",32,29,"OFF",-24.544217366499996,-74.450592333934011,3.096527,"OFF",-15.220111254345003,-98.088864402840002,-8.8484060000000007,"OFF",0.12317585112000072,-75.14639166260001,-1.7696810000000001,"ON",34065.338127990006,73762.035818370015,2009.8340000000001,"OFF",-11.127693346769993,-119.76460682946001,-3.9817830000000001,null,0,0,0,1927.6110058375398,0,1927.6110058375398,0,0,1509.7879541167799,1975.1714118592097,0,3484.9593659759894,0,0,0,82.222994162460282,0,0,0,0,34.662588140790376,0,75.447669896573544,27.887263874903638,null,null,1998.3306570000002,null,{"$f":" -0.6251*I8005^3 + 145.21*I8005^2 - 8340.3*I8005 + 170112","v":31434.163200000039},9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1927.6110058375398,0,0,0,14.815456777651434,0]
[0,0,0,1895.5550251764569,0,1895.5550251764569,1966.5377480000002,"2013-12-29T20:00:00",32,29,"OFF",-24.755459712659988,-73.754793005267999,2.6416179999999998,"OFF",-16.494400811660007,-99.703859328740009,-8.8484060000000007,"OFF",-8.7154192250004078E-2,-45.922803816960005,-1.7696810000000001,"ON",32462.919199439992,73883.094265931999,1978.4960000000001,"OFF",-11.067118261150018,-120.98224963900002,-3.9817830000000001,null,0,0,0,1882.065745281177,0,1882.065745281177,0,0,1509.7879541167799,1925.0917205609796,0,3434.8796746777598,0,0,0,96.430254718823107,0,0,0,0,53.404279439020456,0,89.65493045293637,46.628955173133718,null,null,1966.5377480000002,null,31434.163200000039,9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1882.065745281177,0,0,0,13.489279895279878,0]
[0,0,0,1821.275144456715,0,1821.275144456715,1941.516388,"2013-12-29T21:00:00",32,29,"OFF",-24.973399032680014,-70.971595690604005,2.8157290000000001,"OFF",-15.0738218527,-104.38890867648001,-8.8484060000000007,"OFF",0.10208792195999969,-75.14639166260001,-3.318152,"ON",29817.144313964996,73852.342388376012,1954.8489999999999,"OFF",-9.7713369000099881,-121.06919547956002,-3.9817830000000001,null,0,0,0,1809.8328686307191,0,1809.8328686307191,0,0,1509.7879541167799,1846.3801158125377,0,3356.1680699293174,0,0,0,145.01613136928086,0,0,0,0,108.46888418746221,0,138.2408071033941,101.69355992157547,null,null,1941.516388,null,31434.163200000039,9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1809.8328686307191,0,0,0,11.442275825995921,0]
[0,0,0,1888.0083129506249,0,1888.0083129506249,2088.3551109999999,"2013-12-29T22:00:00",32,29,"OFF",-24.967391225839997,-70.971595690604005,2.7780309999999999,"OFF",-14.935837525419993,-108.34029233824,-8.8484060000000007,"OFF",-0.17055774346000138,-45.922803816960005,-1.7696810000000001,"ON",32200.272159824985,74531.58671566601,2101.2829999999999,"OFF",-10.652943348880003,-120.37338813006001,-5.0878329999999998,null,0,0,0,1874.7301603070762,0,1874.7301603070762,0,0,1509.7879541167799,1915.6657429297902,0,3425.4536970465701,0,0,0,226.55283969292373,0,0,0,0,185.61725707020969,0,219.77751542703697,178.84193280432294,null,null,2088.3551109999999,null,31434.163200000039,9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1874.7301603070762,0,0,0,13.278152643548765,0]
[0,0,0,1870.60863728147,0,1870.60863728147,2102.765997,"2013-12-29T23:00:00",32,29,"OFF",-24.910211660740011,-73.058993676602014,2.8988670000000001,"OFF",-15.879349592754988,-107.8489360474,-8.8484060000000007,"OFF",-7.6204290374998387E-2,-33.398399859304,-1.7696810000000001,"ON",31589.578132375002,73916.356664530002,2114.4670000000001,"OFF",-11.424565986959989,-118.98177343106001,-3.9817830000000001,null,0,0,0,1857.8146188424535,0,1857.8146188424535,0,0,1509.7879541167799,1898.5494735523428,0,3408.3374276691229,0,0,0,256.65238115754664,0,0,0,0,215.91752644765734,0,249.87705689165989,209.14220218177059,null,null,2102.765997,null,31434.163200000039,9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1857.8146188424535,0,0,0,12.794018439016554,0]
[0,0,0,1870.1382472552091,0,1870.1382472552091,2156.2190369999998,"2013-12-30",32,29,"OFF",-25.5018225343,-73.058993676602014,3.1209069999999999,"OFF",-15.021815901120007,-109.93635809590002,-8.8484060000000007,"OFF",0.22172672962500625,-62.621995725778007,-1.7696810000000001,"ON",31572.967263570001,73859.304472288015,2167.6979999999999,"OFF",-10.361165048289994,-118.98177343106001,-3.9817830000000001,null,0,0,0,1857.3572652137148,0,1857.3572652137148,0,0,1509.7879541167799,1898.1715104702225,0,3407.9594645870025,0,0,0,310.34073478628511,0,0,0,0,269.52648952977734,0,303.56541052039836,262.75116526389058,null,null,2156.2190369999998,null,31434.163200000039,9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1857.3572652137148,0,0,0,12.780982041494326,0]
[0,0,0,1809.7465143830932,0,1809.7465143830932,2113.0210219999999,"2013-12-30T01:00:00",32,28,"OFF",-26.134226161110011,-72.363194347936002,3.0969419999999999,"OFF",-15.648479184139994,-108.05346731440001,-8.8484060000000007,"OFF",7.8675337750000532E-2,-33.398399859304,-1.7696810000000001,"ON",29393.749629110007,74052.734905032019,2125.63,"OFF",-10.55708033234,-119.67758078056001,-5.0878329999999998,null,0,0,0,1798.6154458247761,0,1798.6154458247761,0,0,1509.7879541167799,1833.7982711600382,0,3343.5862252768184,0,0,0,327.01455417522402,0,0,0,0,291.8317288399619,0,319.5398953746934,284.35707003943128,null,null,2113.0210219999999,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1798.6154458247761,0,0,0,11.131068558317111,0]
[0,0,0,1824.247530094947,0,1824.247530094947,2137.2345189999996,"2013-12-30T02:00:00",32,28,"OFF",-26.192193320300003,-73.754793005267999,3.0133890000000001,"OFF",-16.02507901008002,-106.23394112150001,-8.8484060000000007,"OFF",-0.8463278703750009,-62.621995725778007,-1.7696810000000001,"ON",29925.723295985008,73848.02717968401,2148.8209999999999,"OFF",-10.313999954160014,-119.67758078056001,-3.9817830000000001,null,0,0,0,1812.7247210588737,0,1812.7247210588737,0,0,1509.7879541167799,1849.5377760550498,0,3359.3257301718295,0,0,0,336.09627894112623,0,0,0,0,299.28322394495012,0,328.62162014059561,291.8085651444195,null,null,2137.2345189999996,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1812.7247210588737,0,0,0,11.52280903607334,0]
[0,0,0,1690.1451377299522,0,1690.1451377299522,2131.6563919999999,"2013-12-30T03:00:00",32,28,"OFF",-27.172881815669992,-71.667395019270003,2.788262,"OFF",-15.958809976499998,-105.08471602598001,-8.8484060000000007,"OFF",0.18007757020000206,-33.398399859304,-1.7696810000000001,"ON",24766.320374510004,73740.596129088008,2143.4679999999998,"OFF",-10.95733304230002,-120.37338813006001,-3.9817830000000001,null,0,0,0,1682.1246507192545,0,1682.1246507192545,0,0,1509.7879541167799,1707.880824876821,0,3217.6687789936009,0,0,0,461.34334928074531,0,0,0,0,435.58717512317889,0,453.8686904802147,428.11251632264828,null,null,2131.6563919999999,null,31434.163200000039,9.5537635568402326,6580.4775286685926,79.451436166799766,6120.7113408000041,71.976777366269161,-7.4746588005306052,null,null,null,null,null,null,null,null,null,1682.1246507192545,0,0,0,8.0204870106977069,0]
[0,0,0,1750.0492876951155,0,1750.0492876951155,2119.3629939999996,"2013-12-30T04:00:00",31,27,"OFF",-27.316575450430005,-72.363194347936002,2.8388640000000001,"OFF",-15.17579524827001,-109.93635809590002,-8.8484060000000007,"OFF",7.3534153874999619E-2,-33.398399859304,-1.7696810000000001,"ON",27140.57643356,74457.554417846011,2131.1239999999998,"OFF",-10.782339574719991,-119.67758078056001,-3.9817830000000001,null,0,0,0,1740.4990623127132,0,1740.4990623127132,0,0,1509.7879541167799,1770.0454085571937,0,3279.8333626739736,0,0,0,390.62493768728655,0,0,0,0,361.0785914428061,0,380.62762184201927,351.08127559753882,null,null,2119.3629939999996,null,32487.155900000012,9.5288097691634306,6818.7227338996781,83.537574043904385,6219.6926546000013,73.540258198637076,-9.997315845267309,null,null,null,null,null,null,null,null,null,1740.4990623127132,0,0,0,9.5502253824022318,0]
[0,0,0,1703.9504155122336,0,1703.9504155122336,2136.1469669999997,"2013-12-30T05:00:00",30,26,"OFF",-27.623410939079992,-72.363194347936002,3.009887,"OFF",-15.053721923925004,-105.25130874816,-8.8484060000000007,"OFF",-3.3982030997499933E-2,-62.621995725778007,-1.7696810000000001,"ON",25324.417706149994,74538.404424566004,2148.8429999999998,"OFF",-11.020627309509972,-118.28596608156001,-5.0878329999999998,null,0,0,0,1695.5828138702036,0,1695.5828138702036,0,0,1509.7879541167799,1721.3565016655202,0,3231.1444557823002,0,0,0,453.26018612979624,0,0,0,0,427.48649833447962,0,440.27901801097528,414.50533021565866,null,null,2136.1469669999997,null,33714.300000000047,9.5097922351801838,7090.4388163767808,88.375132939241695,6335.0442000000039,75.393964820420734,-12.98116811882096,null,null,null,null,null,null,null,null,null,1695.5828138702036,0,0,0,8.3676016420299675,0]
[0,0,0,1667.9888076941149,0,1667.9888076941149,2128.3962110000002,"2013-12-30T06:00:00",30,26,"OFF",-27.681865916320003,-71.667395019270003,2.8388640000000001,"OFF",-15.733867646034998,-104.86125559074002,-8.8484060000000007,"OFF",-0.30496940612500029,-33.398399859304,-1.1724140000000001,"ON",23855.950235310007,74129.550432250006,2140.6660000000002,"OFF",-11.73532070255999,-118.98177343106001,-5.0878329999999998,null,0,0,0,1660.5181781957085,0,1660.5181781957085,0,0,1509.7879541167799,1684.0261878976391,0,3193.8141420144193,0,0,0,480.14782180429165,0,0,0,0,456.63981210236102,0,467.16665368547069,443.65864398354006,null,null,2128.3962110000002,null,33714.300000000047,9.5097922351801838,7090.4388163767808,88.375132939241695,6335.0442000000039,75.393964820420734,-12.98116811882096,null,null,null,null,null,null,null,null,null,1660.5181781957085,0,0,0,7.4706294984064243,0]
[0,0,0,1704.3969053057788,0,1704.3969053057788,2123.256277,"2013-12-30T07:00:00",30,26,"OFF",-28.434501650070001,-72.363194347936002,2.876147,"OFF",-15.940442723290003,-110.65109461364001,-8.8484060000000007,"OFF",-9.5246579625001451E-2,-62.621995725778007,-1.7696810000000001,"ON",25342.354146549998,74283.325861698017,2134.98,"OFF",-11.976919758089998,-118.98177343106001,-3.9817830000000001,null,0,0,0,1696.0180211771644,0,1696.0180211771644,0,0,1509.7879541167799,1722.1755587638982,0,3231.9635128806781,0,0,0,438.96197882283559,0,0,0,0,412.80444123610187,0,425.98081070401463,399.82327311728091,null,null,2123.256277,null,33714.300000000047,9.5097922351801838,7090.4388163767808,88.375132939241695,6335.0442000000039,75.393964820420734,-12.98116811882096,null,null,null,null,null,null,null,null,null,1696.0180211771644,0,0,0,8.3788841286143452,0]
[0,0,0,1776.8476398052915,0,1776.8476398052915,2108.8403159999998,"2013-12-30T08:00:00",29,24,"OFF",-28.873382597100004,-72.363194347936002,2.9121860000000002,"OFF",-15.153877986079985,-110.63216544540002,-8.8484060000000007,"OFF",-0.3771684917500005,-45.922803816960005,-1.7696810000000001,"ON",28165.051696200004,74954.212479960013,2120.5279999999998,"OFF",-11.548825420370006,-120.37338813006001,-3.9817830000000001,null,0,0,0,1766.594310195544,0,1766.594310195544,0,0,1509.7879541167799,1797.4929206419977,0,3307.2808747587778,0,0,0,353.93368980445575,0,0,0,0,323.03507935800212,0,336.54483069802421,305.64622025157058,null,null,2108.8403159999998,null,35119.346100000024,9.4359919233422094,7443.6999067631295,94.947095426490151,6467.118533400002,77.558236320058612,-17.388859106431539,null,null,null,null,null,null,null,null,null,1766.594310195544,0,0,0,10.253329609747425,0]
[0,0,0,1843.4284212108669,0,1843.4284212108669,2089.0191549999995,"2013-12-30T09:00:00",30,25,"OFF",-28.90816756217999,-72.614551243828004,2.9996559999999999,"OFF",-14.173294779280008,-109.91742892766,-8.8484060000000007,"OFF",3.3883209512999772E-2,-62.621995725778007,-2.4333119999999999,"ON",30620.769687119995,74283.606590888012,2101.2829999999999,"OFF",-12.156452776160004,-118.28596608156001,-3.9817830000000001,null,0,0,0,1831.3830746749552,0,1831.3830746749552,0,0,1509.7879541167799,1869.0018235351422,0,3378.7897776519221,0,0,0,269.89992532504471,0,0,0,0,232.28117646485771,0,256.0873051100337,218.4685562498467,null,null,2089.0191549999995,null,33714.300000000047,9.4489453579005236,7136.0979925258198,89.206585035431729,6335.0442000000039,75.393964820420734,-13.812620215010995,null,null,null,null,null,null,null,null,null,1831.3830746749552,0,0,0,12.045346535911676,0]
[0,0,0,1886.0669095238209,0,1886.0669095238209,2091.3342789999997,"2013-12-30T10:00:00",32,27,"OFF",-28.915205420500005,-72.111837452044,3.258149,"OFF",-15.090727852690016,-108.56367256514001,-8.8484060000000007,"OFF",-0.43468182662499921,-33.398399859304,-1.7696810000000001,"ON",32132.49002646,74958.246959462005,2102.6759999999999,"OFF",-11.396929194629996,-119.67758078056001,-3.9817830000000001,null,0,0,0,1872.8429586527382,0,1872.8429586527382,0,0,1509.7879541167799,1912.6968737235652,0,3422.4848278403451,0,0,0,229.83304134726177,0,0,0,0,189.97912627643473,0,221.64555735778703,181.79164228695998,null,null,2091.3342789999997,null,31434.163200000039,9.4929166795605724,6622.6565050721856,80.164261355743918,6120.7113408000041,71.976777366269161,-8.1874839894747566,null,null,null,null,null,null,null,null,null,1872.8429586527382,0,0,0,13.223950871082707,0]
[0,0,0,1955.6497290701857,0,1955.6497290701857,2126.1562859999999,"2013-12-30T11:00:00",34,28,"OFF",-28.636632903340011,-73.058993676602014,2.701206,"OFF",-15.373834600319999,-110.63216544540002,-8.8484060000000007,"OFF",-1.2446466538749996,-33.398399859304,-1.7696810000000001,"ON",34508.791678760004,74791.39757059401,2139.1610000000001,"OFF",-11.547708227249997,-121.06919547956002,-5.0878329999999998,null,0,0,0,1940.4556616817285,0,1940.4556616817285,0,0,1509.7879541167799,1986.664840233565,0,3496.4527943503449,0,0,0,198.70533831827152,0,0,0,0,152.49615976643508,0,193.82463643230727,147.61545788047084,null,null,2126.1562859999999,null,29835.629600000044,9.4992747557896848,6281.6647306291698,74.531919088678961,5970.4491824000042,69.651217202714733,-4.8807018859642284,null,null,null,null,null,null,null,null,null,1940.4556616817285,0,0,0,15.194067388457142,0]
[0,0,0,1806.184133840587,0,1806.184133840587,2128.9566719999998,"2013-12-30T12:00:00",36,29,"OFF",-29.244475412639996,-73.754793005267999,2.7655419999999999,"OFF",-14.68059156273001,-105.06578685774001,-8.8484060000000007,"OFF",0.13692412575999843,-62.621995725778007,-1.7696810000000001,"ON",29262.182431589994,74540.778591430004,2140.7910000000002,"OFF",-12.448273529579996,-118.28596608156001,-3.9817830000000001,null,0,0,0,1795.1488560780472,0,1795.1488560780472,0,0,1509.7879541167799,1829.1455260822013,0,3338.9334801989812,0,0,0,345.64214392195299,0,0,0,0,311.64547391779888,0,342.84984332529024,308.85317332113613,null,null,2128.9566719999998,null,28888.694400000008,9.52784369801652,6064.0571603864519,71.093170232875778,5881.4372736000005,68.300869636213008,-2.7923005966627699,null,null,null,null,null,null,null,null,null,1795.1488560780472,0,0,0,11.035277762539863,0]
[0,0,0,1893.6133353920466,0,1893.6133353920466,2175.127696,"2013-12-30T13:00:00",38,31,"OFF",-28.713652804249993,-73.754793005267999,2.7776160000000001,"OFF",-14.30729948031999,-107.1531286979,-8.8484060000000007,"OFF",-0.44354714825000058,-45.922803816960005,-1.7696810000000001,"ON",32395.469744925009,75050.654987976013,2188.056,"OFF",-12.196231077869991,-120.37338813006001,-5.0878329999999998,null,0,0,0,1880.1784416440362,0,1880.1784416440362,0,0,1509.7879541167799,1920.469099713154,0,3430.2570538299342,0,0,0,307.87755835596386,0,0,0,0,267.586900286846,0,306.73021295827232,266.43955488915446,null,null,2175.127696,null,28563.352800000052,9.6384476176697333,5926.9612562164348,68.988953257844088,5850.8551632000053,67.841607860152536,-1.1473453976915522,null,null,null,null,null,null,null,null,null,1880.1784416440362,0,0,0,13.434893748010381,0]
[0,0,0,1905.3523466026736,0,1905.3523466026736,2274.4904369999999,"2013-12-30T14:00:00",41,33,"OFF",-28.973096436410014,-70.275796361938006,3.0973570000000001,"OFF",-14.550384055680015,-105.74258483066002,-8.8484060000000007,"OFF",-0.14659432573700087,-45.922803816960005,-1.7696810000000001,"ON",32801.927689655015,75259.525526169993,2287.0990000000002,"OFF",-12.68995749077,-119.67758078056001,-5.0878329999999998,null,0,0,0,1891.5879631289276,0,1891.5879631289276,0,0,1509.7879541167799,1932.4071786855543,0,3442.1951328023342,0,0,0,395.51103687107252,0,0,0,0,354.69182131444586,0,394.63982957706685,353.82061402044019,null,null,2274.4904369999999,null,29175.192900000024,9.7809970073459169,5965.6889534038901,69.578489201619448,5908.3681326000024,68.707281907613748,-0.87120729400569985,null,null,null,null,null,null,null,null,null,1891.5879631289276,0,0,0,13.764383473745966,0]
[0,0,0,1948.4996678426496,0,1948.4996678426496,2273.0212339999998,"2013-12-30T15:00:00",43,34,"OFF",-28.996916863529989,-71.667395019270003,2.5941040000000002,"OFF",-15.344320446875008,-107.86786521564001,-8.8484060000000007,"OFF",-0.21352894212500037,-62.621995725778007,-1.7696810000000001,"ON",34269.464144254991,74947.394771060004,2285.027,"OFF",-12.045434986449989,-117.59015873206,-3.9817830000000001,null,0,0,0,1933.5105596019102,0,1933.5105596019102,0,0,1509.7879541167799,1978.7177600950511,0,3488.5057142118312,0,0,0,351.5164403980898,0,0,0,0,306.30923990494898,0,349.69844470135473,304.49124420821391,null,null,2273.0212339999998,null,30272.564300000085,9.8792496994881276,6128.5148611171544,72.09912883575528,6011.521044200008,70.281133139020227,-1.8179956967350535,null,null,null,null,null,null,null,null,null,1933.5105596019102,0,0,0,14.98910824073937,0]
[0,0,0,1995.0298264217981,0,1995.0298264217981,2297.032753,"2013-12-30T16:00:00",42,33,"OFF",-29.485018233090006,-73.058993676602014,3.0836229999999998,"OFF",-16.827868982224988,-106.45732134840001,-8.8484060000000007,"OFF",-0.19496636197999798,-33.398399859304,-1.7696810000000001,"ON",35808.273239400005,74404.673059284003,2308.549,"OFF",-11.938966928069988,-119.67758078056001,-3.9817830000000001,null,0,0,0,1978.6971621501152,0,1978.6971621501152,0,0,1509.7879541167799,2029.4024873004282,0,3539.1904414172081,0,0,0,329.85183784988476,0,0,0,0,279.14651269957176,0,328.30833447069119,277.60300932037819,null,null,2297.032753,null,29657.431200000021,9.7974349394529767,6054.1215906570533,70.939056940108657,5953.6985328000019,69.395553560915062,-1.543503379193595,null,null,null,null,null,null,null,null,null,1978.6971621501152,0,0,0,16.332664271682916,0]
[0,0,0,2027.1174412576383,0,2027.1174412576383,2418.7702859999999,"2013-12-30T17:00:00",42,34,"OFF",-29.001870669169993,-74.450592333934011,3.0232060000000001,"OFF",-15.317975111870021,-102.959435641,-8.8484060000000007,"OFF",-8.3488039245999235E-2,-33.398399859304,-1.7696810000000001,"ON",36844.798156965,74975.644148407999,2431.453,"OFF",-12.108141455619993,-117.59015873206,-5.0878329999999998,null,0,0,0,2009.8452981206381,0,2009.8452981206381,0,0,1509.7879541167799,2061.8696406786203,0,3571.6575947954002,0,0,0,421.60770187936191,0,0,0,0,369.5833593213797,0,420.64154557468839,368.61720301670618,null,null,2418.7702859999999,null,29657.431200000021,9.8582818167326369,6016.7545930086799,70.361709865588551,5953.6985328000019,69.395553560915062,-0.96615630467348979,null,null,null,null,null,null,null,null,null,2009.8452981206381,0,0,0,17.272143137000285,0]
[0,0,0,1969.3073416298746,0,1969.3073416298746,2131.8309169999998,"2013-12-30T18:00:00",41,33,"OFF",-29.154827004929999,-73.754793005267999,2.9627870000000001,"OFF",-15.624516634510027,-108.74927466390001,-8.8484060000000007,"OFF",-0.2561818737800014,-45.922803816960005,-1.7696810000000001,"ON",34963.004270775011,75582.516490516005,2143.4679999999998,"OFF",-12.215165040049998,-121.06919547956002,-3.9817830000000001,null,0,0,0,1953.7202412584579,0,1953.7202412584579,0,0,1509.7879541167799,1999.1506913868182,0,3508.9386455035983,0,0,0,189.74775874154193,0,0,0,0,144.31730861318169,0,188.87655144753623,143.44610131917599,null,null,2131.8309169999998,null,29175.192900000024,9.7809970073459169,5965.6889534038901,69.578489201619448,5908.3681326000024,68.707281907613748,-0.87120729400569985,null,null,null,null,null,null,null,null,null,1953.7202412584579,0,0,0,15.587100371416682,0]
[0,0,0,1951.254030801289,0,1951.254030801289,2195.9401709999997,"2013-12-30T19:00:00",38,31,"OFF",-29.489941725150008,-73.058993676602014,2.789091,"OFF",-14.878560340184983,-104.18445761782,-8.8484060000000007,"OFF",-4.3237473500002413E-2,-33.398399859304,-1.7696810000000001,"ON",34361.784885224995,74923.596956581998,2208.857,"OFF",-12.534537680140017,-118.98177343106001,-5.0878329999999998,null,0,0,0,1936.186033636181,0,1936.186033636181,0,0,1509.7879541167799,1981.6893170762839,0,3491.4772711930636,0,0,0,272.67096636381893,0,0,0,0,227.16768292371603,0,271.5236209661274,226.02033752602449,null,null,2195.9401709999997,null,28563.352800000052,9.6384476176697333,5926.9612562164348,68.988953257844088,5850.8551632000053,67.841607860152536,-1.1473453976915522,null,null,null,null,null,null,null,null,null,1936.186033636181,0,0,0,15.067997165107954,0]
[0,0,0,1950.6230449048655,0,1950.6230449048655,2310.702131,"2013-12-30T20:00:00",38,31,"OFF",-29.030234068080002,-71.667395019270003,3.2440009999999999,"OFF",-15.803227984274974,-106.66185261540001,-8.8484060000000007,"OFF",-0.53508130124999698,-33.398399859304,-1.7696810000000001,"ON",34340.649533165,75156.000621732004,2322.058,"OFF",-13.030004659069979,-121.06919547956002,-3.9817830000000001,null,0,0,0,1935.5731273979188,0,1935.5731273979188,0,0,1509.7879541167799,1980.4591963792564,0,3490.2471504960363,0,0,0,386.48487260208117,0,0,0,0,341.59880362074364,0,385.33752720438963,340.4514582230521,null,null,2310.702131,null,28563.352800000052,9.6384476176697333,5926.9612562164348,68.988953257844088,5850.8551632000053,67.841607860152536,-1.1473453976915522,null,null,null,null,null,null,null,null,null,1935.5731273979188,0,0,0,15.049917506946713,0]
[0,0,0,1963.4184537547271,0,1963.4184537547271,2190.4970129999997,"2013-12-30T21:00:00",36,30,"OFF",-28.706644933050011,-73.754793005267999,2.9498829999999998,"OFF",-15.041237489849999,-106.43839218016001,-8.8484060000000007,"OFF",-5.2905455655499686E-2,-33.398399859304,-1.7696810000000001,"ON",34767.625489460006,75455.185750766002,2202.1469999999999,"OFF",-12.449929189950009,-116.89443159090001,-3.9817830000000001,null,0,0,0,1948.0010660918513,0,1948.0010660918513,0,0,1509.7879541167799,1993.2479429335281,0,3503.035897050308,0,0,0,254.14593390814866,0,0,0,0,208.89905706647187,0,251.94911085521701,206.70223401354022,null,null,2190.4970129999997,null,28888.694400000008,9.5886905752961802,6025.5765212462666,70.497692689144657,5881.4372736000005,68.300869636213008,-2.1968230529316486,null,null,null,null,null,null,null,null,null,1948.0010660918513,0,0,0,15.417387662875853,0]
[0,0,0,1934.889074974963,0,1934.889074974963,2289.0966660000004,"2013-12-30T22:00:00",37,31,"OFF",-28.614525228169978,-73.058993676602014,3.2435860000000001,"OFF",-14.774758828124986,-104.18445761782,-8.8484060000000007,"OFF",-9.8303183249998052E-2,-45.922803816960005,-1.7696810000000001,"ON",33810.909078240016,75387.417724300016,2301.5590000000002,"OFF",-13.34301945314999,-116.89443159090001,-5.0878329999999998,null,0,0,0,1920.2885678195375,0,1920.2885678195375,0,0,1509.7879541167799,1963.2925811515458,0,3473.0805352683255,0,0,0,381.27043218046265,0,0,0,0,338.26641884845435,0,379.99937677354347,336.99536344153518,null,null,2289.0966660000004,null,28650.199700000056,9.6414079454701351,5943.1568215015532,69.235024646349373,5859.0187718000052,67.963969239430199,-1.2710554069191744,null,null,null,null,null,null,null,null,null,1920.2885678195375,0,0,0,14.600507155425476,0]
[0,0,0,1877.7983339743591,0,1877.7983339743591,2274.3373279999996,"2013-12-30T23:00:00",32,29,"OFF",-29.087490971610016,-70.275796361938006,3.3052480000000002,"OFF",-13.276002501509986,-105.74258483066002,-8.8484060000000007,"OFF",3.6714529718499048E-2,-62.621995725778007,-1.7696810000000001,"ON",31842.800780860012,75402.593142228012,2286.7379999999998,"OFF",-13.46426982299001,-119.67758078056001,-5.0878329999999998,null,0,0,0,1864.80471817744,0,1864.80471817744,0,0,1509.7879541167799,1903.0389443251081,0,3412.8268984418883,0,0,0,421.93328182255982,0,0,0,0,383.69905567489172,0,415.15795755667307,376.92373140900497,null,null,2274.3373279999996,null,31434.163200000039,9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1864.80471817744,0,0,0,12.99361579691913,0]
[0,0,0,1892.0412687985593,0,1892.0412687985593,2239.5896240000002,"2013-12-31",34,31,"OFF",-28.972445284349984,-71.667395019270003,3.1475439999999999,"OFF",-13.835080453919989,-107.17213807448,-8.8484060000000007,"OFF",5.9221559256499287E-2,-33.398399859304,-1.7696810000000001,"ON",32340.795849599996,75809.217342692005,2252.1480000000001,"OFF",-13.36835371416999,-118.89482759050001,-5.0878329999999998,null,0,0,0,1878.6503750844497,0,1878.6503750844497,0,0,1509.7879541167799,1917.1928476034245,0,3426.9808017202045,0,0,0,373.49762491555043,0,0,0,0,334.95515239657561,0,370.50351819558455,331.96104567660973,null,null,2239.5896240000002,null,29835.629600000044,9.6818153876286672,6163.2304284842548,72.645323922680589,5970.4491824000042,69.651217202714733,-2.9941067199658562,null,null,null,null,null,null,null,null,null,1878.6503750844497,0,0,0,13.390893714109552,0]
[0,0,0,1858.5355218099264,0,1858.5355218099264,2233.3521310000001,"2013-12-31T01:00:00",32,29,"OFF",-28.920132876109996,-73.058993676602014,3.2440009999999999,"OFF",-14.623728938439982,-107.35765996490001,-8.8484060000000007,"OFF",-0.23620168012499912,-62.621995725778007,-1.7696810000000001,"ON",31161.522600329994,75002.77862983002,2244.7080000000001,"OFF",-13.579004656630008,-118.37299213046002,-3.9817830000000001,null,0,0,0,1846.0752181318946,0,1846.0752181318946,0,0,1509.7879541167799,1883.5356000867,0,3393.3235542034799,0,0,0,398.63278186810544,0,0,0,0,361.17239991330007,0,391.85745760221869,354.39707564741332,null,null,2233.3521310000001,null,31434.163200000039,9.6146104341198928,6538.8324187213884,78.752101632155899,6120.7113408000041,71.976777366269161,-6.7753242658867379,null,null,null,null,null,null,null,null,null,1846.0752181318946,0,0,0,12.460303678031778,0]
[0,0,0,1802.987044310431,0,1802.987044310431,2188.2849630000001,"2013-12-31T02:00:00",31,28,"OFF",-29.349761098229987,-73.058993676602014,2.9498829999999998,"OFF",-14.356864187199974,-108.34029233824,-8.8484060000000007,"OFF",-9.4274991620000539E-2,-45.922803816960005,-1.7696810000000001,"ON",29143.806143080004,75440.026374506007,2201.0410000000002,"OFF",-13.487476355149973,-115.50281689190001,-5.0878329999999998,null,0,0,0,1792.0375830496332,0,1792.0375830496332,0,0,1509.7879541167799,1824.1853181069896,0,3333.9732722237695,0,0,0,409.00341695036695,0,0,0,0,376.85568189301057,0,399.75893864013943,367.61120358278305,null,null,2188.2849630000001,null,32487.155900000012,9.589656646443089,6775.4575784629087,82.784736508864597,6219.6926546000013,73.540258198637076,-9.244478310227521,null,null,null,null,null,null,null,null,null,1792.0375830496332,0,0,0,10.949461260797761,0]
[0,0,0,1907.5287415990504,0,1907.5287415990504,2162.7468530000001,"2013-12-31T03:00:00",29,26,"OFF",-29.858238569429975,-70.275796361938006,3.2937729999999998,"OFF",-14.707718523494977,-105.27023791640001,-8.8484060000000007,"OFF",-0.22011059437500083,-45.922803816960005,-1.7696810000000001,"ON",32876.937849199996,75545.644716618001,2175.1590000000001,"OFF",-13.254452771279972,-119.67758078056001,-5.0878329999999998,null,0,0,0,1893.7030924411888,0,1893.7030924411888,0,0,1509.7879541167799,1934.0743628781524,0,3443.8623169949324,0,0,0,281.4559075588113,0,0,0,0,241.08463712184766,0,265.86161491291841,225.4903444759548,null,null,2162.7468530000001,null,35119.346100000024,9.5576856779015298,7348.9225914177096,93.152528965951475,6467.118533400002,77.558236320058612,-15.594292645892864,null,null,null,null,null,null,null,null,null,1893.7030924411888,0,0,0,13.825649157861562,0]
[0,0,0,1775.2749888054736,0,1775.2749888054736,2171.9099579999997,"2013-12-31T04:00:00",29,26,"OFF",-30.073921639720027,-71.918751915162005,2.8628279999999999,"OFF",-15.914596388099989,-108.52581422866001,-8.8484060000000007,"OFF",-3.4060341800006074E-3,-45.922803816960005,-1.7696810000000001,"ON",28105.531608770012,75468.829189400014,2183.6469999999999,"OFF",-13.257891450510007,-119.67758078056001,-3.9817830000000001,null,0,0,0,1765.0632219409194,0,1765.0632219409194,0,0,1509.7879541167799,1794.9961104842334,0,3304.7840646010136,0,0,0,418.58377805908049,0,0,0,0,388.65088951576649,0,402.98948541318759,373.0565968698736,null,null,2171.9099579999997,null,35119.346100000024,9.5576856779015298,7348.9225914177096,93.152528965951475,6467.118533400002,77.558236320058612,-15.594292645892864,null,null,null,null,null,null,null,null,null,1765.0632219409194,0,0,0,10.211766864554193,0]
[0,0,0,1817.9413658949416,0,1817.9413658949416,2135.813052,"2013-12-31T05:00:00",26,24,"OFF",-30.153156179929994,-72.807636780710013,2.985922,"OFF",-14.682808309030023,-107.66341415698001,-8.8484060000000007,"OFF",-0.10385688731999887,-33.398399859304,-1.7696810000000001,"ON",29695.081038000015,75255.771775858011,2147.4270000000001,"OFF",-13.660089561930015,-118.98177343106001,-3.9817830000000001,null,0,0,0,1806.5892712868201,0,1806.5892712868201,0,0,1509.7879541167799,1840.25380937194,0,3350.0417634887199,0,0,0,340.83772871318001,0,0,0,0,307.17319062806018,0,312.44611245649298,278.78157437137315,null,null,2135.813052,null,40439.402400000021,9.6173353053695951,8409.689610680769,114.54928556542984,6967.2038256000014,86.157669308742783,-28.391616256687058,null,null,null,null,null,null,null,null,null,1806.5892712868201,0,0,0,11.352094608121433,0]
[0,0,0,1915.6663579343349,0,1915.6663579343349,2113.382944,"2013-12-31T06:00:00",29,26,"OFF",-30.851790783029983,-72.363194347936002,2.8388640000000001,"OFF",-15.425068758949976,-102.97836480924001,-8.8484060000000007,"OFF",-0.16553675187500322,-33.398399859304,-1.7696810000000001,"ON",33156.456328480002,75105.902492568013,2126.25,"OFF",-12.385300646649988,-120.37338813006001,-5.0878329999999998,null,0,0,0,1901.6111448729464,0,1901.6111448729464,0,0,1509.7879541167799,1943.6397826119571,0,3453.4277367287368,0,0,0,224.6388551270536,0,0,0,0,182.61021738804288,0,209.04456248116074,167.01592474215002,null,null,2113.382944,null,35119.346100000024,9.5576856779015298,7348.9225914177096,93.152528965951475,6467.118533400002,77.558236320058612,-15.594292645892864,null,null,null,null,null,null,null,null,null,1901.6111448729464,0,0,0,14.055213061388486,0]
[0,0,0,1932.2567656752724,0,1932.2567656752724,2120.7510899999997,"2013-12-31T07:00:00",28,25,"OFF",-30.59728610733,-73.746972692118007,2.8259599999999998,"OFF",-15.690147616395018,-105.96604526590001,-8.8484060000000007,"OFF",-4.6009504875999932E-2,-62.621995725778007,-1.7696810000000001,"ON",33721.766529164997,75558.590342694006,2132.5250000000001,"OFF",-13.09930555324998,-119.67758078056001,-3.9817830000000001,null,0,0,0,1917.7311768379786,0,1917.7311768379786,0,0,1509.7879541167799,1960.1190440974615,0,3469.9069982142414,0,0,0,214.79382316202145,0,0,0,0,172.40595590253861,0,195.20275230933981,152.81488504985697,null,null,2120.7510899999997,null,36706.044800000032,9.5509241884995237,7686.385961308034,99.647077307127333,6616.268211200003,80.056006454445679,-19.591070852681653,null,null,null,null,null,null,null,null,null,1917.7311768379786,0,0,0,14.525588837293753,0]
[0,0,0,1858.1864695791319,0,1858.1864695791319,2135.283019,"2013-12-31T08:00:00",26,24,"OFF",-30.742632701060003,-73.762621339252007,3.3918889999999999,"OFF",-15.530475160080012,-103.67417215874002,-8.8484060000000007,"OFF",-0.11597585176000315,-62.621995725778007,-1.7696810000000001,"ON",31149.093259499998,75345.115845784007,2146.491,"OFF",-12.729608433989979,-120.37338813006001,-3.9817830000000001,null,0,0,0,1845.7357866789509,0,1845.7357866789509,0,0,1509.7879541167799,1882.4845643390988,0,3392.2725184558785,0,0,0,300.75521332104904,0,0,0,0,264.00643566090116,0,272.36359706436201,235.6148194042141,null,null,2135.283019,null,40439.402400000021,9.6173353053695951,8409.689610680769,114.54928556542984,6967.2038256000014,86.157669308742783,-28.391616256687058,null,null,null,null,null,null,null,null,null,1845.7357866789509,0,0,0,12.450682900180936,0]
[0,0,0,1730.5817743470488,0,1730.5817743470488,2141.778335,"2013-12-31T09:00:00",33,30,"OFF",-31.450129414019997,-72.363194347936002,3.0232049999999999,"OFF",-13.93493119186501,-103.46972110008001,-8.8484060000000007,"OFF",-0.27106569924999813,-33.398399859304,-1.7696810000000001,"ON",26382.228978550007,75838.020157586012,2153.355,"OFF",-13.330400884149977,-119.67758078056001,-3.9817830000000001,null,0,0,0,1721.5352545056355,0,1721.5352545056355,0,0,1509.7879541167799,1747.5216678972765,0,3257.3096220140565,0,0,0,431.8197454943645,0,0,0,0,405.83333210272349,0,427.11261871919851,401.1262053275575,null,null,2141.778335,null,30551.57130000004,9.645372629758878,6334.9696217519358,75.392755338905431,6037.7477022000039,70.685628563739428,-4.7071267751660031,null,null,null,null,null,null,null,null,null,1721.5352545056355,0,0,0,9.0465198414133283,0]
[0,0,0,1852.2005782656715,0,1852.2005782656715,2144.838546,"2013-12-31T10:00:00",39,33,"OFF",-31.426008646950013,-72.363194347936002,3.2444160000000002,"OFF",-15.039963851249992,-107.1531286979,-8.8484060000000007,"OFF",-0.77909430175000405,-33.398399859304,-1.7696810000000001,"ON",30935.468126399999,75569.578885274008,2156.194,"OFF",-13.909420011300007,-116.98137743146002,-3.9817830000000001,null,0,0,0,1839.9146394267027,0,1839.9146394267027,0,0,1509.7879541167799,1875.738303795107,0,3385.5262579118871,0,0,0,316.27936057329725,0,0,0,0,280.455696204893,0,316.1634317600014,280.33976739159715,null,null,2144.838546,null,28624.403100000054,9.7622223780025799,5864.3210514237044,68.043534584539174,5856.5938914000053,67.927605771243336,-0.11592881329583804,null,null,null,null,null,null,null,null,null,1839.9146394267027,0,0,0,12.285938838968832,0]
[0,0,0,1917.6540387368007,0,1917.6540387368007,2232.4229409999998,"2013-12-31T11:00:00",43,35,"OFF",-31.201439423419991,-72.363194347936002,3.1338110000000001,"OFF",-15.854109030240028,-104.36997950824001,-8.8484060000000007,"OFF",-0.58041506612499905,-33.398399859304,-1.7696810000000001,"ON",33224.5056864,75734.767961503996,2243.8890000000001,"OFF",-13.490314880139994,-117.5032128915,-3.9817830000000001,null,0,0,0,1903.5426362232702,0,1903.5426362232702,0,0,1509.7879541167799,1944.3270844120448,0,3454.1150385288247,0,0,0,340.34636377672996,0,0,0,0,299.56191558795535,0,339.11513668528391,298.33068849650931,null,null,2232.4229409999998,null,30272.564300000085,9.9400965767677878,6091.0000353022297,71.512360230466271,6011.521044200008,70.281133139020227,-1.2312270914460441,null,null,null,null,null,null,null,null,null,1903.5426362232702,0,0,0,14.111402513530493,0]
[0,0,0,2004.5167681169555,0,2004.5167681169555,2393.4917970000006,"2013-12-31T12:00:00",47,37,"OFF",-33.484168872350025,-73.058993676602014,2.8517679999999999,"OFF",-16.473688817300022,-102.97836480924001,-8.8484060000000007,"OFF",-0.16172067528000242,-33.398399859304,-1.7696810000000001,"ON",36116.758643699999,75538.690653540005,2407.4520000000002,"OFF",-14.060589560149994,-119.67758078056001,-6.1938839999999997,null,0,0,0,1987.9074100820242,0,1987.9074100820242,0,0,1509.7879541167799,2036.436854894444,0,3546.2248090112239,0,0,0,419.54458991797605,0,0,0,0,371.01514510555626,0,414.35619742390804,365.82675261148825,null,null,2393.4917970000006,null,33987.03270000004,10.188404454205815,6671.7085786617072,80.998970058992924,6360.681073800004,75.810577564924898,-5.1883924940680259,null,null,null,null,null,null,null,null,null,1987.9074100820242,0,0,0,16.609358034931347,0]
[0,0,0,1994.0005418181374,0,1994.0005418181374,2471.3237199999999,"2013-12-31T13:00:00",50,39,"OFF",-31.721494692060023,-73.746972692118007,3.1346400000000001,"OFF",-13.914132924120002,-100.19513541124002,-8.8484060000000007,"OFF",-0.12960774709999703,-33.398399859304,-1.7696810000000001,"ON",35774.699805860015,75789.590361894006,2483.895,"OFF",-14.193551823709999,-117.59015873206,-5.0878329999999998,null,0,0,0,1977.6978424948118,0,1977.6978424948118,0,0,1509.7879541167799,2024.6830459616558,0,3534.4710000784357,0,0,0,506.19715750518822,0,0,0,0,459.21195403834417,0,496.58870201026326,449.60349854341922,null,null,2471.3237199999999,null,37984.500000000058,10.446358841895256,7272.2946961505359,91.718425789003788,6736.4430000000057,82.109970294078821,-9.6084554949249679,null,null,null,null,null,null,null,null,null,1977.6978424948118,0,0,0,16.302699323325669,0]
[0,0,0,2079.8809495202959,0,2079.8809495202959,2280.8090219999999,"2013-12-31T14:00:00",52,41,"OFF",-32.968541008979997,-73.762621339252007,3.0969419999999999,"OFF",-15.580743303799968,-104.36997950824001,-8.8484060000000007,"OFF",-6.5582300000013578E-4,-75.14639166260001,-1.7696810000000001,"ON",38508.542481239994,75800.578904473994,2293.4180000000001,"OFF",-13.685985788230001,-119.06879947996001,-5.0878329999999998,null,0,0,0,2061.0424081415094,0,2061.0424081415094,0,0,1509.7879541167799,2115.3139314504851,0,3625.1018855672651,0,0,0,232.37559185849068,0,0,0,0,178.10406854951498,0,219.60871008414966,165.33718677517396,null,null,2280.8090219999999,null,41170.179200000071,10.676642018747401,7712.1962369269759,100.15580261999438,7035.8968448000069,87.388920845653359,-12.766881774341016,null,null,null,null,null,null,null,null,null,2061.0424081415094,0,0,0,18.838541378786431,0]
[0,0,0,2130.8834565304905,0,2130.8834565304905,2172.510088,"2013-12-31T15:00:00",54,42,"OFF",-31.610102038690012,-71.659566685286009,2.9619580000000001,"OFF",-14.815644810690008,-108.52581422866001,-8.8484060000000007,"OFF",-6.278276660599974E-2,-33.398399859304,-1.7696810000000001,"ON",40072.003969849997,74617.31338945801,2184.1480000000001,"OFF",-13.958787673809988,-118.89482759050001,-3.9817830000000001,null,0,0,0,2110.506855313442,0,2110.506855313442,0,0,1509.7879541167799,2173.0804330974765,0,3682.8683872142565,0,0,0,73.641144686558164,0,0,0,0,11.067566902523595,0,56.288632880397913,-6.2849449036366565,null,null,2172.510088,null,44737.413600000087,10.859084291658576,8239.6291249650221,110.92510478972397,7371.2168784000078,93.572592983563723,-17.352511806160251,null,null,null,null,null,null,null,null,null,2110.506855313442,0,0,0,20.376601217048574,0]
[0,0,0,2151.9994398803769,0,2151.9994398803769,2291.7848489999997,"2013-12-31T16:00:00",53,41,"OFF",-31.331661271679987,-72.37102268192001,3.070719,"OFF",-14.715219929369994,-104.38890867648001,-8.8484060000000007,"OFF",4.9716649160999479E-2,-45.922803816960005,-1.7696810000000001,"ON",40707.222188400003,76248.678837551997,2303.3139999999999,"OFF",-14.12791974853001,-119.67758078056001,-3.9817830000000001,null,0,0,0,2130.9795344481663,0,2130.9795344481663,0,0,1509.7879541167799,2190.0677840674898,0,3699.8557381842697,0,0,0,172.33446555183355,0,0,0,0,113.24621593251004,0,156.89135565054912,97.80310603122561,null,null,2291.7848489999997,null,42907.977300000086,10.735877892761508,7993.3802766013387,105.8084841553399,7199.249866200008,90.365374254055467,-15.44310990128443,null,null,null,null,null,null,null,null,null,2130.9795344481663,0,0,0,21.019905432210635,0]
[0,0,0,2130.0591907236221,0,2130.0591907236221,2272.6398089999998,"2013-12-31T17:00:00",51,41,"OFF",-30.43046389565,-74.450592333934011,3.1706789999999998,"OFF",-14.181587222399962,-104.35105034,-8.8484060000000007,"OFF",5.5396546800003207E-2,-33.398399859304,-1.7696810000000001,"ON",40047.068171524996,76031.025486127997,2284.069,"OFF",-14.46781576275,-118.98177343106001,-3.9817830000000001,null,0,0,0,2109.7076252304382,0,2109.7076252304382,0,0,1509.7879541167799,2167.6069198609307,0,3677.3948739777106,0,0,0,174.36137476956173,0,0,0,0,116.46208013906926,0,164.0555149791042,106.15622034861171,null,null,2272.6398089999998,null,39527.769900000014,10.620657638067961,7443.5635244129089,94.944496565722019,6881.5103706000009,84.638636775264473,-10.305859790457546,null,null,null,null,null,null,null,null,null,2109.7076252304382,0,0,0,20.351565493183898,0]
[0,0,0,2124.7701596259371,0,2124.7701596259371,2242.8337329999999,"2013-12-31T18:00:00",46,38,"OFF",-29.958877408739998,-73.754793005267999,3.2946029999999999,"OFF",-16.073420619050022,-105.28916708464001,-8.8484060000000007,"OFF",0.11256205896000009,-45.922803816960005,-1.7696810000000001,"ON",39886.810133759995,76194.546228886,2254.1390000000001,"OFF",-14.469707482859997,-119.67758078056001,-3.9817830000000001,null,0,0,0,2104.5791027760006,0,2104.5791027760006,0,0,1509.7879541167799,2161.5046762566803,0,3671.2926303734603,0,0,0,149.55989722399954,0,0,0,0,92.634323743319783,0,146.58613483641474,89.660561355734984,null,null,2242.8337329999999,null,32877.826400000049,10.211442103450036,6439.4090603308532,77.100465979226982,6256.415681600005,74.126703591642183,-2.9737623875847987,null,null,null,null,null,null,null,null,null,2104.5791027760006,0,0,0,20.191056849936558,0]
[0,0,0,2108.642554627063,0,2108.642554627063,2249.3620899999996,"2013-12-31T19:00:00",43,37,"OFF",-30.159734860799986,-74.450592333934011,2.8259599999999998,"OFF",-15.689107304779991,-102.26362829150001,-8.8484060000000007,"OFF",4.0034341461500679E-2,-33.398399859304,-1.7696810000000001,"ON",39395.403777989988,75970.355897752015,2261.136,"OFF",-12.798679188400003,-119.67758078056001,-3.9817830000000001,null,0,0,0,2088.9394519406792,0,2088.9394519406792,0,0,1509.7879541167799,2145.1788683110299,0,3654.9668224278098,0,0,0,172.19654805932078,0,0,0,0,115.95713168897009,0,172.10708380996951,115.86766743961883,null,null,2249.3620899999996,null,30272.564300000085,10.061790331327108,6017.3315688654902,70.370597388371493,6011.521044200008,70.281133139020227,-8.946424935126629E-2,null,null,null,null,null,null,null,null,null,2088.9394519406792,0,0,0,19.703102686383772,0]
[0,0,0,2036.4473799861494,0,2036.4473799861494,2124.723285,"2013-12-31T20:00:00",42,36,"OFF",-29.605365406259995,-73.058993676602014,3.0232049999999999,"OFF",-14.308620455819986,-104.18445761782,-8.8484060000000007,"OFF",7.1026503169499378E-2,-75.14639166260001,-1.7696810000000001,"ON",37142.589662999984,75974.262043909999,2137.4059999999999,"OFF",-13.706901948999995,-116.89443159090001,-5.0878329999999998,null,0,0,0,2018.9001706664956,0,2018.9001706664956,0,0,1509.7879541167799,2068.9672629952115,0,3578.7552171119914,0,0,0,118.50582933350438,0,0,0,0,68.438737004788436,0,118.66284800896966,68.595755680253717,null,null,2124.723285,null,29657.431200000021,9.9799755712919591,5943.3875339958804,69.238534885449781,5953.6985328000019,69.395553560915062,0.15701867546528092,null,null,null,null,null,null,null,null,null,2018.9001706664956,0,0,0,17.547209319653803,0]
[0,0,0,2015.5110522841157,0,2015.5110522841157,2095.9051360000003,"2013-12-31T21:00:00",43,37,"OFF",-30.457367005699975,-73.754793005267999,3.3310559999999998,"OFF",-14.954070054365017,-103.67417215874002,-8.8484060000000007,"OFF",3.4852308000003648E-2,-33.398399859304,-1.7696810000000001,"ON",36472.113358959992,75516.689505878006,2108.2800000000002,"OFF",-13.63245276959999,-116.19862424140001,-5.0878329999999998,null,0,0,0,1998.5799074895931,0,1998.5799074895931,0,0,1509.7879541167799,2048.1099774889558,0,3557.8979316057357,0,0,0,109.7000925104071,0,0,0,0,60.170022511044408,0,109.61062826105584,60.080558261693142,null,null,2095.9051360000003,null,30272.564300000085,10.061790331327108,6017.3315688654902,70.370597388371493,6011.521044200008,70.281133139020227,-8.946424935126629E-2,null,null,null,null,null,null,null,null,null,1998.5799074895931,0,0,0,16.931144794522652,0]
[0,0,0,1994.2173376035162,0,1994.2173376035162,2227.2341479999995,"2013-12-31T22:00:00",43,36,"OFF",-30.286827634590001,-70.971595690604005,2.9730180000000002,"OFF",-15.151632021060008,-108.05346731440001,-8.8484060000000007,"OFF",2.3557224856999386E-2,-33.398399859304,-1.7696810000000001,"ON",35781.773006825002,75653.075767214003,2238.8609999999999,"OFF",-14.919147850724963,-120.28644228950002,-3.9817830000000001,null,0,0,0,1977.9083277319912,0,1977.9083277319912,0,0,1509.7879541167799,2025.263404968533,0,3535.0513590853129,0,0,0,260.95267226800866,0,0,0,0,213.59759503146688,0,260.29753649455449,212.94245925801275,null,null,2227.2341479999995,null,30272.564300000085,10.000943454047448,6053.941698420178,70.936268912474361,6011.521044200008,70.281133139020227,-0.6551357734541341,null,null,null,null,null,null,null,null,null,1977.9083277319912,0,0,0,16.30900987152495,0]
[0,0,0,1979.3080937186558,0,1979.3080937186558,2349.0728439999998,"2013-12-31T23:00:00",41,35,"OFF",-29.932063541190015,-75.14639166260001,3.1467139999999998,"OFF",-14.988753173299983,-105.53813377200001,-8.8484060000000007,"OFF",0.11430057999999989,-45.922803816960005,-1.7696810000000001,"ON",35293.199406399995,75780.967965343996,2360.5259999999998,"OFF",-13.876260933830007,-119.06879947996001,-3.9817830000000001,null,0,0,0,1963.4319402724975,0,1963.4319402724975,0,0,1509.7879541167799,2009.2078396489117,0,3518.9957937656918,0,0,0,397.09405972750233,0,0,0,0,351.31816035108818,0,397.33560730601971,351.55970792960557,null,null,2349.0728439999998,null,29175.192900000024,9.9026907619052373,5892.3768501858849,68.465734329096364,5908.3681326000024,68.707281907613748,{"$f":"BM8057-BK8057","v":0.24154757851738395},null,null,null,null,null,null,null,null,null,1963.4319402724975,0,0,0,15.876153446158241,0]
[null,null,null,null,null,{"$f":"SUM(F3:F8057)","v":38204600.618092723},{"$f":"SUM(G3:G8057)","v":41694750.881634541},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(AK3:AK8057)","v":37890531.833135024},null,null,null,null,null,{"$f":"SUM(AQ3:AQ8057)","v":41090076.72506021},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"SUM(BX3:BX8057)","v":37890531.833135024},{"$f":"SUM(BY3:BY8057)","v":233040.49316662533},4097.424434407656,28277.260023709234,20844.774879492779,27808.832453365601]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0,null,null,null,null,null,0]

{"sheet":"dataregression1","index":3,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
["SUMMARY OUTPUT"]
[]
["Regression Statistics"]
["Multiple R",0.99553548938717273]
["R Square",0.99109091062935761]
["Adjusted R Square",0.99077821687244794]
["Standard Error",7.5936333380277185E-3]
["Observations",3258]
[]
["ANOVA"]
[null,"df","SS","MS","F","Significance F"]
["Regression",3,20.879996281514039,6.9599987605046794,120700.73531603883,0]
["Residual",3255,0.18769393497168149,5.7663267272405989E-5]
["Total",3258,21.067690216485719]
[]
[null,"Coefficients","Standard Error","t Stat","P-value","Lower 95%","Upper 95%","Lower 95.0%","Upper 95.0%"]
["Intercept",0,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"}]
["X Variable 1",5.9952418215565562,7.5231754962521616E-2,79.690309292176153,0,5.8477354417566882,6.1427482013564241,5.8477354417566882,6.1427482013564241]
["X Variable 2",-275.37735246486966,646.66972687632938,-0.42583925150640839,0.67025313802109598,-1543.2981976613733,992.54349273163382,-1543.2981976613733,992.54349273163382]
["X Variable 3",1.9290969856861098E-4,4.0249047639893097E-6,47.929009474849614,0,1.8501809573319834E-4,2.0080130140402361E-4,1.8501809573319834E-4,2.0080130140402361E-4]

{"sheet":"dataregression2","index":4,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
["SUMMARY OUTPUT"]
[]
["Regression Statistics"]
["Multiple R",0.99665897725499752]
["R Square",0.99332911694297765]
["Adjusted R Square",0.99275531073340006]
["Standard Error",8.6483745591399725E-3]
["Observations",1769]
[]
["ANOVA"]
[null,"df","SS","MS","F","Significance F"]
["Regression",3,19.668422047517545,6.5561406825058484,87655.522541084953,0]
["Residual",1766,0.13208687952180703,7.4794382515179514E-5]
["Total",1769,19.800508927039353]
[]
[null,"Coefficients","Standard Error","t Stat","P-value","Lower 95%","Upper 95%","Lower 95.0%","Upper 95.0%"]
["Intercept",0,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"}]
["X Variable 1",6.2472609034885238,8.697513708016566E-2,71.828123682407934,0,6.0766758546368278,6.4178459523402198,6.0766758546368278,6.4178459523402198]
["X Variable 2",1055.0913103380276,786.47975741185235,1.3415365117725626,0.17991880374208655,-487.43788068023991,2597.6205013562949,-487.43788068023991,2597.6205013562949]
["X Variable 3",3.4759297217464561E-4,7.2968185731281388E-6,47.636236078928967,0,3.3328166213196351E-4,3.6190428221732771E-4,3.3328166213196351E-4,3.6190428221732771E-4]

{"sheet":"dataregression3","index":5,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
["SUMMARY OUTPUT"]
[]
["Regression Statistics"]
["Multiple R",0.99717433132758004]
["R Square",0.99435664705860649]
["Adjusted R Square",0.99373162437264684]
["Standard Error",5.5269917586988435E-3]
["Observations",1621]
[]
["ANOVA"]
[null,"df","SS","MS","F","Significance F"]
["Regression",3,8.7088562119735951,2.9029520706578649,95030.32869814703,0]
["Residual",1618,4.9426078123372949E-2,3.0547637900724936E-5]
["Total",1621,8.7582822900969681]
[]
[null,"Coefficients","Standard Error","t Stat","P-value","Lower 95%","Upper 95%","Lower 95.0%","Upper 95.0%"]
["Intercept",0,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"}]
["X Variable 1",6.0586910101321516,5.2543473370295191E-2,115.30815573295081,0,5.9556306000929187,6.1617514201713846,5.9556306000929187,6.1617514201713846]
["X Variable 2",-8362.7438511773817,559.63266667995913,-14.943273238121819,2.1437103696501571E-47,-9460.4248455973775,-7265.0628567573858,-9460.4248455973775,-7265.0628567573858]
["X Variable 3",2.1385843246112644E-4,4.0663972721182322E-6,52.591623038770429,0,2.0588247382410474E-4,2.2183439109814813E-4,2.0588247382410474E-4,2.2183439109814813E-4]

{"sheet":"dataregression4","index":6,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
["SUMMARY OUTPUT"]
[]
["Regression Statistics"]
["Multiple R",0.98922600751210699]
["R Square",0.9785680939383431]
["Adjusted R Square",0.97819350205180455]
["Standard Error",1.6784872409213853E-2]
["Observations",2787]
[]
["ANOVA"]
[null,"df","SS","MS","F","Significance F"]
["Regression",3,35.812577078043958,11.937525692681319,42371.928495872766,0]
["Residual",2784,0.78434172595335039,2.817319417935885E-4]
["Total",2787,36.596918803997312]
[]
[null,"Coefficients","Standard Error","t Stat","P-value","Lower 95%","Upper 95%","Lower 95.0%","Upper 95.0%"]
["Intercept",0,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"}]
["X Variable 1",8.5187560366382602,0.11850458949529814,71.885452478414393,0,8.2863902872381558,8.7511217860383645,8.2863902872381558,8.7511217860383645]
["X Variable 2",-5130.80147033297,1095.5483794711772,-4.6833180227144471,2.9580193253891379E-6,-7278.9707630504463,-2982.6321776154937,-7278.9707630504463,-2982.6321776154937]
["X Variable 3",2.4212896608681209E-4,7.5195238413826193E-6,32.200039682604647,1.1923824508777509E-193,2.2738455998426072E-4,2.5687337218936349E-4,2.2738455998426072E-4,2.5687337218936349E-4]

{"sheet":"dataregression6","index":7,"n_rows":20,"n_cols":9,"rows_kept":20,"cut":false,"hidden":false,"merged":[]}
["SUMMARY OUTPUT"]
[]
["Regression Statistics"]
["Multiple R",0.9877400586063243]
["R Square",0.97563042337562489]
["Adjusted R Square",0.97535261167940002]
["Standard Error",1.1808483278083193E-2]
["Observations",3778]
[]
["ANOVA"]
[null,"df","SS","MS","F","Significance F"]
["Regression",3,21.07378496385256,7.0245949879508531,50377.087040556849,0]
["Residual",3775,0.52638704691610827,1.3944027732877042E-4]
["Total",3778,21.60017201076867]
[]
[null,"Coefficients","Standard Error","t Stat","P-value","Lower 95%","Upper 95%","Lower 95.0%","Upper 95.0%"]
["Intercept",0,{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"},{"$error":"#N/A"}]
["X Variable 1",7.0171618302994743,0.10498793351365668,66.837793596410691,0,6.8113232648820645,7.223000395716884,6.8113232648820645,7.223000395716884]
["X Variable 2",-2120.8171746670459,939.09519414632587,-2.258362291583178,2.3979934659025925E-2,-3962.0002619436309,-279.63408739046099,-3962.0002619436309,-279.63408739046099]
["X Variable 3",8.8516238487205262E-5,5.2903701104694396E-6,16.731577685280474,1.1255350522586283E-60,7.814397800334194E-5,9.8888498971068584E-5,7.814397800334194E-5,9.8888498971068584E-5]